## Data
| Case | Over Design % | Total Area (m2) | Duty (MegaWatts) | EMTD (C) | U (W/m2-K) | Shell h (W/m2-K) | Tube h (W/m2-K) | Shell Velocity (m/s) | Tube Velocity (m/s) | Shell DP (kPa) | Tube DP (kPa) | Shells In Series | Shells In Parallel | Shell ID (mm) | Baffle Spacing (mm) | Tube Passes | Tube Length (m) | Tube Dia. (mm) | Tube Pitch Ratio | Cross Passes | Shell Type | Baffle Type | UA | Cost of Construction | Tube Count Approx | Shell Cost | Tube Cost | Operational Cost / year | As | Operational Cost 10 years with I = 0.1 | Op Cost
C | Xist Rating 1 | -96.76 | 62.906 | 150.275 | 35.8 | 2421.44 | 7615.74 | 58746.1 | 2.44 | 10.95 | 11.167 | 280.118 | 1 | 1 | 1000 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 152323.1046 | 13282.5483 | 973.9444 | 2799.3852 | 10483.1631 | 292123.4589 | 0.038101 | -2255699.9159 | 2255699.9159
C | Xist Rating 2 | -96.71 | 63.608 | 150.275 | 35.8 | 2432.89 | 7739.5 | 58285.2 | 2.4 | 10.85 | 11.169 | 274.936 | 1 | 1 | 1010 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 154751.2671 | 13521.2538 | 993.5206 | 2827.3791 | 10693.8747 | 286734.1685 | 0.038482 | -2214085.244 | 2214085.244
C | Xist Rating 3 | -96.47 | 68.672 | 150.275 | 35.8 | 2422.75 | 7707.9 | 54968.4 | 2.42 | 10.07 | 11.219 | 238.249 | 1 | 1 | 1020 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 166375.088 | 13762.0558 | 1013.2917 | 2855.373 | 10906.6829 | 248662.5379 | 0.038863 | -1920106.2047 | 1920106.2047
C | Xist Rating 4 | -96.41 | 70.221 | 150.274 | 35.8 | 2409.68 | 7594.63 | 54179.9 | 2.33 | 9.89 | 11.083 | 230.483 | 1 | 1 | 1030 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 169210.1393 | 14004.9545 | 1033.2576 | 2883.3668 | 11121.5877 | 240548.4812 | 0.039244 | -1857451.6097 | 1857451.6097
C | Xist Rating 5 | -96.35 | 70.998 | 150.274 | 35.8 | 2426.45 | 7772.96 | 53795.3 | 2.26 | 9.8 | 11.048 | 226.779 | 1 | 1 | 1040 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 172273.0971 | 14249.9499 | 1053.4182 | 2911.3607 | 11338.5892 | 236673.6045 | 0.039625 | -1827530.8383 | 1827530.8383
C | Xist Rating 6 | -96.27 | 72.426 | 150.274 | 35.8 | 2433.21 | 7861.44 | 53044.2 | 2.21 | 9.63 | 11.018 | 219.367 | 1 | 1 | 1050 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 176227.6675 | 14497.0418 | 1073.7737 | 2939.3545 | 11557.6873 | 228958.3265 | 0.040006 | -1767955.5074 | 1767955.5074
C | Xist Rating 7 | -96.23 | 73.183 | 150.274 | 35.8 | 2439.04 | 7932.12 | 52677.2 | 2.17 | 9.54 | 10.994 | 215.899 | 1 | 1 | 1060 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 178496.2643 | 14746.2304 | 1094.3239 | 2967.3484 | 11778.8821 | 225344.3138 | 0.040387 | -1740049.0587 | 1740049.0587
C | Xist Rating 8 | -95.97 | 78.753 | 150.274 | 35.8 | 2420.72 | 7816.23 | 49858.2 | 2.15 | 8.9 | 10.987 | 189.001 | 1 | 1 | 1070 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 190638.9622 | 14997.5156 | 1115.0689 | 2995.3422 | 12002.1734 | 197410.2093 | 0.040768 | -1524349.3086 | 1524349.3086
C | Xist Rating 9 | -95.92 | 79.892 | 150.274 | 35.8 | 2422.1 | 7844.36 | 49381.2 | 2.11 | 8.79 | 10.944 | 184.871 | 1 | 1 | 1080 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 193506.4132 | 15250.8975 | 1136.0087 | 3023.3361 | 12227.5614 | 193106.1315 | 0.041149 | -1491114.361 | 1491114.361
C | Xist Rating 10 | -95.85 | 81.4 | 150.274 | 35.8 | 2417.65 | 7815.98 | 48760.8 | 2.06 | 8.65 | 10.889 | 179.548 | 1 | 1 | 1090 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 196796.71 | 15506.376 | 1157.1433 | 3051.3299 | 12455.0461 | 187556.284 | 0.04153 | -1448259.9094 | 1448259.9094
C | Xist Rating 11 | -95.8 | 82.507 | 150.274 | 35.8 | 2418.82 | 7841.75 | 48307.1 | 2.03 | 8.55 | 10.869 | 175.692 | 1 | 1 | 1100 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 199569.5817 | 15763.9511 | 1178.4727 | 3079.3238 | 12684.6273 | 183543.7799 | 0.041911 | -1417276.4159 | 1417276.4159
C | Xist Rating 12 | -95.77 | 83.452 | 150.274 | 35.8 | 2409.09 | 7749.2 | 48011.2 | 1.96 | 8.49 | 10.779 | 173.457 | 1 | 1 | 1110 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 201043.3787 | 16023.6229 | 1199.9969 | 3107.3176 | 12916.3053 | 181185.9938 | 0.042292 | -1399070.2171 | 1399070.2171
C | Xist Rating 13 | -95.46 | 89.548 | 150.274 | 35.8 | 2411.6 | 7857.75 | 45448.7 | 1.99 | 7.92 | 10.883 | 151.778 | 1 | 1 | 1120 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 215953.9568 | 16285.3913 | 1221.7158 | 3135.3115 | 13150.0798 | 158708.4811 | 0.042673 | -1225504.8221 | 1225504.8221
C | Xist Rating 14 | -95.4 | 90.447 | 150.274 | 35.8 | 2419.1 | 7947.06 | 45190.4 | 1.92 | 7.86 | 10.828 | 149.956 | 1 | 1 | 1130 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 218800.3377 | 16549.2563 | 1243.6296 | 3163.3053 | 13385.951 | 156782.1088 | 0.043054 | -1210629.8858 | 1210629.8858
C | Xist Rating 15 | -95.33 | 92.026 | 150.274 | 35.8 | 2418.9 | 7963.23 | 44682.8 | 1.86 | 7.75 | 10.755 | 146.165 | 1 | 1 | 1140 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 222601.6914 | 16815.2179 | 1265.7381 | 3191.2992 | 13623.9188 | 152814.3432 | 0.043435 | -1179991.8512 | 1179991.8512
C | Xist Rating 16 | -95.24 | 93.541 | 150.274 | 35.8 | 2426.98 | 8070.19 | 44188.3 | 1.82 | 7.64 | 10.732 | 142.47 | 1 | 1 | 1150 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 227022.1362 | 17083.2762 | 1288.0414 | 3219.293 | 13863.9832 | 148961.7244 | 0.043816 | -1150242.9507 | 1150242.9507
C | Xist Rating 17 | -95.17 | 95.136 | 150.274 | 35.8 | 2424.42 | 8060.58 | 43705.6 | 1.77 | 7.53 | 10.686 | 138.981 | 1 | 1 | 1160 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 230649.6211 | 17353.4312 | 1310.5395 | 3247.2869 | 14106.1443 | 145315.0238 | 0.044197 | -1122084.0948 | 1122084.0948
C | Xist Rating 18 | -94.89 | 100.692 | 150.274 | 35.8 | 2424.65 | 8140.36 | 41834.8 | 1.78 | 7.13 | 10.755 | 125.065 | 1 | 1 | 1170 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 244142.8578 | 17625.6827 | 1333.2324 | 3275.2807 | 14350.402 | 130883.8035 | 0.044578 | -1010650.0375 | 1010650.0375
C | Xist Rating 19 | -94.85 | 101.234 | 150.274 | 35.8 | 2431.86 | 8227.1 | 41726.7 | 1.74 | 7.11 | 10.721 | 124.471 | 1 | 1 | 1180 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 246186.9152 | 17900.0309 | 1356.1201 | 3303.2746 | 14596.7563 | 130249.6329 | 0.044959 | -1005753.1399 | 1005753.1399
C | Xist Rating 20 | -94.73 | 104.251 | 150.273 | 35.8 | 2418.6 | 8114.36 | 40887.7 | 1.69 | 6.93 | 10.671 | 118.764 | 1 | 1 | 1190 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 252141.4686 | 18176.4757 | 1379.2026 | 3331.2684 | 14845.2073 | 124298.1833 | 0.04534 | -959797.6236 | 959797.6236
C | Xist Rating 21 | -94.67 | 105.042 | 150.273 | 35.8 | 2430.19 | 8255.88 | 40683.4 | 1.66 | 6.88 | 10.666 | 117.452 | 1 | 1 | 1200 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 255272.018 | 18455.0172 | 1402.4799 | 3359.2623 | 15095.7549 | 122926.0909 | 0.045721 | -949202.6901 | 949202.6901
C | Xist Rating 22 | -94.61 | 106.705 | 150.273 | 35.8 | 2424.11 | 8205.06 | 40282.4 | 1.62 | 6.8 | 10.621 | 114.911 | 1 | 1 | 1210 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 258664.6576 | 18735.6552 | 1425.9519 | 3387.2562 | 15348.3991 | 120268.1089 | 0.046102 | -928678.4577 | 928678.4577
C | Xist Rating 23 | -94.32 | 113.156 | 150.273 | 35.8 | 2411.72 | 8149.73 | 38539.1 | 1.62 | 6.43 | 10.656 | 103.436 | 1 | 1 | 1220 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 272900.5883 | 19018.39 | 1449.6188 | 3415.25 | 15603.14 | 108362.1528 | 0.046483 | -836743.8205 | 836743.8205
C | Xist Rating 24 | -94.24 | 114.67 | 150.273 | 35.8 | 2414.19 | 8196.54 | 38184.1 | 1.6 | 6.35 | 10.644 | 101.276 | 1 | 1 | 1230 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 276835.1673 | 19303.2213 | 1473.4804 | 3443.2439 | 15859.9775 | 106113.9254 | 0.046864 | -819383.6041 | 819383.6041
C | Xist Rating 25 | -94.17 | 116.324 | 150.273 | 35.8 | 2409.6 | 8162.24 | 37836.5 | 1.56 | 6.28 | 10.608 | 99.256 | 1 | 1 | 1240 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 280294.3104 | 19590.1493 | 1497.5369 | 3471.2377 | 16118.9116 | 103997.006 | 0.047245 | -803037.3141 | 803037.3141
C | Xist Rating 26 | -94.13 | 117.258 | 150.273 | 35.7 | 2409.09 | 8165.69 | 37665.3 | 1.52 | 6.24 | 10.58 | 98.339 | 1 | 1 | 1250 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 282485.0752 | 19879.1739 | 1521.7881 | 3499.2316 | 16379.9423 | 103025.9611 | 0.047626 | -795539.1627 | 795539.1627
C | Xist Rating 27 | -94.02 | 119.552 | 150.273 | 35.8 | 2410.62 | 8210.99 | 37163.2 | 1.49 | 6.14 | 10.567 | 95.369 | 1 | 1 | 1260 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 288194.4422 | 20170.2951 | 1546.2341 | 3527.2254 | 16643.0697 | 99929.8089 | 0.048007 | -771631.4958 | 771631.4958
C | Xist Rating 28 | -93.73 | 125.677 | 150.273 | 35.8 | 2407.27 | 8252.96 | 35779.4 | 1.49 | 5.85 | 10.616 | 87.185 | 1 | 1 | 1270 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 302538.4718 | 20463.513 | 1570.8749 | 3555.2193 | 16908.2938 | 91441.9517 | 0.048388 | -706090.5121 | 706090.5121
C | Xist Rating 29 | -93.65 | 127.399 | 150.273 | 35.7 | 2407.03 | 8268.69 | 35479.2 | 1.45 | 5.79 | 10.593 | 85.619 | 1 | 1 | 1280 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 306653.215 | 20758.8275 | 1595.7105 | 3583.2131 | 17175.6144 | 89796.476 | 0.048769 | -693384.5853 | 693384.5853
C | Xist Rating 30 | -93.55 | 129.07 | 150.273 | 35.7 | 2413.31 | 8362.16 | 35185.2 | 1.41 | 5.73 | 10.586 | 84.078 | 1 | 1 | 1290 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 311485.9217 | 21056.2387 | 1620.7408 | 3611.207 | 17445.0317 | 88177.9631 | 0.04915 | -680886.8578 | 680886.8578
C | Xist Rating 31 | -93.42 | 131.342 | 150.273 | 35.7 | 2421.24 | 8487.3 | 34754 | 1.39 | 5.64 | 10.584 | 81.748 | 1 | 1 | 1300 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 318010.5041 | 21355.7465 | 1645.966 | 3639.2008 | 17716.5456 | 85752.4531 | 0.049531 | -662157.7123 | 662157.7123
C | Xist Rating 32 | -93.35 | 132.674 | 150.273 | 35.7 | 2425.19 | 8550.85 | 34542.6 | 1.36 | 5.59 | 10.565 | 80.705 | 1 | 1 | 1310 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 321759.6581 | 21657.3509 | 1671.3859 | 3667.1947 | 17990.1562 | 84655.7315 | 0.049912 | -653689.1191 | 653689.1191
C | Xist Rating 33 | -93.06 | 138.896 | 150.273 | 35.7 | 2420 | 8572.14 | 33365.2 | 1.36 | 5.35 | 10.605 | 74.416 | 1 | 1 | 1320 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 336128.32 | 21961.0519 | 1697.0007 | 3695.1885 | 18265.8634 | 78134.2743 | 0.050293 | -603332.1553 | 603332.1553
C | Xist Rating 34 | -92.96 | 141.386 | 150.273 | 35.7 | 2413.94 | 8525.54 | 32982.1 | 1.32 | 5.28 | 10.565 | 72.56 | 1 | 1 | 1330 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 341297.3208 | 22266.8496 | 1722.8102 | 3723.1824 | 18543.6672 | 76184.849 | 0.050674 | -588279.2098 | 588279.2098
C | Xist Rating 35 | -92.85 | 143.773 | 150.273 | 35.7 | 2414.22 | 8558.29 | 32609.1 | 1.3 | 5.2 | 10.55 | 70.75 | 1 | 1 | 1340 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 347099.6521 | 22574.7439 | 1748.8145 | 3751.1762 | 18823.5677 | 74297.555 | 0.051055 | -573706.0259 | 573706.0259
C | Xist Rating 36 | -92.78 | 145.122 | 150.273 | 35.7 | 2417.56 | 8615.05 | 32426 | 1.27 | 5.16 | 10.534 | 69.927 | 1 | 1 | 1350 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 350841.1423 | 22884.7348 | 1775.0136 | 3779.1701 | 19105.5647 | 73428.6365 | 0.051436 | -566996.4669 | 566996.4669
C | Xist Rating 37 | -92.7 | 145.859 | 150.273 | 35.7 | 2434.07 | 8838.89 | 32304.8 | 1.26 | 5.14 | 10.543 | 69.35 | 1 | 1 | 1360 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 355031.0161 | 23196.8224 | 1801.4075 | 3807.1639 | 19389.6585 | 72829.6892 | 0.051817 | -562371.5551 | 562371.5551
C | Xist Rating 38 | -92.34 | 154.943 | 150.273 | 35.7 | 2406.42 | 8602.63 | 30904 | 1.25 | 4.86 | 10.559 | 62.642 | 1 | 1 | 1370 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 372857.9341 | 23511.0066 | 1827.9962 | 3835.1578 | 19675.8488 | 65864.1502 | 0.052198 | -508585.5089 | 508585.5089
C | Xist Rating 39 | -92.29 | 155.941 | 150.273 | 35.7 | 2406.89 | 8618.34 | 30795.5 | 1.22 | 4.84 | 10.542 | 62.222 | 1 | 1 | 1380 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 375332.8335 | 23827.2874 | 1854.7797 | 3863.1516 | 19964.1358 | 65413.0194 | 0.052579 | -505101.9969 | 505101.9969
C | Xist Rating 40 | -92.2 | 158.05 | 150.273 | 35.7 | 2405.63 | 8626.5 | 30528.3 | 1.2 | 4.79 | 10.526 | 61.069 | 1 | 1 | 1390 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 380209.8215 | 24145.6649 | 1881.7579 | 3891.1455 | 20254.5194 | 64207.0628 | 0.05296 | -495789.9197 | 495789.9197
C | Xist Rating 41 | -92.11 | 160.154 | 150.273 | 35.7 | 2404.28 | 8633.45 | 30266.3 | 1.18 | 4.73 | 10.511 | 59.951 | 1 | 1 | 1400 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 385055.0591 | 24466.139 | 1908.931 | 3919.1393 | 20546.9997 | 63037.3616 | 0.053341 | -486757.7973 | 486757.7973
C | Xist Rating 42 | -92 | 162.603 | 150.273 | 35.7 | 2402.97 | 8645.69 | 29958.7 | 1.16 | 4.67 | 10.499 | 58.632 | 1 | 1 | 1410 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 390730.1309 | 24788.7098 | 1936.2988 | 3947.1332 | 20841.5766 | 61658.9756 | 0.053722 | -476114.2653 | 476114.2653
C | Xist Rating 43 | -91.7 | 169.296 | 150.273 | 35.7 | 2397.99 | 8670.61 | 29053 | 1.17 | 4.49 | 10.544 | 54.645 | 1 | 1 | 1420 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 405970.115 | 25113.3771 | 1963.8614 | 3975.1271 | 21138.2501 | 57533.9754 | 0.054103 | -444262.1077 | 444262.1077
C | Xist Rating 44 | -91.64 | 170.886 | 150.273 | 35.7 | 2392.88 | 8618.49 | 28911.8 | 1.13 | 4.47 | 10.517 | 54.151 | 1 | 1 | 1430 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 408909.6917 | 25440.1411 | 1991.6188 | 4003.1209 | 21437.0202 | 56997.4968 | 0.054484 | -440119.5621 | 440119.5621
C | Xist Rating 45 | -91.5 | 174.072 | 150.273 | 35.7 | 2390.21 | 8622.07 | 28542.9 | 1.12 | 4.39 | 10.507 | 52.649 | 1 | 1 | 1440 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 416068.6351 | 25769.0018 | 2019.571 | 4031.1148 | 21737.887 | 55435.4879 | 0.054865 | -428058.1429 | 428058.1429
C | Xist Rating 46 | -91.41 | 176.214 | 150.273 | 35.7 | 2389.55 | 8637.25 | 28317.7 | 1.1 | 4.35 | 10.495 | 51.778 | 1 | 1 | 1450 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 421072.1637 | 26099.959 | 2047.718 | 4059.1086 | 22040.8504 | 54521.7145 | 0.055246 | -421002.2271 | 421002.2271
C | Xist Rating 47 | -91.31 | 177.445 | 150.273 | 35.7 | 2401.24 | 8806.69 | 28185.2 | 1.08 | 4.33 | 10.501 | 51.267 | 1 | 1 | 1460 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 426088.0318 | 26433.0129 | 2076.0598 | 4087.1025 | 22345.9105 | 53982.904 | 0.055627 | -416841.6751 | 416841.6751
C | Xist Rating 48 | -91.01 | 185.303 | 150.273 | 35.7 | 2380.12 | 8625.24 | 27311.1 | 1.07 | 4.16 | 10.52 | 47.789 | 1 | 1 | 1470 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 441043.3764 | 26768.1635 | 2104.5964 | 4115.0963 | 22653.0671 | 50370.5103 | 0.056008 | -388947.7288 | 388947.7288
C | Xist Rating 49 | -90.87 | 187.796 | 150.273 | 35.7 | 2386.56 | 8739.33 | 27067.5 | 1.06 | 4.11 | 10.518 | 46.888 | 1 | 1 | 1480 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 448186.4218 | 27105.4106 | 2133.3277 | 4143.0902 | 22962.3205 | 49432.7492 | 0.056389 | -381706.5862 | 381706.5862
C | Xist Rating 50 | -90.75 | 189.941 | 150.273 | 35.7 | 2392.54 | 8844.61 | 26867.9 | 1.04 | 4.07 | 10.514 | 46.169 | 1 | 1 | 1490 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 454441.4401 | 27444.7544 | 2162.2539 | 4171.084 | 23273.6704 | 48676.7389 | 0.05677 | -375868.8747 | 375868.8747
C | Xist Rating 51 | -90.64 | 192.177 | 150.273 | 35.7 | 2394.97 | 8902.91 | 26671.5 | 1.01 | 4.03 | 10.505 | 45.482 | 1 | 1 | 1500 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 460258.1497 | 27786.1948 | 2191.3748 | 4199.0779 | 23587.117 | 47946.3728 | 0.057151 | -370229.1812 | 370229.1812
C | Xist Rating 52 | -90.5 | 194.697 | 150.273 | 35.7 | 2401.35 | 9022.35 | 26440.2 | 1 | 3.99 | 10.504 | 44.655 | 1 | 1 | 1510 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 467535.6409 | 28129.7319 | 2220.6906 | 4227.0717 | 23902.6602 | 47085.1125 | 0.057532 | -363578.7576 | 363578.7576
C | Xist Rating 53 | -90.15 | 202.238 | 150.273 | 35.7 | 2400.6 | 9117.26 | 25682.4 | 1 | 3.85 | 10.553 | 41.84 | 1 | 1 | 1520 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 485492.5428 | 28475.3656 | 2250.2011 | 4255.0656 | 24220.3 | 44169.7863 | 0.057913 | -341067.382 | 341067.382
C | Xist Rating 54 | -90.05 | 205.102 | 150.273 | 35.7 | 2392.4 | 9030.45 | 25469.7 | 0.98 | 3.81 | 10.531 | 41.16 | 1 | 1 | 1530 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 490686.0248 | 28823.0959 | 2279.9064 | 4283.0594 | 24540.0365 | 43452.3843 | 0.058294 | -335527.7934 | 335527.7934
C | Xist Rating 55 | -89.96 | 206.607 | 150.273 | 35.7 | 2397.84 | 9123.92 | 25365 | 0.96 | 3.79 | 10.524 | 40.844 | 1 | 1 | 1540 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 495410.5289 | 29172.9229 | 2309.8065 | 4311.0533 | 24861.8696 | 43113.8419 | 0.058675 | -332913.6588 | 332913.6588
C | Xist Rating 56 | -89.78 | 210.655 | 150.273 | 35.7 | 2396.48 | 9156.01 | 25022.5 | 0.94 | 3.72 | 10.52 | 39.676 | 1 | 1 | 1550 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 504830.4944 | 29524.8465 | 2339.9013 | 4339.0471 | 25185.7993 | 41890.5194 | 0.059056 | -323467.4866 | 323467.4866
C | Xist Rating 57 | -89.67 | 211.936 | 150.273 | 35.7 | 2410.64 | 9382.62 | 24921.7 | 0.93 | 3.7 | 10.525 | 39.355 | 1 | 1 | 1560 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 510901.399 | 29878.8667 | 2370.191 | 4367.041 | 25511.8257 | 41554.5629 | 0.059437 | -320873.3197 | 320873.3197
C | Xist Rating 58 | -89.32 | 221.207 | 150.273 | 35.7 | 2387.86 | 9166.76 | 24163.3 | 0.92 | 3.56 | 10.549 | 36.812 | 1 | 1 | 1570 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 528211.347 | 30234.9836 | 2400.6755 | 4395.0348 | 25839.9487 | 38912.1959 | 0.059818 | -300469.6622 | 300469.6622
C | Xist Rating 59 | -89.2 | 223.472 | 150.273 | 35.7 | 2391.75 | 9250.55 | 24008.6 | 0.91 | 3.53 | 10.543 | 36.347 | 1 | 1 | 1580 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 534489.156 | 30593.1971 | 2431.3547 | 4423.0287 | 26170.1684 | 38425.7866 | 0.0602 | -296713.7385 | 296713.7385
C | Xist Rating 60 | -89.09 | 225.772 | 150.273 | 35.7 | 2393.92 | 9309.58 | 23856 | 0.89 | 3.5 | 10.536 | 35.894 | 1 | 1 | 1590 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 540480.1062 | 30953.5072 | 2462.2288 | 4451.0225 | 26502.4846 | 37944.1751 | 0.060581 | -292994.8621 | 292994.8621
C | Xist Rating 61 | -88.95 | 228.667 | 150.273 | 35.7 | 2396.37 | 9384.31 | 23646.1 | 0.88 | 3.46 | 10.534 | 35.242 | 1 | 1 | 1600 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 547970.7388 | 31315.9139 | 2493.2976 | 4479.0164 | 26836.8975 | 37263.5948 | 0.060962 | -287739.6012 | 287739.6012
C | Xist Rating 62 | -88.88 | 230.367 | 150.273 | 35.7 | 2396.09 | 9396.22 | 23557.3 | 0.86 | 3.45 | 10.524 | 35.018 | 1 | 1 | 1610 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 551980.065 | 31680.4173 | 2524.5612 | 4507.0103 | 27173.4071 | 37019.3014 | 0.061343 | -285853.2325 | 285853.2325
C | Xist Rating 63 | -88.46 | 240.582 | 150.273 | 35.7 | 2382.03 | 9321.39 | 22805.8 | 0.86 | 3.31 | 10.561 | 32.655 | 1 | 1 | 1620 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 573073.5415 | 32047.0173 | 2556.0196 | 4535.0041 | 27512.0132 | 34571.6972 | 0.061724 | -266953.4817 | 266953.4817
C | Xist Rating 64 | -88.38 | 241.938 | 150.273 | 35.7 | 2389.07 | 9446.26 | 22723.9 | 0.85 | 3.29 | 10.558 | 32.433 | 1 | 1 | 1630 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 578006.8177 | 32415.714 | 2587.6728 | 4562.998 | 27852.716 | 34337.3191 | 0.062105 | -265143.6762 | 265143.6762
C | Xist Rating 65 | -88.28 | 244.385 | 150.273 | 35.7 | 2387.21 | 9444.04 | 22589.2 | 0.84 | 3.27 | 10.548 | 32.073 | 1 | 1 | 1640 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 583398.3159 | 32786.5073 | 2619.5208 | 4590.9918 | 28195.5155 | 33959.1034 | 0.062486 | -262223.195 | 262223.195
C | Xist Rating 66 | -88.15 | 247.637 | 150.273 | 35.6 | 2383.27 | 9419.99 | 22403.6 | 0.82 | 3.24 | 10.538 | 31.563 | 1 | 1 | 1650 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 590185.833 | 33159.3972 | 2651.5635 | 4618.9857 | 28540.4115 | 33417.2316 | 0.062867 | -258039.0045 | 258039.0045
C | Xist Rating 67 | -88.01 | 250.645 | 150.273 | 35.6 | 2383.89 | 9467.32 | 22221.2 | 0.81 | 3.2 | 10.535 | 31.049 | 1 | 1 | 1660 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 5 | E | Rod | 597510.109 | 33534.3837 | 2683.8011 | 4646.9795 | 28887.4042 | 32879.2948 | 0.063248 | -253885.1988 | 253885.1988
C | Xist Rating 68 | -87.64 | 259.96 | 150.273 | 35.6 | 2371.83 | 9402.62 | 21633.4 | 0.81 | 3.1 | 10.554 | 29.349 | 1 | 1 | 1670 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 616580.9268 | 33911.4669 | 2716.2334 | 4674.9734 | 29236.4936 | 31118.8245 | 0.063629 | -240291.3144 | 240291.3144
C | Xist Rating 69 | -87.56 | 261.427 | 150.273 | 35.6 | 2376.37 | 9490.61 | 21560.8 | 0.8 | 3.08 | 10.549 | 29.173 | 1 | 1 | 1680 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 621247.28 | 34290.6467 | 2748.8606 | 4702.9672 | 29587.6795 | 30931.6318 | 0.06401 | -238845.8617 | 238845.8617
C | Xist Rating 70 | -87.4 | 265.532 | 150.273 | 35.6 | 2370.76 | 9449.28 | 21346.5 | 0.78 | 3.04 | 10.54 | 28.612 | 1 | 1 | 1690 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 629512.6443 | 34671.9232 | 2781.6825 | 4730.9611 | 29940.9621 | 30336.3027 | 0.064391 | -234248.8885 | 234248.8885
C | Xist Rating 71 | -87.27 | 268.208 | 150.273 | 35.6 | 2372.37 | 9507.03 | 21206.2 | 0.77 | 3.02 | 10.536 | 28.249 | 1 | 1 | 1700 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 636288.613 | 35055.2963 | 2814.6992 | 4758.9549 | 30296.3414 | 29954.7466 | 0.064772 | -231302.6128 | 231302.6128
C | Xist Rating 72 | -87.14 | 271.409 | 150.273 | 35.6 | 2370.17 | 9509.23 | 21045.2 | 0.76 | 2.99 | 10.53 | 27.838 | 1 | 1 | 1710 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 643285.4695 | 35440.766 | 2847.9107 | 4786.9488 | 30653.8172 | 29523.1348 | 0.065153 | -227969.8213 | 227969.8213
C | Xist Rating 73 | -86.8 | 280.075 | 150.273 | 35.6 | 2360.38 | 9465.84 | 20567.6 | 0.76 | 2.9 | 10.565 | 26.556 | 1 | 1 | 1720 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 661083.4285 | 35828.3323 | 2881.317 | 4814.9426 | 31013.3897 | 28197.4179 | 0.065534 | -217732.9866 | 217732.9866
C | Xist Rating 74 | -86.64 | 284.049 | 150.273 | 35.6 | 2357.13 | 9460.9 | 20374.8 | 0.75 | 2.87 | 10.558 | 26.075 | 1 | 1 | 1730 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 669540.4194 | 36217.9953 | 2914.9181 | 4842.9365 | 31375.0588 | 27692.8994 | 0.065915 | -213837.2284 | 213837.2284
C | Xist Rating 75 | -86.55 | 286.013 | 150.273 | 35.6 | 2358.23 | 9499.94 | 20290.3 | 0.74 | 2.85 | 10.552 | 25.883 | 1 | 1 | 1740 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 674484.437 | 36609.7549 | 2948.714 | 4870.9303 | 31738.8246 | 27488.4761 | 0.066296 | -212258.7262 | 212258.7262
C | Xist Rating 76 | -86.41 | 289.771 | 150.273 | 35.6 | 2353.8 | 9470.31 | 20123.9 | 0.73 | 2.82 | 10.544 | 25.486 | 1 | 1 | 1750 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 682062.9798 | 37003.6112 | 2982.7046 | 4898.9242 | 32104.687 | 27070.9569 | 0.066677 | -209034.7538 | 209034.7538
C | Xist Rating 77 | -86.31 | 292.563 | 150.273 | 35.6 | 2349.9 | 9438.67 | 20001 | 0.72 | 2.8 | 10.537 | 25.198 | 1 | 1 | 1760 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 687493.7937 | 37399.5641 | 3016.8901 | 4926.918 | 32472.646 | 26766.6037 | 0.067058 | -206684.6186 | 206684.6186
C | Xist Rating 78 | -85.91 | 302.82 | 150.273 | 35.6 | 2339.14 | 9396.82 | 19497.5 | 0.72 | 2.71 | 10.573 | 23.931 | 1 | 1 | 1770 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 708338.3748 | 37797.6136 | 3051.2703 | 4954.9119 | 32842.7017 | 25456.2834 | 0.067439 | -196566.6724 | 196566.6724
C | Xist Rating 79 | -85.79 | 305.722 | 150.273 | 35.6 | 2337.64 | 9403.17 | 19383.2 | 0.71 | 2.69 | 10.565 | 23.679 | 1 | 1 | 1780 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 714667.9761 | 38197.7597 | 3085.8453 | 4982.9057 | 33214.854 | 25189.1049 | 0.06782 | -194503.5911 | 194503.5911
C | Xist Rating 80 | -85.72 | 307.448 | 150.273 | 35.6 | 2337.53 | 9416.91 | 19326.2 | 0.7 | 2.68 | 10.557 | 23.571 | 1 | 1 | 1790 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 718668.9234 | 38600.0025 | 3120.6151 | 5010.8996 | 33589.1029 | 25071.3832 | 0.068201 | -193594.5751 | 193594.5751
C | Xist Rating 81 | -85.53 | 312.314 | 150.273 | 35.6 | 2333.85 | 9413.46 | 19122.1 | 0.69 | 2.65 | 10.553 | 23.099 | 1 | 1 | 1800 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 728894.0289 | 39004.3419 | 3155.5797 | 5038.8934 | 33965.4484 | 24575.7839 | 0.068582 | -189767.6887 | 189767.6887
C | Xist Rating 82 | -85.47 | 315.089 | 150.273 | 35.6 | 2324.35 | 9290.32 | 19014 | 0.68 | 2.63 | 10.628 | 22.854 | 1 | 1 | 1810 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 732377.1171 | 39410.7779 | 3190.7391 | 5066.8873 | 34343.8906 | 24320.1915 | 0.068963 | -187794.0724 | 187794.0724
C | Xist Rating 83 | -85.07 | 325.604 | 150.274 | 35.6 | 2313.53 | 9243.39 | 18563.8 | 0.68 | 2.55 | 10.663 | 21.801 | 1 | 1 | 1820 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 753294.6221 | 39819.3106 | 3226.0933 | 5094.8812 | 34724.4294 | 23231.8338 | 0.069344 | -179390.0626 | 179390.0626
C | Xist Rating 84 | -84.92 | 323.896 | 150.274 | 35.6 | 2351.61 | 9860.57 | 18632.6 | 0.66 | 2.56 | 10.694 | 21.971 | 1 | 1 | 1830 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 761677.0726 | 40229.9399 | 3261.6423 | 5122.875 | 35107.0649 | 23395.8135 | 0.069725 | -180656.2703 | 180656.2703
C | Xist Rating 85 | -84.78 | 326.122 | 150.274 | 35.6 | 2358.76 | 10016.1 | 18546.6 | 0.66 | 2.55 | 10.696 | 21.787 | 1 | 1 | 1840 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 769243.5287 | 40642.6658 | 3297.386 | 5150.8689 | 35491.797 | 23208.0024 | 0.070106 | -179206.0428 | 179206.0428
C | Xist Rating 86 | -84.66 | 329.997 | 150.274 | 35.6 | 2352.77 | 9954.15 | 18410.6 | 0.65 | 2.52 | 10.685 | 21.503 | 1 | 1 | 1850 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 776407.0417 | 41057.4884 | 3333.3246 | 5178.8627 | 35878.6257 | 22906.7705 | 0.070487 | -176880.0102 | 176880.0102
C | Xist Rating 87 | -84.46 | 334.314 | 150.274 | 35.6 | 2352.5 | 10000.4 | 18260.7 | 0.63 | 2.5 | 10.689 | 21.19 | 1 | 1 | 1860 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 786473.685 | 41474.4076 | 3369.4579 | 5206.8566 | 36267.5511 | 22567.2268 | 0.070868 | -174258.1437 | 174258.1437
C | Xist Rating 88 | -84.08 | 343.908 | 150.274 | 35.6 | 2344.8 | 9994.65 | 17881.1 | 0.63 | 2.43 | 10.728 | 20.344 | 1 | 1 | 1870 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 806395.4784 | 41893.4235 | 3405.7861 | 5234.8504 | 36658.573 | 21693.7352 | 0.071249 | -167513.2729 | 167513.2729
C | Xist Rating 89 | -83.93 | 348.211 | 150.274 | 35.6 | 2339.33 | 9946.17 | 17740.3 | 0.63 | 2.41 | 10.716 | 20.061 | 1 | 1 | 1880 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 814580.4386 | 42314.5359 | 3442.309 | 5262.8443 | 37051.6917 | 21402.2326 | 0.07163 | -165262.367 | 165262.367
C | Xist Rating 90 | -83.78 | 351.034 | 150.274 | 35.6 | 2343.37 | 10053.7 | 17647.9 | 0.62 | 2.39 | 10.719 | 19.879 | 1 | 1 | 1890 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 822602.5446 | 42737.745 | 3479.0267 | 5290.8381 | 37446.9069 | 21207.3312 | 0.072011 | -163757.3899 | 163757.3899
C | Xist Rating 91 | -83.66 | 354.314 | 150.274 | 35.6 | 2340.01 | 10026.3 | 17556.5 | 0.6 | 2.38 | 10.716 | 19.714 | 1 | 1 | 1900 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 829098.3031 | 43163.0508 | 3515.9392 | 5318.832 | 37844.2188 | 21020.5465 | 0.072392 | -162315.0882 | 162315.0882
C | Xist Rating 92 | -83.53 | 357.316 | 150.274 | 35.6 | 2339.66 | 10053.8 | 17466.5 | 0.59 | 2.36 | 10.717 | 19.544 | 1 | 1 | 1910 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 835997.9526 | 43590.4531 | 3553.0464 | 5346.8258 | 38243.6273 | 20837.7598 | 0.072773 | -160903.6579 | 160903.6579
C | Xist Rating 93 | -83.07 | 368.997 | 150.274 | 35.6 | 2329.88 | 10034.5 | 17051.7 | 0.6 | 2.29 | 10.756 | 18.669 | 1 | 1 | 1920 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 859718.7304 | 44019.9521 | 3590.3485 | 5374.8197 | 38645.1324 | 19943.1453 | 0.073154 | -153995.6815 | 153995.6815
C | Xist Rating 94 | -82.92 | 373.376 | 150.274 | 35.6 | 2325.59 | 10005.6 | 16925.2 | 0.59 | 2.27 | 10.752 | 18.433 | 1 | 1 | 1930 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 868319.4918 | 44451.5478 | 3627.8454 | 5402.8135 | 39048.7342 | 19691.4431 | 0.073535 | -152052.104 | 152052.104
C | Xist Rating 95 | -82.81 | 374.741 | 150.274 | 35.6 | 2334.04 | 10181.3 | 16883.4 | 0.58 | 2.26 | 10.759 | 18.359 | 1 | 1 | 1940 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 874660.4836 | 44885.24 | 3665.537 | 5430.8074 | 39454.4326 | 19608.4409 | 0.073916 | -151411.1829 | 151411.1829
C | Xist Rating 96 | -82.68 | 379.186 | 150.274 | 35.6 | 2325.04 | 10057.3 | 16773.4 | 0.57 | 2.24 | 10.759 | 18.171 | 1 | 1 | 1950 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 881622.6174 | 45321.0289 | 3703.4235 | 5458.8012 | 39862.2277 | 19406.5961 | 0.074297 | -149852.591 | 149852.591
C | Xist Rating 97 | -82.49 | 383.888 | 150.274 | 35.6 | 2322.92 | 10073.9 | 16638.1 | 0.56 | 2.22 | 10.763 | 17.917 | 1 | 1 | 1960 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 891741.113 | 45758.9144 | 3741.5047 | 5486.7951 | 40272.1194 | 19136.3108 | 0.074678 | -147765.5193 | 147765.5193
C | Xist Rating 98 | -82.08 | 394.532 | 150.274 | 35.6 | 2314.24 | 10053.9 | 16304.2 | 0.56 | 2.16 | 10.803 | 17.259 | 1 | 1 | 1970 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 913041.7357 | 46198.8966 | 3779.7807 | 5514.7889 | 40684.1077 | 18457.6585 | 0.075059 | -142525.1467 | 142525.1467
C | Xist Rating 99 | -81.94 | 397.957 | 150.274 | 35.6 | 2314.02 | 10089.1 | 16215.2 | 0.55 | 2.15 | 10.801 | 17.104 | 1 | 1 | 1980 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 920880.4571 | 46640.9754 | 3818.2515 | 5542.7828 | 41098.1926 | 18289.7174 | 0.07544 | -141228.35 | 141228.35
C | Xist Rating 100 | -81.77 | 402.531 | 150.274 | 35.6 | 2309.68 | 10057 | 16102.4 | 0.55 | 2.13 | 10.797 | 16.911 | 1 | 1 | 1990 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 929717.8001 | 47085.1508 | 3856.9171 | 5570.7766 | 41514.3742 | 18091.7538 | 0.075821 | -139699.7275 | 139699.7275
C | Xist Rating 101 | -81.64 | 406.082 | 150.274 | 35.6 | 2307.25 | 10050 | 16015.8 | 0.54 | 2.12 | 10.793 | 16.765 | 1 | 1 | 2000 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 936932.6945 | 47531.4229 | 3895.7775 | 5598.7705 | 41932.6524 | 17932.9218 | 0.076202 | -138473.2689 | 138473.2689
C | Xist Rating 102 | -81.54 | 408.781 | 150.274 | 35.6 | 2306.26 | 10058.9 | 15954.6 | 0.53 | 2.11 | 10.791 | 16.668 | 1 | 1 | 2010 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 942755.2691 | 47979.7916 | 3934.8326 | 5626.7644 | 42353.0272 | 17824.9802 | 0.076583 | -137639.7725 | 137639.7725
C | Xist Rating 103 | -81.09 | 420.909 | 150.274 | 35.6 | 2296.22 | 10025.6 | 15615.7 | 0.53 | 2.05 | 10.825 | 16.038 | 1 | 1 | 2020 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 966499.664 | 48430.2569 | 3974.0826 | 5654.7582 | 42775.4987 | 17174.9215 | 0.076964 | -132620.1912 | 132620.1912
C | Xist Rating 104 | -80.91 | 425.555 | 150.274 | 35.6 | 2293.54 | 10029.4 | 15500.5 | 0.53 | 2.03 | 10.82 | 15.84 | 1 | 1 | 2030 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 976027.4147 | 48882.8189 | 4013.5273 | 5682.7521 | 43200.0668 | 16971.6294 | 0.077345 | -131050.4233 | 131050.4233
C | Xist Rating 105 | -80.79 | 429.035 | 150.274 | 35.6 | 2290.21 | 9998.66 | 15432.4 | 0.52 | 2.02 | 10.814 | 15.74 | 1 | 1 | 2040 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 982580.2474 | 49337.4775 | 4053.1669 | 5710.7459 | 43626.7316 | 16860.1707 | 0.077726 | -130189.7689 | 130189.7689
C | Xist Rating 106 | -80.69 | 431.701 | 150.274 | 35.6 | 2291.08 | 10048.3 | 15364.9 | 0.51 | 2.01 | 10.81 | 15.627 | 1 | 1 | 2050 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 989061.5271 | 49794.2327 | 4093.0012 | 5738.7398 | 44055.4929 | 16735.2165 | 0.078107 | -129224.9057 | 129224.9057
C | Xist Rating 107 | -80.52 | 436.67 | 150.274 | 35.6 | 2284.86 | 9978.32 | 15264.9 | 0.5 | 1.99 | 10.807 | 15.473 | 1 | 1 | 2060 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 997729.8162 | 50253.0845 | 4133.0303 | 5766.7336 | 44486.3509 | 16567.6386 | 0.078488 | -127930.9139 | 127930.9139
C | Xist Rating 108 | -80.04 | 449.752 | 150.274 | 35.6 | 2274.4 | 9942.84 | 14936.7 | 0.5 | 1.94 | 10.844 | 14.898 | 1 | 1 | 2070 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1022915.9488 | 50714.033 | 4173.2542 | 5794.7275 | 44919.3056 | 15974.6407 | 0.078869 | -123351.9411 | 123351.9411
C | Xist Rating 109 | -79.93 | 453.034 | 150.274 | 35.6 | 2272.23 | 9933.41 | 14874 | 0.5 | 1.93 | 10.839 | 14.807 | 1 | 1 | 2080 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1029397.4458 | 51177.0781 | 4213.6729 | 5822.7213 | 45354.3568 | 15882.3346 | 0.07925 | -122639.1782 | 122639.1782
C | Xist Rating 110 | -79.78 | 457.108 | 150.274 | 35.6 | 2269.61 | 9925.97 | 14791.3 | 0.49 | 1.91 | 10.835 | 14.681 | 1 | 1 | 2090 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1037456.8879 | 51642.2199 | 4254.2864 | 5850.7152 | 45791.5047 | 15743.5751 | 0.079631 | -121567.7141 | 121567.7141
C | Xist Rating 111 | -79.64 | 461.191 | 150.274 | 35.6 | 2266.69 | 9912.7 | 14709.6 | 0.49 | 1.9 | 10.83 | 14.557 | 1 | 1 | 2100 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1045377.0278 | 52109.4583 | 4295.0947 | 5878.709 | 46230.7493 | 15616.9505 | 0.080012 | -120589.9523 | 120589.9523
C | Xist Rating 112 | -79.52 | 464.835 | 150.274 | 35.6 | 2264.4 | 9905.99 | 14639 | 0.48 | 1.89 | 10.827 | 14.452 | 1 | 1 | 2110 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1052572.374 | 52578.7933 | 4336.0977 | 5906.7029 | 46672.0904 | 15499.9077 | 0.080393 | -119686.1786 | 119686.1786
C | Xist Rating 113 | -79.07 | 477.403 | 150.274 | 35.6 | 2254.49 | 9865.82 | 14359.3 | 0.48 | 1.84 | 10.866 | 13.991 | 1 | 1 | 2120 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1076300.2895 | 53050.225 | 4377.2956 | 5934.6967 | 47115.5282 | 15025.2684 | 0.080774 | -116021.1395 | 116021.1395
C | Xist Rating 114 | -78.9 | 482.392 | 150.274 | 35.6 | 2250.84 | 9847.98 | 14264 | 0.47 | 1.83 | 10.861 | 13.849 | 1 | 1 | 2130 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1085787.2093 | 53523.7532 | 4418.6882 | 5962.6906 | 47561.0627 | 14869.5407 | 0.081155 | -114818.6514 | 114818.6514
C | Xist Rating 115 | -78.73 | 487.407 | 150.274 | 35.6 | 2246.09 | 9808.85 | 14170.1 | 0.47 | 1.81 | 10.857 | 13.711 | 1 | 1 | 2140 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1094759.9886 | 53999.3782 | 4460.2756 | 5990.6844 | 48008.6937 | 14728.3357 | 0.081536 | -113728.3041 | 113728.3041
C | Xist Rating 116 | -78.64 | 490.256 | 150.274 | 35.6 | 2244.7 | 9807.84 | 14123.7 | 0.46 | 1.81 | 10.853 | 13.65 | 1 | 1 | 2150 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1100477.6432 | 54477.0997 | 4502.0578 | 6018.6783 | 48458.4214 | 14656.634 | 0.081917 | -113174.643 | 113174.643
C | Xist Rating 117 | -78.52 | 493.846 | 150.274 | 35.6 | 2242.51 | 9802.05 | 14059.1 | 0.46 | 1.79 | 10.849 | 13.559 | 1 | 1 | 2160 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1107454.5935 | 54956.9179 | 4544.0348 | 6046.6721 | 48910.2458 | 14564.1904 | 0.082298 | -112460.8174 | 112460.8174
C | Xist Rating 118 | -78.04 | 507.581 | 150.274 | 35.6 | 2231.53 | 9747.24 | 13786.1 | 0.46 | 1.75 | 10.889 | 13.134 | 1 | 1 | 2170 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1132682.2289 | 55438.8327 | 4586.2066 | 6074.666 | 49364.1667 | 14126.8553 | 0.082679 | -109083.8318 | 109083.8318
C | Xist Rating 119 | -77.87 | 512.345 | 150.274 | 35.6 | 2229.26 | 9754.18 | 13699.1 | 0.45 | 1.74 | 10.883 | 13.008 | 1 | 1 | 2180 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1142150.2147 | 55922.8442 | 4628.5732 | 6102.6598 | 49820.1843 | 13987.3454 | 0.08306 | -108006.5735 | 108006.5735
C | Xist Rating 120 | -77.74 | 516.169 | 150.274 | 35.6 | 2227.02 | 9746.62 | 13638.9 | 0.45 | 1.73 | 10.878 | 12.93 | 1 | 1 | 2190 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1149518.6864 | 56408.9522 | 4671.1346 | 6130.6537 | 50278.2985 | 13908.3169 | 0.083441 | -107396.3361 | 107396.3361
C | Xist Rating 121 | -77.61 | 520.399 | 150.274 | 35.6 | 2223.11 | 9706.82 | 13579.4 | 0.44 | 1.72 | 10.876 | 12.857 | 1 | 1 | 2200 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1156904.2209 | 56897.1569 | 4713.8907 | 6158.6475 | 50738.5094 | 13823.8867 | 0.083822 | -106744.3884 | 106744.3884
C | Xist Rating 122 | -77.44 | 525.42 | 150.274 | 35.6 | 2219.68 | 9691.04 | 13495.2 | 0.43 | 1.7 | 10.872 | 12.74 | 1 | 1 | 2210 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1166264.2656 | 57387.4583 | 4756.8417 | 6186.6414 | 51200.8169 | 13693.583 | 0.084203 | -105738.2179 | 105738.2179
C | Xist Rating 123 | -76.97 | 539.021 | 150.274 | 35.6 | 2210.86 | 9672.87 | 13246.1 | 0.43 | 1.66 | 10.912 | 12.369 | 1 | 1 | 2220 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1191699.9681 | 57879.8563 | 4799.9874 | 6214.6353 | 51665.221 | 13312.1072 | 0.084584 | -102792.563 | 102792.563
C | Xist Rating 124 | -76.82 | 543.066 | 150.274 | 35.6 | 2209.5 | 9686.09 | 13182.5 | 0.43 | 1.65 | 10.907 | 12.285 | 1 | 1 | 2230 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1199904.327 | 58374.3509 | 4843.3279 | 6242.6291 | 52131.7218 | 13226.7616 | 0.084965 | -102133.5474 | 102133.5474
C | Xist Rating 125 | -76.67 | 548.004 | 150.274 | 35.6 | 2205.7 | 9657.19 | 13111.7 | 0.42 | 1.64 | 10.903 | 12.196 | 1 | 1 | 2240 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1208732.4228 | 58870.9421 | 4886.8633 | 6270.623 | 52600.3192 | 13125.3175 | 0.085346 | -101350.2223 | 101350.2223
C | Xist Rating 126 | -76.49 | 553.333 | 150.274 | 35.6 | 2201.76 | 9630.45 | 13034 | 0.42 | 1.63 | 10.9 | 12.096 | 1 | 1 | 2250 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1218306.4661 | 59369.63 | 4930.5934 | 6298.6168 | 53071.0132 | 13023.3932 | 0.085727 | -100563.19 | 100563.19
C | Xist Rating 127 | -76.4 | 556.145 | 150.274 | 35.6 | 2200.6 | 9632.38 | 12995.6 | 0.42 | 1.62 | 10.895 | 12.051 | 1 | 1 | 2260 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1223852.687 | 59870.4145 | 4974.5182 | 6326.6107 | 53543.8038 | 12978.5001 | 0.086108 | -100216.5375 | 100216.5375
C | Xist Rating 128 | -75.9 | 571.007 | 150.274 | 35.6 | 2190.03 | 9586.11 | 12751.8 | 0.41 | 1.59 | 10.935 | 11.708 | 1 | 1 | 2270 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1250522.4602 | 60373.2956 | 5018.6379 | 6354.6045 | 54018.6911 | 12614.9291 | 0.086489 | -97409.1388 | 97409.1388
C | Xist Rating 129 | -75.75 | 575.89 | 150.274 | 35.6 | 2186.65 | 9564.3 | 12686.1 | 0.41 | 1.58 | 10.93 | 11.628 | 1 | 1 | 2280 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1259269.8685 | 60878.2734 | 5062.9524 | 6382.5984 | 54495.6751 | 12533.6494 | 0.08687 | -96781.5182 | 96781.5182
C | Xist Rating 130 | -75.55 | 581.406 | 150.274 | 35.6 | 2184.71 | 9579.33 | 12606.8 | 0.41 | 1.56 | 10.926 | 11.527 | 1 | 1 | 2290 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1270203.5023 | 61385.3478 | 5107.4617 | 6410.5922 | 54974.7556 | 12430.6014 | 0.087251 | -95985.8092 | 95985.8092
C | Xist Rating 131 | -75.42 | 585.393 | 150.274 | 35.6 | 2182.43 | 9568.61 | 12557 | 0.4 | 1.56 | 10.921 | 11.47 | 1 | 1 | 2300 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1277579.245 | 61894.5189 | 5152.1657 | 6438.5861 | 55455.9328 | 12361.9445 | 0.087632 | -95455.6584 | 95455.6584
| Xist Rating 132 | -75.3 | 589.646 | 150.274 | 35.6 | 2179.02 | 9536.19 | 12507.6 | 0.4 | 1.55 | 10.918 | 11.416 | 1 | 1 | 2310 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1284850.4269 | 62405.7865 | 5197.0645 | 6466.5799 | 55939.2066 | 12307.6994 | 0.088013 | -95036.7925 | 95036.7925
| Xist Rating 133 | -74.79 | 604.784 | 150.274 | 35.6 | 2168.9 | 9498.62 | 12277.1 | 0.4 | 1.51 | 10.957 | 11.104 | 1 | 1 | 2320 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1311716.0176 | 62919.1508 | 5242.1582 | 6494.5738 | 56424.5771 | 11987.2678 | 0.088394 | -92562.5044 | 92562.5044
| Xist Rating 134 | -74.64 | 609.699 | 150.274 | 35.6 | 2165.76 | 9480.06 | 12216.8 | 0.39 | 1.5 | 10.952 | 11.034 | 1 | 1 | 2330 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1320461.7062 | 63434.6118 | 5287.4466 | 6522.5676 | 56912.0441 | 11904.8902 | 0.088775 | -91926.4062 | 91926.4062
| Xist Rating 135 | -74.48 | 614.59 | 150.274 | 35.6 | 2163.35 | 9475.33 | 12157.2 | 0.39 | 1.49 | 10.947 | 10.965 | 1 | 1 | 2340 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1329573.2765 | 63952.1693 | 5332.9298 | 6550.5615 | 57401.6079 | 11834.9438 | 0.089156 | -91386.2991 | 91386.2991
| Xist Rating 136 | -74.35 | 619.135 | 150.274 | 35.6 | 2160.19 | 9451.67 | 12104.7 | 0.38 | 1.49 | 10.942 | 10.907 | 1 | 1 | 2350 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1337449.2356 | 64471.8235 | 5378.6078 | 6578.5553 | 57893.2682 | 11764.8931 | 0.089537 | -90845.3863 | 90845.3863
| Xist Rating 137 | -74.18 | 624.515 | 150.274 | 35.6 | 2156.62 | 9428.91 | 12039.8 | 0.38 | 1.48 | 10.939 | 10.832 | 1 | 1 | 2360 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1346841.5393 | 64993.5744 | 5424.4805 | 6606.5492 | 58387.0252 | 11688.749 | 0.089918 | -90257.4211 | 90257.4211
| Xist Rating 138 | -73.72 | 638.545 | 150.274 | 35.6 | 2148.29 | 9407.57 | 11846.8 | 0.38 | 1.45 | 10.976 | 10.585 | 1 | 1 | 2370 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1371779.838 | 65517.4218 | 5470.5481 | 6634.543 | 58882.8788 | 11435.5968 | 0.090299 | -88302.6471 | 88302.6471
| Xist Rating 139 | -73.56 | 643.674 | 150.274 | 35.6 | 2144.77 | 9380.48 | 11791.1 | 0.38 | 1.44 | 10.97 | 10.525 | 1 | 1 | 2380 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1380532.685 | 66043.3659 | 5516.8105 | 6662.5369 | 59380.8291 | 11374.9132 | 0.09068 | -87834.0648 | 87834.0648
| Xist Rating 140 | -73.42 | 648.61 | 150.274 | 35.6 | 2141.93 | 9370.98 | 11730 | 0.37 | 1.43 | 10.963 | 10.453 | 1 | 1 | 2390 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1389277.2173 | 66571.4067 | 5563.2676 | 6690.5307 | 59880.8759 | 11289.9802 | 0.091061 | -87178.2342 | 87178.2342
C | Xist Rating 141 | -71.22 | 744.54 | 150.274 | 35.6 | 2022.74 | 8121.04 | 10538.6 | 0.41 | 1.25 | 10.946 | 9.013 | 1 | 1 | 2400 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1506010.8396 | 67101.544 | 5609.9196 | 6718.5246 | 60383.0194 | 9842.7865 | 0.091442 | -76003.388 | 76003.388
C | Xist Rating 142 | -70.5 | 745.986 | 150.274 | 35.6 | 2069.2 | 8926.15 | 10537.9 | 0.39 | 1.25 | 10.962 | 9.021 | 1 | 1 | 2410 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1543594.2312 | 67633.778 | 5656.7663 | 6746.5185 | 60887.2596 | 9830.1308 | 0.091823 | -75905.6647 | 75905.6647
C | Xist Rating 143 | -70.48 | 747.387 | 150.274 | 35.6 | 2067.97 | 8903.38 | 10537.9 | 0.39 | 1.25 | 11.003 | 9.032 | 1 | 1 | 2420 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1545573.8944 | 68168.1087 | 5703.8078 | 6774.5123 | 61393.5964 | 9845.2052 | 0.092204 | -76022.0648 | 76022.0648
C | Xist Rating 144 | -70.19 | 748.744 | 150.274 | 35.6 | 2084.85 | 9224.95 | 10537.8 | 0.39 | 1.25 | 10.998 | 9.041 | 1 | 1 | 2430 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1561018.9284 | 68704.5359 | 5751.0441 | 6802.5062 | 61902.0298 | 9856.2628 | 0.092585 | -76107.4485 | 76107.4485
C | Xist Rating 145 | -70.16 | 750.114 | 150.274 | 35.6 | 2084.51 | 9218.48 | 10537.8 | 0.38 | 1.25 | 10.991 | 9.052 | 1 | 1 | 2440 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1563620.1341 | 69243.0598 | 5798.4752 | 6830.5 | 62412.5598 | 9857.2892 | 0.092966 | -76115.3744 | 76115.3744
C | Xist Rating 146 | -70.14 | 751.441 | 150.274 | 35.6 | 2083.33 | 9195.27 | 10537.9 | 0.38 | 1.25 | 10.986 | 9.063 | 1 | 1 | 2450 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1565499.5785 | 69783.6804 | 5846.1011 | 6858.4939 | 62925.1865 | 9870.3762 | 0.093347 | -76216.4284 | 76216.4284
C | Xist Rating 147 | -70.11 | 752.913 | 150.274 | 35.6 | 2082.51 | 9179.31 | 10537.8 | 0.37 | 1.25 | 10.983 | 9.074 | 1 | 1 | 2460 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1567948.8516 | 70326.3975 | 5893.9217 | 6886.4877 | 63439.9098 | 9871.4344 | 0.093728 | -76224.6 | 76224.6
C | Xist Rating 148 | -70.08 | 754.266 | 150.274 | 35.6 | 2082.01 | 9169.63 | 10537.9 | 0.36 | 1.25 | 11.021 | 9.084 | 1 | 1 | 2470 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1570389.3547 | 70871.2113 | 5941.9372 | 6914.4816 | 63956.7297 | 9872.9955 | 0.094109 | -76236.6544 | 76236.6544
C | Xist Rating 149 | -70.06 | 755.614 | 150.274 | 35.6 | 2080.87 | 9147.55 | 10537.9 | 0.36 | 1.25 | 11.014 | 9.095 | 1 | 1 | 2480 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1572334.5042 | 71418.1217 | 5990.1474 | 6942.4754 | 64475.6463 | 9885.9173 | 0.09449 | -76336.433 | 76336.433
C | Xist Rating 150 | -70.05 | 757.012 | 150.274 | 35.6 | 2079.15 | 9114.33 | 10537.9 | 0.35 | 1.25 | 11.015 | 9.105 | 1 | 1 | 2490 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1573941.4998 | 71967.1288 | 6038.5525 | 6970.4693 | 64996.6595 | 9885.8256 | 0.094871 | -76335.7247 | 76335.7247
C | Xist Rating 151 | -70.03 | 757.997 | 150.274 | 35.6 | 2079.02 | 9111.83 | 10537.9 | 0.35 | 1.25 | 11.008 | 9.114 | 1 | 1 | 2500 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1575890.9229 | 72518.2325 | 6087.1523 | 6998.4631 | 65519.7694 | 9896.6256 | 0.095252 | -76419.1197 | 76419.1197
C | Xist Rating 152 | -70 | 759.846 | 150.274 | 35.6 | 2077.41 | 9081.09 | 10537.9 | 0.34 | 1.25 | 11.007 | 9.127 | 1 | 1 | 2510 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1578511.6789 | 73071.4328 | 6135.9469 | 7026.457 | 66044.9758 | 9899.4298 | 0.095633 | -76440.7726 | 76440.7726
C | Xist Rating 153 | -69.98 | 761.3 | 150.274 | 35.6 | 2076 | 9054.16 | 10537.9 | 0.34 | 1.25 | 11.045 | 9.138 | 1 | 1 | 2520 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1580458.8 | 73626.7298 | 6184.9363 | 7054.4508 | 66572.2789 | 9913.9902 | 0.096014 | -76553.2042 | 76553.2042
C | Xist Rating 154 | -69.96 | 762.638 | 150.274 | 35.6 | 2074.76 | 9030.55 | 10537.9 | 0.33 | 1.25 | 11.039 | 9.148 | 1 | 1 | 2530 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1582290.8169 | 74184.1234 | 6234.1205 | 7082.4447 | 67101.6787 | 9913.3082 | 0.096395 | -76547.938 | 76547.938
C | Xist Rating 155 | -69.95 | 763.789 | 150.274 | 35.6 | 2073.75 | 9011.62 | 10537.9 | 0.33 | 1.25 | 11.032 | 9.157 | 1 | 1 | 2540 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1583907.4387 | 74743.6136 | 6283.4995 | 7110.4385 | 67633.175 | 9924.0246 | 0.096776 | -76630.6871 | 76630.6871
C | Xist Rating 156 | -69.92 | 765.336 | 150.274 | 35.6 | 2072.19 | 8982.05 | 10537.9 | 0.32 | 1.25 | 11.032 | 9.169 | 1 | 1 | 2550 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1585921.6058 | 75305.2004 | 6333.0732 | 7138.4324 | 68166.7681 | 9925.5085 | 0.097157 | -76642.1459 | 76642.1459
C | Xist Rating 157 | -69.89 | 766.785 | 150.274 | 35.6 | 2071.86 | 8975.87 | 10537.9 | 0.32 | 1.25 | 11.028 | 9.179 | 1 | 1 | 2560 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1588671.1701 | 75868.8839 | 6382.8418 | 7166.4262 | 68702.4577 | 9937.329 | 0.097538 | -76733.4208 | 76733.4208
C | Xist Rating 158 | -69.87 | 768.174 | 150.274 | 35.6 | 2070.9 | 8957.93 | 10537.8 | 0.31 | 1.25 | 11.023 | 9.189 | 1 | 1 | 2570 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1590811.5366 | 76434.664 | 6432.8051 | 7194.4201 | 69240.244 | 9936.4131 | 0.097919 | -76726.3483 | 76726.3483
C | Xist Rating 159 | -69.84 | 769.539 | 150.274 | 35.6 | 2069.81 | 8937.68 | 10537.8 | 0.31 | 1.25 | 11.059 | 9.2 | 1 | 1 | 2580 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1592799.5176 | 77002.5408 | 6482.9633 | 7222.4139 | 69780.1269 | 9950.659 | 0.0983 | -76836.3508 | 76836.3508
C | Xist Rating 160 | -69.82 | 770.899 | 150.274 | 35.6 | 2068.73 | 8917.66 | 10537.8 | 0.31 | 1.25 | 11.054 | 9.21 | 1 | 1 | 2590 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1594781.8883 | 77572.5142 | 6533.3162 | 7250.4078 | 70322.1064 | 9962.4007 | 0.098681 | -76927.0175 | 76927.0175
C | Xist Rating 161 | -69.81 | 772.076 | 150.274 | 35.6 | 2067.61 | 8896.71 | 10537.8 | 0.3 | 1.25 | 11.049 | 9.219 | 1 | 1 | 2600 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1596352.0584 | 78144.5842 | 6583.8639 | 7278.4016 | 70866.1825 | 9960.2256 | 0.099062 | -76910.2221 | 76910.2221
C | Xist Rating 162 | -69.78 | 773.764 | 150.274 | 35.6 | 2066.24 | 8871.42 | 10537.8 | 0.3 | 1.25 | 11.046 | 9.23 | 1 | 1 | 2610 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1598782.1274 | 78718.7508 | 6634.6064 | 7306.3955 | 71412.3553 | 9973.0296 | 0.099443 | -77009.0911 | 77009.0911
C | Xist Rating 163 | -69.75 | 775.16 | 150.274 | 35.6 | 2065.4 | 8856.09 | 10537.8 | 0.29 | 1.25 | 11.044 | 9.241 | 1 | 1 | 2620 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1601015.464 | 79295.0141 | 6685.5437 | 7334.3894 | 71960.6248 | 9972.8979 | 0.099824 | -77008.074 | 77008.074
C | Xist Rating 164 | -69.72 | 776.587 | 150.274 | 35.6 | 2064.92 | 8847.09 | 10537.9 | 0.29 | 1.25 | 11.082 | 9.251 | 1 | 1 | 2630 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1603590.028 | 79873.374 | 6736.6758 | 7362.3832 | 72510.9908 | 9986.0176 | 0.10021 | -77109.3812 | 77109.3812
C | Xist Rating 165 | -69.69 | 777.833 | 150.274 | 35.6 | 2064.84 | 8845.77 | 10537.8 | 0.29 | 1.25 | 11.078 | 9.26 | 1 | 1 | 2640 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1606100.6917 | 80453.8306 | 6788.0027 | 7390.3771 | 73063.4535 | 9996.6674 | 0.10059 | -77191.616 | 77191.616
C | Xist Rating 166 | -69.66 | 779.336 | 150.274 | 35.6 | 2064.22 | 8834.29 | 10537.8 | 0.28 | 1.25 | 11.075 | 9.271 | 1 | 1 | 2650 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1608720.9579 | 81036.3838 | 6839.5243 | 7418.3709 | 73618.0129 | 9996.2721 | 0.10097 | -77188.5636 | 77188.5636
C | Xist Rating 167 | -69.63 | 780.676 | 150.274 | 35.6 | 2063.66 | 8823.97 | 10537.9 | 0.28 | 1.25 | 11.073 | 9.281 | 1 | 1 | 2660 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1611049.8342 | 81621.0336 | 6891.2408 | 7446.3648 | 74174.6688 | 10007.9804 | 0.10135 | -77278.9715 | 77278.9715
C | Xist Rating 168 | -69.59 | 782.064 | 150.274 | 35.6 | 2063.82 | 8826.96 | 10537.9 | 0.27 | 1.25 | 11.071 | 9.291 | 1 | 1 | 2670 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1614039.3245 | 82207.78 | 6943.152 | 7474.3586 | 74733.4214 | 10006.4381 | 0.10173 | -77267.0626 | 77267.0626
C | Xist Rating 169 | -69.53 | 783.48 | 150.275 | 35.6 | 2065.26 | 8853.36 | 10537.9 | 0.27 | 1.25 | 11.111 | 9.301 | 1 | 1 | 2680 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1618089.9048 | 82796.6231 | 6995.258 | 7502.3525 | 75294.2706 | 10019.4604 | 0.10211 | -77367.6172 | 77367.6172
C | Xist Rating 170 | -69.5 | 784.857 | 150.275 | 35.6 | 2064.82 | 8845.28 | 10537.9 | 0.27 | 1.25 | 11.107 | 9.311 | 1 | 1 | 2690 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1620588.4307 | 83387.5628 | 7047.5588 | 7530.3463 | 75857.2165 | 10031.0599 | 0.10249 | -77457.1853 | 77457.1853
C | Xist Rating 171 | -69.46 | 786.058 | 150.275 | 35.6 | 2065.47 | 8857.25 | 10538 | 0.26 | 1.25 | 11.104 | 9.32 | 1 | 1 | 2700 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1623579.2173 | 83980.5992 | 7100.0544 | 7558.3402 | 76422.259 | 10028.2138 | 0.10287 | -77435.2085 | 77435.2085
C | Xist Rating 172 | -69.37 | 787.714 | 150.275 | 35.6 | 2068.23 | 8907.98 | 10538.1 | 0.26 | 1.25 | 11.11 | 9.331 | 1 | 1 | 2710 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1629173.7262 | 84575.7321 | 7152.7448 | 7586.334 | 76989.3981 | 10041.1209 | 0.10325 | -77534.8737 | 77534.8737
C | Xist Rating 173 | -69.41 | 789.058 | 150.275 | 35.6 | 2063.1 | 8813.71 | 10538 | 0.26 | 1.25 | 11.098 | 9.34 | 1 | 1 | 2720 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 4 | E | Rod | 1627905.5598 | 85172.9617 | 7205.63 | 7614.3279 | 77558.6339 | 10051.3817 | 0.10363 | -77614.1055 | 77614.1055
C | Xist Rating 174 | -68.92 | 790.38 | 150.275 | 35.6 | 2094.07 | 9407.79 | 10538.5 | 0.25 | 1.25 | 11.185 | 9.352 | 1 | 1 | 2730 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1655111.0466 | 85772.288 | 7258.71 | 7642.3217 | 78129.9663 | 10054.2179 | 0.10402 | -77636.0059 | 77636.0059
C | Xist Rating 175 | -68.87 | 791.664 | 150.275 | 35.6 | 2094.9 | 9424.55 | 10538.5 | 0.24 | 1.25 | 11.182 | 9.361 | 1 | 1 | 2740 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1658456.9136 | 86373.7109 | 7311.9847 | 7670.3156 | 78703.3953 | 10050.992 | 0.1044 | -77611.0963 | 77611.0963
C | Xist Rating 176 | -68.77 | 793.212 | 150.275 | 35.6 | 2098.82 | 9504.2 | 10538.5 | 0.24 | 1.25 | 11.187 | 9.372 | 1 | 1 | 2750 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1664809.2098 | 86977.2304 | 7365.4543 | 7698.3094 | 79278.9209 | 10063.7664 | 0.10478 | -77709.7365 | 77709.7365
C | Xist Rating 177 | -68.68 | 794.636 | 150.275 | 35.6 | 2102.17 | 9573.4 | 10538.5 | 0.24 | 1.25 | 11.193 | 9.382 | 1 | 1 | 2760 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1670459.9601 | 87582.8465 | 7419.1186 | 7726.3033 | 79856.5432 | 10075.533 | 0.10516 | -77800.5953 | 77800.5953
C | Xist Rating 178 | -68.61 | 795.872 | 150.275 | 35.6 | 2105.19 | 9636.31 | 10538.5 | 0.23 | 1.25 | 11.196 | 9.391 | 1 | 1 | 2770 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1675461.7757 | 88190.5593 | 7472.9777 | 7754.2971 | 80436.2621 | 10072.2716 | 0.10554 | -77775.4115 | 77775.4115
C | Xist Rating 179 | -68.54 | 797.419 | 150.275 | 35.6 | 2106.62 | 9666.36 | 10538.5 | 0.23 | 1.25 | 11.238 | 9.401 | 1 | 1 | 2780 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1679858.8138 | 88800.3687 | 7527.0316 | 7782.291 | 81018.0777 | 10085.0146 | 0.10592 | -77873.8096 | 77873.8096
C | Xist Rating 180 | -68.49 | 798.828 | 150.275 | 35.6 | 2107.41 | 9682.99 | 10538.5 | 0.23 | 1.25 | 11.238 | 9.411 | 1 | 1 | 2790 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1683458.1155 | 89412.2747 | 7581.2803 | 7810.2848 | 81601.9899 | 10096.5582 | 0.1063 | -77962.9462 | 77962.9462
C | Xist Rating 181 | -68.42 | 799.802 | 150.275 | 35.6 | 2110.65 | 9751.85 | 10538.4 | 0.23 | 1.25 | 11.239 | 9.419 | 1 | 1 | 2800 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1688102.0913 | 90026.2774 | 7635.7238 | 7838.2787 | 82187.9987 | 10106.0537 | 0.10668 | -78036.2675 | 78036.2675
C | Xist Rating 182 | -68.37 | 801.547 | 150.275 | 35.6 | 2110.49 | 9748.5 | 10538.4 | 0.22 | 1.25 | 11.241 | 9.43 | 1 | 1 | 2810 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1691656.928 | 90642.3767 | 7690.3621 | 7866.2725 | 82776.1041 | 10104.5349 | 0.10706 | -78024.5403 | 78024.5403
C | Xist Rating 183 | -68.32 | 803.022 | 150.275 | 35.6 | 2110.84 | 9755.86 | 10538.4 | 0.22 | 1.25 | 11.242 | 9.44 | 1 | 1 | 2820 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1695050.9585 | 91260.5726 | 7745.1952 | 7894.2664 | 83366.3062 | 10116.0562 | 0.10744 | -78113.5049 | 78113.5049
C | Xist Rating 184 | -68.27 | 804.394 | 150.275 | 35.6 | 2111.73 | 9775.06 | 10538.4 | 0.22 | 1.25 | 11.284 | 9.45 | 1 | 1 | 2830 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1698662.9416 | 91880.8652 | 7800.223 | 7922.2603 | 83958.6049 | 10128.722 | 0.10783 | -78211.3063 | 78211.3063
C | Xist Rating 185 | -68.22 | 805.712 | 150.275 | 35.6 | 2112.63 | 9794.3 | 10538.4 | 0.21 | 1.25 | 11.284 | 9.459 | 1 | 1 | 2840 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1702171.3426 | 92503.2544 | 7855.4457 | 7950.2541 | 84553.0003 | 10124.8165 | 0.10821 | -78181.149 | 78181.149
C | Xist Rating 186 | -68.18 | 807.155 | 150.275 | 35.6 | 2113.24 | 9807.44 | 10538.4 | 0.21 | 1.25 | 11.285 | 9.469 | 1 | 1 | 2850 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1705712.2322 | 93127.7402 | 7910.8631 | 7978.248 | 85149.4923 | 10136.2905 | 0.10859 | -78269.7481 | 78269.7481
C | Xist Rating 187 | -68.13 | 808.56 | 150.275 | 35.6 | 2113.84 | 9820.56 | 10538.3 | 0.21 | 1.25 | 11.286 | 9.478 | 1 | 1 | 2860 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1709166.4704 | 93754.3227 | 7966.4753 | 8006.2418 | 85748.0809 | 10146.7261 | 0.10897 | -78350.3297 | 78350.3297
C | Xist Rating 188 | -68.08 | 809.752 | 150.275 | 35.6 | 2115.11 | 9847.86 | 10538.3 | 0.21 | 1.25 | 11.288 | 9.487 | 1 | 1 | 2870 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1712714.5527 | 94383.0018 | 8022.2824 | 8034.2357 | 86348.7661 | 10157.189 | 0.10935 | -78431.1214 | 78431.1214
C | Xist Rating 189 | -68.03 | 811.26 | 150.275 | 35.6 | 2115.59 | 9858.42 | 10538.2 | 0.2 | 1.25 | 11.326 | 9.496 | 1 | 1 | 2880 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1716293.5434 | 95013.7775 | 8078.2842 | 8062.2295 | 86951.548 | 10154.007 | 0.10973 | -78406.5502 | 78406.5502
C | Xist Rating 190 | -67.97 | 812.602 | 150.275 | 35.6 | 2116.92 | 9887.48 | 10538.2 | 0.2 | 1.25 | 11.327 | 9.506 | 1 | 1 | 2890 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1720213.4258 | 95646.6499 | 8134.4807 | 8090.2234 | 87556.4265 | 10165.4332 | 0.11011 | -78494.7808 | 78494.7808
C | Xist Rating 191 | -67.93 | 813.988 | 150.275 | 35.5 | 2118.1 | 9913.49 | 10537.8 | 0.2 | 1.25 | 11.34 | 9.515 | 1 | 1 | 2900 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1724107.9828 | 96281.6189 | 8190.8721 | 8118.2172 | 88163.4017 | 10176.1331 | 0.11049 | -78577.4027 | 78577.4027
C | Xist Rating 194 | -67.85 | 818.306 | 150.275 | 35.5 | 2117.22 | 9895.6 | 10536.7 | 0.19 | 1.25 | 11.387 | 9.542 | 1 | 1 | 2930 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1732533.8293 | 98199.1057 | 8361.215 | 8202.1988 | 89996.9069 | 10193.5018 | 0.11164 | -78711.5187 | 78711.5187
C | Xist Rating 195 | -67.83 | 819.672 | 150.275 | 35.5 | 2116.3 | 9875.66 | 10536.5 | 0.19 | 1.25 | 11.384 | 9.551 | 1 | 1 | 2940 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1734671.8536 | 98842.4612 | 8418.3855 | 8230.1926 | 90612.2686 | 10203.7429 | 0.11202 | -78790.5983 | 78790.5983
C | Xist Rating 196 | -67.83 | 821.08 | 150.275 | 35.5 | 2114.89 | 9845.71 | 10535.9 | 0.19 | 1.25 | 11.388 | 9.56 | 1 | 1 | 2950 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1736493.8812 | 99487.9134 | 8475.7509 | 8258.1865 | 91229.7269 | 10214.1595 | 0.1124 | -78871.0319 | 78871.0319
C | Xist Rating 197 | -68.08 | 822.452 | 150.275 | 35.4 | 2102.9 | 9590.01 | 10537 | 0.19 | 1.25 | 11.39 | 9.568 | 1 | 1 | 2960 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1729534.3108 | 100135.4621 | 8533.311 | 8286.1803 | 91849.2818 | 10223.4877 | 0.11278 | -78943.0624 | 78943.0624
C | Xist Rating 200 | -68 | 826.617 | 150.275 | 35.4 | 2101.08 | 9552.56 | 10536.7 | 0.18 | 1.25 | 11.422 | 9.595 | 1 | 1 | 2990 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1736788.4464 | 102090.6883 | 8707.16 | 8370.1619 | 93720.5264 | 10239.9438 | 0.11392 | -79070.1318 | 79070.1318
C | Xist Rating 201 | -67.99 | 828.048 | 150.275 | 35.3 | 2099.74 | 9525.6 | 10536 | 0.18 | 1.25 | 11.428 | 9.604 | 1 | 1 | 3000 | 152.4 | 2 | 1 | 19.05 | 1.3333 | 3 | E | Rod | 1738685.5075 | 102746.6236 | 8765.4993 | 8398.1557 | 94348.4679 | 10250.3571 | 0.1143 | -79150.5405 | 79150.5405
C | Xist Rating 202 | -96.49 | 67.682 | 150.275 | 35.8 | 2419.99 | 7601.46 | 58746 | 2.44 | 10.95 | 11.565 | 288.189 | 1 | 1 | 1000 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 163789.7632 | 14610.8032 | 973.9444 | 3079.3238 | 11531.4794 | 300548.7097 | 0.038101 | -2320757.4697 | 2320757.4697
C | Xist Rating 203 | -96.44 | 68.432 | 150.275 | 35.8 | 2428.24 | 7692.66 | 58284.9 | 2.41 | 10.85 | 11.569 | 282.851 | 1 | 1 | 1010 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 166169.3197 | 14873.3792 | 993.5206 | 3110.117 | 11763.2621 | 295002.583 | 0.038482 | -2277931.7497 | 2277931.7497
C | Xist Rating 204 | -96.18 | 73.867 | 150.276 | 35.8 | 2418.15 | 7661.5 | 54968 | 2.42 | 10.07 | 11.618 | 245.108 | 1 | 1 | 1020 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 178621.4861 | 15138.2614 | 1013.2917 | 3140.9102 | 11997.3512 | 255829.746 | 0.038863 | -1975449.4856 | 1975449.4856
C | Xist Rating 205 | -96.11 | 75.512 | 150.275 | 35.8 | 2405.19 | 7550.26 | 54179.7 | 2.33 | 9.89 | 11.466 | 237.106 | 1 | 1 | 1030 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 181620.7073 | 15405.45 | 1033.2576 | 3171.7035 | 12233.7465 | 247467.6574 | 0.039244 | -1910879.6537 | 1910879.6537
C | Xist Rating 206 | -96.05 | 76.336 | 150.275 | 35.8 | 2421.4 | 7721.4 | 53795.7 | 2.26 | 9.8 | 11.429 | 233.289 | 1 | 1 | 1040 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 184839.9904 | 15674.9449 | 1053.4182 | 3202.4967 | 12472.4481 | 243474.3697 | 0.039625 | -1880044.5452 | 1880044.5452
C | Xist Rating 207 | -95.96 | 77.86 | 150.275 | 35.8 | 2430.77 | 7835.97 | 53044.1 | 2.21 | 9.63 | 11.398 | 225.658 | 1 | 1 | 1050 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 189259.7522 | 15946.746 | 1073.7737 | 3233.29 | 12713.456 | 235531.046 | 0.040006 | -1818708.305 | 1818708.305
C | Xist Rating 208 | -95.91 | 78.665 | 150.275 | 35.8 | 2436.77 | 7908.17 | 52677.1 | 2.17 | 9.54 | 11.375 | 222.083 | 1 | 1 | 1060 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 191688.5121 | 16220.8535 | 1094.3239 | 3264.0832 | 12956.7703 | 231805.6712 | 0.040387 | -1789941.9485 | 1789941.9485
C | Xist Rating 209 | -95.64 | 84.63 | 150.275 | 35.8 | 2419.13 | 7799.74 | 49858.1 | 2.16 | 8.9 | 11.36 | 194.41 | 1 | 1 | 1070 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 204730.9719 | 16497.2672 | 1115.0689 | 3294.8764 | 13202.3908 | 203071.3592 | 0.040768 | -1568063.2075 | 1568063.2075
C | Xist Rating 210 | -95.58 | 85.841 | 150.275 | 35.8 | 2420.13 | 7823.76 | 49381.3 | 2.11 | 8.79 | 11.313 | 190.153 | 1 | 1 | 1080 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 207746.3793 | 16775.9873 | 1136.0087 | 3325.6697 | 13450.3176 | 198629.1722 | 0.041149 | -1533761.817 | 1533761.817
C | Xist Rating 211 | -95.51 | 87.445 | 150.275 | 35.8 | 2416.47 | 7803.65 | 48760.4 | 2.06 | 8.65 | 11.252 | 184.669 | 1 | 1 | 1090 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 211308.2191 | 17057.0136 | 1157.1433 | 3356.4629 | 13700.5507 | 192910.9701 | 0.04153 | -1489607.376 | 1489607.376
C | Xist Rating 212 | -95.45 | 88.624 | 150.275 | 35.8 | 2417.58 | 7828.78 | 48306.6 | 2.03 | 8.55 | 11.232 | 180.697 | 1 | 1 | 1100 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 214255.6099 | 17340.3462 | 1178.4727 | 3387.2562 | 13953.0901 | 188777.7984 | 0.041911 | -1457692.1194 | 1457692.1194
C | Xist Rating 213 | -95.42 | 89.616 | 150.274 | 35.8 | 2407.85 | 7736.4 | 48011.3 | 1.96 | 8.49 | 11.132 | 178.39 | 1 | 1 | 1110 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 215781.8856 | 17625.9852 | 1199.9969 | 3418.0494 | 14207.9358 | 186343.3313 | 0.042292 | -1438893.8097 | 1438893.8097
C | Xist Rating 214 | -95.09 | 96.155 | 150.275 | 35.8 | 2408.29 | 7822.78 | 45448.7 | 1.99 | 7.92 | 11.243 | 156.095 | 1 | 1 | 1120 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 231569.1249 | 17913.9304 | 1221.7158 | 3448.8426 | 14465.0878 | 163227.6446 | 0.042673 | -1260400.605 | 1260400.605
C | Xist Rating 215 | -95.03 | 97.102 | 150.275 | 35.8 | 2415.64 | 7909.88 | 45189.9 | 1.92 | 7.86 | 11.18 | 154.21 | 1 | 1 | 1130 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 234563.4753 | 18204.1819 | 1243.6296 | 3479.6359 | 14724.5461 | 161234.1136 | 0.043054 | -1245007.087 | 1245007.087
C | Xist Rating 216 | -94.95 | 98.776 | 150.274 | 35.8 | 2415.17 | 7922.96 | 44682.7 | 1.87 | 7.75 | 11.098 | 150.307 | 1 | 1 | 1140 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 238560.8319 | 18496.7397 | 1265.7381 | 3510.4291 | 14986.3106 | 157154.0755 | 0.043435 | -1213502.1143 | 1213502.1143
C | Xist Rating 217 | -94.85 | 100.388 | 150.274 | 35.8 | 2423 | 8026.38 | 44188.2 | 1.82 | 7.64 | 11.073 | 146.501 | 1 | 1 | 1150 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 243240.124 | 18791.6039 | 1288.0414 | 3541.2223 | 15250.3815 | 153179.9035 | 0.043816 | -1182814.6113 | 1182814.6113
C | Xist Rating 218 | -94.77 | 102.078 | 150.274 | 35.8 | 2420.69 | 8019.51 | 43705.6 | 1.77 | 7.53 | 11.022 | 142.906 | 1 | 1 | 1160 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 247099.1938 | 19088.7743 | 1310.5395 | 3572.0156 | 15516.7587 | 149422.0535 | 0.044197 | -1153797.4896 | 1153797.4896
C | Xist Rating 219 | -94.47 | 108.029 | 150.274 | 35.8 | 2420.92 | 8098.48 | 41834.4 | 1.79 | 7.13 | 11.095 | 128.594 | 1 | 1 | 1170 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 261529.5667 | 19388.251 | 1333.2324 | 3602.8088 | 15785.4422 | 134586.2228 | 0.044578 | -1039239.1379 | 1039239.1379
C | Xist Rating 220 | -94.44 | 108.595 | 150.274 | 35.8 | 2427.6 | 8178.5 | 41726.6 | 1.74 | 7.11 | 11.058 | 127.978 | 1 | 1 | 1180 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 263625.222 | 19690.034 | 1356.1201 | 3633.6021 | 16056.4319 | 133922.6623 | 0.044959 | -1034115.2994 | 1034115.2994
C | Xist Rating 221 | -94.31 | 111.804 | 150.274 | 35.8 | 2415.03 | 8074.26 | 40887.6 | 1.69 | 6.93 | 11.002 | 122.102 | 1 | 1 | 1190 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 270010.0141 | 19994.1233 | 1379.2026 | 3664.3953 | 16329.728 | 127794.5296 | 0.04534 | -986795.4832 | 986795.4832
C | Xist Rating 222 | -94.24 | 112.642 | 150.274 | 35.8 | 2426.62 | 8214.86 | 40683.5 | 1.67 | 6.88 | 11 | 120.75 | 1 | 1 | 1200 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 273339.33 | 20300.5189 | 1402.4799 | 3695.1885 | 16605.3303 | 126386.7987 | 0.045721 | -975925.3579 | 975925.3579
C | Xist Rating 223 | -94.17 | 114.402 | 150.274 | 35.8 | 2421.06 | 8170.23 | 40282.4 | 1.62 | 6.8 | 10.949 | 118.131 | 1 | 1 | 1210 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 276974.1061 | 20609.2208 | 1425.9519 | 3725.9818 | 16883.239 | 123640.8937 | 0.046102 | -954722.2073 | 954722.2073
C | Xist Rating 224 | -93.86 | 121.295 | 150.274 | 35.8 | 2408.16 | 8109.19 | 38539.1 | 1.62 | 6.43 | 10.982 | 106.328 | 1 | 1 | 1220 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 292097.7672 | 20920.229 | 1449.6188 | 3756.775 | 17163.454 | 111394.3711 | 0.046483 | -860157.8059 | 860157.8059
C | Xist Rating 225 | -93.77 | 122.905 | 150.274 | 35.8 | 2412.78 | 8180.33 | 38184.1 | 1.6 | 6.35 | 10.973 | 104.104 | 1 | 1 | 1230 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 296542.7259 | 21233.5434 | 1473.4804 | 3787.5682 | 17445.9752 | 109079.8216 | 0.046864 | -842285.4687 | 842285.4687
C | Xist Rating 226 | -93.7 | 124.654 | 150.274 | 35.8 | 2409.21 | 8157.87 | 37836.6 | 1.56 | 6.28 | 10.934 | 102.023 | 1 | 1 | 1240 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 300317.6633 | 21549.1642 | 1497.5369 | 3818.3615 | 17730.8027 | 106898.7982 | 0.047245 | -825444.1843 | 825444.1843
C | Xist Rating 227 | -93.66 | 125.637 | 150.274 | 35.7 | 2407.77 | 8150.54 | 37665.3 | 1.52 | 6.24 | 10.902 | 101.074 | 1 | 1 | 1250 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 302504.9995 | 21867.0913 | 1521.7881 | 3849.1547 | 18017.9366 | 105893.678 | 0.047626 | -817682.9124 | 817682.9124
C | Xist Rating 228 | -93.54 | 128.075 | 150.274 | 35.7 | 2407.23 | 8171.89 | 37162.4 | 1.49 | 6.14 | 10.885 | 98.015 | 1 | 1 | 1260 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 308305.9823 | 22187.3247 | 1546.2341 | 3879.948 | 18307.3767 | 102704.4366 | 0.048007 | -793056.4356 | 793056.4356
C | Xist Rating 229 | -93.22 | 134.618 | 150.274 | 35.7 | 2404.19 | 8216.96 | 35778.7 | 1.5 | 5.85 | 10.935 | 89.598 | 1 | 1 | 1270 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 323647.2494 | 22509.8643 | 1570.8749 | 3910.7412 | 18599.1231 | 93981.1315 | 0.048388 | -725697.3855 | 725697.3855
C | Xist Rating 230 | -93.14 | 136.436 | 150.274 | 35.8 | 2403.83 | 8231.04 | 35479.2 | 1.45 | 5.79 | 10.911 | 87.985 | 1 | 1 | 1280 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 327968.9499 | 22834.7103 | 1595.7105 | 3941.5344 | 18893.1759 | 92280.0191 | 0.048769 | -712561.847 | 712561.847
C | Xist Rating 231 | -93.04 | 138.202 | 150.274 | 35.7 | 2410.46 | 8328.05 | 35184.9 | 1.42 | 5.73 | 10.902 | 86.397 | 1 | 1 | 1290 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 6 | E | Rod | 333130.3929 | 23161.8626 | 1620.7408 | 3972.3277 | 19189.5349 | 90618.3089 | 0.04915 | -699730.5608 | 699730.5608
C | Xist Rating 232 | -92.9 | 140.618 | 150.274 | 35.7 | 2418.06 | 8448.41 | 34753.7 | 1.39 | 5.64 | 10.853 | 83.999 | 1 | 1 | 1300 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 340022.7611 | 23491.3211 | 1645.966 | 4003.1209 | 19488.2002 | 88111.9015 | 0.049531 | -680376.7477 | 680376.7477
C | Xist Rating 233 | -92.82 | 142.022 | 150.274 | 35.7 | 2421.88 | 8509.78 | 34542.6 | 1.36 | 5.59 | 10.835 | 82.923 | 1 | 1 | 1310 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 343960.2414 | 23823.086 | 1671.3859 | 4033.9141 | 19789.1718 | 86980.6831 | 0.049912 | -671641.779 | 671641.779
C | Xist Rating 234 | -92.51 | 148.663 | 150.274 | 35.7 | 2416.37 | 8526.76 | 33365.4 | 1.36 | 5.35 | 10.877 | 76.456 | 1 | 1 | 1320 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 359224.8133 | 24157.1571 | 1697.0007 | 4064.7074 | 20092.4497 | 80274.6987 | 0.050293 | -619859.9451 | 619859.9451
C | Xist Rating 235 | -92.4 | 151.296 | 150.274 | 35.7 | 2410.42 | 8481.91 | 32982.3 | 1.33 | 5.28 | 10.836 | 74.544 | 1 | 1 | 1330 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 364686.9043 | 24493.5345 | 1722.8102 | 4095.5006 | 20398.0339 | 78273.0161 | 0.050674 | -604403.4823 | 604403.4823
C | Xist Rating 236 | -92.28 | 153.828 | 150.274 | 35.7 | 2411 | 8517.92 | 32609.1 | 1.3 | 5.2 | 10.821 | 72.679 | 1 | 1 | 1340 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 370879.308 | 24832.2183 | 1748.8145 | 4126.2939 | 20705.9244 | 76321.9794 | 0.051055 | -589338.0942 | 589338.0942
C | Xist Rating 237 | -92.2 | 155.248 | 150.274 | 35.7 | 2414.21 | 8572.76 | 32426 | 1.27 | 5.16 | 10.804 | 71.831 | 1 | 1 | 1350 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 374801.2741 | 25173.2083 | 1775.0136 | 4157.0871 | 21016.1212 | 75426.6875 | 0.051436 | -582424.8871 | 582424.8871
C | Xist Rating 238 | -92.12 | 156.033 | 150.274 | 35.7 | 2430.89 | 8797.15 | 32304.8 | 1.26 | 5.14 | 10.815 | 71.237 | 1 | 1 | 1360 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 379299.0594 | 25516.5046 | 1801.4075 | 4187.8803 | 21328.6243 | 74810.2285 | 0.051817 | -577664.7542 | 577664.7542
C | Xist Rating 239 | -91.73 | 165.703 | 150.274 | 35.7 | 2402.78 | 8556.26 | 30904.3 | 1.25 | 4.86 | 10.831 | 64.338 | 1 | 1 | 1370 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 398147.8543 | 25862.1073 | 1827.9962 | 4218.6736 | 21643.4337 | 67646.3228 | 0.052198 | -522346.9736 | 522346.9736
C | Xist Rating 240 | -91.69 | 166.75 | 150.274 | 35.7 | 2402.7 | 8564.96 | 30795.4 | 1.23 | 4.84 | 10.812 | 63.902 | 1 | 1 | 1380 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 400650.225 | 26210.0162 | 1854.7797 | 4249.4668 | 21960.5494 | 67184.7609 | 0.052579 | -518782.9149 | 518782.9149
C | Xist Rating 241 | -91.59 | 168.978 | 150.274 | 35.7 | 2402.29 | 8583.77 | 30528.3 | 1.2 | 4.79 | 10.797 | 62.715 | 1 | 1 | 1390 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 405934.1596 | 26560.2314 | 1881.7579 | 4280.26 | 22279.9714 | 65936.6932 | 0.05296 | -509145.6671 | 509145.6671
C | Xist Rating 242 | -91.49 | 171.202 | 150.274 | 35.7 | 2401.22 | 8594.07 | 30266.2 | 1.18 | 4.73 | 10.782 | 61.562 | 1 | 1 | 1400 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 411093.6664 | 26912.7529 | 1908.931 | 4311.0533 | 22601.6996 | 64730.4502 | 0.053341 | -499831.3786 | 499831.3786
C | Xist Rating 243 | -91.37 | 173.794 | 150.274 | 35.7 | 2400.09 | 8608.55 | 29958.5 | 1.16 | 4.67 | 10.771 | 60.204 | 1 | 1 | 1410 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 417121.2415 | 27267.5807 | 1936.2988 | 4341.8465 | 22925.7342 | 63311.4368 | 0.053722 | -488874.133 | 488874.133
C | Xist Rating 244 | -91.04 | 180.931 | 150.274 | 35.7 | 2395.12 | 8633.21 | 29053 | 1.17 | 4.49 | 10.816 | 56.106 | 1 | 1 | 1420 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 433351.4567 | 27624.7148 | 1963.8614 | 4372.6398 | 23252.0751 | 59071.4779 | 0.054103 | -456134.2943 | 456134.2943
C | Xist Rating 245 | -90.98 | 182.592 | 150.274 | 35.7 | 2390.66 | 8589.73 | 28911.8 | 1.13 | 4.47 | 10.789 | 55.594 | 1 | 1 | 1430 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 436515.3907 | 27984.1552 | 1991.6188 | 4403.433 | 23580.7222 | 58515.7516 | 0.054484 | -451843.1229 | 451843.1229
C | Xist Rating 246 | -90.83 | 185.969 | 150.274 | 35.7 | 2387.8 | 8590.8 | 28543 | 1.12 | 4.39 | 10.779 | 54.048 | 1 | 1 | 1440 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 444056.7782 | 28345.9019 | 2019.571 | 4434.2262 | 23911.6757 | 56908.0109 | 0.054865 | -439428.5755 | 439428.5755
C | Xist Rating 247 | -90.74 | 188.232 | 150.274 | 35.7 | 2386.86 | 8602.21 | 28317.8 | 1.1 | 4.35 | 10.767 | 53.15 | 1 | 1 | 1450 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 449283.4315 | 28709.9549 | 2047.718 | 4465.0195 | 24244.9355 | 55965.981 | 0.055246 | -432154.4706 | 432154.4706
C | Xist Rating 248 | -90.64 | 189.534 | 150.274 | 35.7 | 2396.9 | 8748.66 | 28185.1 | 1.08 | 4.33 | 10.772 | 52.624 | 1 | 1 | 1460 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 454294.0446 | 29076.3142 | 2076.0598 | 4495.8127 | 24580.5015 | 55411.3005 | 0.055627 | -427871.3742 | 427871.3742
C | Xist Rating 249 | -90.32 | 197.883 | 150.274 | 35.7 | 2376.78 | 8581.63 | 27311.1 | 1.08 | 4.16 | 10.791 | 49.047 | 1 | 1 | 1470 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 470324.3567 | 29444.9798 | 2104.5964 | 4526.6059 | 24918.3739 | 51703.1585 | 0.056008 | -399238.0851 | 399238.0851
C | Xist Rating 250 | -90.17 | 200.519 | 150.274 | 35.7 | 2381.99 | 8678.32 | 27067.4 | 1.06 | 4.11 | 10.789 | 48.118 | 1 | 1 | 1480 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 477634.2528 | 29815.9517 | 2133.3277 | 4557.3992 | 25258.5525 | 50729.1592 | 0.056389 | -391717.1207 | 391717.1207
C | Xist Rating 251 | -90.03 | 202.784 | 150.274 | 35.7 | 2390.18 | 8812.5 | 26867.8 | 1.04 | 4.07 | 10.787 | 47.379 | 1 | 1 | 1490 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 484690.2611 | 30189.2299 | 2162.2539 | 4588.1924 | 25601.0374 | 49952.2846 | 0.05677 | -385718.3008 | 385718.3008
C | Xist Rating 252 | -89.92 | 205.14 | 150.274 | 35.7 | 2392.63 | 8870.71 | 26671.4 | 1.01 | 4.03 | 10.779 | 46.67 | 1 | 1 | 1500 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 490824.1182 | 30564.8143 | 2191.3748 | 4618.9857 | 25945.8287 | 49198.716 | 0.057151 | -379899.4441 | 379899.4441
C | Xist Rating 253 | -89.77 | 207.803 | 150.274 | 35.7 | 2398.23 | 8978.48 | 26440.2 | 1 | 3.99 | 10.777 | 45.819 | 1 | 1 | 1510 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 498359.3887 | 30942.7051 | 2220.6906 | 4649.7789 | 26292.9262 | 48312.4027 | 0.057532 | -373055.5674 | 373055.5674
C | Xist Rating 254 | -89.39 | 215.836 | 150.274 | 35.7 | 2397.2 | 9068.29 | 25682.3 | 1 | 3.85 | 10.826 | 42.925 | 1 | 1 | 1520 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 517402.0592 | 31322.9022 | 2250.2011 | 4680.5721 | 26642.33 | 45315.1576 | 0.057913 | -349911.6349 | 349911.6349
C | Xist Rating 255 | -89.28 | 218.843 | 150.274 | 35.7 | 2389.51 | 8989.5 | 25469.6 | 0.98 | 3.81 | 10.805 | 42.223 | 1 | 1 | 1530 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 522927.5369 | 31705.4055 | 2279.9064 | 4711.3654 | 26994.0401 | 44574.7237 | 0.058294 | -344194.2006 | 344194.2006
C | Xist Rating 256 | -89.19 | 220.419 | 150.274 | 35.7 | 2394.49 | 9075.57 | 25365 | 0.96 | 3.79 | 10.798 | 41.897 | 1 | 1 | 1540 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 527791.0913 | 32090.2152 | 2309.8065 | 4742.1586 | 27348.0566 | 44225.5384 | 0.058675 | -341497.8843 | 341497.8843
C | Xist Rating 257 | -88.99 | 224.707 | 150.274 | 35.7 | 2393.07 | 9106.5 | 25022.5 | 0.94 | 3.72 | 10.794 | 40.695 | 1 | 1 | 1550 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 537739.5805 | 32477.3311 | 2339.9013 | 4772.9518 | 27704.3793 | 42966.6441 | 0.059056 | -331777.0363 | 331777.0363
C | Xist Rating 258 | -88.88 | 226.059 | 150.274 | 35.7 | 2406.61 | 9321.82 | 24921.6 | 0.93 | 3.7 | 10.799 | 40.364 | 1 | 1 | 1560 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 544035.85 | 32866.7534 | 2370.191 | 4803.7451 | 28063.0083 | 42620.2265 | 0.059437 | -329102.0913 | 329102.0913
C | Xist Rating 259 | -88.51 | 235.893 | 150.274 | 35.7 | 2384.22 | 9113.39 | 24163.3 | 0.92 | 3.56 | 10.823 | 37.749 | 1 | 1 | 1570 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 562420.8085 | 33258.4819 | 2400.6755 | 4834.5383 | 28423.9436 | 39903.009 | 0.059818 | -308120.4581 | 308120.4581
C | Xist Rating 260 | -88.38 | 238.278 | 150.274 | 35.7 | 2388.43 | 9201.15 | 24008.5 | 0.91 | 3.53 | 10.817 | 37.269 | 1 | 1 | 1580 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 569110.3235 | 33652.5168 | 2431.3547 | 4865.3316 | 28787.1852 | 39400.9411 | 0.0602 | -304243.6234 | 304243.6234
C | Xist Rating 261 | -88.27 | 240.698 | 150.274 | 35.7 | 2389.37 | 9241.11 | 23856 | 0.89 | 3.5 | 10.81 | 36.803 | 1 | 1 | 1590 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 575116.5803 | 34048.8579 | 2462.2288 | 4896.1248 | 29152.7331 | 38905.5503 | 0.060581 | -300418.347 | 300418.347
C | Xist Rating 262 | -88.11 | 243.76 | 150.274 | 35.7 | 2393.16 | 9335.26 | 23646.1 | 0.88 | 3.46 | 10.809 | 36.132 | 1 | 1 | 1600 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 583356.6816 | 34447.5053 | 2493.2976 | 4926.918 | 29520.5873 | 38205.2144 | 0.060962 | -295010.5389 | 295010.5389
C | Xist Rating 263 | -88.03 | 245.532 | 150.274 | 35.7 | 2392.5 | 9341.12 | 23557.4 | 0.86 | 3.45 | 10.798 | 35.9 | 1 | 1 | 1610 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 587435.31 | 34848.4591 | 2524.5612 | 4957.7113 | 29890.7478 | 37952.2626 | 0.061343 | -293057.3116 | 293057.3116
C | Xist Rating 264 | -87.58 | 256.382 | 150.274 | 35.7 | 2378.87 | 9273.18 | 22805.8 | 0.86 | 3.31 | 10.836 | 33.471 | 1 | 1 | 1620 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 609899.4483 | 35251.7191 | 2556.0196 | 4988.5045 | 30263.2146 | 35436.2856 | 0.061724 | -273629.6039 | 273629.6039
C | Xist Rating 265 | -87.49 | 257.809 | 150.274 | 35.7 | 2386.12 | 9400.36 | 22723.9 | 0.85 | 3.29 | 10.834 | 33.241 | 1 | 1 | 1630 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 615163.2111 | 35657.2854 | 2587.6728 | 5019.2978 | 30637.9876 | 35193.5667 | 0.062105 | -271755.393 | 271755.393
C | Xist Rating 266 | -87.38 | 260.376 | 150.274 | 35.7 | 2384.31 | 9398.84 | 22589.2 | 0.84 | 3.27 | 10.824 | 32.87 | 1 | 1 | 1640 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 620817.1006 | 36065.158 | 2619.5208 | 5050.091 | 31015.067 | 34803.8298 | 0.062486 | -268745.948 | 268745.948
C | Xist Rating 267 | -87.25 | 263.796 | 150.274 | 35.6 | 2380.42 | 9375.59 | 22403.6 | 0.82 | 3.24 | 10.814 | 32.344 | 1 | 1 | 1650 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 627945.2743 | 36475.3369 | 2651.5635 | 5080.8842 | 31394.4527 | 34245.0376 | 0.062867 | -264431.1033 | 264431.1033
C | Xist Rating 268 | -87.1 | 266.971 | 150.274 | 35.6 | 2381.08 | 9423.16 | 22221.2 | 0.81 | 3.2 | 10.811 | 31.815 | 1 | 1 | 1660 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 635679.3087 | 36887.8221 | 2683.8011 | 5111.6775 | 31776.1447 | 33691.4194 | 0.063248 | -260156.21 | 260156.21
C | Xist Rating 269 | -86.7 | 276.849 | 150.274 | 35.6 | 2368.68 | 9353.34 | 21633.7 | 0.81 | 3.1 | 10.846 | 30.068 | 1 | 1 | 1670 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 655766.6893 | 37302.6136 | 2716.2334 | 5142.4707 | 32160.1429 | 31883.2101 | 0.063629 | -246193.6973 | 246193.6973
C | Xist Rating 270 | -86.61 | 278.388 | 150.274 | 35.6 | 2373.55 | 9445.7 | 21560.8 | 0.8 | 3.08 | 10.842 | 29.886 | 1 | 1 | 1680 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 660767.8374 | 37719.7114 | 2748.8606 | 5173.2639 | 32546.4475 | 31689.7328 | 0.06401 | -244699.7164 | 244699.7164
C | Xist Rating 271 | -86.45 | 282.708 | 150.274 | 35.6 | 2367.83 | 9402.89 | 21346.5 | 0.78 | 3.04 | 10.832 | 29.308 | 1 | 1 | 1690 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 669404.4836 | 38139.1155 | 2781.6825 | 5204.0572 | 32935.0583 | 31076.3513 | 0.064391 | -239963.3472 | 239963.3472
C | Xist Rating 272 | -86.31 | 285.528 | 150.274 | 35.6 | 2369.8 | 9465.86 | 21206.2 | 0.77 | 3.02 | 10.828 | 28.934 | 1 | 1 | 1700 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 676644.2544 | 38560.8259 | 2814.6992 | 5234.8504 | 33325.9755 | 30683.2512 | 0.064772 | -236927.9326 | 236927.9326
C | Xist Rating 273 | -86.17 | 288.896 | 150.274 | 35.6 | 2367.53 | 9466.75 | 21045.2 | 0.76 | 2.99 | 10.822 | 28.511 | 1 | 1 | 1710 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 683969.9469 | 38984.8426 | 2847.9107 | 5265.6437 | 33719.1989 | 30239.0545 | 0.065153 | -233497.963 | 233497.963
C | Xist Rating 274 | -85.8 | 298.077 | 150.274 | 35.6 | 2357.72 | 9423.19 | 20567.6 | 0.76 | 2.9 | 10.856 | 27.193 | 1 | 1 | 1720 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 702782.1044 | 39411.1656 | 2881.317 | 5296.4369 | 34114.7287 | 28875.9925 | 0.065534 | -222972.7596 | 222972.7596
C | Xist Rating 275 | -85.63 | 302.267 | 150.274 | 35.6 | 2354.68 | 9421.58 | 20374.8 | 0.75 | 2.87 | 10.848 | 26.697 | 1 | 1 | 1730 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 711742.0596 | 39839.7949 | 2914.9181 | 5327.2301 | 34512.5647 | 28355.7118 | 0.065915 | -218955.2902 | 218955.2902
C | Xist Rating 276 | -85.54 | 304.326 | 150.274 | 35.6 | 2355.43 | 9454.58 | 20290.4 | 0.74 | 2.85 | 10.841 | 26.499 | 1 | 1 | 1740 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 716818.5902 | 40270.7304 | 2948.714 | 5358.0234 | 34912.7071 | 28144.8711 | 0.066296 | -217327.2345 | 217327.2345
C | Xist Rating 277 | -85.39 | 308.275 | 150.274 | 35.6 | 2351.15 | 9427.49 | 20123.8 | 0.73 | 2.82 | 10.833 | 26.09 | 1 | 1 | 1750 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 724800.7662 | 40703.9723 | 2982.7046 | 5388.8166 | 35315.1557 | 27714.7591 | 0.066677 | -214006.0237 | 214006.0237
C | Xist Rating 278 | -85.28 | 311.212 | 150.274 | 35.6 | 2347.56 | 9401.02 | 20001.1 | 0.72 | 2.8 | 10.826 | 25.794 | 1 | 1 | 1760 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 730588.8427 | 41139.5205 | 3016.8901 | 5419.6098 | 35719.9106 | 27401.9645 | 0.067058 | -211590.7061 | 211590.7061
C | Xist Rating 279 | -84.85 | 322.078 | 150.274 | 35.6 | 2336.77 | 9358.67 | 19497.6 | 0.72 | 2.71 | 10.861 | 24.491 | 1 | 1 | 1770 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 752622.2081 | 41577.3749 | 3051.2703 | 5450.4031 | 36126.9718 | 26054.2943 | 0.067439 | -201184.3547 | 201184.3547
C | Xist Rating 280 | -84.73 | 325.124 | 150.274 | 35.6 | 2335.29 | 9365.52 | 19382.9 | 0.71 | 2.69 | 10.853 | 24.231 | 1 | 1 | 1780 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 759258.826 | 42017.5357 | 3085.8453 | 5481.1963 | 36536.3394 | 25778.671 | 0.06782 | -199056.0647 | 199056.0647
C | Xist Rating 281 | -84.65 | 326.922 | 150.274 | 35.6 | 2335.88 | 9390.24 | 19326.4 | 0.7 | 2.68 | 10.846 | 24.12 | 1 | 1 | 1790 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 763650.5614 | 42460.0027 | 3120.6151 | 5511.9896 | 36948.0132 | 25657.7506 | 0.068201 | -198122.3487 | 198122.3487
C | Xist Rating 282 | -84.51 | 332.052 | 150.274 | 35.6 | 2323.24 | 9243.05 | 19123 | 0.69 | 2.65 | 10.922 | 23.629 | 1 | 1 | 1800 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 771436.4885 | 42904.7761 | 3155.5797 | 5542.7828 | 37361.9933 | 25146.7311 | 0.068582 | -194176.3917 | 194176.3917
C | Xist Rating 283 | -84.4 | 334.97 | 150.274 | 35.6 | 2320.76 | 9233.26 | 19013.6 | 0.68 | 2.63 | 10.921 | 23.381 | 1 | 1 | 1810 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 777384.9772 | 43351.8557 | 3190.7391 | 5573.576 | 37778.2797 | 24883.6451 | 0.068963 | -192144.9112 | 192144.9112
C | Xist Rating 284 | -83.96 | 346.096 | 150.274 | 35.6 | 2310.94 | 9202.16 | 18564.2 | 0.67 | 2.55 | 10.958 | 22.3 | 1 | 1 | 1820 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 799807.0902 | 43801.2417 | 3226.0933 | 5604.3693 | 38196.8724 | 23757.47 | 0.069344 | -183448.8861 | 183448.8861
C | Xist Rating 285 | -83.82 | 344.292 | 150.274 | 35.6 | 2347.12 | 9782.13 | 18632.5 | 0.66 | 2.56 | 10.988 | 22.474 | 1 | 1 | 1830 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 808094.639 | 44252.9339 | 3261.6423 | 5635.1625 | 38617.7714 | 23934.0951 | 0.069725 | -184812.7384 | 184812.7384
C | Xist Rating 286 | -83.65 | 346.638 | 150.274 | 35.6 | 2355.95 | 9965.67 | 18546.7 | 0.66 | 2.55 | 10.995 | 22.284 | 1 | 1 | 1840 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 816661.7961 | 44706.9324 | 3297.386 | 5665.9557 | 39040.9767 | 23740.4122 | 0.070106 | -183317.1701 | 183317.1701
C | Xist Rating 287 | -83.49 | 350.704 | 150.274 | 35.6 | 2352.81 | 9954.88 | 18410.8 | 0.64 | 2.52 | 10.99 | 21.992 | 1 | 1 | 1850 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 825139.8782 | 45163.2373 | 3333.3246 | 5696.749 | 39466.4883 | 23421.9227 | 0.070487 | -180857.879 | 180857.879
C | Xist Rating 288 | -83.33 | 355.236 | 150.274 | 35.6 | 2347.28 | 9906.85 | 18260.5 | 0.63 | 2.5 | 10.982 | 21.669 | 1 | 1 | 1860 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 833838.3581 | 45621.8484 | 3369.4579 | 5727.5422 | 39894.3062 | 23080.0576 | 0.070868 | -178218.0866 | 178218.0866
C | Xist Rating 289 | -82.92 | 365.393 | 150.274 | 35.6 | 2339.82 | 9904.66 | 17881 | 0.64 | 2.43 | 11.021 | 20.799 | 1 | 1 | 1870 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 854953.8493 | 46082.7658 | 3405.7861 | 5758.3355 | 40324.4303 | 22190.9627 | 0.071249 | -171352.7321 | 171352.7321
C | Xist Rating 290 | -82.75 | 369.911 | 150.274 | 35.6 | 2335.2 | 9871.97 | 17740.3 | 0.63 | 2.41 | 11.01 | 20.508 | 1 | 1 | 1880 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 863816.1672 | 46545.9895 | 3442.309 | 5789.1287 | 40756.8608 | 21882.0499 | 0.07163 | -168967.3894 | 168967.3894
C | Xist Rating 291 | -82.59 | 372.878 | 150.274 | 35.6 | 2339 | 9973.91 | 17648 | 0.62 | 2.39 | 11.015 | 20.321 | 1 | 1 | 1890 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 872161.642 | 47011.5195 | 3479.0267 | 5819.9219 | 41191.5976 | 21681.895 | 0.072011 | -167421.8462 | 167421.8462
C | Xist Rating 292 | -82.47 | 376.302 | 150.274 | 35.6 | 2335.59 | 9945.69 | 17556.5 | 0.61 | 2.38 | 11.008 | 20.15 | 1 | 1 | 1900 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 878887.1882 | 47479.3558 | 3515.9392 | 5850.7152 | 41628.6407 | 21497.6282 | 0.072392 | -165998.9867 | 165998.9867
C | Xist Rating 293 | -82.33 | 379.447 | 150.274 | 35.6 | 2335.83 | 9983.44 | 17466.5 | 0.59 | 2.36 | 11.013 | 19.974 | 1 | 1 | 1910 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 886323.686 | 47949.4984 | 3553.0464 | 5881.5084 | 42067.99 | 21299.266 | 0.072773 | -164467.286 | 164467.286
C | Xist Rating 294 | -81.84 | 391.81 | 150.274 | 35.6 | 2325.92 | 9961.27 | 17051.8 | 0.6 | 2.29 | 11.053 | 19.076 | 1 | 1 | 1920 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 911318.7152 | 48421.9473 | 3590.3485 | 5912.3016 | 42509.6457 | 20381.1506 | 0.073154 | -157377.8426 | 157377.8426
C | Xist Rating 295 | -81.67 | 396.405 | 150.274 | 35.6 | 2321.83 | 9936.28 | 16925.2 | 0.59 | 2.27 | 11.047 | 18.833 | 1 | 1 | 1930 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 920385.0211 | 48896.7025 | 3627.8454 | 5943.0949 | 42953.6076 | 20121.8998 | 0.073535 | -155375.9766 | 155375.9766
C | Xist Rating 296 | -81.57 | 397.842 | 150.274 | 35.6 | 2328.85 | 10083.3 | 16883.4 | 0.58 | 2.26 | 11.058 | 18.757 | 1 | 1 | 1940 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 926514.3417 | 49373.764 | 3665.537 | 5973.8881 | 43399.8759 | 20036.8438 | 0.073916 | -154719.1969 | 154719.1969
C | Xist Rating 297 | -81.42 | 402.478 | 150.274 | 35.6 | 2321.24 | 9986.58 | 16773.4 | 0.57 | 2.24 | 11.054 | 18.562 | 1 | 1 | 1950 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 934248.0327 | 49853.1318 | 3703.4235 | 6004.6814 | 43848.4505 | 19827.3467 | 0.074297 | -153101.5152 | 153101.5152
C | Xist Rating 298 | -81.23 | 407.42 | 150.274 | 35.6 | 2317.36 | 9970.3 | 16638.1 | 0.56 | 2.22 | 11.057 | 18.301 | 1 | 1 | 1960 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 944138.8112 | 50334.8059 | 3741.5047 | 6035.4746 | 44299.3313 | 19549.5588 | 0.074678 | -150956.5113 | 150956.5113
C | Xist Rating 299 | -80.79 | 418.674 | 150.274 | 35.6 | 2309.5 | 9965.02 | 16304.2 | 0.56 | 2.16 | 11.098 | 17.625 | 1 | 1 | 1970 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 966927.603 | 50818.7863 | 3779.7807 | 6066.2678 | 44752.5184 | 18852.3369 | 0.075059 | -145572.7482 | 145572.7482
C | Xist Rating 300 | -80.65 | 422.267 | 150.274 | 35.6 | 2308.75 | 9989.62 | 16215.1 | 0.56 | 2.15 | 11.094 | 17.465 | 1 | 1 | 1980 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 974908.9363 | 51305.0729 | 3818.2515 | 6097.0611 | 45208.0119 | 18688.7641 | 0.07544 | -144309.6827 | 144309.6827
C | Xist Rating 301 | -80.48 | 427.056 | 150.274 | 35.6 | 2304.02 | 9950.71 | 16102.2 | 0.55 | 2.13 | 11.089 | 17.265 | 1 | 1 | 1990 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 983945.5651 | 51793.6659 | 3856.9171 | 6127.8543 | 45665.8116 | 18473.708 | 0.075821 | -142649.0761 | 142649.0761
C | Xist Rating 302 | -80.32 | 430.774 | 150.274 | 35.6 | 2304.18 | 9991.94 | 16015.7 | 0.54 | 2.12 | 11.089 | 17.115 | 1 | 1 | 2000 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 992580.8353 | 52284.5652 | 3895.7775 | 6158.6475 | 46125.9176 | 18310.7258 | 0.076202 | -141390.5712 | 141390.5712
C | Xist Rating 303 | -80.21 | 433.593 | 150.274 | 35.6 | 2302.8 | 9993.61 | 15954.5 | 0.53 | 2.11 | 11.086 | 17.015 | 1 | 1 | 2010 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 998477.9604 | 52777.7707 | 3934.8326 | 6189.4408 | 46588.33 | 18199.4259 | 0.076583 | -140531.143 | 140531.143
C | Xist Rating 304 | -79.73 | 446.404 | 150.274 | 35.6 | 2292.84 | 9961.56 | 15615.5 | 0.53 | 2.05 | 11.121 | 16.368 | 1 | 1 | 2020 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1023532.9474 | 53273.2826 | 3974.0826 | 6220.234 | 47053.0486 | 17531.8308 | 0.076964 | -135376.1502 | 135376.1502
C | Xist Rating 305 | -79.54 | 451.289 | 150.274 | 35.6 | 2290.71 | 9975.64 | 15500.5 | 0.53 | 2.03 | 11.115 | 16.165 | 1 | 1 | 2030 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1033772.2252 | 53771.1008 | 4013.5273 | 6251.0273 | 47520.0735 | 17323.3683 | 0.077345 | -133766.4579 | 133766.4579
C | Xist Rating 306 | -79.41 | 454.913 | 150.274 | 35.6 | 2287.19 | 9941.47 | 15432.4 | 0.52 | 2.02 | 11.111 | 16.061 | 1 | 1 | 2040 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1040472.4645 | 54271.2252 | 4053.1669 | 6281.8205 | 47989.4047 | 17207.651 | 0.077726 | -132872.92 | 132872.92
C | Xist Rating 307 | -79.29 | 457.722 | 150.274 | 35.6 | 2288.41 | 9997.24 | 15364.8 | 0.51 | 2.01 | 11.107 | 15.944 | 1 | 1 | 2050 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1047455.602 | 54773.656 | 4093.0012 | 6312.6137 | 48461.0422 | 17078.3391 | 0.078107 | -131874.4079 | 131874.4079
C | Xist Rating 308 | -79.12 | 462.906 | 150.274 | 35.6 | 2282.09 | 9925.69 | 15264.9 | 0.5 | 1.99 | 11.103 | 15.786 | 1 | 1 | 2060 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1056393.1535 | 55278.393 | 4133.0303 | 6343.407 | 48934.986 | 16906.3548 | 0.078488 | -130546.3902 | 130546.3902
C | Xist Rating 309 | -78.61 | 476.719 | 150.274 | 35.6 | 2271.71 | 9891.68 | 14936.7 | 0.5 | 1.94 | 11.14 | 15.195 | 1 | 1 | 2070 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1082967.3195 | 55785.4363 | 4173.2542 | 6374.2002 | 49411.2361 | 16296.8072 | 0.078869 | -125839.6254 | 125839.6254
C | Xist Rating 310 | -78.49 | 480.144 | 150.274 | 35.6 | 2269.64 | 9884.12 | 14874 | 0.5 | 1.93 | 11.135 | 15.101 | 1 | 1 | 2080 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1089754.0282 | 56294.786 | 4213.6729 | 6404.9934 | 49889.7925 | 16201.452 | 0.07925 | -125103.3178 | 125103.3178
C | Xist Rating 311 | -78.34 | 484.41 | 150.274 | 35.6 | 2266.93 | 9874.99 | 14791.3 | 0.49 | 1.91 | 11.131 | 14.971 | 1 | 1 | 2090 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1098123.5613 | 56806.4419 | 4254.2864 | 6435.7867 | 50370.6552 | 16058.3275 | 0.079631 | -123998.1487 | 123998.1487
C | Xist Rating 312 | -78.19 | 488.684 | 150.274 | 35.6 | 2264.15 | 9864.27 | 14709.7 | 0.49 | 1.9 | 11.127 | 14.843 | 1 | 1 | 2100 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1106453.8786 | 57320.4041 | 4295.0947 | 6466.5799 | 50853.8242 | 15927.6601 | 0.080012 | -122989.1691 | 122989.1691
C | Xist Rating 313 | -78.06 | 492.496 | 150.274 | 35.6 | 2261.76 | 9855.71 | 14639 | 0.48 | 1.89 | 11.123 | 14.736 | 1 | 1 | 2110 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1113907.753 | 57836.6726 | 4336.0977 | 6497.3732 | 51339.2995 | 15808.2792 | 0.080393 | -122067.3414 | 122067.3414
C | Xist Rating 314 | -77.57 | 505.746 | 150.275 | 35.6 | 2252.01 | 9818.52 | 14359.3 | 0.48 | 1.84 | 11.162 | 14.262 | 1 | 1 | 2120 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1138945.0495 | 58355.2475 | 4377.2956 | 6528.1664 | 51827.0811 | 15320.2031 | 0.080774 | -118298.547 | 118298.547
C | Xist Rating 315 | -77.39 | 510.975 | 150.275 | 35.6 | 2248.25 | 9798.51 | 14264 | 0.47 | 1.83 | 11.157 | 14.115 | 1 | 1 | 2130 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1148799.5437 | 58876.1286 | 4418.6882 | 6558.9596 | 52317.1689 | 15159.0639 | 0.081155 | -117054.2734 | 117054.2734
C | Xist Rating 316 | -77.23 | 516.229 | 150.275 | 35.6 | 2242.86 | 9747.56 | 14170 | 0.47 | 1.81 | 11.153 | 13.973 | 1 | 1 | 2140 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1157829.3749 | 59399.316 | 4460.2756 | 6589.7529 | 52809.5631 | 15013.7673 | 0.081536 | -115932.3315 | 115932.3315
C | Xist Rating 317 | -77.13 | 519.198 | 150.274 | 35.6 | 2241.6 | 9749.07 | 14123.6 | 0.46 | 1.81 | 11.149 | 13.911 | 1 | 1 | 2150 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1163834.2368 | 59924.8097 | 4502.0578 | 6620.5461 | 53304.2636 | 14940.8043 | 0.081917 | -115368.9303 | 115368.9303
C | Xist Rating 318 | -76.99 | 522.955 | 150.274 | 35.6 | 2240.01 | 9754.42 | 14059.1 | 0.46 | 1.79 | 11.145 | 13.817 | 1 | 1 | 2160 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1171424.4296 | 60452.6097 | 4544.0348 | 6651.3394 | 53801.2703 | 14845.3061 | 0.082298 | -114631.5188 | 114631.5188
C | Xist Rating 319 | -76.48 | 537.421 | 150.275 | 35.6 | 2228.9 | 9697.28 | 13786 | 0.46 | 1.75 | 11.184 | 13.38 | 1 | 1 | 2170 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1197857.6669 | 60982.716 | 4586.2066 | 6682.1326 | 54300.5834 | 14395.5254 | 0.082679 | -111158.431 | 111158.431
C | Xist Rating 320 | -76.3 | 542.424 | 150.275 | 35.6 | 2226.8 | 9707.4 | 13699 | 0.45 | 1.74 | 11.179 | 13.25 | 1 | 1 | 2180 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1207869.7632 | 61515.1286 | 4628.5732 | 6712.9258 | 54802.2027 | 14251.678 | 0.08306 | -110047.6799 | 110047.6799
C | Xist Rating 321 | -76.17 | 546.415 | 150.275 | 35.6 | 2224.57 | 9699.83 | 13638.9 | 0.45 | 1.73 | 11.174 | 13.169 | 1 | 1 | 2190 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1215538.4165 | 62049.8475 | 4671.1346 | 6743.7191 | 55306.1284 | 14169.5937 | 0.083441 | -109413.8466 | 109413.8466
C | Xist Rating 322 | -76.03 | 550.813 | 150.275 | 35.6 | 2220.64 | 9659.91 | 13579.4 | 0.44 | 1.72 | 11.172 | 13.094 | 1 | 1 | 2200 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1223157.3803 | 62586.8726 | 4713.8907 | 6774.5123 | 55812.3603 | 14082.8543 | 0.083822 | -108744.0679 | 108744.0679
C | Xist Rating 323 | -75.85 | 556.074 | 150.275 | 35.6 | 2217.57 | 9650.81 | 13495.4 | 0.43 | 1.7 | 11.169 | 12.974 | 1 | 1 | 2210 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1233133.0202 | 63126.2041 | 4756.8417 | 6805.3055 | 56320.8986 | 13949.2429 | 0.084203 | -107712.3559 | 107712.3559
C | Xist Rating 324 | -75.35 | 570.404 | 150.275 | 35.6 | 2208.28 | 9623.74 | 13246.2 | 0.43 | 1.66 | 11.208 | 12.593 | 1 | 1 | 2220 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1259611.7451 | 63667.8419 | 4799.9874 | 6836.0988 | 56831.7431 | 13557.3965 | 0.084584 | -104686.6225 | 104686.6225
C | Xist Rating 325 | -75.19 | 574.641 | 150.275 | 35.6 | 2207.33 | 9644.51 | 13182.6 | 0.43 | 1.65 | 11.203 | 12.506 | 1 | 1 | 2230 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1268422.3185 | 64211.786 | 4843.3279 | 6866.892 | 57344.894 | 13468.9926 | 0.084965 | -104003.9904 | 104003.9904
C | Xist Rating 326 | -75.02 | 579.794 | 150.275 | 35.6 | 2203.67 | 9618.42 | 13111.8 | 0.42 | 1.64 | 11.199 | 12.414 | 1 | 1 | 2240 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1277674.644 | 64758.0363 | 4886.8633 | 6897.6853 | 57860.3511 | 13364.1927 | 0.085346 | -103194.7539 | 103194.7539
C | Xist Rating 327 | -74.84 | 585.363 | 150.275 | 35.6 | 2199.64 | 9589.88 | 13034.1 | 0.42 | 1.63 | 11.196 | 12.311 | 1 | 1 | 2250 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1287587.8693 | 65306.593 | 4930.5934 | 6928.4785 | 58378.1145 | 13259.2087 | 0.085727 | -102384.0949 | 102384.0949
C | Xist Rating 328 | -74.75 | 588.295 | 150.275 | 35.6 | 2197.93 | 9581.48 | 12995.5 | 0.42 | 1.62 | 11.191 | 12.265 | 1 | 1 | 2260 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1293031.2293 | 65857.456 | 4974.5182 | 6959.2717 | 58898.1842 | 13213.3328 | 0.086108 | -102029.8536 | 102029.8536
C | Xist Rating 329 | -74.21 | 603.935 | 150.275 | 35.6 | 2187.92 | 9545.89 | 12751.8 | 0.41 | 1.59 | 11.231 | 11.912 | 1 | 1 | 2270 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1321361.4652 | 66410.6252 | 5018.6379 | 6990.065 | 59420.5602 | 12839.1314 | 0.086489 | -99140.3695 | 99140.3695
C | Xist Rating 330 | -74.04 | 609.033 | 150.275 | 35.6 | 2185.44 | 9541.24 | 12686 | 0.41 | 1.58 | 11.225 | 11.83 | 1 | 1 | 2280 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1331005.0795 | 66966.1008 | 5062.9524 | 7020.8582 | 59945.2426 | 12755.7872 | 0.08687 | -98496.8074 | 98496.8074
C | Xist Rating 331 | -73.85 | 614.812 | 150.275 | 35.6 | 2182.36 | 9534.34 | 12606.8 | 0.41 | 1.56 | 11.22 | 11.726 | 1 | 1 | 2290 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1341741.1163 | 67523.8826 | 5107.4617 | 7051.6514 | 60472.2312 | 12649.6359 | 0.087251 | -97677.135 | 97677.135
C | Xist Rating 332 | -73.72 | 618.967 | 150.275 | 35.6 | 2179.35 | 9509.7 | 12557.1 | 0.4 | 1.56 | 11.215 | 11.667 | 1 | 1 | 2300 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1348945.7314 | 68083.9708 | 5152.1657 | 7082.4447 | 61001.5261 | 12578.6528 | 0.087632 | -97129.0229 | 97129.0229
| Xist Rating 333 | -73.59 | 623.387 | 150.275 | 35.6 | 2175.99 | 9478.53 | 12507.6 | 0.4 | 1.55 | 11.213 | 11.611 | 1 | 1 | 2310 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1356483.8781 | 68646.3652 | 5197.0645 | 7113.2379 | 61533.1273 | 12522.4249 | 0.088013 | -96694.8459 | 96694.8459
| Xist Rating 334 | -73.04 | 639.328 | 150.275 | 35.6 | 2166.51 | 9452.94 | 12277.1 | 0.4 | 1.51 | 11.252 | 11.291 | 1 | 1 | 2320 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1385110.5053 | 69211.0659 | 5242.1582 | 7144.0312 | 62067.0348 | 12193.7382 | 0.088394 | -94156.8141 | 94156.8141
| Xist Rating 335 | -72.88 | 644.458 | 150.275 | 35.6 | 2163.38 | 9434.65 | 12216.8 | 0.39 | 1.5 | 11.247 | 11.219 | 1 | 1 | 2330 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1394207.548 | 69778.073 | 5287.4466 | 7174.8244 | 62603.2486 | 12109.0284 | 0.088775 | -93502.7072 | 93502.7072
| Xist Rating 336 | -72.72 | 649.565 | 150.275 | 35.6 | 2160.36 | 9418.36 | 12157.1 | 0.39 | 1.49 | 11.242 | 11.148 | 1 | 1 | 2340 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1403294.2434 | 70347.3863 | 5332.9298 | 7205.6176 | 63141.7687 | 12037.0566 | 0.089156 | -92946.9603 | 92946.9603
| Xist Rating 337 | -72.58 | 654.301 | 150.275 | 35.6 | 2157.41 | 9398.6 | 12104.7 | 0.38 | 1.49 | 11.238 | 11.088 | 1 | 1 | 2350 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 5 | E | Rod | 1411595.5204 | 70919.0059 | 5378.6078 | 7236.4109 | 63682.595 | 11964.7098 | 0.089537 | -92388.3173 | 92388.3173
| Xist Rating 338 | -72.39 | 659.921 | 150.275 | 35.6 | 2154.37 | 9386.07 | 12039.9 | 0.38 | 1.48 | 11.232 | 11.01 | 1 | 1 | 2360 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1421714.0048 | 71492.9318 | 5424.4805 | 7267.2041 | 64225.7277 | 11885.3799 | 0.089918 | -91775.7532 | 91775.7532
| Xist Rating 339 | -71.91 | 674.68 | 150.275 | 35.6 | 2145.49 | 9354.14 | 11846.8 | 0.38 | 1.45 | 11.266 | 10.756 | 1 | 1 | 2370 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1447519.1932 | 72069.164 | 5470.5481 | 7297.9973 | 64771.1667 | 11624.887 | 0.090299 | -89764.2964 | 89764.2964
| Xist Rating 340 | -71.74 | 680.025 | 150.275 | 35.6 | 2142.18 | 9331.2 | 11791.1 | 0.37 | 1.44 | 11.261 | 10.694 | 1 | 1 | 2380 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1456735.9545 | 72647.7025 | 5516.8105 | 7328.7906 | 65318.912 | 11550.2029 | 0.09068 | -89187.6051 | 89187.6051
| Xist Rating 341 | -71.58 | 685.2 | 150.275 | 35.6 | 2139.78 | 9329.82 | 11730.1 | 0.37 | 1.43 | 11.256 | 10.621 | 1 | 1 | 2390 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1466177.256 | 73228.5474 | 5563.2676 | 7359.5838 | 65868.9635 | 11476.062 | 0.091061 | -88615.1085 | 88615.1085
C | Xist Rating 342 | -68.75 | 786.432 | 150.275 | 35.6 | 2051.65 | 8608.45 | 10538 | 0.41 | 1.25 | 11.251 | 9.141 | 1 | 1 | 2400 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1613483.2128 | 73811.6985 | 5609.9196 | 7390.3771 | 66421.3214 | 9989.167 | 0.091442 | -77133.7 | 77133.7
C | Xist Rating 343 | -68.47 | 787.878 | 150.275 | 35.6 | 2066.8 | 8881.69 | 10538 | 0.39 | 1.25 | 11.253 | 9.151 | 1 | 1 | 2410 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1628386.2504 | 74397.1558 | 5656.7663 | 7421.1703 | 66975.9856 | 9977.3957 | 0.091823 | -77042.8046 | 77042.8046
C | Xist Rating 344 | -68.46 | 789.279 | 150.275 | 35.6 | 2065.86 | 8864.39 | 10538 | 0.39 | 1.25 | 11.293 | 9.162 | 1 | 1 | 2420 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1630539.9149 | 74984.9195 | 5703.8078 | 7451.9635 | 67532.956 | 9992.4786 | 0.092204 | -77159.2709 | 77159.2709
C | Xist Rating 345 | -68.14 | 790.636 | 150.275 | 35.6 | 2083.17 | 9192.21 | 10537.8 | 0.39 | 1.25 | 11.286 | 9.171 | 1 | 1 | 2430 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1647029.1961 | 75574.9895 | 5751.0441 | 7482.7568 | 68092.2328 | 10003.5019 | 0.092585 | -77244.39 | 77244.39
C | Xist Rating 346 | -68.11 | 792.007 | 150.275 | 35.6 | 2082.63 | 9181.61 | 10537.9 | 0.38 | 1.25 | 11.28 | 9.182 | 1 | 1 | 2440 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1649457.5384 | 76167.3658 | 5798.4752 | 7513.55 | 68653.8158 | 10004.3052 | 0.092966 | -77250.5933 | 77250.5933
C | Xist Rating 347 | -68.1 | 793.333 | 150.275 | 35.6 | 2080.92 | 9148.5 | 10537.8 | 0.38 | 1.25 | 11.275 | 9.193 | 1 | 1 | 2450 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1650862.5064 | 76762.0484 | 5846.1011 | 7544.3432 | 69217.7052 | 10017.4414 | 0.093347 | -77352.0274 | 77352.0274
C | Xist Rating 348 | -68.07 | 794.805 | 150.275 | 35.6 | 2080.25 | 9135.6 | 10537.8 | 0.37 | 1.25 | 11.273 | 9.204 | 1 | 1 | 2460 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1653393.1012 | 77359.0373 | 5893.9217 | 7575.1365 | 69783.9008 | 10018.271 | 0.093728 | -77358.4334 | 77358.4334
C | Xist Rating 349 | -68.04 | 796.159 | 150.275 | 35.6 | 2079.74 | 9125.72 | 10537.8 | 0.36 | 1.25 | 11.31 | 9.215 | 1 | 1 | 2470 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1655803.7187 | 77958.3324 | 5941.9372 | 7605.9297 | 70352.4027 | 10020.5578 | 0.094109 | -77376.0912 | 77376.0912
C | Xist Rating 350 | -68.02 | 797.506 | 150.275 | 35.6 | 2079.11 | 9113.61 | 10537.8 | 0.36 | 1.25 | 11.303 | 9.225 | 1 | 1 | 2480 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1658102.6997 | 78559.9339 | 5990.1474 | 7636.723 | 70923.211 | 10032.4877 | 0.09449 | -77468.2109 | 77468.2109
C | Xist Rating 351 | -68 | 798.904 | 150.275 | 35.6 | 2077.82 | 9088.97 | 10537.9 | 0.35 | 1.25 | 11.305 | 9.236 | 1 | 1 | 2490 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1659978.7093 | 79163.8417 | 6038.5525 | 7667.5162 | 71496.3255 | 10033.1976 | 0.094871 | -77473.6926 | 77473.6926
C | Xist Rating 352 | -67.99 | 799.889 | 150.275 | 35.6 | 2077.15 | 9076.15 | 10537.9 | 0.35 | 1.25 | 11.3 | 9.244 | 1 | 1 | 2500 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1661489.4364 | 79770.0557 | 6087.1523 | 7698.3094 | 72071.7463 | 10043.0831 | 0.095252 | -77550.0257 | 77550.0257
C | Xist Rating 353 | -67.97 | 801.739 | 150.275 | 35.6 | 2074.58 | 9027.24 | 10537.9 | 0.34 | 1.25 | 11.298 | 9.257 | 1 | 1 | 2510 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1663271.6946 | 80378.5761 | 6135.9469 | 7729.1027 | 72649.4734 | 10045.5663 | 0.095633 | -77569.2001 | 77569.2001
C | Xist Rating 354 | -67.93 | 803.193 | 150.275 | 35.6 | 2074.75 | 9030.41 | 10537.8 | 0.34 | 1.25 | 11.336 | 9.268 | 1 | 1 | 2520 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1666424.6767 | 80989.4027 | 6184.9363 | 7759.8959 | 73229.5068 | 10060.171 | 0.096014 | -77681.9741 | 77681.9741
C | Xist Rating 355 | -67.92 | 804.531 | 150.275 | 35.6 | 2073.25 | 9002.08 | 10537.9 | 0.33 | 1.25 | 11.33 | 9.278 | 1 | 1 | 2530 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1667993.8957 | 81602.5357 | 6234.1205 | 7790.6891 | 73811.8465 | 10059.2034 | 0.096395 | -77674.5022 | 77674.5022
C | Xist Rating 356 | -67.91 | 805.682 | 150.275 | 35.6 | 2072.28 | 8983.78 | 10537.9 | 0.33 | 1.25 | 11.324 | 9.288 | 1 | 1 | 2540 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1669598.695 | 82217.9749 | 6283.4995 | 7821.4824 | 74396.4926 | 10071.0389 | 0.096776 | -77765.8928 | 77765.8928
C | Xist Rating 357 | -67.87 | 807.228 | 150.275 | 35.6 | 2071.47 | 8968.5 | 10537.9 | 0.32 | 1.25 | 11.323 | 9.299 | 1 | 1 | 2550 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1672148.5852 | 82835.7205 | 6333.0732 | 7852.2756 | 74983.4449 | 10071.1572 | 0.097157 | -77766.8063 | 77766.8063
C | Xist Rating 358 | -67.85 | 808.677 | 150.275 | 35.6 | 2070.57 | 8951.93 | 10537.8 | 0.32 | 1.25 | 11.318 | 9.309 | 1 | 1 | 2560 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1674422.3359 | 83455.7723 | 6382.8418 | 7883.0689 | 75572.7035 | 10082.9827 | 0.097538 | -77858.12 | 77858.12
C | Xist Rating 359 | -67.83 | 810.066 | 150.275 | 35.6 | 2069.49 | 8931.62 | 10537.8 | 0.31 | 1.25 | 11.315 | 9.32 | 1 | 1 | 2570 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1676423.4863 | 84078.1304 | 6432.8051 | 7913.8621 | 76164.2683 | 10082.8843 | 0.097919 | -77857.3596 | 77857.3596
C | Xist Rating 360 | -67.81 | 811.432 | 150.275 | 35.6 | 2068.41 | 8911.72 | 10537.8 | 0.31 | 1.25 | 11.35 | 9.33 | 1 | 1 | 2580 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1678374.0631 | 84702.7949 | 6482.9633 | 7944.6553 | 76758.1395 | 10096.0963 | 0.0983 | -77959.3796 | 77959.3796
C | Xist Rating 361 | -67.79 | 812.792 | 150.275 | 35.6 | 2067.33 | 8891.6 | 10537.8 | 0.31 | 1.25 | 11.344 | 9.34 | 1 | 1 | 2590 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1680309.2854 | 85329.7656 | 6533.3162 | 7975.4486 | 77354.317 | 10107.8425 | 0.098681 | -78050.0806 | 78050.0806
C | Xist Rating 362 | -67.77 | 813.969 | 150.275 | 35.6 | 2066.48 | 8875.97 | 10537.8 | 0.3 | 1.25 | 11.339 | 9.349 | 1 | 1 | 2600 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1682050.6591 | 85959.0426 | 6583.8639 | 8006.2418 | 77952.8008 | 10105.3697 | 0.099062 | -78030.9866 | 78030.9866
C | Xist Rating 363 | -67.75 | 815.656 | 150.275 | 35.6 | 2065.02 | 8849.1 | 10537.8 | 0.3 | 1.25 | 11.337 | 9.361 | 1 | 1 | 2610 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1684345.9531 | 86590.6259 | 6634.6064 | 8037.035 | 78553.5909 | 10119.2863 | 0.099443 | -78138.4468 | 78138.4468
C | Xist Rating 364 | -67.72 | 817.053 | 150.275 | 35.6 | 2064.28 | 8835.4 | 10537.8 | 0.29 | 1.25 | 11.334 | 9.371 | 1 | 1 | 2620 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1686626.1668 | 87224.5155 | 6685.5437 | 8067.8283 | 79156.6873 | 10117.7794 | 0.099824 | -78126.8109 | 78126.8109
C | Xist Rating 365 | -67.69 | 818.48 | 150.275 | 35.6 | 2063.84 | 8827.4 | 10537.8 | 0.29 | 1.25 | 11.371 | 9.381 | 1 | 1 | 2630 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1689211.7632 | 87860.7114 | 6736.6758 | 8098.6215 | 79762.0899 | 10130.9027 | 0.10021 | -78228.1452 | 78228.1452
C | Xist Rating 366 | -67.66 | 819.725 | 150.275 | 35.6 | 2063.83 | 8827.21 | 10537.8 | 0.29 | 1.25 | 11.367 | 9.391 | 1 | 1 | 2640 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1691773.0467 | 88499.2137 | 6788.0027 | 8129.4148 | 80369.7989 | 10142.6285 | 0.10059 | -78318.6891 | 78318.6891
C | Xist Rating 367 | -67.63 | 821.228 | 150.275 | 35.6 | 2062.73 | 8807.11 | 10537.7 | 0.28 | 1.25 | 11.363 | 9.401 | 1 | 1 | 2650 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1693971.6324 | 89140.0221 | 6839.5243 | 8160.208 | 80979.8141 | 10140.8558 | 0.10097 | -78305.0002 | 78305.0002
C | Xist Rating 368 | -67.59 | 822.569 | 150.275 | 35.6 | 2063.08 | 8813.54 | 10537.8 | 0.28 | 1.25 | 11.362 | 9.411 | 1 | 1 | 2660 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1697025.6525 | 89783.1369 | 6891.2408 | 8191.0012 | 81592.1357 | 10152.6335 | 0.10135 | -78395.9449 | 78395.9449
C | Xist Rating 369 | -67.56 | 823.956 | 150.275 | 35.6 | 2062.42 | 8801.51 | 10537.8 | 0.27 | 1.25 | 11.359 | 9.421 | 1 | 1 | 2670 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1699343.3335 | 90428.558 | 6943.152 | 8221.7945 | 82206.7636 | 10150.7494 | 0.10173 | -78381.3959 | 78381.3959
C | Xist Rating 370 | -67.5 | 825.373 | 150.275 | 35.6 | 2063.97 | 8829.81 | 10537.8 | 0.27 | 1.25 | 11.399 | 9.431 | 1 | 1 | 2680 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1703545.1108 | 91076.2854 | 6995.258 | 8252.5877 | 82823.6977 | 10163.8065 | 0.10211 | -78482.2195 | 78482.2195
C | Xist Rating 371 | -67.49 | 826.75 | 150.275 | 35.6 | 2062.55 | 8803.96 | 10537.8 | 0.27 | 1.25 | 11.394 | 9.441 | 1 | 1 | 2690 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1705213.2125 | 91726.3191 | 7047.5588 | 8283.381 | 83442.9381 | 10175.4083 | 0.10249 | -78571.8055 | 78571.8055
C | Xist Rating 372 | -67.42 | 827.95 | 150.275 | 35.6 | 2064.76 | 8844.2 | 10538 | 0.26 | 1.25 | 11.397 | 9.45 | 1 | 1 | 2700 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1709518.042 | 92378.6591 | 7100.0544 | 8314.1742 | 84064.4849 | 10172.4384 | 0.10287 | -78548.8727 | 78548.8727
C | Xist Rating 373 | -67.33 | 829.607 | 150.275 | 35.6 | 2067.2 | 8888.99 | 10538.1 | 0.26 | 1.25 | 11.402 | 9.461 | 1 | 1 | 2710 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1714963.5904 | 93033.3054 | 7152.7448 | 8344.9674 | 84688.3379 | 10185.348 | 0.10325 | -78648.5576 | 78648.5576
C | Xist Rating 374 | -67.25 | 830.951 | 150.275 | 35.6 | 2070.12 | 8943.09 | 10538.2 | 0.25 | 1.25 | 11.403 | 9.471 | 1 | 1 | 2720 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1720168.2841 | 93690.2579 | 7205.63 | 8375.7607 | 85314.4973 | 10183.1907 | 0.10363 | -78631.899 | 78631.899
C | Xist Rating 375 | -66.93 | 832.273 | 150.275 | 35.6 | 2088.1 | 9288.43 | 10538.4 | 0.25 | 1.25 | 11.473 | 9.482 | 1 | 1 | 2730 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1737869.2513 | 94349.5168 | 7258.71 | 8406.5539 | 85942.9629 | 10198.0335 | 0.10402 | -78746.5113 | 78746.5113
C | Xist Rating 376 | -66.99 | 833.556 | 150.275 | 35.6 | 2082.49 | 9178.49 | 10538.4 | 0.25 | 1.25 | 11.457 | 9.491 | 1 | 1 | 2740 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1735872.0344 | 95011.0819 | 7311.9847 | 8437.3471 | 86573.7348 | 10208.1744 | 0.1044 | -78824.8166 | 78824.8166
C | Xist Rating 377 | -66.78 | 835.104 | 150.275 | 35.6 | 2092.63 | 9378.73 | 10538.4 | 0.24 | 1.25 | 11.475 | 9.502 | 1 | 1 | 2750 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1747563.6835 | 95674.9534 | 7365.4543 | 8468.1404 | 87206.813 | 10207.2915 | 0.10478 | -78817.999 | 78817.999
C | Xist Rating 378 | -66.67 | 836.529 | 150.275 | 35.6 | 2097.16 | 9470.36 | 10538.5 | 0.24 | 1.25 | 11.482 | 9.512 | 1 | 1 | 2760 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1754335.1576 | 96341.1312 | 7419.1186 | 8498.9336 | 87842.1975 | 10219.1188 | 0.10516 | -78909.3263 | 78909.3263
C | Xist Rating 379 | -66.58 | 837.764 | 150.275 | 35.6 | 2101.18 | 9552.95 | 10538.5 | 0.23 | 1.25 | 11.489 | 9.521 | 1 | 1 | 2770 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1760292.9615 | 97009.6152 | 7472.9777 | 8529.7269 | 88479.8884 | 10215.6438 | 0.10554 | -78882.4938 | 78882.4938
C | Xist Rating 380 | -66.5 | 839.312 | 150.275 | 35.6 | 2103.3 | 9596.92 | 10538.5 | 0.23 | 1.25 | 11.533 | 9.532 | 1 | 1 | 2780 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1765324.9296 | 97680.4056 | 7527.0316 | 8560.5201 | 89119.8855 | 10229.5129 | 0.10592 | -78989.5869 | 78989.5869
C | Xist Rating 381 | -66.43 | 840.72 | 150.275 | 35.6 | 2105.09 | 9634.3 | 10538.5 | 0.23 | 1.25 | 11.536 | 9.541 | 1 | 1 | 2790 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1769791.2648 | 98353.5022 | 7581.2803 | 8591.3133 | 89762.1889 | 10240.1347 | 0.1063 | -79071.6055 | 79071.6055
C | Xist Rating 382 | -66.37 | 841.695 | 150.275 | 35.6 | 2107.78 | 9690.98 | 10538.4 | 0.23 | 1.25 | 11.537 | 9.549 | 1 | 1 | 2800 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1774107.8871 | 99028.9051 | 7635.7238 | 8622.1066 | 90406.7986 | 10249.6608 | 0.10668 | -79145.1641 | 79145.1641
C | Xist Rating 383 | -66.32 | 843.439 | 150.275 | 35.6 | 2107.64 | 9687.93 | 10538.4 | 0.22 | 1.25 | 11.54 | 9.56 | 1 | 1 | 2810 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1777665.774 | 99706.6144 | 7690.3621 | 8652.8998 | 91053.7146 | 10247.8252 | 0.10706 | -79130.9897 | 79130.9897
C | Xist Rating 384 | -66.26 | 844.915 | 150.275 | 35.6 | 2108.8 | 9712.62 | 10538.4 | 0.22 | 1.25 | 11.542 | 9.57 | 1 | 1 | 2820 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1781756.752 | 100386.6299 | 7745.1952 | 8683.693 | 91702.9368 | 10259.4038 | 0.10744 | -79220.3967 | 79220.3967
C | Xist Rating 385 | -66.21 | 846.286 | 150.275 | 35.6 | 2109.64 | 9730.42 | 10538.4 | 0.22 | 1.25 | 11.583 | 9.58 | 1 | 1 | 2830 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1785358.797 | 101068.9517 | 7800.223 | 8714.4863 | 92354.4654 | 10272.0712 | 0.10783 | -79318.2111 | 79318.2111
C | Xist Rating 386 | -66.16 | 847.604 | 150.275 | 35.6 | 2110.39 | 9746.49 | 10538.4 | 0.21 | 1.25 | 11.584 | 9.589 | 1 | 1 | 2840 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1788775.0056 | 101753.5798 | 7855.4457 | 8745.2795 | 93008.3003 | 10267.8413 | 0.10821 | -79285.5487 | 79285.5487
C | Xist Rating 387 | -66.11 | 849.047 | 150.275 | 35.6 | 2111.26 | 9765.02 | 10538.3 | 0.21 | 1.25 | 11.584 | 9.599 | 1 | 1 | 2850 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1792558.9692 | 102440.5143 | 7910.8631 | 8776.0728 | 93664.4415 | 10279.3167 | 0.10859 | -79374.1588 | 79374.1588
C | Xist Rating 388 | -66.06 | 850.453 | 150.275 | 35.6 | 2112.12 | 9783.48 | 10538.3 | 0.21 | 1.25 | 11.585 | 9.608 | 1 | 1 | 2860 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1796258.7904 | 103129.755 | 7966.4753 | 8806.866 | 94322.889 | 10289.7805 | 0.10897 | -79454.9577 | 79454.9577
C | Xist Rating 389 | -66.01 | 851.644 | 150.275 | 35.6 | 2113.48 | 9812.83 | 10538.3 | 0.21 | 1.25 | 11.586 | 9.617 | 1 | 1 | 2870 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1799932.5611 | 103821.302 | 8022.2824 | 8837.6592 | 94983.6427 | 10300.2445 | 0.10935 | -79535.7581 | 79535.7581
C | Xist Rating 390 | -65.95 | 853.152 | 150.275 | 35.6 | 2114.34 | 9831.5 | 10538.2 | 0.2 | 1.25 | 11.629 | 9.627 | 1 | 1 | 2880 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1803853.3997 | 104515.1553 | 8078.2842 | 8868.4525 | 95646.7028 | 10297.8734 | 0.10973 | -79517.4488 | 79517.4488
C | Xist Rating 391 | -65.9 | 854.495 | 150.275 | 35.5 | 2115.36 | 9853.54 | 10538.1 | 0.2 | 1.25 | 11.624 | 9.636 | 1 | 1 | 2890 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1807564.5432 | 105211.3149 | 8134.4807 | 8899.2457 | 96312.0692 | 10308.1329 | 0.11011 | -79596.6698 | 79596.6698
C | Xist Rating 392 | -65.84 | 855.881 | 150.275 | 35.5 | 2116.88 | 9886.59 | 10538.1 | 0.2 | 1.25 | 11.627 | 9.645 | 1 | 1 | 2900 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1811797.3713 | 105909.7808 | 8190.8721 | 8930.0389 | 96979.7418 | 10318.5994 | 0.11049 | -79677.4898 | 79677.4898
C | Xist Rating 393 | -65.78 | 857.42 | 150.275 | 35.5 | 2118.4 | 9920.21 | 10537.7 | 0.2 | 1.25 | 11.639 | 9.655 | 1 | 1 | 2910 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1816358.528 | 106610.553 | 8247.4583 | 8960.8322 | 97649.7208 | 10330.3398 | 0.11087 | -79768.146 | 79768.146
C | Xist Rating 396 | -65.73 | 861.564 | 150.275 | 35.5 | 2115.89 | 9866.48 | 10536.7 | 0.19 | 1.25 | 11.683 | 9.682 | 1 | 1 | 2940 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1822974.652 | 108726.7073 | 8418.3855 | 9053.2119 | 99673.4954 | 10347.2729 | 0.11202 | -79898.8986 | 79898.8986
C | Xist Rating 397 | -65.72 | 862.972 | 150.275 | 35.5 | 2114.94 | 9846.2 | 10536.4 | 0.19 | 1.25 | 11.683 | 9.691 | 1 | 1 | 2950 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1825134.0017 | 109436.7047 | 8475.7509 | 9084.0051 | 100352.6996 | 10357.6144 | 0.1124 | -79978.7529 | 79978.7529
C | Xist Rating 398 | -65.72 | 864.344 | 150.275 | 35.5 | 2113.58 | 9817.35 | 10535.8 | 0.19 | 1.25 | 11.687 | 9.699 | 1 | 1 | 2960 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1826860.1915 | 110149.0084 | 8533.311 | 9114.7984 | 101034.21 | 10367.0182 | 0.11278 | -80051.3667 | 80051.3667
C | Xist Rating 399 | -66 | 865.728 | 150.275 | 35.4 | 2101.05 | 9551.54 | 10537.1 | 0.18 | 1.25 | 11.687 | 9.708 | 1 | 1 | 2970 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1818937.8144 | 110863.6183 | 8591.0659 | 9145.5916 | 101718.0267 | 10361.8012 | 0.11316 | -80011.0826 | 80011.0826
C | Xist Rating 402 | -65.9 | 869.94 | 150.275 | 35.4 | 2099.61 | 9521.97 | 10536.9 | 0.18 | 1.25 | 11.721 | 9.735 | 1 | 1 | 3000 | 152.4 | 2 | 1.1 | 19.05 | 1.3333 | 4 | E | Rod | 1826534.7234 | 113021.286 | 8765.4993 | 9237.9713 | 103783.3147 | 10393.4926 | 0.1143 | -80255.7945 | 80255.7945
C | Xist Rating 403 | -96.21 | 72.458 | 150.276 | 35.8 | 2418.47 | 7586.45 | 58746 | 2.44 | 10.95 | 11.832 | 296.259 | 1 | 1 | 1000 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 175237.4993 | 15939.058 | 973.9444 | 3359.2623 | 12579.7957 | 308958.5943 | 0.038101 | -2385696.3694 | 2385696.3694
C | Xist Rating 404 | -96.17 | 73.256 | 150.276 | 35.8 | 2423.12 | 7641.52 | 58284.6 | 2.41 | 10.85 | 11.833 | 290.768 | 1 | 1 | 1010 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 177508.0787 | 16225.5045 | 993.5206 | 3392.8549 | 12832.6496 | 303253.1795 | 0.038482 | -2341640.6682 | 2341640.6682
C | Xist Rating 405 | -95.88 | 79.061 | 150.276 | 35.8 | 2413.22 | 7612.21 | 54967.8 | 2.42 | 10.07 | 11.884 | 251.968 | 1 | 1 | 1020 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 190791.5864 | 16514.467 | 1013.2917 | 3426.4475 | 13088.0195 | 262983.2768 | 0.038863 | -2030687.154 | 2030687.154
C | Xist Rating 406 | -95.82 | 80.802 | 150.276 | 35.8 | 2400.62 | 7505.36 | 54179.5 | 2.33 | 9.89 | 11.73 | 243.728 | 1 | 1 | 1030 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 193974.8972 | 16805.9454 | 1033.2576 | 3460.0402 | 13345.9053 | 254372.9936 | 0.039244 | -1964200.8298 | 1964200.8298
C | Xist Rating 407 | -95.75 | 81.675 | 150.276 | 35.8 | 2416.28 | 7669.53 | 53795.7 | 2.27 | 9.8 | 11.694 | 239.796 | 1 | 1 | 1040 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 197349.669 | 17099.9398 | 1053.4182 | 3493.6328 | 13606.307 | 250265.2497 | 0.039625 | -1932481.9204 | 1932481.9204
C | Xist Rating 408 | -95.65 | 83.294 | 150.276 | 35.8 | 2426.16 | 7788.32 | 53044.7 | 2.22 | 9.63 | 11.665 | 231.951 | 1 | 1 | 1050 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 202084.571 | 17396.4502 | 1073.7737 | 3527.2254 | 13869.2248 | 242099.579 | 0.040006 | -1869428.7753 | 1869428.7753
C | Xist Rating 409 | -95.6 | 84.147 | 150.276 | 35.8 | 2434.85 | 7887.91 | 52677.1 | 2.17 | 9.54 | 11.642 | 228.266 | 1 | 1 | 1060 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 204885.323 | 17695.4765 | 1094.3239 | 3560.818 | 14134.6585 | 238254.2362 | 0.040387 | -1839736.0576 | 1839736.0576
C | Xist Rating 410 | -95.3 | 90.507 | 150.276 | 35.8 | 2415.38 | 7760.85 | 49858.7 | 2.16 | 8.9 | 11.627 | 199.822 | 1 | 1 | 1070 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 218608.7977 | 17997.0188 | 1115.0689 | 3594.4107 | 14402.6081 | 208719.3735 | 0.040768 | -1611675.6768 | 1611675.6768
C | Xist Rating 411 | -95.24 | 91.789 | 150.275 | 35.8 | 2417.89 | 7800.31 | 49381.2 | 2.11 | 8.79 | 11.58 | 195.436 | 1 | 1 | 1080 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 221935.7052 | 18301.077 | 1136.0087 | 3628.0033 | 14673.0737 | 204142.8325 | 0.041149 | -1576336.8399 | 1576336.8399
C | Xist Rating 412 | -95.16 | 93.489 | 150.275 | 35.8 | 2413.9 | 7776.85 | 48760.9 | 2.06 | 8.65 | 11.52 | 189.793 | 1 | 1 | 1090 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 225673.0971 | 18607.6512 | 1157.1433 | 3661.5959 | 14946.0553 | 198259.21 | 0.04153 | -1530905.0669 | 1530905.0669
C | Xist Rating 413 | -95.1 | 94.74 | 150.275 | 35.8 | 2416.28 | 7815.12 | 48306.7 | 2.03 | 8.55 | 11.499 | 185.704 | 1 | 1 | 1100 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 228918.3672 | 18916.7413 | 1178.4727 | 3695.1885 | 15221.5528 | 194004.2849 | 0.041911 | -1498049.6631 | 1498049.6631
C | Xist Rating 414 | -95.07 | 95.78 | 150.275 | 35.8 | 2406.72 | 7724.75 | 48010.7 | 1.96 | 8.49 | 11.397 | 183.32 | 1 | 1 | 1110 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 230515.6416 | 19228.3475 | 1199.9969 | 3728.7812 | 15499.5663 | 191488.9714 | 0.042292 | -1478627.0789 | 1478627.0789
C | Xist Rating 415 | -94.71 | 102.763 | 150.275 | 35.8 | 2405.25 | 7790.81 | 45448.7 | 1.99 | 7.92 | 11.509 | 160.411 | 1 | 1 | 1120 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 247170.7058 | 19542.4695 | 1221.7158 | 3762.3738 | 15780.0957 | 167736.3786 | 0.042673 | -1295215.8535 | 1295215.8535
C | Xist Rating 416 | -94.65 | 103.757 | 150.275 | 35.8 | 2412.01 | 7871.11 | 45189.8 | 1.93 | 7.86 | 11.446 | 158.467 | 1 | 1 | 1130 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 250262.9216 | 19859.1076 | 1243.6296 | 3795.9664 | 16063.1412 | 165686.6679 | 0.043054 | -1279388.531 | 1279388.531
C | Xist Rating 417 | -94.57 | 105.527 | 150.275 | 35.8 | 2411.64 | 7885.05 | 44682.7 | 1.87 | 7.75 | 11.363 | 154.449 | 1 | 1 | 1140 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 254493.1343 | 20178.2615 | 1265.7381 | 3829.559 | 16348.7025 | 161480.8586 | 0.043435 | -1246912.3866 | 1246912.3866
C | Xist Rating 418 | -94.46 | 107.234 | 150.275 | 35.8 | 2419.42 | 7987.2 | 44188.2 | 1.82 | 7.64 | 11.339 | 150.532 | 1 | 1 | 1150 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 259444.0843 | 20499.9315 | 1288.0414 | 3863.1516 | 16636.7798 | 157391.0462 | 0.043816 | -1215331.9391 | 1215331.9391
C | Xist Rating 419 | -94.38 | 109.02 | 150.275 | 35.8 | 2417.11 | 7980.32 | 43705.5 | 1.77 | 7.53 | 11.288 | 146.831 | 1 | 1 | 1160 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 263513.3322 | 20824.1174 | 1310.5395 | 3896.7443 | 16927.3731 | 153522.6408 | 0.044197 | -1185461.138 | 1185461.138
C | Xist Rating 420 | -94.06 | 115.366 | 150.275 | 35.8 | 2417.27 | 8057.83 | 41834.4 | 1.79 | 7.13 | 11.362 | 132.123 | 1 | 1 | 1170 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 278870.7708 | 21150.8192 | 1333.2324 | 3930.3369 | 17220.4824 | 138276.1487 | 0.044578 | -1067731.7674 | 1067731.7674
C | Xist Rating 421 | -94.02 | 115.956 | 150.275 | 35.8 | 2424.83 | 8147.16 | 41726.7 | 1.74 | 7.11 | 11.326 | 131.485 | 1 | 1 | 1180 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 281173.5875 | 21480.0371 | 1356.1201 | 3963.9295 | 17516.1076 | 137589.3414 | 0.044959 | -1062428.4231 | 1062428.4231
C | Xist Rating 422 | -93.88 | 119.356 | 150.275 | 35.8 | 2411.92 | 8039.59 | 40887.6 | 1.7 | 6.93 | 11.269 | 125.44 | 1 | 1 | 1190 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 287877.1235 | 21811.7709 | 1379.2026 | 3997.5221 | 17814.2487 | 131291.1176 | 0.04534 | -1013795.2086 | 1013795.2086
C | Xist Rating 423 | -93.81 | 120.243 | 150.275 | 35.8 | 2422.76 | 8170.71 | 40683.4 | 1.67 | 6.88 | 11.267 | 124.047 | 1 | 1 | 1200 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 291319.9307 | 22146.0206 | 1402.4799 | 4031.1148 | 18114.9058 | 129834.7122 | 0.045721 | -1002549.2321 | 1002549.2321
C | Xist Rating 424 | -93.73 | 122.098 | 150.275 | 35.8 | 2417.73 | 8132.45 | 40282.5 | 1.62 | 6.8 | 11.216 | 121.35 | 1 | 1 | 1210 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 295199.9975 | 22482.7863 | 1425.9519 | 4064.7074 | 18418.0789 | 127007.2801 | 0.046102 | -980716.551 | 980716.551
C | Xist Rating 425 | -93.4 | 129.434 | 150.275 | 35.8 | 2404.67 | 8069.69 | 38539.1 | 1.62 | 6.43 | 11.249 | 109.219 | 1 | 1 | 1220 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 311246.0568 | 22822.068 | 1449.6188 | 4098.3 | 18723.7679 | 114420.3239 | 0.046483 | -883523.4117 | 883523.4117
C | Xist Rating 426 | -93.3 | 131.139 | 150.275 | 35.8 | 2409.51 | 8142.87 | 38184.1 | 1.6 | 6.35 | 11.24 | 106.932 | 1 | 1 | 1230 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 315980.7319 | 23163.8656 | 1473.4804 | 4131.8926 | 19031.9729 | 112040.2485 | 0.046864 | -865145.1006 | 865145.1006
C | Xist Rating 427 | -93.22 | 132.985 | 150.275 | 35.8 | 2406.41 | 8125.82 | 37836.5 | 1.56 | 6.28 | 11.202 | 104.788 | 1 | 1 | 1240 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 320016.4339 | 23508.1791 | 1497.5369 | 4165.4853 | 19342.6939 | 109793.4843 | 0.047245 | -847796.183 | 847796.183
C | Xist Rating 428 | -93.18 | 134.015 | 150.275 | 35.7 | 2407.14 | 8143.34 | 37665.4 | 1.52 | 6.24 | 11.171 | 103.81 | 1 | 1 | 1250 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 322592.8671 | 23855.0087 | 1521.7881 | 4199.0779 | 19655.9308 | 108757.9196 | 0.047626 | -839799.8265 | 839799.8265
C | Xist Rating 429 | -93.05 | 136.597 | 150.274 | 35.7 | 2405.79 | 8155.27 | 37162.4 | 1.49 | 6.14 | 11.153 | 100.663 | 1 | 1 | 1260 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 328623.6966 | 24204.3542 | 1546.2341 | 4232.6705 | 19971.6837 | 105476.9337 | 0.048007 | -814464.9228 | 814464.9228
C | Xist Rating 430 | -92.72 | 143.559 | 150.275 | 35.7 | 2401.61 | 8186.88 | 35778.7 | 1.5 | 5.85 | 11.203 | 92.014 | 1 | 1 | 1270 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 344772.73 | 24556.2156 | 1570.8749 | 4266.2631 | 20289.9525 | 96513.0284 | 0.048388 | -745248.0227 | 745248.0227
C | Xist Rating 431 | -92.63 | 145.473 | 150.275 | 35.8 | 2400.55 | 8192.77 | 35479.1 | 1.46 | 5.79 | 11.179 | 90.35 | 1 | 1 | 1280 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 349215.2102 | 24910.593 | 1595.7105 | 4299.8557 | 20610.7373 | 94764.778 | 0.048769 | -731748.4967 | 731748.4967
C | Xist Rating 432 | -92.53 | 147.335 | 150.274 | 35.7 | 2405.78 | 8272.48 | 35184.7 | 1.42 | 5.73 | 11.171 | 88.715 | 1 | 1 | 1290 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 354455.5963 | 25267.4864 | 1620.7408 | 4333.4484 | 20934.0381 | 93047.6357 | 0.04915 | -718489.179 | 718489.179
C | Xist Rating 433 | -92.37 | 149.894 | 150.274 | 35.7 | 2415.15 | 8412.97 | 34753.4 | 1.39 | 5.64 | 11.171 | 86.25 | 1 | 1 | 1300 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 362016.4941 | 25626.8958 | 1645.966 | 4367.041 | 21259.8548 | 90475.3189 | 0.049531 | -698626.43 | 698626.43
C | Xist Rating 434 | -92.29 | 151.37 | 150.274 | 35.7 | 2418.65 | 8470.05 | 34542.5 | 1.36 | 5.59 | 11.151 | 85.141 | 1 | 1 | 1310 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 366111.0505 | 25988.821 | 1671.3859 | 4400.6336 | 21588.1874 | 89309.3082 | 0.049912 | -689622.805 | 689622.805
C | Xist Rating 435 | -91.96 | 158.43 | 150.275 | 35.7 | 2413.62 | 8492.64 | 33365.2 | 1.36 | 5.35 | 11.193 | 78.495 | 1 | 1 | 1320 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 382389.8166 | 26353.2623 | 1697.0007 | 4434.2262 | 21919.0361 | 82417.6253 | 0.050293 | -636407.0559 | 636407.0559
C | Xist Rating 436 | -91.84 | 161.207 | 150.274 | 35.7 | 2407.71 | 8448.37 | 32982.1 | 1.33 | 5.28 | 11.146 | 76.527 | 1 | 1 | 1330 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 388139.706 | 26720.2195 | 1722.8102 | 4467.8189 | 22252.4006 | 80356.9384 | 0.050674 | -620494.9784 | 620494.9784
C | Xist Rating 437 | -91.71 | 163.882 | 150.274 | 35.7 | 2407.83 | 8478.54 | 32608.8 | 1.3 | 5.2 | 11.13 | 74.609 | 1 | 1 | 1340 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 394599.9961 | 27089.6927 | 1748.8145 | 4501.4115 | 22588.2812 | 78350.4095 | 0.051055 | -605001.0935 | 605001.0935
C | Xist Rating 438 | -91.63 | 165.374 | 150.274 | 35.7 | 2410.87 | 8530.76 | 32425.9 | 1.27 | 5.16 | 11.112 | 73.734 | 1 | 1 | 1350 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 398695.2154 | 27461.6818 | 1775.0136 | 4535.0041 | 22926.6777 | 77426.6203 | 0.051436 | -597867.8385 | 597867.8385
C | Xist Rating 439 | -91.54 | 166.207 | 150.274 | 35.7 | 2427.79 | 8756.65 | 32304.8 | 1.26 | 5.14 | 11.126 | 73.123 | 1 | 1 | 1360 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 403515.6925 | 27836.1869 | 1801.4075 | 4568.5967 | 23267.5902 | 76792.7249 | 0.051817 | -592973.0659 | 592973.0659
C | Xist Rating 440 | -91.13 | 176.464 | 150.274 | 35.7 | 2399.64 | 8516.62 | 30904.2 | 1.25 | 4.86 | 11.137 | 66.032 | 1 | 1 | 1370 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 423450.073 | 28213.2079 | 1827.9962 | 4602.1893 | 23611.0186 | 69429.0284 | 0.052198 | -536112.5534 | 536112.5534
C | Xist Rating 441 | -91.08 | 177.558 | 150.274 | 35.7 | 2399.56 | 8525.17 | 30795.4 | 1.23 | 4.84 | 11.118 | 65.582 | 1 | 1 | 1380 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 426061.0745 | 28592.7449 | 1854.7797 | 4635.782 | 23956.963 | 68952.7204 | 0.052579 | -532434.6292 | 532434.6292
C | Xist Rating 442 | -90.97 | 179.906 | 150.274 | 35.7 | 2399.32 | 8546.01 | 30528.2 | 1.2 | 4.79 | 11.101 | 64.36 | 1 | 1 | 1390 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 431652.0639 | 28974.7979 | 1881.7579 | 4669.3746 | 24305.4233 | 67667.7524 | 0.05296 | -522512.4476 | 522512.4476
C | Xist Rating 443 | -90.87 | 182.25 | 150.274 | 35.7 | 2398.39 | 8557.93 | 30266.2 | 1.18 | 4.73 | 11.086 | 63.174 | 1 | 1 | 1400 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 437106.5775 | 29359.3668 | 1908.931 | 4702.9672 | 24656.3996 | 66427.021 | 0.053341 | -512931.8482 | 512931.8482
C | Xist Rating 444 | -90.74 | 184.986 | 150.274 | 35.7 | 2397.13 | 8570.55 | 29958.5 | 1.16 | 4.67 | 11.074 | 61.776 | 1 | 1 | 1410 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 443435.4902 | 29746.4517 | 1936.2988 | 4736.5598 | 25009.8919 | 64966.1708 | 0.053722 | -501651.5505 | 501651.5505
C | Xist Rating 445 | -90.39 | 192.565 | 150.274 | 35.7 | 2392.19 | 8595.28 | 29053 | 1.17 | 4.49 | 11.12 | 57.566 | 1 | 1 | 1420 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 460652.0674 | 30136.0526 | 1963.8614 | 4770.1525 | 25365.9001 | 60610.325 | 0.054103 | -468016.8636 | 468016.8636
C | Xist Rating 446 | -90.33 | 194.298 | 150.274 | 35.7 | 2387.68 | 8551.39 | 28911.8 | 1.13 | 4.47 | 11.09 | 57.037 | 1 | 1 | 1430 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 463921.4486 | 30528.1694 | 1991.6188 | 4803.7451 | 25724.4243 | 60036.1069 | 0.054484 | -463582.9035 | 463582.9035
C | Xist Rating 447 | -90.17 | 197.867 | 150.274 | 35.7 | 2385.05 | 8555.23 | 28543 | 1.12 | 4.39 | 11.08 | 55.447 | 1 | 1 | 1440 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 471922.6884 | 30922.8021 | 2019.571 | 4837.3377 | 26085.4644 | 58382.6304 | 0.054865 | -450815.1967 | 450815.1967
C | Xist Rating 448 | -90.06 | 200.249 | 150.274 | 35.7 | 2384.06 | 8565.94 | 28317.8 | 1.1 | 4.35 | 11.067 | 54.523 | 1 | 1 | 1450 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 477405.6309 | 31319.9508 | 2047.718 | 4870.9303 | 26449.0205 | 57413.288 | 0.055246 | -443330.1911 | 443330.1911
C | Xist Rating 449 | -89.96 | 201.623 | 150.274 | 35.7 | 2392.95 | 8696.33 | 28185 | 1.08 | 4.33 | 11.072 | 53.981 | 1 | 1 | 1460 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 482473.7578 | 31719.6155 | 2076.0598 | 4904.523 | 26815.0926 | 56841.7467 | 0.055627 | -438916.9007 | 438916.9007
C | Xist Rating 450 | -89.61 | 210.463 | 150.274 | 35.7 | 2374.63 | 8553.67 | 27311.1 | 1.08 | 4.16 | 11.09 | 50.305 | 1 | 1 | 1470 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 499771.7537 | 32121.7961 | 2104.5964 | 4938.1156 | 27183.6806 | 53030.8674 | 0.056008 | -409490.3015 | 409490.3015
C | Xist Rating 451 | -89.46 | 213.243 | 150.274 | 35.7 | 2378.57 | 8633.16 | 27067.3 | 1.06 | 4.11 | 11.087 | 49.349 | 1 | 1 | 1480 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 507213.4025 | 32526.4927 | 2133.3277 | 4971.7082 | 27554.7845 | 52028.5064 | 0.056389 | -401750.3353 | 401750.3353
C | Xist Rating 452 | -89.32 | 215.627 | 150.274 | 35.7 | 2387.18 | 8771.92 | 26867.7 | 1.04 | 4.07 | 11.085 | 48.588 | 1 | 1 | 1490 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 514740.4619 | 32933.7053 | 2162.2539 | 5005.3008 | 27928.4045 | 51228.5284 | 0.05677 | -395573.1168 | 395573.1168
C | Xist Rating 453 | -89.19 | 218.103 | 150.274 | 35.7 | 2390.07 | 8835.53 | 26671.4 | 1.02 | 4.03 | 11.076 | 47.858 | 1 | 1 | 1500 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 521281.4372 | 33343.4338 | 2191.3748 | 5038.8934 | 28304.5404 | 50460.0684 | 0.057151 | -389639.2727 | 389639.2727
C | Xist Rating 454 | -89.04 | 220.909 | 150.274 | 35.7 | 2394.58 | 8927.46 | 26439.9 | 1 | 3.99 | 11.074 | 46.981 | 1 | 1 | 1510 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 528984.2732 | 33755.6783 | 2220.6906 | 5072.4861 | 28683.1922 | 49539.2404 | 0.057532 | -382528.8827 | 382528.8827
C | Xist Rating 455 | -88.63 | 229.433 | 150.274 | 35.7 | 2393.29 | 9012.69 | 25682.1 | 1 | 3.85 | 11.125 | 44.009 | 1 | 1 | 1520 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 549099.7046 | 34170.4387 | 2250.2011 | 5106.0787 | 29064.36 | 46461.2617 | 0.057913 | -358761.5477 | 358761.5477
C | Xist Rating 456 | -88.51 | 232.583 | 150.274 | 35.7 | 2386.61 | 8948.51 | 25469.5 | 0.98 | 3.81 | 11.101 | 43.286 | 1 | 1 | 1530 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 555084.9136 | 34587.7151 | 2279.9064 | 5139.6713 | 29448.0438 | 45698.5417 | 0.058294 | -352872.0254 | 352872.0254
C | Xist Rating 457 | -88.41 | 234.232 | 150.274 | 35.7 | 2391.98 | 9039.79 | 25364.8 | 0.96 | 3.79 | 11.094 | 42.949 | 1 | 1 | 1540 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 560278.2594 | 35007.5075 | 2309.8065 | 5173.2639 | 29834.2435 | 45337.6542 | 0.058675 | -350085.3484 | 350085.3484
C | Xist Rating 458 | -88.21 | 238.759 | 150.274 | 35.7 | 2389.9 | 9060.76 | 25022.4 | 0.94 | 3.72 | 11.089 | 41.714 | 1 | 1 | 1550 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 570610.1341 | 35429.8158 | 2339.9013 | 5206.8566 | 30222.9592 | 44044.1403 | 0.059056 | -340097.1763 | 340097.1763
C | Xist Rating 459 | -88.09 | 240.183 | 150.274 | 35.7 | 2402.72 | 9263.67 | 24921.6 | 0.93 | 3.7 | 11.096 | 41.373 | 1 | 1 | 1560 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 577092.4978 | 35854.64 | 2370.191 | 5240.4492 | 30614.1909 | 43687.3857 | 0.059437 | -337342.4125 | 337342.4125
C | Xist Rating 460 | -87.69 | 250.58 | 150.274 | 35.7 | 2381.27 | 9070.51 | 24163.3 | 0.93 | 3.56 | 11.118 | 38.686 | 1 | 1 | 1570 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 596698.6366 | 36281.9803 | 2400.6755 | 5274.0418 | 31007.9385 | 40903.0059 | 0.059818 | -315842.1697 | 315842.1697
C | Xist Rating 461 | -87.55 | 253.084 | 150.274 | 35.7 | 2385.44 | 9156.9 | 24008.5 | 0.91 | 3.53 | 11.112 | 38.192 | 1 | 1 | 1580 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 603716.697 | 36711.8365 | 2431.3547 | 5307.6344 | 31404.202 | 40378.4876 | 0.0602 | -311791.978 | 311791.978
C | Xist Rating 462 | -87.43 | 255.624 | 150.274 | 35.7 | 2386.3 | 9195.38 | 23856 | 0.89 | 3.5 | 11.104 | 37.712 | 1 | 1 | 1590 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 609995.5512 | 37144.2086 | 2462.2288 | 5341.2271 | 31802.9816 | 39868.1942 | 0.060581 | -307851.6279 | 307851.6279
C | Xist Rating 463 | -87.27 | 258.853 | 150.274 | 35.7 | 2389.51 | 9279.98 | 23646.1 | 0.88 | 3.46 | 11.103 | 37.021 | 1 | 1 | 1600 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 618531.832 | 37579.0967 | 2493.2976 | 5374.8197 | 32204.277 | 39146.9948 | 0.060962 | -302282.7171 | 302282.7171
C | Xist Rating 464 | -87.19 | 260.697 | 150.274 | 35.7 | 2388.79 | 9284.95 | 23557.4 | 0.86 | 3.45 | 11.092 | 36.781 | 1 | 1 | 1610 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 622750.3866 | 38016.5008 | 2524.5612 | 5408.4123 | 32608.0885 | 38885.4266 | 0.061343 | -300262.9566 | 300262.9566
C | Xist Rating 465 | -86.71 | 272.181 | 150.274 | 35.7 | 2375.23 | 9218.04 | 22805.8 | 0.87 | 3.31 | 11.129 | 34.286 | 1 | 1 | 1620 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 646492.4766 | 38456.4208 | 2556.0196 | 5442.0049 | 33014.4159 | 36309.041 | 0.061724 | -280368.7898 | 280368.7898
C | Xist Rating 466 | -86.61 | 273.68 | 150.274 | 35.7 | 2383.32 | 9357.12 | 22723.9 | 0.85 | 3.29 | 11.129 | 34.05 | 1 | 1 | 1630 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 652267.0176 | 38898.8568 | 2587.6728 | 5475.5975 | 33423.2592 | 36052.0327 | 0.062105 | -278384.2404 | 278384.2404
C | Xist Rating 467 | -86.49 | 276.367 | 150.274 | 35.7 | 2381.41 | 9354.01 | 22589.2 | 0.84 | 3.27 | 11.117 | 33.667 | 1 | 1 | 1640 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 658143.1375 | 39343.8087 | 2619.5208 | 5509.1902 | 33834.6186 | 35649.6059 | 0.062486 | -275276.807 | 275276.807
C | Xist Rating 468 | -86.35 | 279.954 | 150.274 | 35.6 | 2377.48 | 9330.3 | 22403.6 | 0.82 | 3.24 | 11.107 | 33.126 | 1 | 1 | 1650 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 665585.0359 | 39791.2766 | 2651.5635 | 5542.7828 | 34248.4938 | 35074.9132 | 0.062867 | -270839.1824 | 270839.1824
C | Xist Rating 469 | -86.19 | 283.297 | 150.274 | 35.6 | 2378.14 | 9377.28 | 22221.4 | 0.81 | 3.2 | 11.103 | 32.582 | 1 | 1 | 1660 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 673719.9276 | 40241.2605 | 2683.8011 | 5576.3754 | 34664.8851 | 34505.5469 | 0.063248 | -266442.6867 | 266442.6867
C | Xist Rating 470 | -85.77 | 293.738 | 150.274 | 35.6 | 2366.01 | 9311.87 | 21633.7 | 0.81 | 3.1 | 11.138 | 30.787 | 1 | 1 | 1670 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 694987.0454 | 40693.7603 | 2716.2334 | 5609.968 | 35083.7923 | 32647.5957 | 0.063629 | -252096.0801 | 252096.0801
C | Xist Rating 471 | -85.68 | 295.348 | 150.274 | 35.6 | 2370.7 | 9400.75 | 21560.8 | 0.8 | 3.08 | 11.134 | 30.598 | 1 | 1 | 1680 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 700181.5036 | 41148.7761 | 2748.8606 | 5643.5607 | 35505.2154 | 32446.735 | 0.06401 | -250545.0869 | 250545.0869
C | Xist Rating 472 | -85.49 | 299.884 | 150.275 | 35.6 | 2365.42 | 9364.99 | 21346.7 | 0.78 | 3.04 | 11.124 | 30.004 | 1 | 1 | 1690 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 709351.6113 | 41606.3078 | 2781.6825 | 5677.1533 | 35929.1546 | 31816.3998 | 0.064391 | -245677.806 | 245677.806
C | Xist Rating 473 | -85.35 | 302.847 | 150.274 | 35.6 | 2367.41 | 9427.84 | 21206.2 | 0.77 | 3.02 | 11.12 | 29.619 | 1 | 1 | 1700 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 716963.0163 | 42066.3555 | 2814.6992 | 5710.7459 | 36355.6096 | 31411.7559 | 0.064772 | -242553.2524 | 242553.2524
C | Xist Rating 474 | -85.21 | 306.383 | 150.275 | 35.6 | 2365.16 | 9428.99 | 21045.1 | 0.76 | 2.99 | 11.113 | 29.184 | 1 | 1 | 1710 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 724644.8163 | 42528.9192 | 2847.9107 | 5744.3385 | 36784.5807 | 30954.9158 | 0.065153 | -239025.6549 | 239025.6549
C | Xist Rating 475 | -84.81 | 316.078 | 150.275 | 35.6 | 2355.61 | 9389.74 | 20567.5 | 0.76 | 2.9 | 11.147 | 27.829 | 1 | 1 | 1720 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 744556.4976 | 42993.9988 | 2881.317 | 5777.9312 | 37216.0677 | 29553.5285 | 0.065534 | -228204.5136 | 228204.5136
C | Xist Rating 476 | -84.63 | 320.484 | 150.275 | 35.6 | 2352.34 | 9384.21 | 20374.7 | 0.75 | 2.87 | 11.138 | 27.32 | 1 | 1 | 1730 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 753887.3326 | 43461.5944 | 2914.9181 | 5811.5238 | 37650.0706 | 29019.5627 | 0.065915 | -224081.3709 | 224081.3709
C | Xist Rating 477 | -84.53 | 322.639 | 150.275 | 35.6 | 2353.02 | 9415.91 | 20290.4 | 0.74 | 2.85 | 11.131 | 27.116 | 1 | 1 | 1740 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 759176.0198 | 43931.7059 | 2948.714 | 5845.1164 | 38086.5895 | 28802.3624 | 0.066296 | -222404.2075 | 222404.2075
C | Xist Rating 478 | -84.38 | 326.78 | 150.275 | 35.6 | 2348.09 | 9378.44 | 20123.9 | 0.73 | 2.82 | 11.12 | 26.695 | 1 | 1 | 1750 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 767308.8502 | 44404.3334 | 2982.7046 | 5878.709 | 38525.6244 | 28359.4853 | 0.066677 | -218984.4283 | 218984.4283
C | Xist Rating 479 | -84.26 | 329.86 | 150.275 | 35.6 | 2345.24 | 9363.92 | 20000.7 | 0.72 | 2.8 | 11.114 | 26.389 | 1 | 1 | 1760 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 773600.8664 | 44879.4769 | 3016.8901 | 5912.3016 | 38967.1752 | 28036.2299 | 0.067058 | -216488.336 | 216488.336
C | Xist Rating 480 | -83.8 | 341.337 | 150.275 | 35.6 | 2334.67 | 9324.97 | 19497.5 | 0.72 | 2.71 | 11.15 | 25.051 | 1 | 1 | 1770 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 796909.2538 | 45357.1363 | 3051.2703 | 5945.8943 | 39411.242 | 26652.3624 | 0.067439 | -205802.478 | 205802.478
C | Xist Rating 481 | -83.67 | 344.527 | 150.275 | 35.6 | 2333.03 | 9329.09 | 19383.1 | 0.71 | 2.69 | 11.141 | 24.784 | 1 | 1 | 1780 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 803791.8268 | 45837.3116 | 3085.8453 | 5979.4869 | 39857.8248 | 26369.2757 | 0.06782 | -203616.5572 | 203616.5572
C | Xist Rating 482 | -83.59 | 346.396 | 150.275 | 35.6 | 2333.62 | 9353.81 | 19326.4 | 0.7 | 2.68 | 11.134 | 24.669 | 1 | 1 | 1790 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 808356.6335 | 46320.003 | 3120.6151 | 6013.0795 | 40306.9235 | 26244.0618 | 0.068201 | -202649.6887 | 202649.6887
C | Xist Rating 483 | -83.44 | 351.789 | 150.275 | 35.6 | 2320.92 | 9206.38 | 19123 | 0.69 | 2.65 | 11.215 | 24.164 | 1 | 1 | 1800 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 816474.1259 | 46805.2103 | 3155.5797 | 6046.6721 | 40758.5381 | 25718.6397 | 0.068582 | -198592.5184 | 198592.5184
C | Xist Rating 484 | -83.32 | 354.851 | 150.275 | 35.6 | 2320.74 | 9233.05 | 19013 | 0.68 | 2.63 | 11.209 | 23.908 | 1 | 1 | 1810 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 823516.9097 | 47292.9335 | 3190.7391 | 6080.2648 | 41212.6688 | 25446.8227 | 0.068963 | -196493.62 | 196493.62
C | Xist Rating 485 | -82.79 | 366.587 | 150.275 | 35.6 | 2317.23 | 9303.09 | 18562.9 | 0.68 | 2.55 | 11.159 | 22.803 | 1 | 1 | 1820 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 849466.394 | 47783.1727 | 3226.0933 | 6113.8574 | 41669.3153 | 24299.9248 | 0.069344 | -187637.5783 | 187637.5783
C | Xist Rating 486 | -82.71 | 364.687 | 150.275 | 35.6 | 2343.19 | 9714.25 | 18632.3 | 0.67 | 2.56 | 11.28 | 22.976 | 1 | 1 | 1830 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 854530.9315 | 48275.9279 | 3261.6423 | 6147.45 | 42128.4779 | 24480.4829 | 0.069725 | -189031.7997 | 189031.7997
C | Xist Rating 487 | -82.52 | 367.153 | 150.275 | 35.6 | 2353.25 | 9917.5 | 18546.7 | 0.66 | 2.55 | 11.293 | 22.782 | 1 | 1 | 1840 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 864002.7973 | 48771.199 | 3297.386 | 6181.0426 | 42590.1564 | 24273.8061 | 0.070106 | -187435.8961 | 187435.8961
C | Xist Rating 488 | -82.37 | 371.41 | 150.275 | 35.6 | 2347.88 | 9867.32 | 18410.6 | 0.65 | 2.52 | 11.283 | 22.481 | 1 | 1 | 1850 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 872026.1108 | 49268.9861 | 3333.3246 | 6214.6353 | 43054.3508 | 23954.6552 | 0.070487 | -184971.4976 | 184971.4976
C | Xist Rating 489 | -82.2 | 376.158 | 150.275 | 35.6 | 2343.01 | 9831.16 | 18260.3 | 0.64 | 2.5 | 11.277 | 22.149 | 1 | 1 | 1860 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 881341.9556 | 49769.2891 | 3369.4579 | 6248.2279 | 43521.0613 | 23603.4339 | 0.070868 | -182259.4599 | 182259.4599
C | Xist Rating 490 | -81.75 | 386.878 | 150.275 | 35.6 | 2336.14 | 9839.19 | 17880.9 | 0.64 | 2.43 | 11.316 | 21.255 | 1 | 1 | 1870 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 903801.1709 | 50272.1081 | 3405.7861 | 6281.8205 | 43990.2876 | 22680.3436 | 0.071249 | -175131.6016 | 175131.6016
C | Xist Rating 491 | -81.58 | 391.611 | 150.275 | 35.6 | 2330.85 | 9794.73 | 17740.2 | 0.63 | 2.41 | 11.305 | 20.956 | 1 | 1 | 1880 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 912786.4993 | 50777.4431 | 3442.309 | 6315.4131 | 44462.03 | 22362.9589 | 0.07163 | -172680.8407 | 172680.8407
C | Xist Rating 492 | -81.42 | 394.722 | 150.275 | 35.6 | 2334.77 | 9897.5 | 17647.7 | 0.62 | 2.39 | 11.31 | 20.763 | 1 | 1 | 1890 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 921585.0839 | 51285.294 | 3479.0267 | 6349.0057 | 44936.2883 | 22156.4064 | 0.072011 | -171085.8969 | 171085.8969
C | Xist Rating 493 | -81.28 | 398.29 | 150.275 | 35.6 | 2331.83 | 9877.72 | 17556.4 | 0.61 | 2.38 | 11.302 | 20.586 | 1 | 1 | 1900 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 928744.5707 | 51795.6609 | 3515.9392 | 6382.5984 | 45413.0625 | 21965.6873 | 0.072392 | -169613.2152 | 169613.2152
C | Xist Rating 494 | -81.12 | 401.579 | 150.275 | 35.6 | 2332.88 | 9929.81 | 17466.7 | 0.6 | 2.36 | 11.309 | 20.406 | 1 | 1 | 1910 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 936835.6175 | 52308.5438 | 3553.0464 | 6416.191 | 45892.3528 | 21772.5313 | 0.072773 | -168121.7155 | 168121.7155
C | Xist Rating 495 | -80.62 | 414.624 | 150.275 | 35.6 | 2321.75 | 9885.36 | 17051.7 | 0.6 | 2.29 | 11.348 | 19.483 | 1 | 1 | 1920 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 962653.272 | 52823.9426 | 3590.3485 | 6449.7836 | 46374.1589 | 20819.0527 | 0.073154 | -160759.2063 | 160759.2063
C | Xist Rating 496 | -80.43 | 419.434 | 150.275 | 35.6 | 2318.86 | 9882.18 | 16925.4 | 0.59 | 2.27 | 11.343 | 19.233 | 1 | 1 | 1930 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 972608.7252 | 53341.8573 | 3627.8454 | 6483.3762 | 46858.4811 | 20552.4076 | 0.073535 | -158700.2433 | 158700.2433
C | Xist Rating 497 | -80.32 | 420.942 | 150.275 | 35.6 | 2324.51 | 10002.5 | 16883.3 | 0.58 | 2.26 | 11.357 | 19.154 | 1 | 1 | 1940 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 978483.8884 | 53862.288 | 3665.537 | 6516.9689 | 47345.3192 | 20464.2083 | 0.073916 | -158019.1918 | 158019.1918
C | Xist Rating 498 | -80.16 | 425.771 | 150.275 | 35.6 | 2317.85 | 9924.04 | 16773.4 | 0.57 | 2.24 | 11.35 | 18.953 | 1 | 1 | 1950 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 986873.3124 | 54385.2347 | 3703.4235 | 6550.5615 | 47834.6732 | 20248.147 | 0.074297 | -156350.8241 | 156350.8241
C | Xist Rating 499 | -79.97 | 430.952 | 150.275 | 35.6 | 2313.93 | 9907.13 | 16638.1 | 0.56 | 2.22 | 11.352 | 18.685 | 1 | 1 | 1960 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 997192.7614 | 54910.6973 | 3741.5047 | 6584.1541 | 48326.5432 | 19962.8561 | 0.074678 | -154147.8831 | 154147.8831
C | Xist Rating 500 | -79.5 | 442.816 | 150.275 | 35.6 | 2306.13 | 9902.66 | 16304.2 | 0.56 | 2.16 | 11.393 | 17.99 | 1 | 1 | 1970 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 1021191.2621 | 55438.6759 | 3779.7807 | 6617.7467 | 48820.9292 | 19245.9767 | 0.075059 | -148612.3307 | 148612.3307
C | Xist Rating 501 | -79.34 | 446.576 | 150.275 | 35.6 | 2306.47 | 9947 | 16215 | 0.56 | 2.15 | 11.39 | 17.826 | 1 | 1 | 1980 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 1030014.1467 | 55969.1705 | 3818.2515 | 6651.3394 | 49317.8311 | 19078.3737 | 0.07544 | -147318.1447 | 147318.1447
C | Xist Rating 502 | -79.16 | 451.581 | 150.275 | 35.6 | 2301.47 | 9903.18 | 16102.2 | 0.55 | 2.13 | 11.385 | 17.62 | 1 | 1 | 1990 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 6 | E | Rod | 1039300.1241 | 56502.181 | 3856.9171 | 6684.932 | 49817.249 | 18856.8968 | 0.075821 | -145607.959 | 145607.959
C | Xist Rating 503 | -79.01 | 455.467 | 150.275 | 35.6 | 2299.16 | 9898.25 | 16015.6 | 0.54 | 2.12 | 11.374 | 17.465 | 1 | 1 | 2000 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1047191.5077 | 57037.7075 | 3895.7775 | 6718.5246 | 50319.1829 | 18687.9973 | 0.076202 | -144303.7615 | 144303.7615
C | Xist Rating 504 | -78.88 | 458.405 | 150.275 | 35.6 | 2300.42 | 9948.84 | 15954.6 | 0.53 | 2.11 | 11.374 | 17.362 | 1 | 1 | 2010 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1054524.0301 | 57575.7499 | 3934.8326 | 6752.1172 | 50823.6327 | 18573.5374 | 0.076583 | -143419.9324 | 143419.9324
C | Xist Rating 505 | -78.36 | 471.898 | 150.275 | 35.6 | 2290.4 | 9915.56 | 15615.7 | 0.53 | 2.05 | 11.409 | 16.698 | 1 | 1 | 2020 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1080835.1792 | 58116.3083 | 3974.0826 | 6785.7098 | 51330.5985 | 17888.3562 | 0.076964 | -138129.1448 | 138129.1448
C | Xist Rating 506 | -78.16 | 477.023 | 150.275 | 35.6 | 2287.89 | 9922.23 | 15500.5 | 0.53 | 2.03 | 11.404 | 16.489 | 1 | 1 | 2030 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1091376.1515 | 58659.3826 | 4013.5273 | 6819.3025 | 51840.0802 | 17673.7793 | 0.077345 | -136472.2391 | 136472.2391
C | Xist Rating 507 | -78.04 | 480.791 | 150.275 | 35.6 | 2284.02 | 9881.84 | 15432.3 | 0.52 | 2.02 | 11.399 | 16.382 | 1 | 1 | 2040 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1098136.2598 | 59204.973 | 4053.1669 | 6852.8951 | 52352.0779 | 17554.7034 | 0.077726 | -135552.7666 | 135552.7666
C | Xist Rating 508 | -77.9 | 483.743 | 150.275 | 35.6 | 2285.64 | 9944.55 | 15364.9 | 0.51 | 2.01 | 11.396 | 16.262 | 1 | 1 | 2050 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1105662.3505 | 59753.0792 | 4093.0012 | 6886.4877 | 52866.5915 | 17422.1254 | 0.078107 | -134529.0341 | 134529.0341
C | Xist Rating 509 | -77.73 | 489.143 | 150.275 | 35.6 | 2279.33 | 9873.83 | 15264.9 | 0.5 | 1.99 | 11.393 | 16.099 | 1 | 1 | 2060 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1114918.3142 | 60303.7014 | 4133.0303 | 6920.0803 | 53383.6211 | 17244.7939 | 0.078488 | -133159.7274 | 133159.7274
C | Xist Rating 510 | -77.18 | 503.685 | 150.275 | 35.6 | 2269.28 | 9845.89 | 14936.8 | 0.5 | 1.94 | 11.43 | 15.492 | 1 | 1 | 2070 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1143002.2968 | 60856.8396 | 4173.2542 | 6953.673 | 53903.1667 | 16618.6954 | 0.078869 | -128325.1604 | 128325.1604
C | Xist Rating 511 | -77.06 | 507.255 | 150.275 | 35.6 | 2266.91 | 9832.67 | 14874 | 0.5 | 1.93 | 11.425 | 15.395 | 1 | 1 | 2080 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1149901.432 | 61412.4938 | 4213.6729 | 6987.2656 | 54425.2282 | 16520.2897 | 0.07925 | -127565.2976 | 127565.2976
C | Xist Rating 512 | -76.89 | 511.712 | 150.275 | 35.6 | 2264.34 | 9826.11 | 14791.3 | 0.49 | 1.91 | 11.42 | 15.261 | 1 | 1 | 2090 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1158689.9501 | 61970.6639 | 4254.2864 | 7020.8582 | 54949.8057 | 16372.7586 | 0.079631 | -126426.102 | 126426.102
C | Xist Rating 513 | -76.73 | 516.178 | 150.275 | 35.6 | 2261.69 | 9817.81 | 14709.7 | 0.49 | 1.9 | 11.416 | 15.13 | 1 | 1 | 2100 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1167434.6208 | 62531.3499 | 4295.0947 | 7054.4508 | 55476.8991 | 16239.0391 | 0.080012 | -125393.5555 | 125393.5555
C | Xist Rating 514 | -76.59 | 520.157 | 150.275 | 35.6 | 2259.49 | 9812.54 | 14639 | 0.48 | 1.89 | 11.413 | 15.019 | 1 | 1 | 2110 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1175289.5399 | 63094.552 | 4336.0977 | 7088.0435 | 56006.5085 | 16115.3398 | 0.080393 | -124438.3819 | 124438.3819
C | Xist Rating 515 | -76.08 | 534.09 | 150.275 | 35.6 | 2249.6 | 9772.75 | 14359.4 | 0.48 | 1.84 | 11.452 | 14.532 | 1 | 1 | 2120 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1201488.864 | 63660.27 | 4377.2956 | 7121.6361 | 56538.6339 | 15613.8256 | 0.080774 | -120565.8222 | 120565.8222
C | Xist Rating 516 | -75.89 | 539.557 | 150.275 | 35.6 | 2245.52 | 9746.8 | 14264 | 0.47 | 1.83 | 11.447 | 14.382 | 1 | 1 | 2130 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1211586.0346 | 64228.5039 | 4418.6882 | 7155.2287 | 57073.2752 | 15449.3564 | 0.081155 | -119295.8353 | 119295.8353
C | Xist Rating 517 | -75.72 | 545.051 | 150.275 | 35.6 | 2240.11 | 9695.74 | 14170 | 0.47 | 1.81 | 11.443 | 14.235 | 1 | 1 | 2140 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1220974.1956 | 64799.2538 | 4460.2756 | 7188.8213 | 57610.4325 | 15298.9284 | 0.081536 | -118134.2702 | 118134.2702
C | Xist Rating 518 | -75.61 | 548.14 | 150.275 | 35.6 | 2238.98 | 9699.77 | 14123.5 | 0.46 | 1.81 | 11.439 | 14.171 | 1 | 1 | 2150 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1227274.4972 | 65372.5197 | 4502.0578 | 7222.4139 | 58150.1057 | 15223.67 | 0.081917 | -117553.1446 | 117553.1446
C | Xist Rating 519 | -75.47 | 552.065 | 150.275 | 35.6 | 2237.48 | 9706.58 | 14059.1 | 0.46 | 1.79 | 11.435 | 14.074 | 1 | 1 | 2160 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1235234.3962 | 65948.3015 | 4544.0348 | 7256.0066 | 58692.2949 | 15125.1162 | 0.082298 | -116792.1379 | 116792.1379
C | Xist Rating 520 | -74.93 | 567.26 | 150.275 | 35.6 | 2226.44 | 9650.82 | 13786.1 | 0.46 | 1.75 | 11.474 | 13.625 | 1 | 1 | 2170 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1262970.3544 | 66526.5992 | 4586.2066 | 7289.5992 | 59237.0001 | 14662.9332 | 0.082679 | -113223.2836 | 113223.2836
C | Xist Rating 521 | -74.74 | 572.502 | 150.275 | 35.6 | 2224.32 | 9660.41 | 13699.1 | 0.45 | 1.74 | 11.469 | 13.492 | 1 | 1 | 2180 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1273427.6486 | 67107.413 | 4628.5732 | 7323.1918 | 59784.2212 | 14515.7468 | 0.08306 | -112086.749 | 112086.749
C | Xist Rating 522 | -74.6 | 576.661 | 150.275 | 35.6 | 2221.98 | 9650.66 | 13639 | 0.45 | 1.73 | 11.465 | 13.409 | 1 | 1 | 2190 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1281329.2088 | 67690.7427 | 4671.1346 | 7356.7844 | 60333.9582 | 14431.6881 | 0.083441 | -111437.6705 | 111437.6705
C | Xist Rating 523 | -74.46 | 581.226 | 150.275 | 35.6 | 2218.08 | 9611.54 | 13579.4 | 0.44 | 1.72 | 11.462 | 13.331 | 1 | 1 | 2200 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1289205.7661 | 68276.5883 | 4713.8907 | 7390.3771 | 60886.2113 | 14341.5616 | 0.083822 | -110741.7371 | 110741.7371
C | Xist Rating 524 | -74.26 | 586.727 | 150.275 | 35.6 | 2215.23 | 9606.7 | 13495.4 | 0.43 | 1.7 | 11.46 | 13.207 | 1 | 1 | 2210 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1299735.2522 | 68864.9499 | 4756.8417 | 7423.9697 | 61440.9803 | 14203.6087 | 0.084203 | -109676.5013 | 109676.5013
C | Xist Rating 525 | -73.73 | 601.788 | 150.275 | 35.6 | 2205.73 | 9575.46 | 13246.2 | 0.43 | 1.66 | 11.498 | 12.816 | 1 | 1 | 2220 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1327381.8452 | 69455.8275 | 4799.9874 | 7457.5623 | 61998.2652 | 13801.3907 | 0.084584 | -106570.6805 | 106570.6805
C | Xist Rating 526 | -73.57 | 606.216 | 150.275 | 35.6 | 2204.51 | 9590.94 | 13182.5 | 0.43 | 1.65 | 11.494 | 12.727 | 1 | 1 | 2230 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1336409.2342 | 70049.2211 | 4843.3279 | 7491.1549 | 62558.0661 | 13711.0086 | 0.084965 | -105872.7739 | 105872.7739
C | Xist Rating 527 | -73.39 | 611.585 | 150.275 | 35.6 | 2201.35 | 9574.5 | 13111.7 | 0.42 | 1.64 | 11.49 | 12.632 | 1 | 1 | 2240 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1346312.6398 | 70645.1305 | 4886.8633 | 7524.7475 | 63120.383 | 13602.8572 | 0.085346 | -105037.6574 | 105037.6574
C | Xist Rating 528 | -73.2 | 617.393 | 150.275 | 35.6 | 2197.35 | 9546.63 | 13034 | 0.42 | 1.63 | 11.486 | 12.526 | 1 | 1 | 2250 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1356628.5085 | 71243.556 | 4930.5934 | 7558.3402 | 63685.2158 | 13494.77 | 0.085727 | -104203.0373 | 104203.0373
C | Xist Rating 529 | -73.08 | 620.444 | 150.275 | 35.6 | 2197.36 | 9570.74 | 12995.5 | 0.42 | 1.62 | 11.481 | 12.479 | 1 | 1 | 2260 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1363338.8278 | 71844.4974 | 4974.5182 | 7591.9328 | 64252.5646 | 13447.9103 | 0.086108 | -103841.1985 | 103841.1985
C | Xist Rating 530 | -72.51 | 636.862 | 150.275 | 35.6 | 2187.03 | 9528.96 | 12751.7 | 0.41 | 1.59 | 11.521 | 12.117 | 1 | 1 | 2270 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1392836.2999 | 72447.9548 | 5018.6379 | 7625.5254 | 64822.4294 | 13064.1219 | 0.086489 | -100877.6864 | 100877.6864
C | Xist Rating 531 | -72.34 | 642.176 | 150.275 | 35.6 | 2183.88 | 9511.5 | 12686.1 | 0.41 | 1.58 | 11.516 | 12.032 | 1 | 1 | 2280 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1402435.3229 | 73053.9281 | 5062.9524 | 7659.118 | 65394.8101 | 12977.7574 | 0.08687 | -100210.8023 | 100210.8023
C | Xist Rating 532 | -72.14 | 648.218 | 150.275 | 35.6 | 2180.55 | 9499.86 | 12606.9 | 0.41 | 1.56 | 11.51 | 11.924 | 1 | 1 | 2290 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1413471.7599 | 73662.4174 | 5107.4617 | 7692.7107 | 65969.7067 | 12867.4634 | 0.087251 | -99359.1419 | 99359.1419
C | Xist Rating 533 | -72.01 | 652.541 | 150.275 | 35.6 | 2176.86 | 9462.5 | 12557 | 0.4 | 1.56 | 11.505 | 11.864 | 1 | 1 | 2300 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1420490.4013 | 74273.4226 | 5152.1657 | 7726.3033 | 66547.1194 | 12795.1962 | 0.087632 | -98801.1137 | 98801.1137
| Xist Rating 534 | -71.87 | 657.128 | 150.275 | 35.6 | 2173.66 | 9434.34 | 12507.6 | 0.4 | 1.55 | 11.503 | 11.806 | 1 | 1 | 2310 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1428372.8485 | 74886.9438 | 5197.0645 | 7759.8959 | 67127.0479 | 12736.9433 | 0.088013 | -98351.3001 | 98351.3001
| Xist Rating 535 | -71.3 | 673.871 | 150.275 | 35.6 | 2164.19 | 9408.93 | 12277.1 | 0.4 | 1.51 | 11.542 | 11.477 | 1 | 1 | 2320 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1458384.8795 | 75502.981 | 5242.1582 | 7793.4885 | 67709.4925 | 12398.9621 | 0.088394 | -95741.4988 | 95741.4988
| Xist Rating 536 | -71.13 | 679.217 | 150.275 | 35.6 | 2161.04 | 9390.44 | 12216.8 | 0.39 | 1.5 | 11.537 | 11.403 | 1 | 1 | 2330 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1467815.1057 | 76121.5341 | 5287.4466 | 7827.0812 | 68294.453 | 12311.9244 | 0.088775 | -95069.4166 | 95069.4166
| Xist Rating 537 | -70.96 | 684.539 | 150.275 | 35.6 | 2157.85 | 9370.91 | 12157.2 | 0.39 | 1.49 | 11.531 | 11.33 | 1 | 1 | 2340 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1477132.4811 | 76742.6032 | 5332.9298 | 7860.6738 | 68881.9294 | 12237.8854 | 0.089156 | -94497.7073 | 94497.7073
| Xist Rating 538 | -70.81 | 689.467 | 150.275 | 35.6 | 2154.97 | 9352.54 | 12104.7 | 0.38 | 1.49 | 11.527 | 11.268 | 1 | 1 | 2350 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1485780.701 | 77366.1883 | 5378.6078 | 7894.2664 | 69471.9219 | 12163.2077 | 0.089537 | -93921.0657 | 93921.0657
| Xist Rating 539 | -70.62 | 695.326 | 150.275 | 35.6 | 2151.67 | 9335.03 | 12039.8 | 0.38 | 1.48 | 11.523 | 11.189 | 1 | 1 | 2360 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1496112.0944 | 77992.2893 | 5424.4805 | 7927.859 | 70064.4302 | 12082.969 | 0.089918 | -93301.4835 | 93301.4835
| Xist Rating 540 | -70.1 | 710.815 | 150.275 | 35.6 | 2143.26 | 9311.89 | 11846.8 | 0.38 | 1.45 | 11.56 | 10.928 | 1 | 1 | 2370 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1523461.3569 | 78620.9062 | 5470.5481 | 7961.4516 | 70659.4546 | 11815.3773 | 0.090299 | -91235.2115 | 91235.2115
| Xist Rating 541 | -69.93 | 716.376 | 150.275 | 35.6 | 2139.9 | 9288.02 | 11791.2 | 0.37 | 1.44 | 11.556 | 10.864 | 1 | 1 | 2380 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1532973.0024 | 79252.0391 | 5516.8105 | 7995.0443 | 71256.9949 | 11738.392 | 0.09068 | -90640.7518 | 90640.7518
| Xist Rating 542 | -69.75 | 721.79 | 150.275 | 35.6 | 2137.75 | 9291.34 | 11730 | 0.37 | 1.43 | 11.55 | 10.789 | 1 | 1 | 2390 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1543006.5725 | 79885.688 | 5563.2676 | 8028.6369 | 71857.0511 | 11662.1834 | 0.091061 | -90052.2889 | 90052.2889
C | Xist Rating 543 | -66.74 | 828.325 | 150.275 | 35.6 | 2049.63 | 8572.87 | 10538.2 | 0.41 | 1.25 | 11.546 | 9.272 | 1 | 1 | 2400 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1697759.7698 | 80521.8529 | 5609.9196 | 8062.2295 | 72459.6233 | 10138.222 | 0.091442 | -78284.6631 | 78284.6631
C | Xist Rating 544 | -66.45 | 829.771 | 150.275 | 35.6 | 2064.44 | 8838.2 | 10538 | 0.39 | 1.25 | 11.547 | 9.281 | 1 | 1 | 2410 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1713012.4432 | 81160.5337 | 5656.7663 | 8095.8221 | 73064.7115 | 10124.7869 | 0.091823 | -78180.9206 | 78180.9206
C | Xist Rating 545 | -66.44 | 831.172 | 150.275 | 35.6 | 2063.49 | 8820.95 | 10538 | 0.39 | 1.25 | 11.587 | 9.292 | 1 | 1 | 2420 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1715115.1103 | 81801.7304 | 5703.8078 | 8129.4148 | 73672.3156 | 10139.9212 | 0.092204 | -78297.7836 | 78297.7836
C | Xist Rating 546 | -66.11 | 832.529 | 150.275 | 35.6 | 2080.5 | 9140.37 | 10537.8 | 0.39 | 1.25 | 11.58 | 9.302 | 1 | 1 | 2430 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1732076.5845 | 82445.4431 | 5751.0441 | 8163.0074 | 74282.4357 | 10152.0344 | 0.092585 | -78391.3187 | 78391.3187
C | Xist Rating 547 | -66.08 | 833.899 | 150.275 | 35.6 | 2079.93 | 9129.37 | 10537.9 | 0.38 | 1.25 | 11.574 | 9.312 | 1 | 1 | 2440 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1734451.5471 | 83091.6718 | 5798.4752 | 8196.6 | 74895.0718 | 10151.5291 | 0.092966 | -78387.4168 | 78387.4168
C | Xist Rating 548 | -66.06 | 835.226 | 150.275 | 35.6 | 2079.21 | 9115.49 | 10537.9 | 0.38 | 1.25 | 11.569 | 9.323 | 1 | 1 | 2450 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1736610.2515 | 83740.4164 | 5846.1011 | 8230.1926 | 75510.2238 | 10164.7154 | 0.093347 | -78489.2377 | 78489.2377
C | Xist Rating 549 | -66.03 | 836.698 | 150.275 | 35.6 | 2078.55 | 9103.03 | 10537.8 | 0.37 | 1.25 | 11.567 | 9.334 | 1 | 1 | 2460 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1739118.6279 | 84391.677 | 5893.9217 | 8263.7853 | 76127.8918 | 10165.2709 | 0.093728 | -78493.5271 | 78493.5271
C | Xist Rating 550 | -66.01 | 838.051 | 150.275 | 35.6 | 2077.48 | 9082.48 | 10537.8 | 0.37 | 1.25 | 11.602 | 9.345 | 1 | 1 | 2470 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1741034.1915 | 85045.4536 | 5941.9372 | 8297.3779 | 76748.0757 | 10180.0465 | 0.094109 | -78607.6209 | 78607.6209
C | Xist Rating 551 | -65.99 | 839.399 | 150.275 | 35.6 | 2076.7 | 9067.53 | 10537.8 | 0.36 | 1.25 | 11.598 | 9.355 | 1 | 1 | 2480 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1743179.9033 | 85701.7461 | 5990.1474 | 8330.9705 | 77370.7756 | 10179.2983 | 0.09449 | -78601.8429 | 78601.8429
C | Xist Rating 552 | -65.96 | 840.797 | 150.275 | 35.6 | 2076.18 | 9057.64 | 10537.9 | 0.35 | 1.25 | 11.594 | 9.366 | 1 | 1 | 2490 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1745645.9155 | 86360.5546 | 6038.5525 | 8364.5631 | 77995.9914 | 10179.4921 | 0.094871 | -78603.3399 | 78603.3399
C | Xist Rating 553 | -65.95 | 841.782 | 150.276 | 35.6 | 2075.9 | 9052.22 | 10537.9 | 0.35 | 1.25 | 11.594 | 9.375 | 1 | 1 | 2500 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1747455.2538 | 87021.879 | 6087.1523 | 8398.1557 | 78623.7232 | 10190.6575 | 0.095252 | -78689.5563 | 78689.5563
C | Xist Rating 554 | -65.93 | 843.631 | 150.276 | 35.6 | 2072.87 | 8994.93 | 10537.9 | 0.34 | 1.25 | 11.592 | 9.387 | 1 | 1 | 2510 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1748737.391 | 87685.7194 | 6135.9469 | 8431.7484 | 79253.971 | 10191.8176 | 0.095633 | -78698.5137 | 78698.5137
C | Xist Rating 555 | -65.91 | 845.085 | 150.276 | 35.6 | 2071.57 | 8970.56 | 10537.9 | 0.34 | 1.25 | 11.63 | 9.398 | 1 | 1 | 2520 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1750652.7335 | 88352.0757 | 6184.9363 | 8465.341 | 79886.7347 | 10206.4671 | 0.096014 | -78811.6338 | 78811.6338
C | Xist Rating 556 | -65.89 | 846.423 | 150.276 | 35.6 | 2071.28 | 8964.98 | 10537.9 | 0.33 | 1.25 | 11.624 | 9.409 | 1 | 1 | 2530 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1753179.0314 | 89020.948 | 6234.1205 | 8498.9336 | 80522.0144 | 10206.2494 | 0.096395 | -78809.9522 | 78809.9522
C | Xist Rating 557 | -65.87 | 847.574 | 150.276 | 35.6 | 2070.69 | 8953.93 | 10537.9 | 0.33 | 1.25 | 11.619 | 9.418 | 1 | 1 | 2540 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1755063.0061 | 89692.3363 | 6283.4995 | 8532.5262 | 81159.8101 | 10217.1274 | 0.096776 | -78893.9497 | 78893.9497
C | Xist Rating 558 | -65.83 | 849.121 | 150.276 | 35.6 | 2069.73 | 8936.04 | 10538 | 0.32 | 1.25 | 11.615 | 9.429 | 1 | 1 | 2550 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1757451.2073 | 90366.2405 | 6333.0732 | 8566.1189 | 81800.1217 | 10216.8425 | 0.097157 | -78891.7492 | 78891.7492
C | Xist Rating 559 | -65.81 | 850.57 | 150.276 | 35.6 | 2069.1 | 8924.36 | 10537.9 | 0.32 | 1.25 | 11.613 | 9.44 | 1 | 1 | 2560 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1759914.387 | 91042.6607 | 6382.8418 | 8599.7115 | 82442.9492 | 10229.8585 | 0.097538 | -78992.256 | 78992.256
C | Xist Rating 560 | -65.79 | 851.959 | 150.276 | 35.6 | 2068.11 | 8906.07 | 10537.8 | 0.31 | 1.25 | 11.609 | 9.45 | 1 | 1 | 2570 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1761944.9275 | 91721.5968 | 6432.8051 | 8633.3041 | 83088.2927 | 10228.3883 | 0.097919 | -78980.9034 | 78980.9034
C | Xist Rating 561 | -65.77 | 853.324 | 150.276 | 35.6 | 2067.07 | 8886.83 | 10537.8 | 0.31 | 1.25 | 11.643 | 9.46 | 1 | 1 | 2580 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1763880.4407 | 92403.049 | 6482.9633 | 8666.8967 | 83736.1522 | 10241.6054 | 0.0983 | -79082.962 | 79082.962
C | Xist Rating 562 | -65.75 | 854.684 | 150.276 | 35.6 | 2065.98 | 8866.68 | 10537.8 | 0.31 | 1.25 | 11.638 | 9.47 | 1 | 1 | 2590 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1765760.0503 | 93087.017 | 6533.3162 | 8700.4894 | 84386.5277 | 10253.4283 | 0.098681 | -79174.2554 | 79174.2554
C | Xist Rating 563 | -65.74 | 855.862 | 150.276 | 35.6 | 2065.16 | 8851.68 | 10537.8 | 0.3 | 1.25 | 11.632 | 9.479 | 1 | 1 | 2600 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1767491.9679 | 93773.501 | 6583.8639 | 8734.082 | 85039.4191 | 10250.6188 | 0.099062 | -79152.561 | 79152.561
C | Xist Rating 564 | -65.71 | 857.549 | 150.276 | 35.6 | 2063.78 | 8826.39 | 10537.8 | 0.3 | 1.25 | 11.629 | 9.491 | 1 | 1 | 2610 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1769792.4752 | 94462.501 | 6634.6064 | 8767.6746 | 85694.8264 | 10264.5397 | 0.099443 | -79260.0544 | 79260.0544
C | Xist Rating 565 | -65.69 | 858.945 | 150.276 | 35.6 | 2062.91 | 8810.47 | 10537.8 | 0.29 | 1.25 | 11.628 | 9.501 | 1 | 1 | 2620 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1771926.23 | 95154.017 | 6685.5437 | 8801.2672 | 86352.7497 | 10262.7972 | 0.099824 | -79246.5997 | 79246.5997
C | Xist Rating 566 | -65.66 | 860.372 | 150.276 | 35.6 | 2062.36 | 8800.35 | 10537.8 | 0.29 | 1.25 | 11.665 | 9.511 | 1 | 1 | 2630 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1774396.7979 | 95848.0489 | 6736.6758 | 8834.8598 | 87013.189 | 10275.9587 | 0.10021 | -79348.2291 | 79348.2291
C | Xist Rating 567 | -65.63 | 861.618 | 150.276 | 35.6 | 2062.27 | 8798.76 | 10537.8 | 0.29 | 1.25 | 11.66 | 9.521 | 1 | 1 | 2640 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1776888.9529 | 96544.5967 | 6788.0027 | 8868.4525 | 87676.1442 | 10287.6884 | 0.10059 | -79438.8031 | 79438.8031
C | Xist Rating 568 | -65.59 | 863.121 | 150.276 | 35.6 | 2061.84 | 8790.93 | 10537.8 | 0.28 | 1.25 | 11.658 | 9.531 | 1 | 1 | 2650 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1779617.4026 | 97243.6605 | 6839.5243 | 8902.0451 | 88341.6154 | 10285.6722 | 0.10097 | -79423.2345 | 79423.2345
C | Xist Rating 569 | -65.57 | 864.461 | 150.276 | 35.6 | 2061.33 | 8781.74 | 10537.8 | 0.28 | 1.25 | 11.654 | 9.541 | 1 | 1 | 2660 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1781939.3931 | 97945.2403 | 6891.2408 | 8935.6377 | 89009.6026 | 10297.3869 | 0.10135 | -79513.6918 | 79513.6918
C | Xist Rating 570 | -65.52 | 865.849 | 150.276 | 35.6 | 2061.76 | 8789.52 | 10537.8 | 0.27 | 1.25 | 11.654 | 9.551 | 1 | 1 | 2670 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1785172.8342 | 98649.336 | 6943.152 | 8969.2303 | 89680.1057 | 10295.2868 | 0.10173 | -79497.4757 | 79497.4757
C | Xist Rating 571 | -65.49 | 867.265 | 150.276 | 35.6 | 2061.29 | 8780.96 | 10537.8 | 0.27 | 1.25 | 11.69 | 9.561 | 1 | 1 | 2680 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1787684.6719 | 99355.9477 | 6995.258 | 9002.823 | 90353.1248 | 10308.2499 | 0.10211 | -79597.5733 | 79597.5733
C | Xist Rating 572 | -65.44 | 868.642 | 150.276 | 35.6 | 2062.37 | 8800.66 | 10537.8 | 0.27 | 1.25 | 11.689 | 9.571 | 1 | 1 | 2690 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1791461.2015 | 100065.0754 | 7047.5588 | 9036.4156 | 91028.6598 | 10320.0171 | 0.10249 | -79688.4367 | 79688.4367
C | Xist Rating 573 | -65.41 | 869.843 | 150.276 | 35.6 | 2062.37 | 8800.59 | 10537.9 | 0.26 | 1.25 | 11.685 | 9.58 | 1 | 1 | 2700 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1793938.1079 | 100776.719 | 7100.0544 | 9070.0082 | 91706.7108 | 10316.5056 | 0.10287 | -79661.3219 | 79661.3219
C | Xist Rating 574 | -65.35 | 871.499 | 150.276 | 35.6 | 2062.71 | 8806.73 | 10537.9 | 0.26 | 1.25 | 11.686 | 9.591 | 1 | 1 | 2710 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1797649.7023 | 101490.8786 | 7152.7448 | 9103.6008 | 92387.2777 | 10329.3225 | 0.10325 | -79760.2905 | 79760.2905
C | Xist Rating 575 | -65.31 | 872.843 | 150.276 | 35.6 | 2063.22 | 8815.92 | 10538 | 0.26 | 1.25 | 11.683 | 9.601 | 1 | 1 | 2720 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1800867.1345 | 102207.5541 | 7205.63 | 9137.1935 | 93070.3606 | 10340.9743 | 0.10363 | -79850.2627 | 79850.2627
C | Xist Rating 576 | -65.07 | 874.165 | 150.276 | 35.6 | 2075.26 | 9039.84 | 10538.2 | 0.25 | 1.25 | 11.743 | 9.611 | 1 | 1 | 2730 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1814119.6579 | 102926.7456 | 7258.71 | 9170.7861 | 93755.9595 | 10340.2598 | 0.10402 | -79844.7455 | 79844.7455
C | Xist Rating 577 | -65.21 | 875.449 | 150.276 | 35.6 | 2065.35 | 8854.95 | 10538.1 | 0.25 | 1.25 | 11.719 | 9.62 | 1 | 1 | 2740 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1808108.5921 | 103648.453 | 7311.9847 | 9204.3787 | 94444.0743 | 10350.1853 | 0.1044 | -79921.3877 | 79921.3877
C | Xist Rating 578 | -64.87 | 876.997 | 150.276 | 35.6 | 2082.73 | 9183.14 | 10538.3 | 0.24 | 1.25 | 11.751 | 9.631 | 1 | 1 | 2750 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1826547.9618 | 104372.6764 | 7365.4543 | 9237.9713 | 95134.7051 | 10349.423 | 0.10478 | -79915.5012 | 79915.5012
C | Xist Rating 579 | -64.69 | 878.421 | 150.276 | 35.6 | 2091.56 | 9357.42 | 10538.4 | 0.24 | 1.25 | 11.767 | 9.642 | 1 | 1 | 2760 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1837270.2268 | 105099.4158 | 7419.1186 | 9271.5639 | 95827.8519 | 10362.5857 | 0.10516 | -80017.1402 | 80017.1402
C | Xist Rating 580 | -64.55 | 879.657 | 150.276 | 35.6 | 2098.14 | 9490.47 | 10538.4 | 0.23 | 1.25 | 11.78 | 9.651 | 1 | 1 | 2770 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1845643.538 | 105828.6711 | 7472.9777 | 9305.1566 | 96523.5146 | 10358.9589 | 0.10554 | -79989.1351 | 79989.1351
C | Xist Rating 581 | -64.47 | 881.204 | 150.276 | 35.6 | 2099.86 | 9525.83 | 10538.4 | 0.23 | 1.25 | 11.823 | 9.662 | 1 | 1 | 2780 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1850405.0314 | 106560.4424 | 7527.0316 | 9338.7492 | 97221.6932 | 10372.8293 | 0.10592 | -80096.2385 | 80096.2385
C | Xist Rating 582 | -64.39 | 882.613 | 150.276 | 35.6 | 2102.32 | 9576.54 | 10538.4 | 0.23 | 1.25 | 11.828 | 9.671 | 1 | 1 | 2790 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1855534.9622 | 107294.7297 | 7581.2803 | 9372.3418 | 97922.3879 | 10383.5385 | 0.1063 | -80178.9322 | 80178.9322
C | Xist Rating 583 | -64.34 | 883.587 | 150.276 | 35.6 | 2104.83 | 9628.92 | 10538.3 | 0.23 | 1.25 | 11.831 | 9.679 | 1 | 1 | 2800 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1859800.4252 | 108031.5329 | 7635.7238 | 9405.9344 | 98625.5984 | 10393.1526 | 0.10668 | -80253.1691 | 80253.1691
C | Xist Rating 584 | -64.26 | 885.332 | 150.276 | 35.6 | 2105.5 | 9642.86 | 10538.4 | 0.22 | 1.25 | 11.838 | 9.691 | 1 | 1 | 2810 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1864066.526 | 108770.852 | 7690.3621 | 9439.5271 | 99331.325 | 10392.1262 | 0.10706 | -80245.2442 | 80245.2442
C | Xist Rating 585 | -64.21 | 886.807 | 150.276 | 35.6 | 2106.23 | 9658.36 | 10538.4 | 0.22 | 1.25 | 11.841 | 9.701 | 1 | 1 | 2820 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1867819.5076 | 109512.6872 | 7745.1952 | 9473.1197 | 100039.5675 | 10403.7621 | 0.10744 | -80335.0928 | 80335.0928
C | Xist Rating 586 | -64.15 | 888.179 | 150.276 | 35.6 | 2107.82 | 9691.86 | 10538.4 | 0.22 | 1.25 | 11.88 | 9.71 | 1 | 1 | 2830 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1872121.4598 | 110257.0382 | 7800.223 | 9506.7123 | 100750.3259 | 10415.3646 | 0.10783 | -80424.6849 | 80424.6849
C | Xist Rating 587 | -64.09 | 889.497 | 150.276 | 35.6 | 2108.93 | 9715.34 | 10538.3 | 0.21 | 1.25 | 11.88 | 9.719 | 1 | 1 | 2840 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1875886.9082 | 111003.9053 | 7855.4457 | 9540.3049 | 101463.6003 | 10410.7592 | 0.10821 | -80389.1228 | 80389.1228
C | Xist Rating 588 | -64.04 | 890.94 | 150.276 | 35.6 | 2109.66 | 9730.94 | 10538.3 | 0.21 | 1.25 | 11.881 | 9.729 | 1 | 1 | 2850 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1879580.4804 | 111753.2883 | 7910.8631 | 9573.8976 | 102179.3907 | 10422.2893 | 0.10859 | -80478.1551 | 80478.1551
C | Xist Rating 589 | -63.99 | 892.345 | 150.276 | 35.6 | 2110.41 | 9746.98 | 10538.3 | 0.21 | 1.25 | 11.883 | 9.738 | 1 | 1 | 2860 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1883213.8114 | 112505.1872 | 7966.4753 | 9607.4902 | 102897.6971 | 10432.808 | 0.10897 | -80559.3778 | 80559.3778
C | Xist Rating 590 | -63.94 | 893.536 | 150.276 | 35.6 | 2111.78 | 9776.28 | 10538.2 | 0.21 | 1.25 | 11.886 | 9.747 | 1 | 1 | 2870 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1886951.4541 | 113259.6022 | 8022.2824 | 9641.0828 | 103618.5194 | 10443.3541 | 0.10935 | -80640.812 | 80640.812
C | Xist Rating 591 | -63.89 | 895.045 | 150.276 | 35.5 | 2112.55 | 9792.91 | 10538.2 | 0.2 | 1.25 | 11.929 | 9.757 | 1 | 1 | 2880 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1890827.3148 | 114016.533 | 8078.2842 | 9674.6754 | 104341.8576 | 10440.6239 | 0.10973 | -80619.7303 | 80619.7303
C | Xist Rating 592 | -63.83 | 896.387 | 150.276 | 35.5 | 2113.77 | 9819.12 | 10538.2 | 0.2 | 1.25 | 11.93 | 9.766 | 1 | 1 | 2890 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1894755.949 | 114775.9799 | 8134.4807 | 9708.268 | 105067.7118 | 10451.0657 | 0.11011 | -80700.3593 | 80700.3593
C | Xist Rating 593 | -63.77 | 897.773 | 150.276 | 35.5 | 2114.87 | 9843.1 | 10538.1 | 0.2 | 1.25 | 11.928 | 9.775 | 1 | 1 | 2900 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1898673.1845 | 115537.9427 | 8190.8721 | 9741.8607 | 105796.082 | 10461.4297 | 0.11049 | -80780.3874 | 80780.3874
C | Xist Rating 594 | -63.7 | 899.313 | 150.276 | 35.5 | 2116.62 | 9881.06 | 10538.1 | 0.2 | 1.25 | 11.932 | 9.785 | 1 | 1 | 2910 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1903503.8821 | 116302.4214 | 8247.4583 | 9775.4533 | 106526.9681 | 10472.9884 | 0.11087 | -80869.6404 | 80869.6404
C | Xist Rating 595 | -63.65 | 900.704 | 150.276 | 35.5 | 2117.98 | 9911.3 | 10537.6 | 0.19 | 1.25 | 11.942 | 9.794 | 1 | 1 | 2920 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1907673.0579 | 117069.4161 | 8304.2393 | 9809.0459 | 107260.3702 | 10468.0357 | 0.11125 | -80831.3971 | 80831.3971
C | Xist Rating 598 | -63.62 | 904.865 | 150.276 | 35.5 | 2114.46 | 9835.43 | 10536.7 | 0.19 | 1.25 | 11.983 | 9.821 | 1 | 1 | 2950 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1913300.8479 | 119385.496 | 8475.7509 | 9909.8238 | 109475.6722 | 10500.1565 | 0.1124 | -81079.4249 | 81079.4249
C | Xist Rating 599 | -63.61 | 906.237 | 150.276 | 35.5 | 2113.38 | 9812.43 | 10536.4 | 0.19 | 1.25 | 11.979 | 9.83 | 1 | 1 | 2960 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1915223.1511 | 120162.5546 | 8533.311 | 9943.4164 | 110219.1382 | 10510.4227 | 0.11278 | -81158.6978 | 81158.6978
C | Xist Rating 600 | -63.9 | 907.62 | 150.276 | 35.4 | 2101.37 | 9557.81 | 10537.5 | 0.18 | 1.25 | 11.987 | 9.838 | 1 | 1 | 2970 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1907245.4394 | 120942.1291 | 8591.0659 | 9977.009 | 110965.1201 | 10503.995 | 0.11316 | -81109.0652 | 81109.0652
C | Xist Rating 601 | -63.91 | 908.844 | 150.276 | 35.4 | 2099.89 | 9527.66 | 10537.2 | 0.18 | 1.25 | 12.026 | 9.846 | 1 | 1 | 2980 | 152.4 | 2 | 1.2 | 19.05 | 1.3333 | 5 | E | Rod | 1908472.4272 | 121724.2195 | 8649.0156 | 10010.6017 | 111713.6179 | 10514.2079 | 0.11354 | -81187.9263 | 81187.9263
C | Xist Rating 604 | -95.94 | 77.233 | 150.277 | 35.8 | 2417.31 | 7575.11 | 58745.7 | 2.44 | 10.95 | 12.229 | 304.327 | 1 | 1 | 1000 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 186696.1032 | 17267.3129 | 973.9444 | 3639.2008 | 13628.112 | 317380.6203 | 0.038101 | -2450729.0217 | 2450729.0217
C | Xist Rating 605 | -95.9 | 78.079 | 150.277 | 35.8 | 2418.37 | 7594.49 | 58284.1 | 2.42 | 10.85 | 12.232 | 298.68 | 1 | 1 | 1010 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 188823.9112 | 17577.6299 | 993.5206 | 3675.5928 | 13902.0371 | 311518.8507 | 0.038482 | -2405465.9905 | 2405465.9905
C | Xist Rating 606 | -95.59 | 84.256 | 150.277 | 35.8 | 2408.81 | 7568.53 | 54967.4 | 2.43 | 10.07 | 12.282 | 258.826 | 1 | 1 | 1020 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 202956.6954 | 17890.6726 | 1013.2917 | 3711.9848 | 14178.6878 | 270154.9512 | 0.038863 | -2086064.9228 | 2086064.9228
C | Xist Rating 607 | -95.52 | 86.093 | 150.277 | 35.8 | 2396.82 | 7468.41 | 54179 | 2.34 | 9.89 | 12.112 | 250.348 | 1 | 1 | 1030 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 206349.4243 | 18206.4409 | 1033.2576 | 3748.3768 | 14458.0641 | 261294.5387 | 0.039244 | -2017647.1663 | 2017647.1663
C | Xist Rating 608 | -95.45 | 87.013 | 150.277 | 35.8 | 2413.04 | 7636.93 | 53795.6 | 2.27 | 9.8 | 12.075 | 246.307 | 1 | 1 | 1040 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 209965.8495 | 18524.9348 | 1053.4182 | 3784.7689 | 14740.166 | 257067.2311 | 0.039625 | -1985005.0177 | 1985005.0177
C | Xist Rating 609 | -95.35 | 88.728 | 150.277 | 35.8 | 2420.27 | 7727.9 | 53044.9 | 2.22 | 9.63 | 12.044 | 238.24 | 1 | 1 | 1050 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 214745.7166 | 18846.1544 | 1073.7737 | 3821.1609 | 15024.9935 | 248670.2958 | 0.040006 | -1920166.1091 | 1920166.1091
C | Xist Rating 610 | -95.28 | 89.629 | 150.277 | 35.8 | 2433.19 | 7870.51 | 52677.1 | 2.17 | 9.54 | 12.023 | 234.452 | 1 | 1 | 1060 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 218084.3865 | 19170.0995 | 1094.3239 | 3857.5529 | 15312.5467 | 244717.6707 | 0.040387 | -1889644.9853 | 1889644.9853
C | Xist Rating 611 | -94.97 | 96.384 | 150.277 | 35.8 | 2411.88 | 7724.82 | 49858.4 | 2.16 | 8.9 | 11.998 | 205.229 | 1 | 1 | 1070 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 232466.6419 | 19496.7703 | 1115.0689 | 3893.9449 | 15602.8255 | 214372.9696 | 0.040768 | -1655331.2472 | 1655331.2472
C | Xist Rating 612 | -94.9 | 97.738 | 150.276 | 35.8 | 2415.55 | 7776.03 | 49380.9 | 2.11 | 8.79 | 11.948 | 200.72 | 1 | 1 | 1080 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 236091.0259 | 19826.1668 | 1136.0087 | 3930.3369 | 15895.8299 | 209667.848 | 0.041149 | -1618999.5453 | 1618999.5453
C | Xist Rating 613 | -94.82 | 99.534 | 150.276 | 35.8 | 2412.26 | 7759.81 | 48760.9 | 2.06 | 8.65 | 11.883 | 194.917 | 1 | 1 | 1090 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 240101.8868 | 20158.2888 | 1157.1433 | 3966.7289 | 16191.5599 | 203617.0116 | 0.04153 | -1572276.5905 | 1572276.5905
C | Xist Rating 614 | -94.75 | 100.856 | 150.276 | 35.8 | 2414.76 | 7799.27 | 48306.5 | 2.03 | 8.55 | 11.863 | 190.712 | 1 | 1 | 1100 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 243543.0346 | 20493.1365 | 1178.4727 | 4003.1209 | 16490.0156 | 199241.519 | 0.041911 | -1538490.1965 | 1538490.1965
C | Xist Rating 615 | -94.71 | 101.944 | 150.276 | 35.8 | 2406.76 | 7725.16 | 48010.7 | 1.95 | 8.49 | 11.751 | 188.253 | 1 | 1 | 1110 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 245354.7414 | 20830.7097 | 1199.9969 | 4039.5129 | 16791.1968 | 196640.5596 | 0.042292 | -1518406.2775 | 1518406.2775
C | Xist Rating 616 | -94.34 | 109.37 | 150.276 | 35.8 | 2403.2 | 7769.34 | 45448.6 | 1.99 | 7.92 | 11.869 | 164.726 | 1 | 1 | 1120 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 262837.984 | 21171.0087 | 1221.7158 | 4075.9049 | 17095.1037 | 172253.4651 | 0.042673 | -1330095.5984 | 1330095.5984
C | Xist Rating 617 | -94.28 | 110.412 | 150.276 | 35.8 | 2408.45 | 7833.35 | 45189.8 | 1.93 | 7.86 | 11.799 | 162.724 | 1 | 1 | 1130 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 265921.7814 | 21514.0332 | 1243.6296 | 4112.2969 | 17401.7362 | 170142.0643 | 0.043054 | -1313791.9208 | 1313791.9208
C | Xist Rating 618 | -94.18 | 112.278 | 150.276 | 35.8 | 2408.75 | 7854.26 | 44682.2 | 1.87 | 7.75 | 11.705 | 158.588 | 1 | 1 | 1140 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 270449.6325 | 21859.7833 | 1265.7381 | 4148.6889 | 17711.0944 | 165811.8842 | 0.043435 | -1280355.4175 | 1280355.4175
C | Xist Rating 619 | -94.08 | 114.081 | 150.276 | 35.8 | 2415.88 | 7948.7 | 44188.1 | 1.83 | 7.64 | 11.68 | 154.563 | 1 | 1 | 1150 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 275606.0063 | 22208.2591 | 1288.0414 | 4185.0809 | 18023.1782 | 161615.2461 | 0.043816 | -1247950.0911 | 1247950.0911
C | Xist Rating 620 | -93.99 | 115.963 | 150.276 | 35.8 | 2413.59 | 7942.18 | 43705.4 | 1.77 | 7.53 | 11.623 | 150.756 | 1 | 1 | 1160 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 279887.1372 | 22559.4605 | 1310.5395 | 4221.473 | 18337.9875 | 157629.5785 | 0.044197 | -1217173.8221 | 1217173.8221
C | Xist Rating 621 | -93.65 | 122.703 | 150.276 | 35.8 | 2413.89 | 8020.34 | 41834.4 | 1.79 | 7.13 | 11.701 | 135.652 | 1 | 1 | 1170 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 296191.5447 | 22913.3875 | 1333.2324 | 4257.865 | 18655.5226 | 141972.8337 | 0.044578 | -1096276.5889 | 1096276.5889
C | Xist Rating 622 | -93.6 | 123.317 | 150.276 | 35.8 | 2421.36 | 8108.1 | 41726.6 | 1.74 | 7.11 | 11.662 | 134.992 | 1 | 1 | 1180 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 298594.8511 | 23270.0402 | 1356.1201 | 4294.257 | 18975.7832 | 141262.2787 | 0.044959 | -1090789.8719 | 1090789.8719
C | Xist Rating 623 | -93.45 | 126.909 | 150.276 | 35.8 | 2408.11 | 7997.46 | 40887.7 | 1.7 | 6.93 | 11.601 | 128.78 | 1 | 1 | 1190 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 305610.832 | 23629.4184 | 1379.2026 | 4330.649 | 19298.7694 | 134789.8082 | 0.04534 | -1040811.1698 | 1040811.1698
C | Xist Rating 624 | -93.38 | 127.843 | 150.276 | 35.8 | 2419.89 | 8138.19 | 40683.4 | 1.67 | 6.88 | 11.599 | 127.345 | 1 | 1 | 1200 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 309365.9973 | 23991.5223 | 1402.4799 | 4367.041 | 19624.4813 | 133289.5031 | 0.045721 | -1029226.2116 | 1029226.2116
C | Xist Rating 625 | -93.3 | 129.794 | 150.275 | 35.8 | 2414.9 | 8100.5 | 40282.5 | 1.62 | 6.8 | 11.543 | 124.569 | 1 | 1 | 1210 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 313439.5306 | 24356.3518 | 1425.9519 | 4403.433 | 19952.9188 | 130378.9385 | 0.046102 | -1006751.6031 | 1006751.6031
C | Xist Rating 626 | -92.94 | 137.573 | 150.275 | 35.8 | 2401.63 | 8035.63 | 38539.1 | 1.62 | 6.43 | 11.575 | 112.111 | 1 | 1 | 1220 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 330399.444 | 24723.9069 | 1449.6188 | 4439.825 | 20284.0819 | 117452.5421 | 0.046483 | -906937.3972 | 906937.3972
C | Xist Rating 627 | -92.84 | 139.374 | 150.275 | 35.8 | 2406.37 | 8107.07 | 38184.1 | 1.6 | 6.35 | 11.567 | 109.759 | 1 | 1 | 1230 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 335385.4124 | 25094.1877 | 1473.4804 | 4476.217 | 20617.9707 | 115004.9298 | 0.046864 | -888037.5838 | 888037.5838
C | Xist Rating 628 | -92.76 | 141.315 | 150.275 | 35.8 | 2403.29 | 8090.38 | 37836.5 | 1.56 | 6.28 | 11.525 | 107.553 | 1 | 1 | 1240 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 339620.9263 | 25467.1941 | 1497.5369 | 4512.609 | 20954.5851 | 112692.9394 | 0.047245 | -870185.0065 | 870185.0065
C | Xist Rating 629 | -92.7 | 142.394 | 150.275 | 35.8 | 2404.22 | 8110.03 | 37665.2 | 1.52 | 6.24 | 11.493 | 106.545 | 1 | 1 | 1250 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 342346.5027 | 25842.9261 | 1521.7881 | 4549.001 | 21293.925 | 111625.6365 | 0.047626 | -861943.5762 | 861943.5762
C | Xist Rating 630 | -92.57 | 145.119 | 150.275 | 35.7 | 2403.41 | 8127.93 | 37162.4 | 1.49 | 6.14 | 11.473 | 103.311 | 1 | 1 | 1260 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 348780.4558 | 26221.3837 | 1546.2341 | 4585.393 | 21635.9907 | 108253.8067 | 0.048007 | -835907.2003 | 835907.2003
C | Xist Rating 631 | -92.21 | 152.5 | 150.275 | 35.7 | 2399.91 | 8167.2 | 35778.8 | 1.5 | 5.85 | 11.524 | 94.429 | 1 | 1 | 1270 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 365986.275 | 26602.5669 | 1570.8749 | 4621.785 | 21980.7819 | 99048.4126 | 0.048388 | -764825.5873 | 764825.5873
C | Xist Rating 632 | -92.12 | 154.51 | 150.275 | 35.7 | 2398.86 | 8173.12 | 35478.7 | 1.46 | 5.79 | 11.493 | 92.715 | 1 | 1 | 1280 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 370647.8586 | 26986.4758 | 1595.7105 | 4658.1771 | 22328.2987 | 97247.13 | 0.048769 | -750916.5609 | 750916.5609
C | Xist Rating 633 | -92.01 | 156.467 | 150.275 | 35.7 | 2402.29 | 8231.39 | 35184.6 | 1.42 | 5.73 | 11.487 | 91.033 | 1 | 1 | 1290 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 375879.1094 | 27373.1103 | 1620.7408 | 4694.5691 | 22678.5412 | 95480.8218 | 0.04915 | -737277.5965 | 737277.5965
C | Xist Rating 634 | -91.85 | 159.17 | 150.275 | 35.7 | 2412.33 | 8378.85 | 34753.3 | 1.39 | 5.64 | 11.488 | 88.501 | 1 | 1 | 1300 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 383970.5661 | 27762.4704 | 1645.966 | 4730.9611 | 23031.5093 | 92838.6552 | 0.049531 | -716875.4869 | 716875.4869
C | Xist Rating 635 | -91.76 | 160.718 | 150.275 | 35.7 | 2415.97 | 8437.33 | 34542.3 | 1.36 | 5.59 | 11.466 | 87.358 | 1 | 1 | 1310 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 388289.8665 | 28154.5561 | 1671.3859 | 4767.3531 | 23387.2031 | 91636.815 | 0.049912 | -707595.1953 | 707595.1953
C | Xist Rating 636 | -91.41 | 168.197 | 150.275 | 35.7 | 2410.54 | 8454.63 | 33365.1 | 1.36 | 5.35 | 11.508 | 80.534 | 1 | 1 | 1320 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 405445.5964 | 28549.3675 | 1697.0007 | 4803.7451 | 23745.6224 | 84560.4714 | 0.050293 | -652953.5453 | 652953.5453
C | Xist Rating 637 | -91.28 | 171.117 | 150.275 | 35.7 | 2404.66 | 8411.02 | 32982 | 1.33 | 5.28 | 11.457 | 78.51 | 1 | 1 | 1330 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 411478.2052 | 28946.9045 | 1722.8102 | 4840.1371 | 24106.7674 | 82440.9401 | 0.050674 | -636587.0868 | 636587.0868
C | Xist Rating 638 | -91.15 | 173.936 | 150.275 | 35.7 | 2404.79 | 8440.92 | 32608.8 | 1.3 | 5.2 | 11.439 | 76.538 | 1 | 1 | 1340 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 418279.5534 | 29347.1671 | 1748.8145 | 4876.5291 | 24470.638 | 80377.801 | 0.051055 | -620656.0738 | 620656.0738
C | Xist Rating 639 | -91.06 | 175.5 | 150.275 | 35.7 | 2408.01 | 8495.05 | 32425.9 | 1.27 | 5.16 | 11.42 | 75.638 | 1 | 1 | 1350 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 422605.755 | 29750.1553 | 1775.0136 | 4912.9211 | 24837.2342 | 79427.5917 | 0.051436 | -613318.809 | 613318.809
C | Xist Rating 640 | -90.97 | 176.381 | 150.275 | 35.7 | 2424.35 | 8712.09 | 32304.8 | 1.26 | 5.14 | 11.437 | 75.009 | 1 | 1 | 1360 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 427609.2773 | 30155.8691 | 1801.4075 | 4949.3131 | 25206.556 | 78775.2213 | 0.051817 | -608281.3776 | 608281.3776
C | Xist Rating 641 | -90.52 | 187.224 | 150.275 | 35.7 | 2396.82 | 8481.25 | 30904.2 | 1.25 | 4.86 | 11.445 | 67.727 | 1 | 1 | 1370 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 448742.2277 | 30564.3086 | 1827.9962 | 4985.7051 | 25578.6035 | 71212.9259 | 0.052198 | -549887.3377 | 549887.3377
C | Xist Rating 642 | -90.48 | 188.366 | 150.275 | 35.7 | 2396.63 | 8488.34 | 30795.4 | 1.23 | 4.84 | 11.424 | 67.262 | 1 | 1 | 1380 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 451443.6066 | 30975.4737 | 1854.7797 | 5022.0971 | 25953.3765 | 70720.6798 | 0.052579 | -546086.3436 | 546086.3436
C | Xist Rating 643 | -90.36 | 190.834 | 150.275 | 35.7 | 2396.66 | 8512.25 | 30528.2 | 1.2 | 4.79 | 11.406 | 66.005 | 1 | 1 | 1390 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 457364.2144 | 31389.3644 | 1881.7579 | 5058.4891 | 26330.8753 | 69398.8864 | 0.05296 | -535879.8054 | 535879.8054
C | Xist Rating 644 | -90.25 | 193.297 | 150.275 | 35.7 | 2395.74 | 8524.29 | 30266.2 | 1.18 | 4.73 | 11.39 | 64.785 | 1 | 1 | 1400 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 463089.3548 | 31805.9807 | 1908.931 | 5094.8812 | 26711.0996 | 68122.5532 | 0.053341 | -526024.2988 | 526024.2988
C | Xist Rating 645 | -90.12 | 196.177 | 150.275 | 35.7 | 2394.12 | 8532.25 | 29958.4 | 1.16 | 4.67 | 11.376 | 63.348 | 1 | 1 | 1410 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 469671.2792 | 32225.3227 | 1936.2988 | 5131.2732 | 27094.0495 | 66620.8315 | 0.053722 | -514428.4018 | 514428.4018
C | Xist Rating 646 | -89.74 | 204.199 | 150.275 | 35.7 | 2389.48 | 8560.4 | 29053 | 1.17 | 4.49 | 11.424 | 59.026 | 1 | 1 | 1420 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 487929.4265 | 32647.3903 | 1963.8614 | 5167.6652 | 27479.7251 | 62149.1721 | 0.054103 | -479899.4328 | 479899.4328
C | Xist Rating 647 | -89.67 | 206.004 | 150.275 | 35.7 | 2385.11 | 8518.57 | 28911.9 | 1.13 | 4.47 | 11.391 | 58.48 | 1 | 1 | 1430 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 491342.2004 | 33072.1835 | 1991.6188 | 5204.0572 | 27868.1263 | 61556.4622 | 0.054484 | -475322.6841 | 475322.6841
C | Xist Rating 648 | -89.51 | 209.764 | 150.275 | 35.7 | 2382.36 | 8520.71 | 28543 | 1.12 | 4.39 | 11.38 | 56.846 | 1 | 1 | 1440 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 499733.363 | 33499.7023 | 2019.571 | 5240.4492 | 28259.2531 | 59857.1777 | 0.054865 | -462201.2597 | 462201.2597
C | Xist Rating 649 | -89.39 | 212.266 | 150.275 | 35.7 | 2381.56 | 8533.78 | 28317.8 | 1.1 | 4.35 | 11.367 | 55.895 | 1 | 1 | 1450 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 505524.215 | 33929.9467 | 2047.718 | 5276.8412 | 28653.1055 | 58859.5564 | 0.055246 | -454497.8925 | 454497.8925
C | Xist Rating 650 | -89.29 | 213.712 | 150.275 | 35.7 | 2390.47 | 8663.71 | 28184.8 | 1.09 | 4.33 | 11.373 | 55.337 | 1 | 1 | 1460 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 510872.1246 | 34362.9168 | 2076.0598 | 5313.2332 | 29049.6836 | 58278.668 | 0.055627 | -450012.4263 | 450012.4263
C | Xist Rating 651 | -88.92 | 223.042 | 150.275 | 35.7 | 2371.84 | 8517.59 | 27311.2 | 1.08 | 4.16 | 11.388 | 51.563 | 1 | 1 | 1470 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 529019.9373 | 34798.6125 | 2104.5964 | 5349.6252 | 29448.9873 | 54358.5052 | 0.056008 | -419741.9684 | 419741.9684
C | Xist Rating 652 | -88.76 | 225.966 | 150.275 | 35.7 | 2375.51 | 8592.92 | 27067.2 | 1.06 | 4.11 | 11.384 | 50.58 | 1 | 1 | 1480 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 536784.4927 | 35237.0338 | 2133.3277 | 5386.0172 | 29851.0166 | 53327.7833 | 0.056389 | -411783.0068 | 411783.0068
C | Xist Rating 653 | -88.6 | 228.47 | 150.275 | 35.7 | 2383.67 | 8724.71 | 26867.5 | 1.04 | 4.07 | 11.382 | 49.797 | 1 | 1 | 1490 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 544597.0849 | 35678.1807 | 2162.2539 | 5422.4092 | 30255.7715 | 52504.7026 | 0.05677 | -405427.3964 | 405427.3964
C | Xist Rating 654 | -88.47 | 231.065 | 150.275 | 35.7 | 2385.88 | 8778.56 | 26671.3 | 1.02 | 4.03 | 11.373 | 49.046 | 1 | 1 | 1500 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 551293.3622 | 36122.0533 | 2191.3748 | 5458.8012 | 30663.2521 | 51714.1733 | 0.057151 | -399323.1383 | 399323.1383
C | Xist Rating 655 | -88.31 | 234.016 | 150.275 | 35.7 | 2391.66 | 8887.1 | 26439.9 | 1 | 3.99 | 11.371 | 48.145 | 1 | 1 | 1510 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 559686.7066 | 36568.6515 | 2220.6906 | 5495.1932 | 31073.4582 | 50768.155 | 0.057532 | -392018.236 | 392018.236
C | Xist Rating 656 | -87.87 | 243.03 | 150.275 | 35.7 | 2389.77 | 8962.99 | 25682.2 | 1.01 | 3.85 | 11.423 | 45.094 | 1 | 1 | 1520 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 580785.8031 | 37017.9753 | 2250.2011 | 5531.5853 | 31486.39 | 47616.1192 | 0.057913 | -367679.0508 | 367679.0508
C | Xist Rating 657 | -87.75 | 246.324 | 150.275 | 35.7 | 2382.53 | 8891.39 | 25469.4 | 0.98 | 3.81 | 11.396 | 44.349 | 1 | 1 | 1530 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 586874.3197 | 37470.0247 | 2279.9064 | 5567.9773 | 31902.0474 | 46822.2925 | 0.058294 | -361549.3311 | 361549.3311
C | Xist Rating 658 | -87.64 | 248.044 | 150.275 | 35.7 | 2389.11 | 8998.8 | 25364.7 | 0.96 | 3.79 | 11.39 | 44.002 | 1 | 1 | 1540 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 592604.4008 | 37924.7998 | 2309.8065 | 5604.3693 | 32320.4305 | 46450.8086 | 0.058675 | -358680.8315 | 358680.8315
C | Xist Rating 659 | -87.42 | 252.811 | 150.275 | 35.7 | 2387.39 | 9024.83 | 25022.3 | 0.95 | 3.72 | 11.386 | 42.732 | 1 | 1 | 1550 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 603558.4533 | 38382.3004 | 2339.9013 | 5640.7613 | 32741.5391 | 45128.6394 | 0.059056 | -348471.3909 | 348471.3909
C | Xist Rating 660 | -87.3 | 254.307 | 150.275 | 35.7 | 2399.64 | 9218.1 | 24921.6 | 0.93 | 3.7 | 11.393 | 42.383 | 1 | 1 | 1560 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 610245.2495 | 38842.5267 | 2370.191 | 5677.1533 | 33165.3734 | 44755.5835 | 0.059437 | -345590.7526 | 345590.7526
C | Xist Rating 661 | -86.87 | 265.266 | 150.275 | 35.7 | 2378.05 | 9023.89 | 24163.2 | 0.93 | 3.56 | 11.413 | 39.623 | 1 | 1 | 1570 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 630815.8113 | 39305.4786 | 2400.6755 | 5713.5453 | 33591.9333 | 41895.3863 | 0.059818 | -323505.0674 | 323505.0674
C | Xist Rating 662 | -86.73 | 267.89 | 150.275 | 35.7 | 2381.64 | 9101.17 | 24008.5 | 0.91 | 3.53 | 11.406 | 39.114 | 1 | 1 | 1580 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 638017.5396 | 39771.1562 | 2431.3547 | 5749.9373 | 34021.2189 | 41354.9311 | 0.0602 | -319331.816 | 319331.816
C | Xist Rating 663 | -86.6 | 270.55 | 150.275 | 35.7 | 2383.59 | 9155.33 | 23856 | 0.89 | 3.5 | 11.398 | 38.62 | 1 | 1 | 1590 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 644880.2745 | 40239.5593 | 2462.2288 | 5786.3293 | 34453.23 | 40829.7996 | 0.060581 | -315276.8898 | 315276.8898
C | Xist Rating 664 | -86.42 | 273.946 | 150.275 | 35.7 | 2387.43 | 9248.67 | 23646 | 0.88 | 3.46 | 11.399 | 37.911 | 1 | 1 | 1600 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 654026.8988 | 40710.6881 | 2493.2976 | 5822.7213 | 34887.9668 | 40089.9399 | 0.060962 | -309563.889 | 309563.889
C | Xist Rating 665 | -86.35 | 275.862 | 150.275 | 35.7 | 2385.96 | 9242.21 | 23557.3 | 0.86 | 3.45 | 11.385 | 37.663 | 1 | 1 | 1610 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 658195.6975 | 41184.5425 | 2524.5612 | 5859.1133 | 35325.4292 | 39819.567 | 0.061343 | -307476.1413 | 307476.1413
C | Xist Rating 666 | -85.83 | 287.981 | 150.275 | 35.7 | 2373.28 | 9188.78 | 22805.8 | 0.87 | 3.31 | 11.423 | 35.102 | 1 | 1 | 1620 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 683459.5477 | 41661.1225 | 2556.0196 | 5895.5053 | 35765.6172 | 37175.0294 | 0.061724 | -287055.7228 | 287055.7228
C | Xist Rating 667 | -85.72 | 289.551 | 150.275 | 35.7 | 2380.58 | 9314.86 | 22723.8 | 0.86 | 3.29 | 11.423 | 34.859 | 1 | 1 | 1630 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 7 | E | Rod | 689299.3196 | 42140.4282 | 2587.6728 | 5931.8973 | 36208.5308 | 36918.7828 | 0.062105 | -285077.0548 | 285077.0548
C | Xist Rating 668 | -85.6 | 292.358 | 150.275 | 35.7 | 2378.94 | 9315.99 | 22589.2 | 0.84 | 3.27 | 11.393 | 34.464 | 1 | 1 | 1640 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 695502.1405 | 42622.4595 | 2619.5208 | 5968.2894 | 36654.1701 | 36494.3322 | 0.062486 | -281799.56 | 281799.56
C | Xist Rating 669 | -85.45 | 296.113 | 150.275 | 35.6 | 2374.79 | 9288.88 | 22403.5 | 0.82 | 3.24 | 11.382 | 33.907 | 1 | 1 | 1650 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 703206.1913 | 43107.2164 | 2651.5635 | 6004.6814 | 37102.535 | 35902.6586 | 0.062867 | -277230.8129 | 277230.8129
C | Xist Rating 670 | -85.29 | 299.623 | 150.275 | 35.6 | 2375.51 | 9336.48 | 22221.4 | 0.81 | 3.2 | 11.379 | 33.349 | 1 | 1 | 1660 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 711757.4327 | 43594.6989 | 2683.8011 | 6041.0734 | 37553.6255 | 35318.71 | 0.063248 | -272721.7169 | 272721.7169
C | Xist Rating 671 | -84.83 | 310.626 | 150.275 | 35.6 | 2363.36 | 9270.99 | 21633.7 | 0.81 | 3.1 | 11.414 | 31.505 | 1 | 1 | 1670 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 734121.0634 | 44084.907 | 2716.2334 | 6077.4654 | 38007.4416 | 33409.9726 | 0.063629 | -257982.9527 | 257982.9527
C | Xist Rating 672 | -84.73 | 312.309 | 150.275 | 35.6 | 2367.89 | 9356.72 | 21561.1 | 0.8 | 3.08 | 11.409 | 31.312 | 1 | 1 | 1680 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 739513.358 | 44577.8408 | 2748.8606 | 6113.8574 | 38463.9834 | 33204.79 | 0.06401 | -256398.5871 | 256398.5871
C | Xist Rating 673 | -84.55 | 317.06 | 150.275 | 35.6 | 2362.28 | 9316 | 21346.7 | 0.78 | 3.04 | 11.398 | 30.7 | 1 | 1 | 1690 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 748984.4968 | 45073.5002 | 2781.6825 | 6150.2494 | 38923.2508 | 32555.3848 | 0.064391 | -251384.0521 | 251384.0521
C | Xist Rating 674 | -84.4 | 320.167 | 150.275 | 35.6 | 2364.34 | 9379.45 | 21206.3 | 0.77 | 3.02 | 11.395 | 30.304 | 1 | 1 | 1700 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 756983.6448 | 45571.8852 | 2814.6992 | 6186.6414 | 39385.2438 | 32139.263 | 0.064772 | -248170.87 | 248170.87
C | Xist Rating 675 | -84.24 | 323.87 | 150.275 | 35.6 | 2362.76 | 9390.92 | 21045.3 | 0.76 | 2.99 | 11.389 | 29.857 | 1 | 1 | 1710 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 765227.0812 | 46072.9958 | 2847.9107 | 6223.0334 | 39849.9624 | 31669.9034 | 0.065153 | -244546.5994 | 244546.5994
C | Xist Rating 676 | -83.82 | 334.08 | 150.275 | 35.6 | 2353.21 | 9351.56 | 20567.5 | 0.76 | 2.9 | 11.422 | 28.466 | 1 | 1 | 1720 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 786160.3968 | 46576.832 | 2881.317 | 6259.4254 | 40317.4066 | 30231.1656 | 0.065534 | -233437.0474 | 233437.0474
C | Xist Rating 677 | -83.63 | 338.701 | 150.275 | 35.6 | 2349.98 | 9346.89 | 20374.8 | 0.75 | 2.87 | 11.411 | 27.943 | 1 | 1 | 1730 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 795940.576 | 47083.3939 | 2914.9181 | 6295.8174 | 40787.5765 | 29682.4249 | 0.065915 | -229199.8171 | 229199.8171
C | Xist Rating 678 | -83.53 | 340.952 | 150.275 | 35.6 | 2350.25 | 9371.76 | 20290.2 | 0.74 | 2.85 | 11.405 | 27.732 | 1 | 1 | 1740 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 801322.438 | 47592.6814 | 2948.714 | 6332.2094 | 41260.472 | 29457.8916 | 0.066296 | -227466.0308 | 227466.0308
C | Xist Rating 679 | -83.36 | 345.284 | 150.275 | 35.6 | 2346.27 | 9349.55 | 20123.5 | 0.73 | 2.82 | 11.396 | 27.299 | 1 | 1 | 1750 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 810129.4907 | 48104.6945 | 2982.7046 | 6368.6014 | 41736.0931 | 29002.5431 | 0.066677 | -223949.9499 | 223949.9499
C | Xist Rating 680 | -83.25 | 348.508 | 150.275 | 35.6 | 2342.1 | 9314.16 | 20000.5 | 0.72 | 2.8 | 11.387 | 26.984 | 1 | 1 | 1760 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 816240.5868 | 48619.4333 | 3016.8901 | 6404.9934 | 42214.4398 | 28669.6434 | 0.067058 | -221379.3868 | 221379.3868
C | Xist Rating 681 | -82.75 | 360.595 | 150.275 | 35.6 | 2332.43 | 9289.42 | 19497.3 | 0.72 | 2.71 | 11.425 | 25.611 | 1 | 1 | 1770 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 841062.5959 | 49136.8976 | 3051.2703 | 6441.3855 | 42695.5122 | 27249.6308 | 0.067439 | -210414.426 | 210414.426
C | Xist Rating 682 | -82.62 | 363.929 | 150.275 | 35.6 | 2330.33 | 9286.22 | 19382.9 | 0.71 | 2.69 | 11.416 | 25.336 | 1 | 1 | 1780 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 848074.6666 | 49657.0876 | 3085.8453 | 6477.7775 | 43179.3102 | 26958.1054 | 0.06782 | -208163.3442 | 208163.3442
C | Xist Rating 683 | -82.53 | 365.87 | 150.275 | 35.6 | 2331.53 | 9320.21 | 19326.4 | 0.7 | 2.68 | 11.41 | 25.218 | 1 | 1 | 1790 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 853036.8811 | 50180.0032 | 3120.6151 | 6514.1695 | 43665.8338 | 26829.699 | 0.068201 | -207171.8243 | 207171.8243
C | Xist Rating 684 | -82.3 | 371.526 | 150.275 | 35.6 | 2327.17 | 9305.76 | 19122 | 0.69 | 2.65 | 11.405 | 24.704 | 1 | 1 | 1800 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 864604.1614 | 50705.6445 | 3155.5797 | 6550.5615 | 44155.083 | 26290.0066 | 0.068582 | -203004.4619 | 203004.4619
C | Xist Rating 685 | -82.24 | 374.732 | 150.275 | 35.6 | 2318.06 | 9190.7 | 19013.3 | 0.68 | 2.63 | 11.492 | 24.436 | 1 | 1 | 1810 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 868651.2599 | 51234.0113 | 3190.7391 | 6586.9535 | 44647.0578 | 26010.7631 | 0.068963 | -200848.2177 | 200848.2177
C | Xist Rating 686 | -81.76 | 387.078 | 150.275 | 35.6 | 2305.23 | 9112.32 | 18564 | 0.68 | 2.55 | 11.529 | 23.297 | 1 | 1 | 1820 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 892303.8179 | 51765.1038 | 3226.0933 | 6623.3455 | 45141.7583 | 24833.4688 | 0.069344 | -191757.4634 | 191757.4634
C | Xist Rating 687 | -81.62 | 385.083 | 150.276 | 35.6 | 2337.28 | 9613.65 | 18632.1 | 0.67 | 2.56 | 11.561 | 23.479 | 1 | 1 | 1830 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 900046.7942 | 52298.9219 | 3261.6423 | 6659.7375 | 45639.1844 | 25018.2912 | 0.069725 | -193184.613 | 193184.613
C | Xist Rating 688 | -81.43 | 387.668 | 150.276 | 35.6 | 2346.75 | 9803.05 | 18546.5 | 0.66 | 2.55 | 11.573 | 23.278 | 1 | 1 | 1840 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 909759.879 | 52835.4656 | 3297.386 | 6696.1295 | 46139.3361 | 24804.1431 | 0.070106 | -191531.0181 | 191531.0181
C | Xist Rating 689 | -81.26 | 392.117 | 150.276 | 35.6 | 2342.78 | 9777.8 | 18410.6 | 0.65 | 2.52 | 11.566 | 22.969 | 1 | 1 | 1850 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 918643.8653 | 53374.7349 | 3333.3246 | 6732.5215 | 46642.2134 | 24476.6966 | 0.070487 | -189002.5629 | 189002.5629
C | Xist Rating 690 | -81.07 | 397.081 | 150.276 | 35.6 | 2338.06 | 9744.72 | 18260.4 | 0.64 | 2.5 | 11.561 | 22.628 | 1 | 1 | 1860 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 928399.2029 | 53916.7299 | 3369.4579 | 6768.9135 | 47147.8164 | 24116.0287 | 0.070868 | -186217.5809 | 186217.5809
C | Xist Rating 691 | -80.6 | 408.363 | 150.276 | 35.6 | 2330.97 | 9748.09 | 17880.8 | 0.64 | 2.43 | 11.598 | 21.711 | 1 | 1 | 1870 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 951881.9021 | 54461.4505 | 3405.7861 | 6805.3055 | 47656.145 | 23169.0271 | 0.071249 | -178905.086 | 178905.086
C | Xist Rating 692 | -80.43 | 413.312 | 150.276 | 35.6 | 2325.71 | 9704.59 | 17740 | 0.63 | 2.41 | 11.584 | 21.403 | 1 | 1 | 1880 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 961243.8515 | 55008.8967 | 3442.309 | 6841.6975 | 48167.1992 | 22841.9799 | 0.07163 | -176379.7138 | 176379.7138
C | Xist Rating 693 | -80.22 | 416.566 | 150.276 | 35.6 | 2332.4 | 9854.97 | 17648 | 0.62 | 2.39 | 11.602 | 21.204 | 1 | 1 | 1890 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 971598.5384 | 55559.0685 | 3479.0267 | 6878.0896 | 48680.979 | 22629.7216 | 0.072011 | -174740.7118 | 174740.7118
C | Xist Rating 694 | -80.1 | 420.277 | 150.276 | 35.6 | 2327.96 | 9808.78 | 17556.4 | 0.61 | 2.38 | 11.584 | 21.023 | 1 | 1 | 1900 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 978388.0449 | 56111.966 | 3515.9392 | 6914.4816 | 49197.4844 | 22434.1616 | 0.072392 | -173230.6489 | 173230.6489
C | Xist Rating 695 | -79.93 | 423.71 | 150.276 | 35.6 | 2328.73 | 9855 | 17466.6 | 0.6 | 2.36 | 11.591 | 20.836 | 1 | 1 | 1910 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 986706.1883 | 56667.5891 | 3553.0464 | 6950.8736 | 49716.7155 | 22233.5717 | 0.072773 | -171681.7472 | 171681.7472
C | Xist Rating 696 | -79.4 | 437.437 | 150.276 | 35.6 | 2317.69 | 9812.17 | 17051.6 | 0.6 | 2.29 | 11.628 | 19.89 | 1 | 1 | 1920 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1013843.3605 | 57225.9378 | 3590.3485 | 6987.2656 | 50238.6722 | 21256.1802 | 0.073154 | -164134.589 | 164134.589
C | Xist Rating 697 | -79.19 | 442.463 | 150.276 | 35.6 | 2314.88 | 9810.25 | 16925.3 | 0.59 | 2.27 | 11.623 | 19.632 | 1 | 1 | 1930 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1024248.7494 | 57787.0121 | 3627.8454 | 7023.6576 | 50763.3545 | 20981.0601 | 0.073535 | -162010.1849 | 162010.1849
C | Xist Rating 698 | -79.08 | 444.043 | 150.276 | 35.6 | 2321.23 | 9942.1 | 16883.3 | 0.58 | 2.26 | 11.643 | 19.552 | 1 | 1 | 1940 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1030725.9329 | 58350.812 | 3665.537 | 7060.0496 | 51290.7624 | 20891.9555 | 0.073916 | -161322.1428 | 161322.1428
C | Xist Rating 699 | -78.92 | 449.063 | 150.276 | 35.6 | 2314.01 | 9854.11 | 16773.3 | 0.57 | 2.24 | 11.633 | 19.344 | 1 | 1 | 1950 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1039136.2726 | 58917.3376 | 3703.4235 | 7096.4416 | 51820.896 | 20668.2997 | 0.074297 | -159595.1317 | 159595.1317
C | Xist Rating 700 | -78.7 | 454.483 | 150.276 | 35.6 | 2311.3 | 9859.09 | 16638.1 | 0.56 | 2.22 | 11.635 | 19.069 | 1 | 1 | 1960 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1050446.5579 | 59486.5888 | 3741.5047 | 7132.8336 | 52353.7552 | 20375.563 | 0.074678 | -157334.6961 | 157334.6961
C | Xist Rating 701 | -78.21 | 466.958 | 150.276 | 35.6 | 2302.99 | 9844.96 | 16304.2 | 0.56 | 2.16 | 11.679 | 18.356 | 1 | 1 | 1970 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1075399.6044 | 60058.5656 | 3779.7807 | 7169.2256 | 52889.34 | 19640.21 | 0.075059 | -151656.4955 | 151656.4955
C | Xist Rating 702 | -78.03 | 470.886 | 150.276 | 35.6 | 2303.51 | 9892.33 | 16215 | 0.56 | 2.15 | 11.677 | 18.187 | 1 | 1 | 1980 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1084690.6099 | 60633.268 | 3818.2515 | 7205.6176 | 53427.6504 | 19467.536 | 0.07544 | -150323.1527 | 150323.1527
C | Xist Rating 703 | -77.85 | 476.106 | 150.276 | 35.6 | 2298.83 | 9854.69 | 16102.1 | 0.55 | 2.13 | 11.671 | 17.975 | 1 | 1 | 1990 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1094486.756 | 61210.6961 | 3856.9171 | 7242.0096 | 53968.6864 | 19239.5951 | 0.075821 | -148563.0535 | 148563.0535
C | Xist Rating 704 | -77.69 | 480.159 | 150.276 | 35.6 | 2296.27 | 9845.02 | 16015.5 | 0.54 | 2.12 | 11.669 | 17.816 | 1 | 1 | 2000 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1102574.7069 | 61790.8498 | 3895.7775 | 7278.4016 | 54512.4481 | 19066.7914 | 0.076202 | -147228.709 | 147228.709
C | Xist Rating 705 | -77.54 | 483.218 | 150.276 | 35.6 | 2297.61 | 9896.44 | 15954.7 | 0.53 | 2.11 | 11.67 | 17.71 | 1 | 1 | 2010 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1110246.509 | 62373.7291 | 3934.8326 | 7314.7937 | 55058.9354 | 18949.0693 | 0.076583 | -146319.6906 | 146319.6906
C | Xist Rating 706 | -77 | 497.393 | 150.276 | 35.6 | 2287.07 | 9853.52 | 15615.8 | 0.53 | 2.05 | 11.705 | 17.028 | 1 | 1 | 2020 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1137572.6085 | 62959.334 | 3974.0826 | 7351.1857 | 55608.1483 | 18245.2655 | 0.076964 | -140885.1038 | 140885.1038
C | Xist Rating 707 | -76.79 | 502.757 | 150.276 | 35.6 | 2284.96 | 9867.5 | 15500.5 | 0.53 | 2.03 | 11.701 | 16.814 | 1 | 1 | 2030 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1148779.6347 | 63547.6645 | 4013.5273 | 7387.5777 | 56160.0869 | 18025.6147 | 0.077345 | -139189.0185 | 139189.0185
C | Xist Rating 708 | -76.66 | 506.668 | 150.276 | 35.6 | 2281.78 | 9840.01 | 15432.3 | 0.52 | 2.02 | 11.695 | 16.703 | 1 | 1 | 2040 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1156104.909 | 64138.7207 | 4053.1669 | 7423.9697 | 56714.751 | 17902.1362 | 0.077726 | -138235.5505 | 138235.5505
C | Xist Rating 709 | -76.52 | 509.764 | 150.276 | 35.6 | 2283.17 | 9897.83 | 15364.9 | 0.52 | 2.01 | 11.693 | 16.58 | 1 | 1 | 2050 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1163877.8719 | 64732.5025 | 4093.0012 | 7460.3617 | 57272.1408 | 17777.0313 | 0.078107 | -137269.5236 | 137269.5236
C | Xist Rating 710 | -76.34 | 515.38 | 150.276 | 35.6 | 2276.62 | 9823.12 | 15264.9 | 0.5 | 1.99 | 11.688 | 16.412 | 1 | 1 | 2060 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1173324.4156 | 65329.0099 | 4133.0303 | 7496.7537 | 57832.2562 | 17583.4639 | 0.078488 | -135774.8472 | 135774.8472
C | Xist Rating 711 | -75.76 | 530.652 | 150.276 | 35.6 | 2266.45 | 9792.72 | 14936.8 | 0.5 | 1.94 | 11.726 | 15.789 | 1 | 1 | 2070 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1202696.2254 | 65928.2429 | 4173.2542 | 7533.1457 | 58395.0972 | 16940.8619 | 0.078869 | -130812.8448 | 130812.8448
C | Xist Rating 712 | -75.62 | 534.365 | 150.276 | 35.6 | 2264.27 | 9783.12 | 14874 | 0.5 | 1.93 | 11.721 | 15.689 | 1 | 1 | 2080 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1209946.6386 | 66530.2016 | 4213.6729 | 7569.5377 | 58960.6639 | 16839.407 | 0.07925 | -130029.4373 | 130029.4373
C | Xist Rating 713 | -75.45 | 539.014 | 150.276 | 35.6 | 2261.7 | 9776.53 | 14791.4 | 0.49 | 1.91 | 11.717 | 15.551 | 1 | 1 | 2090 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1219087.9638 | 67134.8859 | 4254.2864 | 7605.9297 | 59528.9562 | 16687.5569 | 0.079631 | -128856.8911 | 128856.8911
C | Xist Rating 714 | -75.28 | 543.671 | 150.276 | 35.6 | 2259.29 | 9772.67 | 14709.7 | 0.49 | 1.9 | 11.712 | 15.416 | 1 | 1 | 2100 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1228310.4536 | 67742.2958 | 4295.0947 | 7642.3217 | 60099.974 | 16549.7025 | 0.080012 | -127792.4161 | 127792.4161
C | Xist Rating 715 | -75.14 | 547.818 | 150.276 | 35.6 | 2256.69 | 9760.06 | 14639 | 0.48 | 1.89 | 11.709 | 15.302 | 1 | 1 | 2110 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1236255.4024 | 68352.4313 | 4336.0977 | 7678.7137 | 60673.7176 | 16422.6727 | 0.080393 | -126811.5257 | 126811.5257
C | Xist Rating 716 | -74.6 | 562.433 | 150.276 | 35.6 | 2246.75 | 9719.32 | 14359.3 | 0.48 | 1.84 | 11.747 | 14.803 | 1 | 1 | 2120 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1263646.3428 | 68965.2924 | 4377.2956 | 7715.1057 | 61250.1867 | 15908.7146 | 0.080774 | -122842.8774 | 122842.8774
C | Xist Rating 717 | -74.4 | 568.14 | 150.276 | 35.6 | 2243.2 | 9703.34 | 14264 | 0.47 | 1.83 | 11.743 | 14.648 | 1 | 1 | 2130 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1274451.648 | 69580.8792 | 4418.6882 | 7751.4978 | 61829.3815 | 15738.8797 | 0.081155 | -121531.4573 | 121531.4573
C | Xist Rating 718 | -74.23 | 573.873 | 150.276 | 35.6 | 2236.98 | 9637.44 | 14170.1 | 0.47 | 1.81 | 11.74 | 14.497 | 1 | 1 | 2140 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1283742.4235 | 70199.1916 | 4460.2756 | 7787.8898 | 62411.3018 | 15584.4052 | 0.081536 | -120338.6458 | 120338.6458
C | Xist Rating 719 | -74.1 | 577.081 | 150.276 | 35.6 | 2236.35 | 9650.54 | 14123.7 | 0.46 | 1.81 | 11.735 | 14.431 | 1 | 1 | 2150 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1290555.0943 | 70820.2296 | 4502.0578 | 7824.2818 | 62995.9479 | 15506.8018 | 0.081917 | -119739.4128 | 119739.4128
C | Xist Rating 720 | -73.95 | 581.174 | 150.276 | 35.6 | 2234.94 | 9658.91 | 14059.2 | 0.46 | 1.79 | 11.732 | 14.331 | 1 | 1 | 2160 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1298889.0196 | 71443.9933 | 4544.0348 | 7860.6738 | 63583.3195 | 15405.238 | 0.082298 | -118955.1642 | 118955.1642
C | Xist Rating 721 | -73.38 | 597.099 | 150.276 | 35.6 | 2223.82 | 9601.89 | 13786.1 | 0.46 | 1.75 | 11.771 | 13.871 | 1 | 1 | 2170 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1327840.6982 | 72070.4825 | 4586.2066 | 7897.0658 | 64173.4167 | 14931.6928 | 0.082679 | -115298.5738 | 115298.5738
C | Xist Rating 722 | -73.18 | 602.581 | 150.276 | 35.6 | 2221.73 | 9611.66 | 13699.2 | 0.45 | 1.74 | 11.766 | 13.734 | 1 | 1 | 2180 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1338772.2851 | 72699.6974 | 4628.5732 | 7933.4578 | 64766.2396 | 14780.1234 | 0.08306 | -114128.195 | 114128.195
C | Xist Rating 723 | -73.03 | 606.908 | 150.276 | 35.6 | 2219.49 | 9603.99 | 13639 | 0.45 | 1.73 | 11.761 | 13.648 | 1 | 1 | 2190 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1347026.2369 | 73331.6379 | 4671.1346 | 7969.8498 | 65361.7881 | 14692.965 | 0.083441 | -113455.1809 | 113455.1809
C | Xist Rating 724 | -72.88 | 611.64 | 150.276 | 35.6 | 2215.67 | 9566.45 | 13579.5 | 0.44 | 1.72 | 11.758 | 13.568 | 1 | 1 | 2200 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1355192.3988 | 73966.304 | 4713.8907 | 8006.2418 | 65960.0622 | 14600.5292 | 0.083822 | -112741.4166 | 112741.4166
C | Xist Rating 725 | -72.68 | 617.38 | 150.276 | 35.6 | 2212.7 | 9559.44 | 13495.4 | 0.43 | 1.7 | 11.755 | 13.441 | 1 | 1 | 2210 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1366076.726 | 74603.6958 | 4756.8417 | 8042.6338 | 66561.062 | 14459.1834 | 0.084203 | -111649.9815 | 111649.9815
C | Xist Rating 726 | -72.11 | 633.171 | 150.276 | 35.6 | 2203.33 | 9530.29 | 13246.2 | 0.43 | 1.66 | 11.794 | 13.04 | 1 | 1 | 2220 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1395084.6594 | 75243.8131 | 4799.9874 | 8079.0258 | 67164.7873 | 14046.6801 | 0.084584 | -108464.74 | 108464.74
C | Xist Rating 727 | -71.95 | 637.791 | 150.276 | 35.6 | 2201.86 | 9540.91 | 13182.5 | 0.43 | 1.65 | 11.788 | 12.948 | 1 | 1 | 2230 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1404326.4913 | 75886.6561 | 4843.3279 | 8115.4178 | 67771.2383 | 13953.1536 | 0.084965 | -107742.5531 | 107742.5531
C | Xist Rating 728 | -71.75 | 643.375 | 150.276 | 35.6 | 2199.02 | 9530.45 | 13111.6 | 0.42 | 1.64 | 11.785 | 12.85 | 1 | 1 | 2240 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1414794.4925 | 76532.2248 | 4886.8633 | 8151.8098 | 68380.4149 | 13841.6903 | 0.085346 | -106881.8633 | 106881.8633
C | Xist Rating 729 | -71.54 | 649.423 | 150.276 | 35.6 | 2196.54 | 9531.47 | 13033.9 | 0.42 | 1.63 | 11.781 | 12.742 | 1 | 1 | 2250 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1426483.5964 | 77180.519 | 4930.5934 | 8188.2019 | 68992.3171 | 13731.5817 | 0.085727 | -106031.634 | 106031.634
C | Xist Rating 730 | -71.43 | 652.594 | 150.276 | 35.6 | 2195.58 | 9537.01 | 12995.5 | 0.42 | 1.62 | 11.776 | 12.692 | 1 | 1 | 2260 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1432822.3345 | 77831.5389 | 4974.5182 | 8224.5939 | 69606.945 | 13681.662 | 0.086108 | -105646.1672 | 105646.1672
C | Xist Rating 731 | -70.83 | 669.79 | 150.276 | 35.6 | 2185.14 | 9493.09 | 12751.8 | 0.41 | 1.59 | 11.816 | 12.321 | 1 | 1 | 2270 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1463584.9206 | 78485.2843 | 5018.6379 | 8260.9859 | 70224.2985 | 13288.2825 | 0.086489 | -102608.5949 | 102608.5949
C | Xist Rating 732 | -70.64 | 675.319 | 150.276 | 35.6 | 2181.91 | 9474.27 | 12686.1 | 0.41 | 1.58 | 11.81 | 12.233 | 1 | 1 | 2280 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1473485.2793 | 79141.7554 | 5062.9524 | 8297.3779 | 70844.3776 | 13198.8148 | 0.08687 | -101917.7489 | 101917.7489
C | Xist Rating 733 | -70.44 | 681.625 | 150.276 | 35.6 | 2178.36 | 9458.43 | 12606.8 | 0.41 | 1.56 | 11.803 | 12.123 | 1 | 1 | 2290 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1484824.635 | 79800.9522 | 5107.4617 | 8333.7699 | 71467.1823 | 13086.4558 | 0.087251 | -101050.1427 | 101050.1427
C | Xist Rating 734 | -70.3 | 686.115 | 150.276 | 35.6 | 2175.4 | 9434.91 | 12557 | 0.4 | 1.56 | 11.801 | 12.061 | 1 | 1 | 2300 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1492574.571 | 80462.8745 | 5152.1657 | 8370.1619 | 72092.7126 | 13011.9871 | 0.087632 | -100475.1151 | 100475.1151
| Xist Rating 735 | -70.15 | 690.87 | 150.276 | 35.6 | 2172.11 | 9405.24 | 12507.6 | 0.4 | 1.55 | 11.798 | 12.001 | 1 | 1 | 2310 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1500645.6357 | 81127.5225 | 5197.0645 | 8406.5539 | 72720.9686 | 12951.6688 | 0.088013 | -100009.3535 | 100009.3535
| Xist Rating 736 | -69.55 | 708.414 | 150.276 | 35.6 | 2162.4 | 9375.21 | 12277.1 | 0.4 | 1.51 | 11.836 | 11.664 | 1 | 1 | 2320 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1531874.4336 | 81794.8961 | 5242.1582 | 8442.9459 | 73351.9502 | 12605.3909 | 0.088394 | -97335.4873 | 97335.4873
| Xist Rating 737 | -69.36 | 713.976 | 150.276 | 35.6 | 2159.44 | 9360.32 | 12216.8 | 0.39 | 1.5 | 11.832 | 11.588 | 1 | 1 | 2330 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1541788.3334 | 82464.9953 | 5287.4466 | 8479.3379 | 73985.6574 | 12516.0626 | 0.088775 | -96645.7177 | 96645.7177
| Xist Rating 738 | -69.19 | 719.513 | 150.276 | 35.6 | 2156.27 | 9341.12 | 12157.2 | 0.39 | 1.49 | 11.828 | 11.513 | 1 | 1 | 2340 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1551464.2965 | 83137.8202 | 5332.9298 | 8515.7299 | 74622.0902 | 12440.08 | 0.089156 | -96059.0003 | 96059.0003
| Xist Rating 739 | -69.04 | 724.632 | 150.276 | 35.6 | 2152.77 | 9311.19 | 12104.7 | 0.38 | 1.49 | 11.821 | 11.449 | 1 | 1 | 2350 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1559966.0306 | 83813.3706 | 5378.6078 | 8552.1219 | 75261.2487 | 12362.9443 | 0.089537 | -95463.3785 | 95463.3785
| Xist Rating 740 | -68.84 | 730.731 | 150.276 | 35.6 | 2149.56 | 9295.41 | 12039.9 | 0.38 | 1.48 | 11.82 | 11.367 | 1 | 1 | 2360 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1570750.1284 | 84491.6467 | 5424.4805 | 8588.5139 | 75903.1328 | 12279.7607 | 0.089918 | -94821.0572 | 94821.0572
| Xist Rating 741 | -68.29 | 746.951 | 150.276 | 35.6 | 2141.01 | 9269.6 | 11846.8 | 0.38 | 1.45 | 11.855 | 11.099 | 1 | 1 | 2370 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1599229.5605 | 85172.6484 | 5470.5481 | 8624.906 | 76547.7425 | 12004.8694 | 0.090299 | -92698.4193 | 92698.4193
| Xist Rating 742 | -68.11 | 752.726 | 150.276 | 35.6 | 2137.7 | 9246.73 | 11791.2 | 0.37 | 1.44 | 11.85 | 11.034 | 1 | 1 | 2380 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1609102.3702 | 85856.3757 | 5516.8105 | 8661.298 | 77195.0778 | 11926.5417 | 0.09068 | -92093.5937 | 92093.5937
| Xist Rating 743 | -67.92 | 758.38 | 150.276 | 35.6 | 2135.73 | 9253.41 | 11730 | 0.37 | 1.43 | 11.845 | 10.956 | 1 | 1 | 2390 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1619694.9174 | 86542.8287 | 5563.2676 | 8697.69 | 77845.1387 | 11847.306 | 0.091061 | -91481.7564 | 91481.7564
C | Xist Rating 744 | -64.73 | 870.217 | 150.276 | 35.6 | 2047.73 | 8539.78 | 10538.2 | 0.41 | 1.25 | 11.84 | 9.402 | 1 | 1 | 2400 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1781969.4574 | 87232.0073 | 5609.9196 | 8734.082 | 78497.9253 | 10286.1944 | 0.091442 | -79427.2667 | 79427.2667
C | Xist Rating 745 | -64.45 | 871.663 | 150.276 | 35.6 | 2061.53 | 8785.14 | 10537.9 | 0.39 | 1.25 | 11.842 | 9.412 | 1 | 1 | 2410 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1796959.4244 | 87923.9115 | 5656.7663 | 8770.474 | 79153.4375 | 10273.2587 | 0.091823 | -79327.3808 | 79327.3808
C | Xist Rating 746 | -64.42 | 873.064 | 150.276 | 35.6 | 2061.43 | 8783.34 | 10537.9 | 0.39 | 1.25 | 11.881 | 9.423 | 1 | 1 | 2420 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1799760.3215 | 88618.5413 | 5703.8078 | 8806.866 | 79811.6753 | 10288.4023 | 0.092204 | -79444.3154 | 79444.3154
C | Xist Rating 747 | -64.08 | 874.421 | 150.276 | 35.6 | 2078.31 | 9098.29 | 10538 | 0.39 | 1.25 | 11.874 | 9.432 | 1 | 1 | 2430 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1817317.9085 | 89315.8967 | 5751.0441 | 8843.258 | 80472.6387 | 10299.5284 | 0.092585 | -79530.2283 | 79530.2283
C | Xist Rating 748 | -64.06 | 875.792 | 150.276 | 35.6 | 2076.98 | 9072.84 | 10537.9 | 0.38 | 1.25 | 11.869 | 9.443 | 1 | 1 | 2440 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1819002.4682 | 90015.9778 | 5798.4752 | 8879.65 | 81136.3278 | 10299.833 | 0.092966 | -79532.5803 | 79532.5803
C | Xist Rating 749 | -64.03 | 877.118 | 150.276 | 35.6 | 2077.19 | 9076.83 | 10537.8 | 0.38 | 1.25 | 11.863 | 9.453 | 1 | 1 | 2450 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1821940.7384 | 90718.7845 | 5846.1011 | 8916.042 | 81802.7425 | 10311.9893 | 0.093347 | -79626.4479 | 79626.4479
C | Xist Rating 750 | -64 | 878.59 | 150.276 | 35.6 | 2076.28 | 9059.48 | 10537.9 | 0.37 | 1.25 | 11.859 | 9.464 | 1 | 1 | 2460 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1824198.8452 | 91424.3168 | 5893.9217 | 8952.434 | 82471.8828 | 10312.1891 | 0.093728 | -79627.9906 | 79627.9906
C | Xist Rating 751 | -63.97 | 879.944 | 150.276 | 35.6 | 2075.81 | 9050.61 | 10537.8 | 0.37 | 1.25 | 11.896 | 9.475 | 1 | 1 | 2470 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1826596.5546 | 92132.5747 | 5941.9372 | 8988.826 | 83143.7487 | 10327.0951 | 0.094109 | -79743.091 | 79743.091
C | Xist Rating 752 | -63.95 | 881.291 | 150.276 | 35.6 | 2075.02 | 9035.7 | 10537.9 | 0.36 | 1.25 | 11.892 | 9.486 | 1 | 1 | 2480 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1828696.4508 | 92843.5583 | 5990.1474 | 9025.218 | 83818.3402 | 10327.1073 | 0.09449 | -79743.1849 | 79743.1849
C | Xist Rating 753 | -63.93 | 882.689 | 150.276 | 35.6 | 2073.94 | 9015.26 | 10537.8 | 0.35 | 1.25 | 11.886 | 9.496 | 1 | 1 | 2490 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1830644.0247 | 93557.2674 | 6038.5525 | 9061.6101 | 84495.6574 | 10325.9038 | 0.094871 | -79733.8921 | 79733.8921
C | Xist Rating 754 | -63.91 | 883.674 | 150.276 | 35.6 | 2074.36 | 9023.03 | 10537.9 | 0.35 | 1.25 | 11.888 | 9.505 | 1 | 1 | 2500 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1833057.9986 | 94273.7022 | 6087.1523 | 9098.0021 | 85175.7002 | 10337.1935 | 0.095252 | -79821.068 | 79821.068
C | Xist Rating 755 | -63.88 | 885.524 | 150.276 | 35.6 | 2072.63 | 8990.44 | 10537.9 | 0.34 | 1.25 | 11.884 | 9.518 | 1 | 1 | 2510 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1835363.6081 | 94992.8627 | 6135.9469 | 9134.3941 | 85858.4686 | 10339.0308 | 0.095633 | -79835.2556 | 79835.2556
C | Xist Rating 756 | -63.87 | 886.978 | 150.277 | 35.6 | 2070.54 | 8951.31 | 10537.8 | 0.34 | 1.25 | 11.923 | 9.528 | 1 | 1 | 2520 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1836523.4281 | 95714.7487 | 6184.9363 | 9170.7861 | 86543.9626 | 10352.7248 | 0.096014 | -79940.9968 | 79940.9968
C | Xist Rating 757 | -63.86 | 888.316 | 150.277 | 35.6 | 2069.4 | 8930.07 | 10537.8 | 0.33 | 1.25 | 11.917 | 9.539 | 1 | 1 | 2530 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1838281.1304 | 96439.3604 | 6234.1205 | 9207.1781 | 87232.1823 | 10352.2194 | 0.096395 | -79937.0943 | 79937.0943
C | Xist Rating 758 | -63.83 | 889.467 | 150.277 | 35.6 | 2069.36 | 8929.22 | 10537.9 | 0.33 | 1.25 | 11.912 | 9.548 | 1 | 1 | 2540 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1840627.4311 | 97166.6977 | 6283.4995 | 9243.5701 | 87923.1276 | 10363.1408 | 0.096776 | -80021.4265 | 80021.4265
C | Xist Rating 759 | -63.82 | 891.013 | 150.277 | 35.6 | 2067.77 | 8899.63 | 10537.9 | 0.32 | 1.25 | 11.909 | 9.559 | 1 | 1 | 2550 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1842409.951 | 97896.7606 | 6333.0732 | 9279.9621 | 88616.7985 | 10362.6009 | 0.097157 | -80017.257 | 80017.257
C | Xist Rating 760 | -63.79 | 892.462 | 150.277 | 35.6 | 2066.91 | 8883.83 | 10537.9 | 0.32 | 1.25 | 11.905 | 9.57 | 1 | 1 | 2560 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1844638.6324 | 98629.5491 | 6382.8418 | 9316.3541 | 89313.195 | 10375.5857 | 0.097538 | -80117.5223 | 80117.5223
C | Xist Rating 761 | -63.77 | 893.851 | 150.277 | 35.6 | 2065.71 | 8861.7 | 10537.9 | 0.31 | 1.25 | 11.905 | 9.58 | 1 | 1 | 2570 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1846436.9492 | 99365.0633 | 6432.8051 | 9352.7461 | 90012.3171 | 10373.9638 | 0.097919 | -80104.9988 | 80104.9988
C | Xist Rating 762 | -63.75 | 895.217 | 150.277 | 35.6 | 2064.6 | 8841.16 | 10537.9 | 0.31 | 1.25 | 11.94 | 9.59 | 1 | 1 | 2580 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1848265.0182 | 100103.303 | 6482.9633 | 9389.1381 | 90714.1649 | 10387.2579 | 0.0983 | -80207.6518 | 80207.6518
C | Xist Rating 763 | -63.74 | 896.577 | 150.277 | 35.6 | 2063.43 | 8819.91 | 10537.9 | 0.3 | 1.25 | 11.935 | 9.601 | 1 | 1 | 2590 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1850023.8791 | 100844.2684 | 6533.3162 | 9425.5301 | 91418.7383 | 10386.3045 | 0.098681 | -80200.2901 | 80200.2901
C | Xist Rating 764 | -63.71 | 897.754 | 150.277 | 35.6 | 2063.7 | 8824.84 | 10537.9 | 0.3 | 1.25 | 11.927 | 9.61 | 1 | 1 | 2600 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1852694.9298 | 101587.9595 | 6583.8639 | 9461.9221 | 92126.0373 | 10396.9762 | 0.099062 | -80282.6944 | 80282.6944
C | Xist Rating 765 | -63.68 | 899.441 | 150.277 | 35.6 | 2062.48 | 8802.62 | 10537.8 | 0.3 | 1.25 | 11.923 | 9.621 | 1 | 1 | 2610 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1855079.0737 | 102334.3761 | 6634.6064 | 9498.3141 | 92836.0619 | 10409.8632 | 0.099443 | -80382.2041 | 80382.2041
C | Xist Rating 766 | -63.66 | 900.838 | 150.277 | 35.6 | 2061.6 | 8786.62 | 10537.8 | 0.29 | 1.25 | 11.921 | 9.631 | 1 | 1 | 2620 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1857167.6208 | 103083.5184 | 6685.5437 | 9534.7062 | 93548.8122 | 10407.7809 | 0.099824 | -80366.1256 | 80366.1256
C | Xist Rating 767 | -63.63 | 902.264 | 150.277 | 35.6 | 2061.09 | 8777.26 | 10537.8 | 0.29 | 1.25 | 11.958 | 9.642 | 1 | 1 | 2630 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1859647.3078 | 103835.3863 | 6736.6758 | 9571.0982 | 94264.2881 | 10422.019 | 0.10021 | -80476.0681 | 80476.0681
C | Xist Rating 768 | -63.61 | 903.51 | 150.277 | 35.6 | 2060.74 | 8771.03 | 10537.8 | 0.28 | 1.25 | 11.953 | 9.651 | 1 | 1 | 2640 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1861899.1974 | 104589.9798 | 6788.0027 | 9607.4902 | 94982.4896 | 10418.6035 | 0.10059 | -80449.6946 | 80449.6946
C | Xist Rating 769 | -63.57 | 905.013 | 150.277 | 35.6 | 2060.38 | 8764.54 | 10537.8 | 0.28 | 1.25 | 11.951 | 9.662 | 1 | 1 | 2650 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1864670.6849 | 105347.2989 | 6839.5243 | 9643.8822 | 95703.4167 | 10431.4607 | 0.10097 | -80548.9742 | 80548.9742
C | Xist Rating 770 | -63.54 | 906.354 | 150.277 | 35.6 | 2059.94 | 8756.53 | 10537.8 | 0.28 | 1.25 | 11.947 | 9.671 | 1 | 1 | 2660 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1867034.8588 | 106107.3437 | 6891.2408 | 9680.2742 | 96427.0695 | 10442.1736 | 0.10135 | -80631.6964 | 80631.6964
C | Xist Rating 771 | -63.51 | 907.741 | 150.277 | 35.6 | 2059.79 | 8753.91 | 10537.8 | 0.27 | 1.25 | 11.946 | 9.681 | 1 | 1 | 2670 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1869755.8344 | 106870.114 | 6943.152 | 9716.6662 | 97153.4478 | 10439.7273 | 0.10173 | -80612.8071 | 80612.8071
C | Xist Rating 772 | -63.48 | 909.158 | 150.277 | 35.6 | 2059.01 | 8739.81 | 10537.7 | 0.27 | 1.25 | 11.981 | 9.691 | 1 | 1 | 2680 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 6 | E | Rod | 1871965.4136 | 107635.61 | 6995.258 | 9753.0582 | 97882.5518 | 10452.6933 | 0.10211 | -80712.927 | 80712.927
C | Xist Rating 773 | -63.43 | 910.535 | 150.277 | 35.6 | 2060.04 | 8758.39 | 10537.8 | 0.27 | 1.25 | 11.978 | 9.701 | 1 | 1 | 2690 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1875738.5214 | 108403.8317 | 7047.5588 | 9789.4502 | 98614.3814 | 10464.4306 | 0.10249 | -80803.5596 | 80803.5596
C | Xist Rating 774 | -63.41 | 911.735 | 150.277 | 35.6 | 2059.39 | 8746.56 | 10537.8 | 0.26 | 1.25 | 11.972 | 9.71 | 1 | 1 | 2700 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1877617.9416 | 109174.7789 | 7100.0544 | 9825.8422 | 99348.9367 | 10460.5414 | 0.10287 | -80773.5281 | 80773.5281
C | Xist Rating 775 | -63.35 | 913.392 | 150.277 | 35.6 | 2059.9 | 8755.74 | 10537.9 | 0.26 | 1.25 | 11.973 | 9.721 | 1 | 1 | 2710 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1881496.1808 | 109948.4518 | 7152.7448 | 9862.2342 | 100086.2175 | 10473.3918 | 0.10325 | -80872.755 | 80872.755
C | Xist Rating 776 | -63.25 | 914.736 | 150.277 | 35.6 | 2063.66 | 8823.95 | 10538 | 0.26 | 1.25 | 11.979 | 9.731 | 1 | 1 | 2720 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1887704.0938 | 110724.8503 | 7205.63 | 9898.6262 | 100826.224 | 10485.3623 | 0.10363 | -80965.1885 | 80965.1885
C | Xist Rating 777 | -63.17 | 916.058 | 150.277 | 35.6 | 2066.03 | 8867.41 | 10538.1 | 0.25 | 1.25 | 12.02 | 9.741 | 1 | 1 | 2730 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1892603.3097 | 111503.9744 | 7258.71 | 9935.0182 | 101568.9561 | 10483.7388 | 0.10402 | -80952.6524 | 80952.6524
C | Xist Rating 778 | -62.85 | 917.341 | 150.277 | 35.6 | 2082.46 | 9177.9 | 10538.3 | 0.25 | 1.25 | 12.05 | 9.751 | 1 | 1 | 2740 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1910325.9389 | 112285.8241 | 7311.9847 | 9971.4103 | 102314.4139 | 10496.392 | 0.1044 | -81050.3564 | 81050.3564
C | Xist Rating 779 | -63.1 | 918.889 | 150.277 | 35.6 | 2065.67 | 8860.64 | 10538.2 | 0.25 | 1.25 | 12.015 | 9.761 | 1 | 1 | 2750 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1898121.4406 | 113070.3995 | 7365.4543 | 10007.8023 | 103062.5972 | 10507.0487 | 0.10478 | -81132.6448 | 81132.6448
C | Xist Rating 780 | -62.76 | 920.314 | 150.277 | 35.6 | 2082.77 | 9183.89 | 10538.4 | 0.24 | 1.25 | 12.048 | 9.772 | 1 | 1 | 2760 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1916802.3898 | 113857.7005 | 7419.1186 | 10044.1943 | 103813.5062 | 10505.9339 | 0.10516 | -81124.037 | 81124.037
C | Xist Rating 781 | -62.56 | 921.549 | 150.277 | 35.6 | 2092.72 | 9380.65 | 10538.4 | 0.24 | 1.25 | 12.069 | 9.781 | 1 | 1 | 2770 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1928544.0233 | 114647.7271 | 7472.9777 | 10080.5863 | 104567.1408 | 10517.2023 | 0.10554 | -81211.0485 | 81211.0485
C | Xist Rating 782 | -62.45 | 923.097 | 150.277 | 35.6 | 2096.29 | 9452.75 | 10538.5 | 0.23 | 1.25 | 12.116 | 9.792 | 1 | 1 | 2780 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1935079.0101 | 115440.4793 | 7527.0316 | 10116.9783 | 105323.501 | 10516.2318 | 0.10592 | -81203.5541 | 81203.5541
C | Xist Rating 783 | -62.36 | 924.505 | 150.277 | 35.6 | 2099.08 | 9509.83 | 10538.4 | 0.23 | 1.25 | 12.123 | 9.802 | 1 | 1 | 2790 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1940609.9554 | 116235.9571 | 7581.2803 | 10153.3703 | 106082.5868 | 10528.0672 | 0.1063 | -81294.9443 | 81294.9443
C | Xist Rating 784 | -62.28 | 925.48 | 150.277 | 35.6 | 2102.81 | 9586.68 | 10538.4 | 0.23 | 1.25 | 12.129 | 9.81 | 1 | 1 | 2800 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1946108.5988 | 117034.1606 | 7635.7238 | 10189.7623 | 106844.3983 | 10537.7982 | 0.10668 | -81370.0847 | 81370.0847
C | Xist Rating 785 | -62.22 | 927.224 | 150.277 | 35.6 | 2102.88 | 9588.21 | 10538.4 | 0.22 | 1.25 | 12.132 | 9.821 | 1 | 1 | 2810 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1949840.8051 | 117835.0897 | 7690.3621 | 10226.1543 | 107608.9354 | 10535.278 | 0.10706 | -81350.6238 | 81350.6238
C | Xist Rating 786 | -62.15 | 928.7 | 150.277 | 35.6 | 2104.41 | 9620.12 | 10538.4 | 0.22 | 1.25 | 12.136 | 9.831 | 1 | 1 | 2820 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1954365.567 | 118638.7444 | 7745.1952 | 10262.5463 | 108376.1981 | 10546.9706 | 0.10744 | -81440.911 | 81440.911
C | Xist Rating 787 | -62.1 | 930.071 | 150.277 | 35.6 | 2105.5 | 9642.98 | 10538.4 | 0.22 | 1.25 | 12.18 | 9.84 | 1 | 1 | 2830 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1958264.4905 | 119445.1248 | 7800.223 | 10298.9383 | 109146.1864 | 10558.7418 | 0.10783 | -81531.8052 | 81531.8052
C | Xist Rating 788 | -62.04 | 931.389 | 150.277 | 35.6 | 2107.01 | 9674.87 | 10538.3 | 0.21 | 1.25 | 12.178 | 9.849 | 1 | 1 | 2840 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1962445.9369 | 120254.2307 | 7855.4457 | 10335.3303 | 109918.9004 | 10553.7305 | 0.10821 | -81493.1097 | 81493.1097
C | Xist Rating 789 | -61.98 | 932.832 | 150.277 | 35.6 | 2107.72 | 9689.92 | 10538.3 | 0.21 | 1.25 | 12.18 | 9.859 | 1 | 1 | 2850 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1966148.663 | 121066.0623 | 7910.8631 | 10371.7223 | 110694.34 | 10565.3155 | 0.10859 | -81582.5658 | 81582.5658
C | Xist Rating 790 | -61.93 | 934.238 | 150.277 | 35.6 | 2108.52 | 9706.7 | 10538.3 | 0.21 | 1.25 | 12.182 | 9.869 | 1 | 1 | 2860 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1969859.5078 | 121880.6195 | 7966.4753 | 10408.1144 | 111472.5051 | 10576.9009 | 0.10897 | -81672.0248 | 81672.0248
C | Xist Rating 791 | -61.88 | 935.429 | 150.277 | 35.6 | 2109.9 | 9736.21 | 10538.2 | 0.21 | 1.25 | 12.185 | 9.877 | 1 | 1 | 2870 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1973661.6471 | 122697.9023 | 8022.2824 | 10444.5064 | 112253.396 | 10586.4366 | 0.10935 | -81745.6573 | 81745.6573
C | Xist Rating 792 | -61.82 | 936.937 | 150.277 | 35.5 | 2110.76 | 9754.47 | 10538.2 | 0.2 | 1.25 | 12.229 | 9.887 | 1 | 1 | 2880 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1977649.1421 | 123517.9108 | 8078.2842 | 10480.8984 | 113037.0124 | 10583.3744 | 0.10973 | -81722.0118 | 81722.0118
C | Xist Rating 793 | -61.76 | 938.28 | 150.277 | 35.5 | 2111.98 | 9780.61 | 10538.2 | 0.2 | 1.25 | 12.231 | 9.896 | 1 | 1 | 2890 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1981628.5944 | 124340.6449 | 8134.4807 | 10517.2904 | 113823.3545 | 10593.869 | 0.11011 | -81803.0485 | 81803.0485
C | Xist Rating 794 | -61.7 | 939.666 | 150.277 | 35.5 | 2113.38 | 9810.83 | 10538.1 | 0.2 | 1.25 | 12.229 | 9.906 | 1 | 1 | 2900 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1985871.3311 | 125166.1045 | 8190.8721 | 10553.6824 | 114612.4222 | 10605.2985 | 0.11049 | -81891.304 | 81891.304
C | Xist Rating 795 | -61.64 | 941.205 | 150.277 | 35.5 | 2114.44 | 9833.66 | 10538 | 0.2 | 1.25 | 12.231 | 9.916 | 1 | 1 | 2910 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1990121.5002 | 125994.2899 | 8247.4583 | 10590.0744 | 115404.2155 | 10616.832 | 0.11087 | -81980.3624 | 81980.3624
C | Xist Rating 796 | -61.54 | 942.597 | 150.277 | 35.5 | 2117.85 | 9907.88 | 10538.1 | 0.19 | 1.25 | 12.238 | 9.925 | 1 | 1 | 2920 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1996279.0564 | 126825.2008 | 8304.2393 | 10626.4664 | 116198.7344 | 10611.4402 | 0.11125 | -81938.7281 | 81938.7281
C | Xist Rating 797 | -61.55 | 943.983 | 150.277 | 35.5 | 2116.52 | 9879.25 | 10537.6 | 0.19 | 1.25 | 12.281 | 9.934 | 1 | 1 | 2930 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1997958.8992 | 127658.8374 | 8361.215 | 10662.8584 | 116995.979 | 10622.9019 | 0.11164 | -82027.2329 | 82027.2329
C | Xist Rating 800 | -61.51 | 948.129 | 150.277 | 35.5 | 2113.25 | 9809.33 | 10536.8 | 0.19 | 1.25 | 12.278 | 9.961 | 1 | 1 | 2960 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 2003633.6092 | 130176.1008 | 8533.311 | 10772.0344 | 119404.0663 | 10654.0036 | 0.11278 | -82267.3914 | 82267.3914
C | Xist Rating 801 | -61.5 | 949.512 | 150.277 | 35.5 | 2111.97 | 9782.12 | 10536.5 | 0.18 | 1.25 | 12.275 | 9.969 | 1 | 1 | 2970 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 2005340.8586 | 131020.6398 | 8591.0659 | 10808.4264 | 120212.2134 | 10646.9397 | 0.11316 | -82212.8464 | 82212.8464
C | Xist Rating 802 | -61.82 | 950.736 | 150.277 | 35.4 | 2100.24 | 9534.3 | 10537.7 | 0.18 | 1.25 | 12.32 | 9.977 | 1 | 1 | 2980 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 1996773.7766 | 131867.9045 | 8649.0156 | 10844.8185 | 121023.0861 | 10657.3201 | 0.11354 | -82293.0008 | 82293.0008
C | Xist Rating 803 | -61.51 | 952.295 | 150.277 | 35.5 | 2109.36 | 9727.47 | 10535.3 | 0.18 | 1.25 | 12.329 | 9.987 | 1 | 1 | 2990 | 152.4 | 2 | 1.3 | 19.05 | 1.3333 | 5 | E | Rod | 2008732.9812 | 132717.8948 | 8707.16 | 10881.2105 | 121836.6843 | 10668.9162 | 0.11392 | -82382.5431 | 82382.5431
C | Xist Rating 805 | -95.67 | 82.009 | 150.278 | 35.8 | 2415.92 | 7561.44 | 58745.6 | 2.44 | 10.95 | 12.627 | 312.397 | 1 | 1 | 1000 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 198127.1833 | 18595.5677 | 973.9444 | 3919.1393 | 14676.4283 | 325804.8327 | 0.038101 | -2515778.5564 | 2515778.5564
C | Xist Rating 806 | -95.63 | 82.903 | 150.278 | 35.8 | 2413.82 | 7549.76 | 58284.1 | 2.42 | 10.85 | 12.631 | 306.595 | 1 | 1 | 1010 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 200112.9195 | 18929.7553 | 993.5206 | 3958.3307 | 14971.4245 | 319782.2803 | 0.038482 | -2469274.0034 | 2469274.0034
C | Xist Rating 807 | -95.3 | 89.451 | 150.278 | 35.8 | 2407.11 | 7551.8 | 54967.4 | 2.43 | 10.07 | 12.682 | 265.686 | 1 | 1 | 1020 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 215318.3966 | 19266.8782 | 1013.2917 | 3997.5221 | 15269.356 | 277323.4913 | 0.038863 | -2141418.4893 | 2141418.4893
C | Xist Rating 808 | -95.23 | 91.383 | 150.278 | 35.8 | 2393.04 | 7431.82 | 54179.1 | 2.34 | 9.89 | 12.494 | 256.97 | 1 | 1 | 1030 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 218683.1743 | 19606.9364 | 1033.2576 | 4036.7135 | 15570.2228 | 268212.7451 | 0.039244 | -2071067.7225 | 2071067.7225
C | Xist Rating 809 | -95.15 | 92.351 | 150.278 | 35.8 | 2408.69 | 7593.59 | 53795.5 | 2.27 | 9.8 | 12.455 | 252.815 | 1 | 1 | 1040 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 222444.9302 | 19949.9298 | 1053.4182 | 4075.9049 | 15874.0249 | 263865.9912 | 0.039625 | -2037503.2409 | 2037503.2409
C | Xist Rating 810 | -95.04 | 94.162 | 150.278 | 35.8 | 2417.79 | 7702.69 | 53044.6 | 2.22 | 9.63 | 12.423 | 244.528 | 1 | 1 | 1050 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 227663.942 | 20295.8586 | 1073.7737 | 4115.0963 | 16180.7622 | 255239.9742 | 0.040006 | -1970895.4239 | 1970895.4239
C | Xist Rating 811 | -94.97 | 95.111 | 150.278 | 35.8 | 2429.54 | 7832.47 | 52677.8 | 2.18 | 9.54 | 12.405 | 240.641 | 1 | 1 | 1060 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 231075.9789 | 20644.7226 | 1094.3239 | 4154.2877 | 16490.4349 | 251190.2179 | 0.040387 | -1939624.2792 | 1939624.2792
C | Xist Rating 812 | -94.64 | 102.261 | 150.277 | 35.8 | 2406.9 | 7673.96 | 49858.2 | 2.16 | 8.9 | 12.368 | 210.633 | 1 | 1 | 1070 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 246132.0009 | 20996.5219 | 1115.0689 | 4193.4791 | 16803.0428 | 220023.3466 | 0.040768 | -1698961.9605 | 1698961.9605
C | Xist Rating 813 | -94.56 | 103.687 | 150.277 | 35.8 | 2411.79 | 7737.21 | 49381.6 | 2.11 | 8.79 | 12.317 | 206.007 | 1 | 1 | 1080 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 250071.2697 | 21351.2565 | 1136.0087 | 4232.6705 | 17118.586 | 215196.0811 | 0.041149 | -1661687.0964 | 1661687.0964
C | Xist Rating 814 | -94.47 | 105.578 | 150.277 | 35.8 | 2409.46 | 7730.92 | 48761.8 | 2.06 | 8.65 | 12.248 | 200.045 | 1 | 1 | 1090 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 254385.9679 | 21708.9264 | 1157.1433 | 4271.8619 | 17437.0645 | 208979.1685 | 0.04153 | -1613681.7446 | 1613681.7446
C | Xist Rating 815 | -94.4 | 106.973 | 150.277 | 35.8 | 2413.25 | 7783.57 | 48306.8 | 2.03 | 8.55 | 12.227 | 195.719 | 1 | 1 | 1100 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 258152.5922 | 22069.5316 | 1178.4727 | 4311.0533 | 17758.4783 | 204477.7146 | 0.041911 | -1578922.7109 | 1578922.7109
C | Xist Rating 816 | -94.36 | 108.108 | 150.277 | 35.8 | 2404.89 | 7705.99 | 48010.6 | 1.96 | 8.49 | 12.104 | 193.184 | 1 | 1 | 1110 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 259987.8481 | 22433.072 | 1199.9969 | 4350.2447 | 18082.8274 | 201801.6668 | 0.042292 | -1558258.9793 | 1558258.9793
C | Xist Rating 817 | -93.96 | 115.977 | 150.277 | 35.8 | 2403.43 | 7771.75 | 45447.9 | 2 | 7.92 | 12.229 | 169.04 | 1 | 1 | 1120 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 278742.6011 | 22799.5478 | 1221.7158 | 4389.4361 | 18410.1117 | 176775.6526 | 0.042673 | -1365014.7311 | 1365014.7311
C | Xist Rating 818 | -93.9 | 117.066 | 150.277 | 35.8 | 2405.37 | 7800.85 | 45189.8 | 1.93 | 7.86 | 12.152 | 166.981 | 1 | 1 | 1130 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 281587.0444 | 23168.9588 | 1243.6296 | 4428.6275 | 18740.3313 | 174597.4607 | 0.043054 | -1348195.3106 | 1348195.3106
C | Xist Rating 819 | -93.8 | 119.028 | 150.277 | 35.8 | 2405.62 | 7821.1 | 44682.1 | 1.87 | 7.75 | 12.047 | 162.73 | 1 | 1 | 1140 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 286336.1374 | 23541.3051 | 1265.7381 | 4467.8189 | 19073.4863 | 170146.0252 | 0.043435 | -1313822.5056 | 1313822.5056
C | Xist Rating 820 | -93.69 | 120.927 | 150.277 | 35.8 | 2412.64 | 7913.82 | 44188.1 | 1.83 | 7.64 | 12.021 | 158.594 | 1 | 1 | 1150 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 291753.3173 | 23916.5867 | 1288.0414 | 4507.0103 | 19409.5765 | 165833.601 | 0.043816 | -1280523.109 | 1280523.109
C | Xist Rating 821 | -93.6 | 122.905 | 150.277 | 35.8 | 2410.58 | 7909.63 | 43705.4 | 1.78 | 7.53 | 11.959 | 154.681 | 1 | 1 | 1160 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 296272.3349 | 24294.8036 | 1310.5395 | 4546.2016 | 19748.602 | 161742.8265 | 0.044197 | -1248935.2327 | 1248935.2327
C | Xist Rating 822 | -93.23 | 130.041 | 150.277 | 35.8 | 2410.69 | 7985.22 | 41834.3 | 1.79 | 7.13 | 12.041 | 139.181 | 1 | 1 | 1170 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 313488.5383 | 24675.9558 | 1333.2324 | 4585.393 | 20090.5628 | 145669.6125 | 0.044578 | -1124822.1353 | 1124822.1353
C | Xist Rating 823 | -93.18 | 130.679 | 150.277 | 35.8 | 2418.19 | 8072.65 | 41726.7 | 1.74 | 7.11 | 11.999 | 138.499 | 1 | 1 | 1180 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 316006.651 | 25060.0432 | 1356.1201 | 4624.5844 | 20435.4588 | 144935.3081 | 0.044959 | -1119152.0314 | 1119152.0314
C | Xist Rating 824 | -93.03 | 134.461 | 150.276 | 35.8 | 2405.01 | 7963.4 | 40887.4 | 1.7 | 6.93 | 11.932 | 132.118 | 1 | 1 | 1190 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 323380.0496 | 25447.066 | 1379.2026 | 4663.7758 | 20783.2902 | 138286.3311 | 0.04534 | -1067810.3927 | 1067810.3927
C | Xist Rating 825 | -92.95 | 135.444 | 150.276 | 35.8 | 2416.8 | 8103.34 | 40683.4 | 1.67 | 6.88 | 11.932 | 130.643 | 1 | 1 | 1200 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 327341.0592 | 25837.024 | 1402.4799 | 4702.9672 | 21134.0568 | 136744.3838 | 0.045721 | -1055903.8846 | 1055903.8846
C | Xist Rating 826 | -92.86 | 137.49 | 150.276 | 35.8 | 2411.67 | 8064.22 | 40282.5 | 1.62 | 6.8 | 11.87 | 127.789 | 1 | 1 | 1210 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 331580.5083 | 26229.9173 | 1425.9519 | 4742.1586 | 21487.7587 | 133751.6353 | 0.046102 | -1032794.6743 | 1032794.6743
C | Xist Rating 827 | -92.48 | 145.712 | 150.276 | 35.8 | 2398.64 | 8002.26 | 38539.1 | 1.62 | 6.43 | 11.901 | 115.003 | 1 | 1 | 1220 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 349510.6317 | 26625.7459 | 1449.6188 | 4781.35 | 21844.3959 | 120484.7604 | 0.046483 | -930351.3826 | 930351.3826
C | Xist Rating 828 | -92.38 | 147.609 | 150.276 | 35.8 | 2404.11 | 8081.57 | 38184.2 | 1.6 | 6.35 | 11.894 | 112.587 | 1 | 1 | 1230 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 354868.273 | 27024.5098 | 1473.4804 | 4820.5414 | 22203.9684 | 117970.6496 | 0.046864 | -910938.086 | 910938.086
C | Xist Rating 829 | -92.29 | 149.646 | 150.276 | 35.8 | 2400.82 | 8062.43 | 37836.5 | 1.56 | 6.28 | 11.848 | 110.319 | 1 | 1 | 1240 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 359273.1097 | 27426.209 | 1497.5369 | 4859.7328 | 22566.4762 | 115593.433 | 0.047245 | -892581.849 | 892581.849
C | Xist Rating 830 | -92.23 | 150.772 | 150.276 | 35.8 | 2401.32 | 8077.03 | 37665.2 | 1.52 | 6.24 | 11.814 | 109.28 | 1 | 1 | 1250 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 362051.819 | 27830.8435 | 1521.7881 | 4898.9242 | 22931.9193 | 114493.2682 | 0.047626 | -884086.6683 | 884086.6683
C | Xist Rating 831 | -92.1 | 153.641 | 150.276 | 35.8 | 2399.35 | 8081.8 | 37162.2 | 1.5 | 6.14 | 11.792 | 105.958 | 1 | 1 | 1260 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 8 | E | Rod | 368638.5333 | 28238.4132 | 1546.2341 | 4938.1156 | 23300.2976 | 111036.2171 | 0.048007 | -857392.2357 | 857392.2357
C | Xist Rating 832 | -91.71 | 161.441 | 150.276 | 35.8 | 2395.89 | 8120.76 | 35778.6 | 1.5 | 5.85 | 11.792 | 96.844 | 1 | 1 | 1270 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 386794.8775 | 28648.9182 | 1570.8749 | 4977.307 | 23671.6113 | 101579.2711 | 0.048388 | -784368.2054 | 784368.2054
C | Xist Rating 833 | -91.61 | 163.546 | 150.276 | 35.7 | 2395.86 | 8138.47 | 35478.7 | 1.46 | 5.79 | 11.761 | 95.082 | 1 | 1 | 1280 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 391833.3196 | 29062.3586 | 1595.7105 | 5016.4984 | 24045.8602 | 99727.7057 | 0.048769 | -770070.9086 | 770070.9086
C | Xist Rating 834 | -91.5 | 165.6 | 150.276 | 35.7 | 2400.26 | 8207.61 | 35184.6 | 1.42 | 5.73 | 11.757 | 93.352 | 1 | 1 | 1290 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 397483.056 | 29478.7342 | 1620.7408 | 5055.6898 | 24423.0444 | 97911.2692 | 0.04915 | -756044.8677 | 756044.8677
C | Xist Rating 835 | -91.33 | 168.447 | 150.276 | 35.7 | 2407.05 | 8315.57 | 34753.1 | 1.4 | 5.64 | 11.756 | 90.749 | 1 | 1 | 1300 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 405460.3514 | 29898.045 | 1645.966 | 5094.8812 | 24803.1639 | 95201.7576 | 0.049531 | -735122.7373 | 735122.7373
C | Xist Rating 836 | -91.24 | 170.066 | 150.276 | 35.7 | 2412.92 | 8400.27 | 34541.9 | 1.36 | 5.59 | 11.736 | 89.576 | 1 | 1 | 1310 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 410355.6527 | 30320.2912 | 1671.3859 | 5134.0725 | 25186.2187 | 93961.7666 | 0.049912 | -725547.8551 | 725547.8551
C | Xist Rating 837 | -90.86 | 177.964 | 150.276 | 35.7 | 2407.05 | 8411.87 | 33365.1 | 1.36 | 5.35 | 11.779 | 82.573 | 1 | 1 | 1320 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 428368.2462 | 30745.4727 | 1697.0007 | 5173.2639 | 25572.2087 | 86699.7768 | 0.050293 | -669472.6948 | 669472.6948
C | Xist Rating 838 | -90.73 | 181.028 | 150.276 | 35.7 | 2401.27 | 8369.58 | 32982.1 | 1.33 | 5.28 | 11.727 | 80.494 | 1 | 1 | 1330 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 434697.1056 | 31173.5894 | 1722.8102 | 5212.4553 | 25961.1341 | 84522.7294 | 0.050674 | -652662.1116 | 652662.1116
C | Xist Rating 839 | -90.58 | 183.99 | 150.276 | 35.7 | 2401.92 | 8405.66 | 32608.7 | 1.3 | 5.2 | 11.709 | 78.467 | 1 | 1 | 1340 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 441929.2608 | 31604.6415 | 1748.8145 | 5251.6467 | 26352.9947 | 82402.1473 | 0.051055 | -636287.5392 | 636287.5392
C | Xist Rating 840 | -90.49 | 185.626 | 150.276 | 35.7 | 2405.28 | 8461.22 | 32425.6 | 1.28 | 5.16 | 11.691 | 77.541 | 1 | 1 | 1350 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 446482.5053 | 32038.6288 | 1775.0136 | 5290.8381 | 26747.7906 | 81431.7556 | 0.051436 | -628794.4318 | 628794.4318
C | Xist Rating 841 | -90.39 | 186.555 | 150.276 | 35.7 | 2421.09 | 8670.1 | 32304.7 | 1.26 | 5.14 | 11.707 | 76.896 | 1 | 1 | 1360 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 451666.445 | 32475.5514 | 1801.4075 | 5330.0295 | 27145.5219 | 80755.6069 | 0.051817 | -623573.3904 | 623573.3904
C | Xist Rating 842 | -89.92 | 197.984 | 150.276 | 35.7 | 2394 | 8446 | 30904.2 | 1.26 | 4.86 | 11.715 | 69.422 | 1 | 1 | 1370 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 473973.696 | 32915.4093 | 1827.9962 | 5369.2209 | 27546.1883 | 73001.1007 | 0.052198 | -563695.1493 | 563695.1493
C | Xist Rating 843 | -89.87 | 199.175 | 150.276 | 35.7 | 2393.53 | 8449.48 | 30795.7 | 1.23 | 4.84 | 11.696 | 68.944 | 1 | 1 | 1380 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 476731.3378 | 33358.2024 | 1854.7797 | 5408.4123 | 27949.7901 | 72488.1294 | 0.052579 | -559734.1205 | 559734.1205
C | Xist Rating 844 | -89.75 | 201.761 | 150.276 | 35.7 | 2393.78 | 8476.09 | 30528.2 | 1.21 | 4.79 | 11.677 | 67.651 | 1 | 1 | 1390 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 482971.4466 | 33803.9309 | 1881.7579 | 5447.6037 | 28356.3272 | 71135.7923 | 0.05296 | -549291.7323 | 549291.7323
C | Xist Rating 845 | -89.63 | 204.345 | 150.276 | 35.7 | 2393.2 | 8492.29 | 30266.3 | 1.18 | 4.73 | 11.661 | 66.397 | 1 | 1 | 1400 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 489038.454 | 34252.5946 | 1908.931 | 5486.7951 | 28765.7995 | 69816.6803 | 0.053341 | -539105.8991 | 539105.8991
C | Xist Rating 846 | -89.49 | 207.368 | 150.276 | 35.7 | 2391.67 | 8501.09 | 29958.5 | 1.16 | 4.67 | 11.648 | 64.921 | 1 | 1 | 1410 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 495955.8246 | 34704.1937 | 1936.2988 | 5525.9865 | 29178.2072 | 68274.3313 | 0.053722 | -527196.2886 | 527196.2886
C | Xist Rating 847 | -89.09 | 215.833 | 150.276 | 35.7 | 2386.89 | 8527.15 | 29052.9 | 1.17 | 4.49 | 11.696 | 60.486 | 1 | 1 | 1420 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 515169.6294 | 35158.728 | 1963.8614 | 5565.1779 | 29593.5501 | 63685.6361 | 0.054103 | -491763.6005 | 491763.6005
C | Xist Rating 848 | -89.02 | 217.71 | 150.276 | 35.7 | 2382.69 | 8487.74 | 28911.8 | 1.14 | 4.47 | 11.663 | 59.923 | 1 | 1 | 1430 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 518735.4399 | 35616.1976 | 1991.6188 | 5604.3693 | 30011.8283 | 63082.1928 | 0.054484 | -487103.9719 | 487103.9719
C | Xist Rating 849 | -88.84 | 221.662 | 150.276 | 35.7 | 2379.8 | 8488.1 | 28543.1 | 1.12 | 4.39 | 11.651 | 58.245 | 1 | 1 | 1440 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 527511.2276 | 36076.6025 | 2019.571 | 5643.5607 | 30433.0418 | 61329.6284 | 0.054865 | -473571.134 | 473571.134
C | Xist Rating 850 | -88.72 | 224.283 | 150.276 | 35.7 | 2378.96 | 8500.48 | 28317.8 | 1.1 | 4.35 | 11.638 | 57.268 | 1 | 1 | 1450 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 533560.2857 | 36539.9426 | 2047.718 | 5682.7521 | 30857.1906 | 60304.79 | 0.055246 | -465657.603 | 465657.603
C | Xist Rating 851 | -88.62 | 225.801 | 150.276 | 35.7 | 2387.04 | 8618.76 | 28184.8 | 1.09 | 4.33 | 11.644 | 56.694 | 1 | 1 | 1460 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 538996.019 | 37006.2181 | 2076.0598 | 5721.9434 | 31284.2746 | 59707.2419 | 0.055627 | -461043.4949 | 461043.4949
C | Xist Rating 852 | -88.22 | 235.622 | 150.276 | 35.7 | 2369.54 | 8487.9 | 27311.2 | 1.08 | 4.16 | 11.66 | 52.821 | 1 | 1 | 1470 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 558315.7539 | 37475.4288 | 2104.5964 | 5761.1348 | 31714.294 | 55684.2927 | 0.056008 | -429979.3482 | 429979.3482
C | Xist Rating 853 | -88.06 | 238.689 | 150.276 | 35.7 | 2372.18 | 8549.51 | 27067.2 | 1.06 | 4.11 | 11.655 | 51.811 | 1 | 1 | 1480 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 566213.272 | 37947.5749 | 2133.3277 | 5800.3262 | 32147.2486 | 54625.2318 | 0.056389 | -421801.5604 | 421801.5604
C | Xist Rating 854 | -87.89 | 241.313 | 150.276 | 35.7 | 2380.21 | 8678.56 | 26867.6 | 1.04 | 4.07 | 11.654 | 51.006 | 1 | 1 | 1490 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 574375.6157 | 38422.6562 | 2162.2539 | 5839.5176 | 32583.1386 | 53779.1404 | 0.05677 | -415268.2671 | 415268.2671
C | Xist Rating 855 | -87.75 | 244.028 | 150.276 | 35.7 | 2383.16 | 8741.87 | 26671.1 | 1.02 | 4.03 | 11.645 | 50.234 | 1 | 1 | 1500 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 581557.7685 | 38900.6728 | 2191.3748 | 5878.709 | 33021.9638 | 52966.5636 | 0.057151 | -408993.7645 | 408993.7645
C | Xist Rating 856 | -87.58 | 247.122 | 150.276 | 35.7 | 2387.52 | 8830.19 | 26439.8 | 1 | 3.99 | 11.643 | 49.308 | 1 | 1 | 1510 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 590008.7174 | 39381.6247 | 2220.6906 | 5917.9004 | 33463.7243 | 51994.3391 | 0.057532 | -401486.5041 | 401486.5041
C | Xist Rating 857 | -87.12 | 256.627 | 150.276 | 35.7 | 2386.66 | 8919.41 | 25682.1 | 1.01 | 3.85 | 11.697 | 46.179 | 1 | 1 | 1520 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 612481.3958 | 39865.5118 | 2250.2011 | 5957.0918 | 33908.42 | 48761.7452 | 0.057913 | -376525.2714 | 376525.2714
C | Xist Rating 858 | -87 | 260.065 | 150.276 | 35.7 | 2378.47 | 8835.21 | 25469.4 | 0.98 | 3.81 | 11.669 | 45.413 | 1 | 1 | 1530 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 618556.8005 | 40352.3343 | 2279.9064 | 5996.2832 | 34356.0511 | 47945.6031 | 0.058294 | -370223.2383 | 370223.2383
C | Xist Rating 859 | -86.88 | 261.857 | 150.276 | 35.7 | 2384.5 | 8933.86 | 25364.7 | 0.96 | 3.79 | 11.661 | 45.055 | 1 | 1 | 1540 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 624398.0165 | 40842.092 | 2309.8065 | 6035.4746 | 34806.6174 | 47562.3063 | 0.058675 | -367263.5219 | 367263.5219
C | Xist Rating 860 | -86.64 | 266.863 | 150.276 | 35.7 | 2384.55 | 8984.26 | 25022.3 | 0.95 | 3.72 | 11.66 | 43.751 | 1 | 1 | 1550 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 636348.1667 | 41334.7851 | 2339.9013 | 6074.666 | 35260.1191 | 46204.9544 | 0.059056 | -356782.4105 | 356782.4105
C | Xist Rating 861 | -86.51 | 268.431 | 150.276 | 35.7 | 2396.02 | 9164.89 | 24921.6 | 0.93 | 3.7 | 11.667 | 43.391 | 1 | 1 | 1560 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 643166.0446 | 41830.4134 | 2370.191 | 6113.8574 | 35716.556 | 45820.2086 | 0.059437 | -353811.5052 | 353811.5052
C | Xist Rating 862 | -86.06 | 279.952 | 150.276 | 35.7 | 2375.32 | 8984.8 | 24163.2 | 0.93 | 3.56 | 11.687 | 40.56 | 1 | 1 | 1570 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 664975.5846 | 42328.977 | 2400.6755 | 6153.0488 | 36175.9282 | 42886.3922 | 0.059818 | -331157.3523 | 331157.3523
C | Xist Rating 863 | -85.91 | 282.696 | 150.276 | 35.7 | 2378.65 | 9057.69 | 24008.5 | 0.91 | 3.53 | 11.68 | 40.037 | 1 | 1 | 1580 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 672434.8404 | 42830.4759 | 2431.3547 | 6192.2402 | 36638.2357 | 42331.1241 | 0.0602 | -326869.7198 | 326869.7198
C | Xist Rating 864 | -85.77 | 285.475 | 150.276 | 35.7 | 2380.42 | 9108.74 | 23856 | 0.89 | 3.5 | 11.672 | 39.529 | 1 | 1 | 1590 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 679550.3995 | 43334.91 | 2462.2288 | 6231.4316 | 37103.4785 | 41791.1749 | 0.060581 | -322700.3747 | 322700.3747
C | Xist Rating 865 | -85.59 | 289.04 | 150.276 | 35.7 | 2384.08 | 9198.58 | 23646 | 0.88 | 3.46 | 11.673 | 38.801 | 1 | 1 | 1600 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 689094.4832 | 43842.2795 | 2493.2976 | 6270.623 | 37571.6565 | 41031.4965 | 0.060962 | -316834.3394 | 316834.3394
C | Xist Rating 866 | -85.5 | 291.027 | 150.276 | 35.7 | 2384.1 | 9214.43 | 23557.3 | 0.86 | 3.45 | 11.661 | 38.544 | 1 | 1 | 1610 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 693837.4707 | 44352.5842 | 2524.5612 | 6309.8144 | 38042.7699 | 40751.6138 | 0.061343 | -314673.1598 | 314673.1598
C | Xist Rating 867 | -84.96 | 303.78 | 150.276 | 35.7 | 2369.95 | 9139.12 | 22805.7 | 0.87 | 3.31 | 11.698 | 35.917 | 1 | 1 | 1620 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 719943.411 | 44865.8243 | 2556.0196 | 6349.0057 | 38516.8185 | 38038.7789 | 0.061724 | -293725.368 | 293725.368
C | Xist Rating 868 | -84.84 | 305.423 | 150.276 | 35.7 | 2377.51 | 9268.09 | 22724 | 0.86 | 3.29 | 11.698 | 35.668 | 1 | 1 | 1630 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 726146.2367 | 45381.9996 | 2587.6728 | 6388.1971 | 38993.8025 | 37776.2077 | 0.062105 | -291697.8626 | 291697.8626
C | Xist Rating 869 | -84.72 | 308.349 | 150.276 | 35.7 | 2376.33 | 9276.09 | 22589.2 | 0.84 | 3.27 | 11.687 | 35.262 | 1 | 1 | 1640 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 732738.9792 | 45901.1102 | 2619.5208 | 6427.3885 | 39473.7217 | 37341.2086 | 0.062486 | -288338.9149 | 288338.9149
C | Xist Rating 870 | -84.56 | 312.271 | 150.276 | 35.7 | 2372.44 | 9253.15 | 22403.5 | 0.82 | 3.24 | 11.675 | 34.689 | 1 | 1 | 1650 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 740844.2112 | 46423.1561 | 2651.5635 | 6466.5799 | 39956.5762 | 36732.5342 | 0.062867 | -283638.892 | 283638.892
C | Xist Rating 871 | -84.38 | 315.95 | 150.276 | 35.6 | 2372.94 | 9296.93 | 22221.3 | 0.81 | 3.2 | 11.671 | 34.115 | 1 | 1 | 1660 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 749730.393 | 46948.1372 | 2683.8011 | 6505.7713 | 40442.3659 | 36131.799 | 0.063248 | -279000.1746 | 279000.1746
C | Xist Rating 872 | -83.9 | 327.515 | 150.276 | 35.6 | 2360.93 | 9233.63 | 21633.7 | 0.81 | 3.1 | 11.705 | 32.224 | 1 | 1 | 1670 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 773239.9889 | 47476.0537 | 2716.2334 | 6544.9627 | 40931.091 | 34174.2976 | 0.063629 | -263884.8673 | 263884.8673
C | Xist Rating 873 | -83.8 | 329.269 | 150.276 | 35.6 | 2365.42 | 9318.29 | 21561.1 | 0.8 | 3.08 | 11.702 | 32.025 | 1 | 1 | 1680 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 778859.478 | 48006.9054 | 2748.8606 | 6584.1541 | 41422.7513 | 33962.891 | 0.06401 | -262252.4418 | 262252.4418
C | Xist Rating 874 | -83.6 | 334.236 | 150.276 | 35.6 | 2359.84 | 9278.06 | 21346.8 | 0.79 | 3.04 | 11.689 | 31.396 | 1 | 1 | 1690 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 788743.4822 | 48540.6925 | 2781.6825 | 6623.3455 | 41917.347 | 33304.2291 | 0.064391 | -257166.4293 | 257166.4293
C | Xist Rating 875 | -83.44 | 337.486 | 150.276 | 35.6 | 2361.41 | 9333.43 | 21206.4 | 0.78 | 3.02 | 11.685 | 30.99 | 1 | 1 | 1700 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 796942.8153 | 49077.4148 | 2814.6992 | 6662.5369 | 42414.8779 | 32877.593 | 0.064772 | -253872.0584 | 253872.0584
C | Xist Rating 876 | -83.27 | 341.357 | 150.276 | 35.6 | 2360.49 | 9355.34 | 21045.1 | 0.76 | 2.99 | 11.679 | 30.529 | 1 | 1 | 1710 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 805769.7849 | 49617.0724 | 2847.9107 | 6701.7283 | 42915.3441 | 32384.668 | 0.065153 | -250065.8224 | 250065.8224
C | Xist Rating 877 | -82.83 | 352.082 | 150.276 | 35.6 | 2350.77 | 9313.27 | 20567.8 | 0.76 | 2.9 | 11.708 | 29.103 | 1 | 1 | 1720 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 827663.8031 | 50159.6653 | 2881.317 | 6740.9197 | 43418.7456 | 30909.4472 | 0.065534 | -238674.5581 | 238674.5581
C | Xist Rating 878 | -82.63 | 356.919 | 150.276 | 35.6 | 2347.7 | 9310.82 | 20374.8 | 0.75 | 2.87 | 11.7 | 28.565 | 1 | 1 | 1730 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 837938.7363 | 50705.1934 | 2914.9181 | 6780.1111 | 43925.0824 | 30345.1791 | 0.065915 | -234317.4297 | 234317.4297
C | Xist Rating 879 | -82.52 | 359.265 | 150.276 | 35.6 | 2348.21 | 9339.41 | 20290.3 | 0.74 | 2.85 | 11.695 | 28.349 | 1 | 1 | 1740 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 843629.6656 | 51253.6569 | 2948.714 | 6819.3025 | 44434.3544 | 30115.3829 | 0.066296 | -232543.0038 | 232543.0038
C | Xist Rating 880 | -82.36 | 363.789 | 150.276 | 35.6 | 2343.03 | 9298.43 | 20123.3 | 0.73 | 2.82 | 11.681 | 27.903 | 1 | 1 | 1750 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 852368.5407 | 51805.0556 | 2982.7046 | 6858.4939 | 44946.5618 | 29646.1162 | 0.066677 | -228919.4511 | 228919.4511
C | Xist Rating 881 | -82.22 | 367.156 | 150.276 | 35.6 | 2341 | 9296.68 | 20000.7 | 0.72 | 2.8 | 11.678 | 27.58 | 1 | 1 | 1760 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 859512.196 | 52359.3897 | 3016.8901 | 6897.6853 | 45461.7044 | 29305.1178 | 0.067058 | -226286.3515 | 226286.3515
C | Xist Rating 882 | -81.7 | 379.854 | 150.276 | 35.6 | 2330.37 | 9256.79 | 19497.4 | 0.72 | 2.71 | 11.714 | 26.172 | 1 | 1 | 1770 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 885200.366 | 52916.659 | 3051.2703 | 6936.8766 | 45979.7823 | 27848.7374 | 0.067439 | -215040.5684 | 215040.5684
C | Xist Rating 883 | -81.55 | 383.331 | 150.276 | 35.6 | 2328.95 | 9264.16 | 19383.4 | 0.71 | 2.69 | 11.706 | 25.889 | 1 | 1 | 1780 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 892758.7325 | 53476.8636 | 3085.8453 | 6976.068 | 46500.7955 | 27548.8234 | 0.06782 | -212724.7116 | 212724.7116
C | Xist Rating 884 | -81.47 | 385.344 | 150.276 | 35.6 | 2329.09 | 9281.41 | 19326.4 | 0.7 | 2.68 | 11.697 | 25.766 | 1 | 1 | 1790 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 897500.857 | 54040.0035 | 3120.6151 | 7015.2594 | 47024.744 | 27414.9156 | 0.068201 | -211690.7115 | 211690.7115
C | Xist Rating 885 | -81.3 | 391.264 | 150.276 | 35.6 | 2316.27 | 9133.64 | 19123.2 | 0.69 | 2.65 | 11.791 | 25.234 | 1 | 1 | 1800 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 906273.0653 | 54606.0786 | 3155.5797 | 7054.4508 | 47551.6278 | 26861.9002 | 0.068582 | -207420.473 | 207420.473
C | Xist Rating 886 | -81.16 | 394.613 | 150.276 | 35.6 | 2315.61 | 9152.31 | 19013.5 | 0.68 | 2.63 | 11.786 | 24.963 | 1 | 1 | 1810 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 913769.8089 | 55175.0891 | 3190.7391 | 7093.6422 | 48081.4469 | 26574.2718 | 0.068963 | -205199.4825 | 205199.4825
C | Xist Rating 887 | -80.56 | 407.57 | 150.276 | 35.6 | 2313.79 | 9247.76 | 18563.1 | 0.68 | 2.55 | 11.725 | 23.799 | 1 | 1 | 1820 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 943031.3903 | 55747.0348 | 3226.0933 | 7132.8336 | 48614.2012 | 25365.6681 | 0.069344 | -195866.9653 | 195866.9653
C | Xist Rating 888 | -80.54 | 405.479 | 150.276 | 35.6 | 2331.57 | 9517.7 | 18632.1 | 0.67 | 2.56 | 11.853 | 23.981 | 1 | 1 | 1830 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 945402.672 | 56321.9159 | 3261.6423 | 7172.025 | 49149.8909 | 25555.6656 | 0.069725 | -197334.0755 | 197334.0755
C | Xist Rating 889 | -80.3 | 408.184 | 150.276 | 35.6 | 2344.62 | 9765.98 | 18546.5 | 0.66 | 2.55 | 11.869 | 23.776 | 1 | 1 | 1840 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 957036.3701 | 56899.7322 | 3297.386 | 7211.2164 | 49688.5158 | 25337.4281 | 0.070106 | -195648.9034 | 195648.9034
C | Xist Rating 890 | -80.12 | 412.824 | 150.276 | 35.6 | 2341.47 | 9754.96 | 18410.6 | 0.65 | 2.52 | 11.863 | 23.458 | 1 | 1 | 1850 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 966615.0113 | 57480.4838 | 3333.3246 | 7250.4078 | 50230.076 | 25000.5311 | 0.070487 | -193047.4741 | 193047.4741
C | Xist Rating 891 | -79.92 | 418.003 | 150.276 | 35.6 | 2336.49 | 9717.44 | 18260.3 | 0.64 | 2.5 | 11.855 | 23.107 | 1 | 1 | 1860 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 976659.8295 | 58064.1707 | 3369.4579 | 7289.5992 | 50774.5715 | 24629.157 | 0.070868 | -190179.8221 | 190179.8221
C | Xist Rating 892 | -79.47 | 429.848 | 150.276 | 35.6 | 2325.37 | 9650.91 | 17880.7 | 0.64 | 2.43 | 11.882 | 22.166 | 1 | 1 | 1870 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 999555.6438 | 58650.7928 | 3405.7861 | 7328.7906 | 51322.0023 | 23656.7794 | 0.071249 | -182671.3798 | 182671.3798
C | Xist Rating 893 | -79.23 | 435.012 | 150.276 | 35.6 | 2324.99 | 9692.04 | 17740.1 | 0.63 | 2.41 | 11.881 | 21.85 | 1 | 1 | 1880 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1011398.5499 | 59240.3503 | 3442.309 | 7367.982 | 51872.3683 | 23321.9565 | 0.07163 | -180085.9661 | 180085.9661
C | Xist Rating 894 | -79.08 | 438.409 | 150.276 | 35.6 | 2325.79 | 9738.17 | 17647.6 | 0.62 | 2.39 | 11.883 | 21.646 | 1 | 1 | 1890 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1019647.2681 | 59832.843 | 3479.0267 | 7407.1734 | 52425.6697 | 23103.4976 | 0.072011 | -178399.0843 | 178399.0843
C | Xist Rating 895 | -78.92 | 442.265 | 150.276 | 35.6 | 2323.34 | 9727.24 | 17556.5 | 0.61 | 2.38 | 11.881 | 21.459 | 1 | 1 | 1900 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1027531.9651 | 60428.2711 | 3515.9392 | 7446.3648 | 52981.9063 | 22902.3765 | 0.072392 | -176846.0809 | 176846.0809
C | Xist Rating 896 | -78.74 | 445.841 | 150.276 | 35.6 | 2324.89 | 9786.62 | 17466.6 | 0.6 | 2.36 | 11.884 | 21.267 | 1 | 1 | 1910 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1036531.2825 | 61026.6344 | 3553.0464 | 7485.5562 | 53541.0782 | 22696.2157 | 0.072773 | -175254.1612 | 175254.1612
C | Xist Rating 897 | -78.18 | 460.251 | 150.277 | 35.6 | 2313.96 | 9745.81 | 17051.4 | 0.6 | 2.29 | 11.92 | 20.297 | 1 | 1 | 1920 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1065002.404 | 61627.933 | 3590.3485 | 7524.7475 | 54103.1854 | 21693.9273 | 0.073154 | -167514.7564 | 167514.7564
C | Xist Rating 898 | -77.95 | 465.492 | 150.277 | 35.6 | 2312.92 | 9775.23 | 16925.2 | 0.59 | 2.27 | 11.917 | 20.032 | 1 | 1 | 1930 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1076645.7566 | 62232.1669 | 3627.8454 | 7563.9389 | 54668.2279 | 21411.4658 | 0.073535 | -165333.6634 | 165333.6634
C | Xist Rating 899 | -77.84 | 467.144 | 150.277 | 35.6 | 2317.66 | 9876.96 | 16883.3 | 0.59 | 2.26 | 11.937 | 19.949 | 1 | 1 | 1940 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1082680.963 | 62839.336 | 3665.537 | 7603.1303 | 55236.2057 | 21329.4482 | 0.073916 | -164700.3451 | 164700.3451
C | Xist Rating 900 | -77.67 | 472.355 | 150.276 | 35.6 | 2311.08 | 9801.16 | 16773.3 | 0.57 | 2.24 | 11.926 | 19.736 | 1 | 1 | 1950 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1091650.1934 | 63449.4405 | 3703.4235 | 7642.3217 | 55807.1188 | 21089.9891 | 0.074297 | -162851.3055 | 162851.3055
C | Xist Rating 901 | -77.44 | 478.015 | 150.277 | 35.6 | 2308.21 | 9803.03 | 16638.1 | 0.56 | 2.22 | 11.93 | 19.453 | 1 | 1 | 1960 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1103359.0032 | 64062.4802 | 3741.5047 | 7681.5131 | 56380.9671 | 20788.8602 | 0.074678 | -160526.068 | 160526.068
C | Xist Rating 902 | -76.92 | 491.1 | 150.277 | 35.6 | 2299.68 | 9784.78 | 16304.2 | 0.57 | 2.16 | 11.974 | 18.722 | 1 | 1 | 1970 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1129372.848 | 64678.4553 | 3779.7807 | 7720.7045 | 56957.7507 | 20045.4619 | 0.075059 | -154785.7435 | 154785.7435
C | Xist Rating 903 | -76.73 | 495.196 | 150.277 | 35.6 | 2300.81 | 9842.59 | 16215 | 0.56 | 2.15 | 11.975 | 18.548 | 1 | 1 | 1980 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1139351.9088 | 65297.3656 | 3818.2515 | 7759.8959 | 57537.4697 | 19857.245 | 0.07544 | -153332.3823 | 153332.3823
C | Xist Rating 904 | -76.53 | 500.631 | 150.277 | 35.6 | 2296 | 9802.82 | 16102.1 | 0.55 | 2.13 | 11.968 | 18.331 | 1 | 1 | 1990 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1149448.776 | 65919.2112 | 3856.9171 | 7799.0873 | 58120.1239 | 19623.8715 | 0.075821 | -151530.3343 | 151530.3343
C | Xist Rating 905 | -76.36 | 504.852 | 150.277 | 35.6 | 2294.39 | 9810.55 | 16015.7 | 0.54 | 2.12 | 11.966 | 18.167 | 1 | 1 | 2000 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1158327.3803 | 66543.9921 | 3895.7775 | 7838.2787 | 58705.7134 | 19445.6823 | 0.076202 | -150154.4041 | 150154.4041
C | Xist Rating 906 | -76.23 | 508.03 | 150.277 | 35.6 | 2293.25 | 9816.11 | 15954.5 | 0.53 | 2.11 | 11.965 | 18.057 | 1 | 1 | 2010 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1165039.7975 | 67171.7082 | 3934.8326 | 7877.4701 | 59294.2381 | 19323.515 | 0.076583 | -149211.061 | 149211.061
C | Xist Rating 907 | -75.66 | 522.887 | 150.277 | 35.6 | 2283.43 | 9786.4 | 15615.6 | 0.53 | 2.05 | 11.999 | 17.358 | 1 | 1 | 2020 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1193975.8624 | 67802.3597 | 3974.0826 | 7916.6615 | 59885.6982 | 18602.0788 | 0.076964 | -143640.3217 | 143640.3217
C | Xist Rating 908 | -75.42 | 528.491 | 150.277 | 35.6 | 2282.39 | 9819.68 | 15500.5 | 0.53 | 2.03 | 11.996 | 17.138 | 1 | 1 | 2030 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1206222.5735 | 68435.9464 | 4013.5273 | 7955.8529 | 60480.0935 | 18376.3151 | 0.077345 | -141897.0341 | 141897.0341
C | Xist Rating 909 | -75.28 | 532.546 | 150.277 | 35.6 | 2278.79 | 9784.62 | 15432.3 | 0.52 | 2.02 | 11.99 | 17.024 | 1 | 1 | 2040 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1213560.4993 | 69072.4684 | 4053.1669 | 7995.0443 | 61077.4242 | 18249.5214 | 0.077726 | -140917.9672 | 140917.9672
C | Xist Rating 910 | -75.13 | 535.786 | 150.277 | 35.6 | 2280.77 | 9852.96 | 15364.8 | 0.52 | 2.01 | 11.989 | 16.898 | 1 | 1 | 2050 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1222004.6352 | 69711.9258 | 4093.0012 | 8034.2357 | 61677.6901 | 18121.4176 | 0.078107 | -139928.7832 | 139928.7832
C | Xist Rating 911 | -74.94 | 541.616 | 150.277 | 35.6 | 2274.33 | 9780.49 | 15264.9 | 0.5 | 1.99 | 11.984 | 16.725 | 1 | 1 | 2060 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1231813.5173 | 70354.3184 | 4133.0303 | 8073.4271 | 62280.8913 | 17922.18 | 0.078488 | -138390.3235 | 138390.3235
C | Xist Rating 912 | -74.34 | 557.619 | 150.277 | 35.6 | 2263.6 | 9739.77 | 14936.8 | 0.51 | 1.94 | 12.022 | 16.086 | 1 | 1 | 2070 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1262226.3684 | 70999.6462 | 4173.2542 | 8112.6185 | 62887.0278 | 17274.1832 | 0.078869 | -133386.664 | 133386.664
C | Xist Rating 913 | -74.19 | 561.476 | 150.277 | 35.6 | 2262.04 | 9741.6 | 14874 | 0.5 | 1.93 | 12.017 | 15.983 | 1 | 1 | 2080 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1270081.171 | 71647.9094 | 4213.6729 | 8151.8098 | 63496.0996 | 17158.5244 | 0.07925 | -132493.5769 | 132493.5769
C | Xist Rating 914 | -74.02 | 566.316 | 150.277 | 35.6 | 2258.91 | 9724.61 | 14791.3 | 0.49 | 1.91 | 12.013 | 15.842 | 1 | 1 | 2090 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1279256.8756 | 72299.1079 | 4254.2864 | 8191.0012 | 64108.1066 | 17003.3478 | 0.079631 | -131295.3447 | 131295.3447
C | Xist Rating 915 | -73.84 | 571.165 | 150.277 | 35.6 | 2256.33 | 9717.54 | 14709.7 | 0.49 | 1.9 | 12.009 | 15.703 | 1 | 1 | 2100 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1288736.7244 | 72953.2416 | 4295.0947 | 8230.1926 | 64723.049 | 16861.4506 | 0.080012 | -130199.6518 | 130199.6518
C | Xist Rating 916 | -73.68 | 575.479 | 150.277 | 35.6 | 2254.4 | 9717.47 | 14639 | 0.48 | 1.89 | 12.005 | 15.585 | 1 | 1 | 2110 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1297359.8576 | 73610.3106 | 4336.0977 | 8269.384 | 65340.9266 | 16730.0057 | 0.080393 | -129184.6695 | 129184.6695
C | Xist Rating 917 | -73.11 | 590.776 | 150.277 | 35.6 | 2244.48 | 9676.96 | 14359.3 | 0.48 | 1.84 | 12.043 | 15.073 | 1 | 1 | 2120 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1325984.9165 | 74270.3149 | 4377.2956 | 8308.5754 | 65961.7395 | 16202.6108 | 0.080774 | -125112.2659 | 125112.2659
C | Xist Rating 918 | -72.9 | 596.723 | 150.277 | 35.6 | 2240.82 | 9658.9 | 14264 | 0.47 | 1.83 | 12.038 | 14.914 | 1 | 1 | 2130 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1337148.8329 | 74933.2545 | 4418.6882 | 8347.7668 | 66585.4877 | 16028.3581 | 0.081155 | -123766.7327 | 123766.7327
C | Xist Rating 919 | -72.72 | 602.696 | 150.277 | 35.6 | 2234.9 | 9598.82 | 14170.1 | 0.47 | 1.81 | 12.035 | 14.759 | 1 | 1 | 2140 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1346965.2904 | 75599.1294 | 4460.2756 | 8386.9582 | 67212.1712 | 15869.7917 | 0.081536 | -122542.3251 | 122542.3251
C | Xist Rating 920 | -72.6 | 606.023 | 150.277 | 35.6 | 2233.35 | 9594.79 | 14123.7 | 0.46 | 1.81 | 12.032 | 14.691 | 1 | 1 | 2150 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1353461.4671 | 76267.9396 | 4502.0578 | 8426.1496 | 67841.79 | 15789.9778 | 0.081917 | -121926.0233 | 121926.0233
C | Xist Rating 921 | -72.44 | 610.283 | 150.277 | 35.6 | 2232.38 | 9611.41 | 14059.2 | 0.46 | 1.79 | 12.028 | 14.589 | 1 | 1 | 2160 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1362383.5635 | 76939.685 | 4544.0348 | 8465.341 | 68474.3441 | 15686.3538 | 0.082298 | -121125.8657 | 121125.8657
C | Xist Rating 922 | -71.85 | 626.939 | 150.277 | 35.6 | 2220.56 | 9541.34 | 13786.1 | 0.46 | 1.75 | 12.067 | 14.117 | 1 | 1 | 2170 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1392155.6658 | 77614.3658 | 4586.2066 | 8504.5324 | 69109.8334 | 15200.4076 | 0.082679 | -117373.5184 | 117373.5184
C | Xist Rating 923 | -71.64 | 632.66 | 150.277 | 35.6 | 2218.6 | 9553.37 | 13699.2 | 0.45 | 1.74 | 12.062 | 13.976 | 1 | 1 | 2180 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1403619.476 | 78291.9818 | 4628.5732 | 8543.7238 | 69748.258 | 15044.456 | 0.08306 | -116169.3014 | 116169.3014
C | Xist Rating 924 | -71.47 | 637.154 | 150.277 | 35.6 | 2217.09 | 9559.1 | 13639 | 0.45 | 1.73 | 12.057 | 13.888 | 1 | 1 | 2190 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1412627.7619 | 78972.5331 | 4671.1346 | 8582.9152 | 70389.618 | 14955.2803 | 0.083441 | -115480.7103 | 115480.7103
C | Xist Rating 925 | -71.31 | 642.054 | 150.277 | 35.6 | 2213.27 | 9522.05 | 13579.4 | 0.44 | 1.72 | 12.053 | 13.805 | 1 | 1 | 2200 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1421038.8566 | 79656.0197 | 4713.8907 | 8622.1066 | 71033.9132 | 14859.4535 | 0.083822 | -114740.7611 | 114740.7611
C | Xist Rating 926 | -71.1 | 648.034 | 150.277 | 35.6 | 2210.43 | 9517.24 | 13495.4 | 0.43 | 1.7 | 12.05 | 13.674 | 1 | 1 | 2210 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1432433.7946 | 80342.4416 | 4756.8417 | 8661.298 | 71681.1436 | 14713.7196 | 0.084203 | -113615.4426 | 113615.4426
C | Xist Rating 927 | -70.5 | 664.554 | 150.277 | 35.6 | 2200.98 | 9486.58 | 13246.1 | 0.43 | 1.66 | 12.089 | 13.263 | 1 | 1 | 2220 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1462670.0629 | 81031.7988 | 4799.9874 | 8700.4894 | 72331.3094 | 14290.8881 | 0.084584 | -110350.4501 | 110350.4501
C | Xist Rating 928 | -70.33 | 669.366 | 150.277 | 35.6 | 2199.51 | 9497.04 | 13182.5 | 0.43 | 1.65 | 12.084 | 13.169 | 1 | 1 | 2230 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1472277.2107 | 81724.0912 | 4843.3279 | 8739.6807 | 72984.4105 | 14195.3845 | 0.084965 | -109612.9962 | 109612.9962
C | Xist Rating 929 | -70.11 | 675.166 | 150.277 | 35.6 | 2197.72 | 9506.18 | 13111.6 | 0.42 | 1.64 | 12.08 | 13.069 | 1 | 1 | 2240 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1483825.8215 | 82419.319 | 4886.8633 | 8778.8721 | 73640.4468 | 14081.5619 | 0.085346 | -108734.0883 | 108734.0883
C | Xist Rating 930 | -69.89 | 681.453 | 150.277 | 35.6 | 2194.62 | 9495.32 | 13034 | 0.42 | 1.63 | 12.076 | 12.957 | 1 | 1 | 2250 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1495530.3829 | 83117.482 | 4930.5934 | 8818.0635 | 74299.4185 | 13967.3549 | 0.085727 | -107852.2118 | 107852.2118
C | Xist Rating 931 | -69.78 | 684.743 | 150.277 | 35.6 | 2193.59 | 9499.55 | 12995.5 | 0.42 | 1.62 | 12.071 | 12.906 | 1 | 1 | 2260 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1502045.3974 | 83818.5803 | 4974.5182 | 8857.2549 | 74961.3254 | 13916.4522 | 0.086108 | -107459.1548 | 107459.1548
C | Xist Rating 932 | -69.14 | 702.717 | 150.277 | 35.6 | 2183.18 | 9456.23 | 12751.8 | 0.41 | 1.59 | 12.111 | 12.525 | 1 | 1 | 2270 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1534157.7001 | 84522.6139 | 5018.6379 | 8896.4463 | 75626.1676 | 13512.443 | 0.086489 | -104339.5035 | 104339.5035
C | Xist Rating 933 | -68.96 | 708.462 | 150.277 | 35.6 | 2179.36 | 9426.31 | 12686.2 | 0.41 | 1.58 | 12.105 | 12.435 | 1 | 1 | 2280 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1543993.7443 | 85229.5828 | 5062.9524 | 8935.6377 | 76293.9451 | 13420.9526 | 0.08687 | -103633.0381 | 103633.0381
C | Xist Rating 934 | -68.74 | 715.031 | 150.277 | 35.6 | 2176 | 9414.01 | 12606.9 | 0.41 | 1.56 | 12.1 | 12.322 | 1 | 1 | 2290 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1555907.456 | 85939.487 | 5107.4617 | 8974.8291 | 76964.6578 | 13305.6165 | 0.087251 | -102742.4435 | 102742.4435
C | Xist Rating 935 | -68.59 | 719.688 | 150.277 | 35.6 | 2173.35 | 9396.44 | 12557 | 0.4 | 1.56 | 12.096 | 12.257 | 1 | 1 | 2300 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1564133.9148 | 86652.3264 | 5152.1657 | 9014.0205 | 77638.3059 | 13227.6982 | 0.087632 | -102140.779 | 102140.779
| Xist Rating 936 | -68.44 | 724.611 | 150.277 | 35.6 | 2170.08 | 9367.43 | 12507.6 | 0.4 | 1.55 | 12.093 | 12.196 | 1 | 1 | 2310 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1572463.8389 | 87368.1012 | 5197.0645 | 9053.2119 | 78314.8893 | 13166.3943 | 0.088013 | -101667.4068 | 101667.4068
| Xist Rating 937 | -67.8 | 742.958 | 150.277 | 35.6 | 2160.56 | 9340.78 | 12277.1 | 0.4 | 1.51 | 12.132 | 11.851 | 1 | 1 | 2320 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 7 | E | Rod | 1605205.3365 | 88086.8112 | 5242.1582 | 9092.4033 | 78994.4079 | 12811.9029 | 0.088394 | -98930.1182 | 98930.1182
| Xist Rating 938 | -67.61 | 748.734 | 150.277 | 35.6 | 2157.47 | 9323.39 | 12216.8 | 0.39 | 1.5 | 12.122 | 11.772 | 1 | 1 | 2330 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1615371.143 | 88808.4565 | 5287.4466 | 9131.5947 | 79676.8618 | 12718.9586 | 0.088775 | -98212.4271 | 98212.4271
| Xist Rating 939 | -67.43 | 754.487 | 150.277 | 35.6 | 2154.31 | 9304.35 | 12157.2 | 0.39 | 1.49 | 12.119 | 11.695 | 1 | 1 | 2340 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1625398.889 | 89533.0371 | 5332.9298 | 9170.7861 | 80362.251 | 12640.9906 | 0.089156 | -97610.379 | 97610.379
| Xist Rating 940 | -67.26 | 759.798 | 150.277 | 35.6 | 2151.26 | 9282.91 | 12104.7 | 0.38 | 1.49 | 12.114 | 11.629 | 1 | 1 | 2350 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1634523.0455 | 90260.553 | 5378.6078 | 9209.9775 | 81050.5755 | 12561.6023 | 0.089537 | -96997.3633 | 96997.3633
| Xist Rating 941 | -67.06 | 766.136 | 150.277 | 35.6 | 2148.02 | 9266.66 | 12039.9 | 0.38 | 1.48 | 12.111 | 11.545 | 1 | 1 | 2360 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1645675.4507 | 90991.0041 | 5424.4805 | 9249.1689 | 81741.8353 | 12476.3113 | 0.089918 | -96338.7685 | 96338.7685
| Xist Rating 942 | -66.48 | 783.086 | 150.277 | 35.6 | 2139.51 | 9241.38 | 11846.8 | 0.38 | 1.45 | 12.146 | 11.271 | 1 | 1 | 2370 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1675420.3279 | 91724.3906 | 5470.5481 | 9288.3603 | 82436.0303 | 12195.2385 | 0.090299 | -94168.3993 | 94168.3993
| Xist Rating 943 | -66.29 | 789.077 | 150.277 | 35.6 | 2136.32 | 9220.94 | 11791.1 | 0.37 | 1.44 | 12.142 | 11.204 | 1 | 1 | 2380 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1685720.9766 | 92460.7123 | 5516.8105 | 9327.5516 | 83133.1607 | 12114.6124 | 0.09068 | -93545.826 | 93545.826
| Xist Rating 944 | -66.09 | 794.97 | 150.277 | 35.6 | 2134.02 | 9221.45 | 11730 | 0.37 | 1.43 | 12.134 | 11.124 | 1 | 1 | 2390 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1696481.8794 | 93199.9694 | 5563.2676 | 9366.743 | 83833.2263 | 12033.2292 | 0.091061 | -92917.4064 | 92917.4064
C | Xist Rating 945 | -62.75 | 912.11 | 150.277 | 35.6 | 2044.97 | 8491.98 | 10538.2 | 0.4 | 1.25 | 12.137 | 9.532 | 1 | 1 | 2400 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1865237.5867 | 93942.1617 | 5609.9196 | 9405.9344 | 84536.2272 | 10421.2422 | 0.091442 | -80470.0702 | 80470.0702
C | Xist Rating 946 | -62.43 | 913.556 | 150.277 | 35.6 | 2059.94 | 8756.46 | 10537.9 | 0.39 | 1.25 | 12.13 | 9.542 | 1 | 1 | 2410 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1881870.5466 | 94687.2893 | 5656.7663 | 9445.1258 | 85242.1634 | 10420.3972 | 0.091823 | -80463.5448 | 80463.5448
C | Xist Rating 947 | -62.4 | 914.957 | 150.277 | 35.6 | 2059.62 | 8750.5 | 10538 | 0.39 | 1.25 | 12.17 | 9.553 | 1 | 1 | 2420 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1884463.7363 | 95435.3521 | 5703.8078 | 9484.3172 | 85951.0349 | 10435.6334 | 0.092204 | -80581.1948 | 80581.1948
C | Xist Rating 948 | -62.05 | 916.314 | 150.277 | 35.6 | 2076.3 | 9059.87 | 10537.9 | 0.39 | 1.25 | 12.163 | 9.562 | 1 | 1 | 2430 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1902542.7582 | 96186.3503 | 5751.0441 | 9523.5086 | 86662.8417 | 10446.81 | 0.092585 | -80667.4979 | 80667.4979
C | Xist Rating 949 | -62.03 | 917.684 | 150.277 | 35.6 | 2075.39 | 9042.59 | 10537.9 | 0.38 | 1.25 | 12.158 | 9.573 | 1 | 1 | 2440 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1904552.1968 | 96940.2838 | 5798.4752 | 9562.7 | 87377.5838 | 10446.8491 | 0.092966 | -80667.7992 | 80667.7992
C | Xist Rating 950 | -62.01 | 919.011 | 150.277 | 35.6 | 2074.32 | 9022.26 | 10537.9 | 0.38 | 1.25 | 12.156 | 9.584 | 1 | 1 | 2450 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1906322.8975 | 97697.1525 | 5846.1011 | 9601.8914 | 88095.2611 | 10460.26 | 0.093347 | -80771.3549 | 80771.3549
C | Xist Rating 951 | -61.97 | 920.483 | 150.277 | 35.6 | 2074.42 | 9024.28 | 10537.8 | 0.37 | 1.25 | 12.149 | 9.595 | 1 | 1 | 2460 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1909468.3449 | 98456.9565 | 5893.9217 | 9641.0828 | 88815.8737 | 10460.0642 | 0.093728 | -80769.8431 | 80769.8431
C | Xist Rating 952 | -61.94 | 921.836 | 150.277 | 35.6 | 2073.76 | 9011.78 | 10537.9 | 0.36 | 1.25 | 12.187 | 9.605 | 1 | 1 | 2470 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1911666.6234 | 99219.6958 | 5941.9372 | 9680.2742 | 89539.4216 | 10460.5277 | 0.094109 | -80773.4223 | 80773.4223
C | Xist Rating 953 | -61.92 | 923.184 | 150.277 | 35.6 | 2073.17 | 9000.72 | 10537.8 | 0.36 | 1.25 | 12.181 | 9.616 | 1 | 1 | 2480 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1913917.3733 | 99985.3704 | 5990.1474 | 9719.4656 | 90265.9049 | 10473.6777 | 0.09449 | -80874.9628 | 80874.9628
C | Xist Rating 954 | -61.89 | 924.582 | 150.277 | 35.6 | 2072.43 | 8986.62 | 10537.8 | 0.35 | 1.25 | 12.176 | 9.627 | 1 | 1 | 2490 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1916131.4743 | 100753.9803 | 6038.5525 | 9758.657 | 90995.3233 | 10473.2759 | 0.094871 | -80871.86 | 80871.86
C | Xist Rating 955 | -61.88 | 925.567 | 150.277 | 35.6 | 2072.16 | 8981.61 | 10537.8 | 0.35 | 1.25 | 12.171 | 9.635 | 1 | 1 | 2500 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1917922.9147 | 101525.5255 | 6087.1523 | 9797.8484 | 91727.6771 | 10483.298 | 0.095252 | -80949.2482 | 80949.2482
C | Xist Rating 956 | -61.85 | 927.416 | 150.277 | 35.6 | 2070.88 | 8957.54 | 10537.9 | 0.34 | 1.25 | 12.175 | 9.648 | 1 | 1 | 2510 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1920567.2461 | 102300.0059 | 6135.9469 | 9837.0398 | 92462.9662 | 10485.1674 | 0.095633 | -80963.683 | 80963.683
C | Xist Rating 957 | -61.83 | 928.87 | 150.277 | 35.6 | 2069.46 | 8931.06 | 10537.9 | 0.34 | 1.25 | 12.214 | 9.659 | 1 | 1 | 2520 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1922259.3102 | 103077.4217 | 6184.9363 | 9876.2312 | 93201.1905 | 10499.9442 | 0.096014 | -81077.7857 | 81077.7857
C | Xist Rating 958 | -61.81 | 930.208 | 150.277 | 35.6 | 2068.69 | 8916.76 | 10537.9 | 0.33 | 1.25 | 12.209 | 9.669 | 1 | 1 | 2530 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1924311.9875 | 103857.7727 | 6234.1205 | 9915.4226 | 93942.3502 | 10498.1521 | 0.096395 | -81063.9474 | 81063.9474
C | Xist Rating 959 | -61.8 | 931.359 | 150.277 | 35.6 | 2067.85 | 8901.19 | 10537.9 | 0.33 | 1.25 | 12.203 | 9.678 | 1 | 1 | 2540 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1925910.7082 | 104641.059 | 6283.4995 | 9954.6139 | 94686.4451 | 10509.0791 | 0.096776 | -81148.323 | 81148.323
C | Xist Rating 960 | -61.78 | 932.906 | 150.277 | 35.6 | 2066.33 | 8873.04 | 10537.9 | 0.32 | 1.25 | 12.2 | 9.689 | 1 | 1 | 2550 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1927691.655 | 105427.2806 | 6333.0732 | 9993.8053 | 95433.4753 | 10508.2495 | 0.097157 | -81141.9175 | 81141.9175
C | Xist Rating 961 | -61.76 | 934.355 | 150.277 | 35.6 | 2065.48 | 8857.37 | 10537.9 | 0.32 | 1.25 | 12.196 | 9.7 | 1 | 1 | 2560 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1929891.5654 | 106216.4375 | 6382.8418 | 10032.9967 | 96183.4408 | 10521.2761 | 0.097538 | -81242.5051 | 81242.5051
C | Xist Rating 962 | -61.74 | 935.744 | 150.277 | 35.6 | 2064.71 | 8843.17 | 10537.9 | 0.31 | 1.25 | 12.197 | 9.711 | 1 | 1 | 2570 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1932039.9942 | 107008.5297 | 6432.8051 | 10072.1881 | 96936.3415 | 10520.435 | 0.097919 | -81236.0101 | 81236.0101
C | Xist Rating 963 | -61.72 | 937.109 | 150.277 | 35.6 | 2063.6 | 8822.95 | 10537.9 | 0.31 | 1.25 | 12.232 | 9.721 | 1 | 1 | 2580 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1933818.1324 | 107803.5571 | 6482.9633 | 10111.3795 | 97692.1776 | 10533.7696 | 0.0983 | -81338.9764 | 81338.9764
C | Xist Rating 964 | -61.7 | 938.469 | 150.277 | 35.6 | 2062.51 | 8803.01 | 10537.9 | 0.3 | 1.25 | 12.225 | 9.731 | 1 | 1 | 2590 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1935601.6972 | 108601.5198 | 6533.3162 | 10150.5709 | 98450.9489 | 10531.4096 | 0.098681 | -81320.7535 | 81320.7535
C | Xist Rating 965 | -61.69 | 939.646 | 150.277 | 35.6 | 2061.59 | 8786.39 | 10537.9 | 0.3 | 1.25 | 12.221 | 9.74 | 1 | 1 | 2600 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1937164.7971 | 109402.4179 | 6583.8639 | 10189.7623 | 99212.6556 | 10542.2602 | 0.099062 | -81404.5388 | 81404.5388
C | Xist Rating 966 | -61.67 | 941.334 | 150.277 | 35.6 | 2060.15 | 8760.15 | 10537.9 | 0.3 | 1.25 | 12.218 | 9.752 | 1 | 1 | 2610 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1939289.2401 | 110206.2512 | 6634.6064 | 10228.9537 | 99977.2975 | 10556.2603 | 0.099443 | -81512.6438 | 81512.6438
C | Xist Rating 967 | -61.65 | 942.73 | 150.277 | 35.6 | 2059.31 | 8745 | 10537.9 | 0.29 | 1.25 | 12.216 | 9.762 | 1 | 1 | 2620 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1941373.3163 | 111013.0198 | 6685.5437 | 10268.1451 | 100744.8747 | 10553.8713 | 0.099824 | -81494.1964 | 81494.1964
C | Xist Rating 968 | -61.62 | 944.157 | 150.277 | 35.6 | 2058.48 | 8730.12 | 10537.9 | 0.29 | 1.25 | 12.251 | 9.772 | 1 | 1 | 2630 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1943528.3014 | 111822.7237 | 6736.6758 | 10307.3365 | 101515.3872 | 10567.0408 | 0.10021 | -81595.8881 | 81595.8881
C | Xist Rating 969 | -61.59 | 945.403 | 150.277 | 35.6 | 2058.48 | 8730.22 | 10537.8 | 0.28 | 1.25 | 12.248 | 9.781 | 1 | 1 | 2640 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1946093.1674 | 112635.3628 | 6788.0027 | 10346.5279 | 102288.8349 | 10563.3829 | 0.10059 | -81567.643 | 81567.643
C | Xist Rating 970 | -61.56 | 946.906 | 150.277 | 35.6 | 2057.72 | 8716.51 | 10537.8 | 0.28 | 1.25 | 12.245 | 9.792 | 1 | 1 | 2650 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1948467.4143 | 113450.9373 | 6839.5243 | 10385.7193 | 103065.218 | 10576.2439 | 0.10097 | -81666.9517 | 81666.9517
C | Xist Rating 971 | -61.54 | 948.246 | 150.277 | 35.6 | 2057.42 | 8711.09 | 10537.8 | 0.28 | 1.25 | 12.242 | 9.802 | 1 | 1 | 2660 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1950940.2853 | 114269.447 | 6891.2408 | 10424.9107 | 103844.5364 | 10588.0656 | 0.10135 | -81758.2357 | 81758.2357
C | Xist Rating 972 | -61.52 | 949.634 | 150.277 | 35.6 | 2056.25 | 8690.11 | 10537.9 | 0.27 | 1.25 | 12.239 | 9.812 | 1 | 1 | 2670 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1952684.9125 | 115090.892 | 6943.152 | 10464.1021 | 104626.79 | 10585.2386 | 0.10173 | -81736.4069 | 81736.4069
C | Xist Rating 973 | -61.45 | 951.05 | 150.277 | 35.6 | 2058.08 | 8723.02 | 10537.9 | 0.27 | 1.25 | 12.279 | 9.822 | 1 | 1 | 2680 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1957336.984 | 115915.2724 | 6995.258 | 10503.2935 | 105411.9789 | 10598.4023 | 0.10211 | -81838.053 | 81838.053
C | Xist Rating 974 | -61.42 | 952.427 | 150.277 | 35.6 | 2058.25 | 8726.1 | 10537.7 | 0.27 | 1.25 | 12.269 | 9.831 | 1 | 1 | 2690 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1960332.8728 | 116742.5879 | 7047.5588 | 10542.4848 | 106200.1031 | 10608.9093 | 0.10249 | -81919.1853 | 81919.1853
C | Xist Rating 975 | -61.37 | 953.628 | 150.277 | 35.6 | 2059.16 | 8742.37 | 10537.8 | 0.26 | 1.25 | 12.269 | 9.841 | 1 | 1 | 2700 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1963672.6325 | 117572.8388 | 7100.0544 | 10581.6762 | 106991.1626 | 10605.9304 | 0.10287 | -81896.1831 | 81896.1831
C | Xist Rating 976 | -61.35 | 955.284 | 150.277 | 35.6 | 2057.3 | 8709.02 | 10537.8 | 0.26 | 1.25 | 12.263 | 9.852 | 1 | 1 | 2710 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1965305.7732 | 118406.025 | 7152.7448 | 10620.8676 | 107785.1574 | 10618.5943 | 0.10325 | -81993.9701 | 81993.9701
C | Xist Rating 977 | -61.27 | 956.628 | 150.277 | 35.6 | 2059.47 | 8747.9 | 10537.9 | 0.26 | 1.25 | 12.267 | 9.861 | 1 | 1 | 2720 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1970146.6672 | 119242.1464 | 7205.63 | 10660.059 | 108582.0874 | 10629.4967 | 0.10363 | -82078.1561 | 82078.1561
C | Xist Rating 978 | -61.22 | 957.95 | 150.277 | 35.6 | 2060.5 | 8766.56 | 10538 | 0.25 | 1.25 | 12.306 | 9.871 | 1 | 1 | 2730 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1973855.975 | 120081.2032 | 7258.71 | 10699.2504 | 109381.9528 | 10627.4932 | 0.10402 | -82062.6853 | 82062.6853
C | Xist Rating 979 | -60.99 | 959.234 | 150.277 | 35.6 | 2071.26 | 8964.51 | 10538.2 | 0.25 | 1.25 | 12.324 | 9.881 | 1 | 1 | 2740 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1986823.0148 | 120923.1952 | 7311.9847 | 10738.4418 | 110184.7534 | 10639.8099 | 0.1044 | -82157.7916 | 82157.7916
C | Xist Rating 980 | -60.77 | 960.782 | 150.277 | 35.6 | 2080.96 | 9148.9 | 10538.3 | 0.24 | 1.25 | 12.344 | 9.892 | 1 | 1 | 2750 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1999348.9107 | 121768.1225 | 7365.4543 | 10777.6332 | 110990.4893 | 10638.0146 | 0.10478 | -82143.9287 | 82143.9287
C | Xist Rating 981 | -60.97 | 962.206 | 150.277 | 35.6 | 2068.05 | 8904.58 | 10538.2 | 0.24 | 1.25 | 12.312 | 9.901 | 1 | 1 | 2760 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 1989890.1183 | 122615.9851 | 7419.1186 | 10816.8246 | 111799.1605 | 10647.7389 | 0.10516 | -82219.0172 | 82219.0172
C | Xist Rating 982 | -60.58 | 963.442 | 150.277 | 35.6 | 2087.21 | 9270.93 | 10538.3 | 0.24 | 1.25 | 12.353 | 9.911 | 1 | 1 | 2770 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2010905.7768 | 123466.783 | 7472.9777 | 10856.016 | 112610.767 | 10660.6702 | 0.10554 | -82318.8691 | 82318.8691
C | Xist Rating 983 | -60.45 | 964.989 | 150.278 | 35.6 | 2092.18 | 9369.8 | 10538.4 | 0.23 | 1.25 | 12.405 | 9.922 | 1 | 1 | 2780 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2018930.686 | 124320.5162 | 7527.0316 | 10895.2074 | 113425.3088 | 10659.5195 | 0.10592 | -82309.9844 | 82309.9844
C | Xist Rating 984 | -60.35 | 966.398 | 150.278 | 35.6 | 2095.28 | 9432.21 | 10538.4 | 0.23 | 1.25 | 12.413 | 9.932 | 1 | 1 | 2790 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2024874.4014 | 125177.1846 | 7581.2803 | 10934.3988 | 114242.7858 | 10671.4136 | 0.1063 | -82401.8268 | 82401.8268
C | Xist Rating 985 | -60.24 | 967.372 | 150.277 | 35.6 | 2100.01 | 9528.85 | 10538.4 | 0.23 | 1.25 | 12.424 | 9.94 | 1 | 1 | 2800 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2031490.8737 | 126036.7883 | 7635.7238 | 10973.5902 | 115063.1982 | 10681.3188 | 0.10668 | -82478.3126 | 82478.3126
C | Xist Rating 986 | -60.19 | 969.117 | 150.277 | 35.6 | 2100.1 | 9530.68 | 10538.4 | 0.22 | 1.25 | 12.428 | 9.951 | 1 | 1 | 2810 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2035242.6117 | 126899.3274 | 7690.3621 | 11012.7816 | 115886.5458 | 10678.4851 | 0.10706 | -82456.4313 | 82456.4313
C | Xist Rating 987 | -60.12 | 970.592 | 150.277 | 35.6 | 2101.7 | 9563.82 | 10538.3 | 0.22 | 1.25 | 12.433 | 9.961 | 1 | 1 | 2820 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2039893.2064 | 127764.8017 | 7745.1952 | 11051.973 | 116712.8287 | 10690.2347 | 0.10744 | -82547.1586 | 82547.1586
C | Xist Rating 988 | -60.04 | 971.964 | 150.278 | 35.6 | 2103.59 | 9603.14 | 10538.3 | 0.22 | 1.25 | 12.478 | 9.97 | 1 | 1 | 2830 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2044613.7508 | 128633.2113 | 7800.223 | 11091.1644 | 117542.0469 | 10702.0631 | 0.10783 | -82638.4945 | 82638.4945
C | Xist Rating 989 | -59.98 | 973.282 | 150.278 | 35.6 | 2105.25 | 9637.85 | 10538.3 | 0.21 | 1.25 | 12.48 | 9.98 | 1 | 1 | 2840 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2049001.9305 | 129504.5562 | 7855.4457 | 11130.3558 | 118374.2004 | 10697.8473 | 0.10821 | -82605.9413 | 82605.9413
C | Xist Rating 990 | -59.93 | 974.725 | 150.278 | 35.6 | 2105.86 | 9650.71 | 10538.3 | 0.21 | 1.25 | 12.48 | 9.989 | 1 | 1 | 2850 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2052634.3885 | 130378.8363 | 7910.8631 | 11169.5471 | 119209.2892 | 10708.3686 | 0.10859 | -82687.1836 | 82687.1836
C | Xist Rating 991 | -59.87 | 976.13 | 150.278 | 35.6 | 2106.75 | 9669.39 | 10538.3 | 0.21 | 1.25 | 12.483 | 9.999 | 1 | 1 | 2860 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2056461.8775 | 131256.0518 | 7966.4753 | 11208.7385 | 120047.3132 | 10720.0091 | 0.10897 | -82777.0686 | 82777.0686
C | Xist Rating 992 | -59.82 | 977.321 | 150.278 | 35.6 | 2108.16 | 9699.16 | 10538.2 | 0.21 | 1.25 | 12.487 | 10.007 | 1 | 1 | 2870 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2060349.0394 | 132136.2025 | 8022.2824 | 11247.9299 | 120888.2726 | 10729.6002 | 0.10935 | -82851.1285 | 82851.1285
C | Xist Rating 993 | -59.76 | 978.83 | 150.278 | 35.5 | 2108.93 | 9715.63 | 10538.2 | 0.2 | 1.25 | 12.531 | 10.017 | 1 | 1 | 2880 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2064283.9519 | 133019.2885 | 8078.2842 | 11287.1213 | 121732.1672 | 10726.1765 | 0.10973 | -82824.692 | 82824.692
C | Xist Rating 994 | -59.7 | 980.172 | 150.278 | 35.5 | 2110.21 | 9742.68 | 10538.2 | 0.2 | 1.25 | 12.532 | 10.027 | 1 | 1 | 2890 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2068368.7561 | 133905.3098 | 8134.4807 | 11326.3127 | 122578.9971 | 10737.7108 | 0.11011 | -82913.7567 | 82913.7567
C | Xist Rating 995 | -59.64 | 981.558 | 150.278 | 35.5 | 2111.7 | 9774.63 | 10538.1 | 0.2 | 1.25 | 12.53 | 10.036 | 1 | 1 | 2900 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2072756.0286 | 134794.2664 | 8190.8721 | 11365.5041 | 123428.7623 | 10748.1288 | 0.11049 | -82994.2015 | 82994.2015
C | Xist Rating 996 | -59.57 | 983.098 | 150.278 | 35.5 | 2112.89 | 9800.28 | 10538.1 | 0.2 | 1.25 | 12.531 | 10.046 | 1 | 1 | 2910 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2077177.9332 | 135686.1583 | 8247.4583 | 11404.6955 | 124281.4628 | 10759.6632 | 0.11087 | -83083.2669 | 83083.2669
C | Xist Rating 997 | -59.47 | 984.489 | 150.278 | 35.5 | 2115.95 | 9866.46 | 10538.1 | 0.2 | 1.25 | 12.535 | 10.055 | 1 | 1 | 2920 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2083129.4995 | 136580.9855 | 8304.2393 | 11443.8869 | 125137.0986 | 10770.2378 | 0.11125 | -83164.9211 | 83164.9211
C | Xist Rating 998 | -59.43 | 985.875 | 150.278 | 35.5 | 2116.28 | 9873.63 | 10538.1 | 0.19 | 1.25 | 12.574 | 10.065 | 1 | 1 | 2930 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2086387.545 | 137478.7479 | 8361.215 | 11483.0783 | 125995.6696 | 10766.2567 | 0.11164 | -83134.1805 | 83134.1805
C | Xist Rating 999 | -59.41 | 987.241 | 150.278 | 35.5 | 2115.55 | 9857.65 | 10538.1 | 0.19 | 1.25 | 12.57 | 10.074 | 1 | 1 | 2940 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2088557.6976 | 138379.4457 | 8418.3855 | 11522.2697 | 126857.176 | 10776.5739 | 0.11202 | -83213.8473 | 83213.8473
C | Xist Rating 1002 | -59.4 | 991.405 | 150.278 | 35.5 | 2111.84 | 9778.93 | 10536.8 | 0.18 | 1.25 | 12.578 | 10.1 | 1 | 1 | 2970 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2093688.7352 | 141099.1506 | 8591.0659 | 11639.8439 | 129459.3067 | 10790.2439 | 0.11316 | -83319.4031 | 83319.4031
C | Xist Rating 1003 | -59.4 | 992.628 | 150.278 | 35.5 | 2110.8 | 9756.86 | 10536.6 | 0.18 | 1.25 | 12.616 | 10.108 | 1 | 1 | 2980 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2095239.1824 | 142011.5895 | 8649.0156 | 11679.0353 | 130332.5542 | 10800.4804 | 0.11354 | -83398.4467 | 83398.4467
C | Xist Rating 1004 | -59.42 | 994.187 | 150.278 | 35.5 | 2109.04 | 9720.24 | 10535.7 | 0.18 | 1.25 | 12.628 | 10.117 | 1 | 1 | 2990 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2096780.1505 | 142926.9636 | 8707.16 | 11718.2267 | 131208.737 | 10811.1343 | 0.11392 | -83480.7133 | 83480.7133
C | Xist Rating 1005 | -59.4 | 995.618 | 150.278 | 35.5 | 2108.22 | 9703.19 | 10535.5 | 0.18 | 1.25 | 12.626 | 10.126 | 1 | 1 | 3000 | 152.4 | 2 | 1.4 | 19.05 | 1.3333 | 6 | E | Rod | 2098981.78 | 143845.2731 | 8765.4993 | 11757.418 | 132087.855 | 10821.4512 | 0.1143 | -83560.3781 | 83560.3781
C | Xist Rating 1006 | -95.39 | 86.785 | 150.279 | 35.8 | 2414.88 | 7551.3 | 58745.7 | 2.44 | 10.95 | 12.894 | 320.468 | 1 | 1 | 1000 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 209575.3608 | 19923.8225 | 973.9444 | 4199.0779 | 15724.7446 | 334215.7558 | 0.038101 | -2580725.4752 | 2580725.4752
C | Xist Rating 1007 | -95.35 | 87.726 | 150.279 | 35.8 | 2411.75 | 7529.48 | 58284.2 | 2.42 | 10.85 | 12.897 | 314.512 | 1 | 1 | 1010 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 211573.1805 | 20281.8807 | 993.5206 | 4241.0687 | 16040.812 | 328033.2153 | 0.038482 | -2532985.5367 | 2532985.5367
C | Xist Rating 1008 | -95 | 94.645 | 150.279 | 35.8 | 2406.07 | 7541.53 | 54967.5 | 2.43 | 10.07 | 12.951 | 272.547 | 1 | 1 | 1020 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 227722.4952 | 20643.0838 | 1013.2917 | 4283.0594 | 16360.0243 | 284478.5155 | 0.038863 | -2196667.6895 | 2196667.6895
C | Xist Rating 1009 | -94.93 | 96.673 | 150.278 | 35.8 | 2389.3 | 7395.88 | 54179.3 | 2.34 | 9.89 | 12.759 | 263.593 | 1 | 1 | 1030 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 230980.7989 | 21007.4318 | 1033.2576 | 4325.0502 | 16682.3816 | 275119.3498 | 0.039244 | -2124398.693 | 2124398.693
C | Xist Rating 1010 | -94.85 | 97.69 | 150.278 | 35.8 | 2404.92 | 7556.19 | 53795.5 | 2.28 | 9.8 | 12.719 | 259.323 | 1 | 1 | 1040 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 234936.6348 | 21374.9248 | 1053.4182 | 4367.041 | 17007.8838 | 270658.4052 | 0.039625 | -2089952.4616 | 2089952.4616
C | Xist Rating 1011 | -94.73 | 99.596 | 150.278 | 35.8 | 2413.88 | 7663.1 | 53045 | 2.23 | 9.63 | 12.689 | 250.822 | 1 | 1 | 1050 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 240412.7925 | 21745.5627 | 1073.7737 | 4409.0318 | 17336.531 | 261810.0488 | 0.040006 | -2021627.7983 | 2021627.7983
C | Xist Rating 1012 | -94.66 | 100.593 | 150.278 | 35.8 | 2425.94 | 7795.21 | 52677.9 | 2.18 | 9.54 | 12.671 | 246.825 | 1 | 1 | 1060 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 244032.5824 | 22119.3456 | 1094.3239 | 4451.0225 | 17668.3231 | 257639.8446 | 0.040387 | -1989426.587 | 1989426.587
C | Xist Rating 1013 | -94.31 | 108.137 | 150.278 | 35.8 | 2405.07 | 7655.43 | 49858.3 | 2.17 | 8.9 | 12.634 | 216.044 | 1 | 1 | 1070 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 260077.0546 | 22496.2735 | 1115.0689 | 4493.0133 | 18003.2601 | 225676.2784 | 0.040768 | -1742612.4012 | 1742612.4012
C | Xist Rating 1014 | -94.23 | 109.636 | 150.278 | 35.8 | 2408.44 | 7702.85 | 49381.6 | 2.12 | 8.79 | 12.583 | 211.289 | 1 | 1 | 1080 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 264051.7278 | 22876.3463 | 1136.0087 | 4535.0041 | 18341.3422 | 220714.6922 | 0.041149 | -1704300.3485 | 1704300.3485
C | Xist Rating 1015 | -94.13 | 111.623 | 150.278 | 35.8 | 2406.25 | 7698.01 | 48761.8 | 2.06 | 8.65 | 12.513 | 205.168 | 1 | 1 | 1090 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 268592.8438 | 23259.564 | 1157.1433 | 4576.9949 | 18682.5691 | 214326.0679 | 0.04153 | -1654969.0849 | 1654969.0849
C | Xist Rating 1016 | -94.05 | 113.089 | 150.278 | 35.8 | 2411.46 | 7764.92 | 48306.7 | 2.03 | 8.55 | 12.494 | 200.728 | 1 | 1 | 1100 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 272709.5999 | 23645.9267 | 1178.4727 | 4618.9857 | 19026.941 | 209706.2781 | 0.041911 | -1619296.2926 | 1619296.2926
C | Xist Rating 1017 | -94.01 | 114.273 | 150.277 | 35.8 | 2403.36 | 7690.28 | 48011.1 | 1.96 | 8.49 | 12.371 | 198.121 | 1 | 1 | 1110 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 274639.1573 | 24035.4343 | 1199.9969 | 4660.9764 | 19374.4579 | 206954.7715 | 0.042292 | -1598049.8876 | 1598049.8876
C | Xist Rating 1018 | -93.59 | 122.584 | 150.278 | 35.8 | 2400.67 | 7742.92 | 45448 | 2 | 7.92 | 12.495 | 173.355 | 1 | 1 | 1120 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 294283.7313 | 24428.0869 | 1221.7158 | 4702.9672 | 19725.1197 | 181283.4816 | 0.042673 | -1399822.9918 | 1399822.9918
C | Xist Rating 1019 | -93.53 | 123.721 | 150.278 | 35.8 | 2400.98 | 7754.85 | 45189.8 | 1.93 | 7.86 | 12.416 | 171.235 | 1 | 1 | 1130 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 297051.6466 | 24823.8844 | 1243.6296 | 4744.958 | 20078.9264 | 179041.0411 | 0.043054 | -1382507.4606 | 1382507.4606
C | Xist Rating 1020 | -93.43 | 125.779 | 150.277 | 35.8 | 2401.8 | 7780.87 | 44682.1 | 1.88 | 7.75 | 12.312 | 166.87 | 1 | 1 | 1140 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 302096.0022 | 25222.8269 | 1265.7381 | 4786.9488 | 20435.8781 | 174477.0227 | 0.043435 | -1347265.3207 | 1347265.3207
C | Xist Rating 1021 | -93.31 | 127.774 | 150.277 | 35.8 | 2409.54 | 7880.49 | 44188 | 1.83 | 7.64 | 12.286 | 162.625 | 1 | 1 | 1150 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 307876.564 | 25624.9144 | 1288.0414 | 4828.9396 | 20795.9748 | 170044.7865 | 0.043816 | -1313040.7671 | 1313040.7671
C | Xist Rating 1022 | -93.21 | 129.847 | 150.277 | 35.8 | 2407.55 | 7877.12 | 43705.4 | 1.78 | 7.53 | 12.225 | 158.606 | 1 | 1 | 1160 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 312613.1449 | 26030.1467 | 1310.5395 | 4870.9303 | 21159.2164 | 165843.5521 | 0.044197 | -1280599.9491 | 1280599.9491
C | Xist Rating 1023 | -92.82 | 137.378 | 150.277 | 35.8 | 2407.63 | 7951.74 | 41834.3 | 1.79 | 7.13 | 12.307 | 142.71 | 1 | 1 | 1170 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 330755.3941 | 26438.5241 | 1333.2324 | 4912.9211 | 21525.6029 | 149359.4446 | 0.044578 | -1153314.04 | 1153314.04
C | Xist Rating 1024 | -92.77 | 138.04 | 150.277 | 35.8 | 2414.87 | 8035.85 | 41726.3 | 1.75 | 7.11 | 12.265 | 142.006 | 1 | 1 | 1180 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 333348.6548 | 26850.0463 | 1356.1201 | 4954.9119 | 21895.1344 | 148608.2905 | 0.044959 | -1147513.8273 | 1147513.8273
C | Xist Rating 1025 | -92.6 | 142.014 | 150.277 | 35.8 | 2402.53 | 7936.29 | 40887 | 1.7 | 6.93 | 12.196 | 135.454 | 1 | 1 | 1190 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 341192.8954 | 27264.7136 | 1379.2026 | 4996.9027 | 22267.8109 | 141774.7014 | 0.04534 | -1094746.6637 | 1094746.6637
C | Xist Rating 1026 | -92.52 | 143.044 | 150.277 | 35.8 | 2413.83 | 8070.05 | 40683.5 | 1.67 | 6.88 | 12.199 | 133.941 | 1 | 1 | 1200 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 345283.8985 | 27682.5257 | 1402.4799 | 5038.8934 | 22643.6323 | 140193.3358 | 0.045721 | -1082535.7779 | 1082535.7779
C | Xist Rating 1027 | -92.43 | 145.186 | 150.277 | 35.8 | 2408.57 | 8029.64 | 40282.5 | 1.62 | 6.8 | 12.137 | 131.009 | 1 | 1 | 1210 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 349690.644 | 28103.4829 | 1425.9519 | 5080.8842 | 23022.5986 | 137119.0603 | 0.046102 | -1058797.037 | 1058797.037
C | Xist Rating 1028 | -92.03 | 153.852 | 150.277 | 35.8 | 2395.87 | 7971.45 | 38539.1 | 1.63 | 6.43 | 12.168 | 117.894 | 1 | 1 | 1220 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 368609.3912 | 28527.5849 | 1449.6188 | 5122.875 | 23404.7099 | 123517.3674 | 0.046483 | -953768.3704 | 953768.3704
C | Xist Rating 1029 | -91.91 | 155.844 | 150.277 | 35.8 | 2401.34 | 8050.32 | 38184.2 | 1.6 | 6.35 | 12.161 | 115.415 | 1 | 1 | 1230 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 374234.431 | 28954.832 | 1473.4804 | 5164.8658 | 23789.9662 | 120931.0766 | 0.046864 | -933797.7179 | 933797.7179
C | Xist Rating 1030 | -91.82 | 157.977 | 150.277 | 35.8 | 2398.28 | 8033.9 | 37836.5 | 1.56 | 6.28 | 12.116 | 113.085 | 1 | 1 | 1240 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 378873.0796 | 29385.2239 | 1497.5369 | 5206.8566 | 24178.3674 | 118489.1576 | 0.047245 | -914941.8667 | 914941.8667
C | Xist Rating 1031 | -91.76 | 159.151 | 150.277 | 35.8 | 2399.07 | 8051.69 | 37665.2 | 1.53 | 6.24 | 12.081 | 112.016 | 1 | 1 | 1250 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 381814.3896 | 29818.7609 | 1521.7881 | 5248.8473 | 24569.9135 | 117364.1085 | 0.047626 | -906254.5361 | 906254.5361
C | Xist Rating 1032 | -91.62 | 162.163 | 150.277 | 35.8 | 2396.65 | 8051.22 | 37162.2 | 1.5 | 6.14 | 12.058 | 108.606 | 1 | 1 | 1260 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 388647.954 | 30255.4427 | 1546.2341 | 5290.8381 | 24964.6046 | 113808.696 | 0.048007 | -878800.5833 | 878800.5833
C | Xist Rating 1033 | -91.22 | 170.382 | 150.277 | 35.8 | 2392.24 | 8079.06 | 35778.6 | 1.5 | 5.85 | 12.11 | 99.259 | 1 | 1 | 1270 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 407594.6357 | 30695.2695 | 1570.8749 | 5332.8289 | 25362.4406 | 104114.3991 | 0.048388 | -803943.7919 | 803943.7919
C | Xist Rating 1034 | -91.11 | 172.583 | 150.277 | 35.7 | 2392.16 | 8095.89 | 35478.3 | 1.46 | 5.79 | 12.077 | 97.448 | 1 | 1 | 1280 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 412846.1493 | 31138.2413 | 1595.7105 | 5374.8197 | 25763.4216 | 102211.2638 | 0.048769 | -789248.2855 | 789248.2855
C | Xist Rating 1035 | -90.99 | 174.732 | 150.277 | 35.7 | 2397.29 | 8173 | 35184.6 | 1.42 | 5.73 | 12.073 | 95.671 | 1 | 1 | 1290 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 418883.2763 | 31584.358 | 1620.7408 | 5416.8105 | 26167.5476 | 100345.4938 | 0.04915 | -774841.3043 | 774841.3043
C | Xist Rating 1036 | -90.81 | 177.723 | 150.277 | 35.7 | 2404.98 | 8290.9 | 34753 | 1.4 | 5.64 | 12.074 | 93 | 1 | 1 | 1300 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 427420.2605 | 32033.6197 | 1645.966 | 5458.8012 | 26574.8185 | 97565.3603 | 0.049531 | -753373.8505 | 753373.8505
C | Xist Rating 1037 | -90.72 | 179.414 | 150.277 | 35.7 | 2408 | 8340.89 | 34541.8 | 1.36 | 5.59 | 12.05 | 91.792 | 1 | 1 | 1310 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 432028.912 | 32486.0263 | 1671.3859 | 5500.792 | 26985.2343 | 96288.155 | 0.049912 | -743511.6098 | 743511.6098
C | Xist Rating 1038 | -90.32 | 187.731 | 150.277 | 35.7 | 2402.59 | 8357.68 | 33364.9 | 1.37 | 5.35 | 12.092 | 84.611 | 1 | 1 | 1320 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 451040.6233 | 32941.5779 | 1697.0007 | 5542.7828 | 27398.7951 | 88848.5781 | 0.050293 | -686065.1688 | 686065.1688
C | Xist Rating 1039 | -90.18 | 190.938 | 150.277 | 35.7 | 2396.82 | 8315.82 | 32981.8 | 1.33 | 5.28 | 12.035 | 82.475 | 1 | 1 | 1330 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 457644.0172 | 33400.2744 | 1722.8102 | 5584.7736 | 27815.5008 | 86604.4161 | 0.050674 | -668736.3451 | 668736.3451
C | Xist Rating 1040 | -90.02 | 194.044 | 150.277 | 35.7 | 2398.79 | 8367.46 | 32608.7 | 1.31 | 5.2 | 12.018 | 80.396 | 1 | 1 | 1340 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 465470.8068 | 33862.1158 | 1748.8145 | 5626.7644 | 28235.3515 | 84436.7575 | 0.051055 | -651998.2598 | 651998.2598
C | Xist Rating 1041 | -89.92 | 195.752 | 150.277 | 35.7 | 2402.51 | 8427.04 | 32425.6 | 1.28 | 5.16 | 11.999 | 79.444 | 1 | 1 | 1350 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 470296.1375 | 34327.1023 | 1775.0136 | 5668.7551 | 28658.3471 | 83431.8749 | 0.051436 | -644238.8225 | 644238.8225
C | Xist Rating 1042 | -89.82 | 196.729 | 150.277 | 35.7 | 2418.32 | 8634.67 | 32304.7 | 1.27 | 5.14 | 12.018 | 78.782 | 1 | 1 | 1360 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 475753.6753 | 34795.2336 | 1801.4075 | 5710.7459 | 29084.4877 | 82745.4296 | 0.051817 | -638938.2743 | 638938.2743
C | Xist Rating 1043 | -89.32 | 208.745 | 150.277 | 35.7 | 2391.42 | 8413.97 | 30904.2 | 1.26 | 4.86 | 12.022 | 71.116 | 1 | 1 | 1370 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 499196.9679 | 35266.5099 | 1827.9962 | 5752.7367 | 29513.7732 | 74784.0716 | 0.052198 | -577462.7776 | 577462.7776
C | Xist Rating 1044 | -89.27 | 209.983 | 150.277 | 35.7 | 2390.88 | 8416.6 | 30795.8 | 1.23 | 4.84 | 12.002 | 70.624 | 1 | 1 | 1380 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 502044.155 | 35740.9312 | 1854.7797 | 5794.7275 | 29946.2037 | 74256.0888 | 0.052579 | -573385.8349 | 573385.8349
C | Xist Rating 1045 | -89.14 | 212.689 | 150.277 | 35.7 | 2391.3 | 8445.12 | 30528.2 | 1.21 | 4.79 | 11.981 | 69.296 | 1 | 1 | 1390 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 508603.2057 | 36218.4974 | 1881.7579 | 5836.7182 | 30381.7791 | 72867.041 | 0.05296 | -562659.9754 | 562659.9754
C | Xist Rating 1046 | -89.01 | 215.393 | 150.276 | 35.7 | 2390.64 | 8460.07 | 30266.3 | 1.18 | 4.73 | 11.964 | 68.008 | 1 | 1 | 1400 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 514927.1215 | 36699.2085 | 1908.931 | 5878.709 | 30820.4995 | 71512.1385 | 0.053341 | -552197.7779 | 552197.7779
C | Xist Rating 1047 | -88.86 | 218.56 | 150.276 | 35.7 | 2389.39 | 8472.47 | 29958.5 | 1.16 | 4.67 | 11.951 | 66.493 | 1 | 1 | 1410 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 522225.0784 | 37183.0646 | 1936.2988 | 5920.6998 | 31262.3648 | 69929.0653 | 0.053722 | -539973.7061 | 539973.7061
C | Xist Rating 1048 | -88.44 | 227.467 | 150.277 | 35.7 | 2384.69 | 8499.16 | 29053 | 1.17 | 4.49 | 12 | 61.946 | 1 | 1 | 1420 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 542438.2802 | 37670.0657 | 1963.8614 | 5962.6906 | 31707.3751 | 65224.4831 | 0.054103 | -503646.1697 | 503646.1697
C | Xist Rating 1049 | -88.37 | 229.415 | 150.276 | 35.7 | 2380.26 | 8456.97 | 28911.6 | 1.14 | 4.47 | 11.964 | 61.366 | 1 | 1 | 1430 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 546067.3479 | 38160.2117 | 1991.6188 | 6004.6814 | 32155.5303 | 64602.7411 | 0.054484 | -498845.2423 | 498845.2423
C | Xist Rating 1050 | -88.18 | 233.559 | 150.276 | 35.7 | 2377.63 | 8460.48 | 28543.1 | 1.12 | 4.39 | 11.952 | 59.644 | 1 | 1 | 1440 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 555316.8852 | 38653.5026 | 2019.571 | 6046.6721 | 32606.8305 | 62804.248 | 0.054865 | -484957.7553 | 484957.7553
C | Xist Rating 1051 | -88.05 | 236.3 | 150.276 | 35.7 | 2376.75 | 8472.33 | 28317.9 | 1.1 | 4.35 | 11.938 | 58.64 | 1 | 1 | 1450 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 561626.025 | 39149.9385 | 2047.718 | 6088.6629 | 33061.2756 | 61751.0584 | 0.055246 | -476825.3044 | 476825.3044
C | Xist Rating 1052 | -87.94 | 237.89 | 150.276 | 35.7 | 2384.15 | 8581.28 | 28184.8 | 1.09 | 4.33 | 11.944 | 58.051 | 1 | 1 | 1460 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 567165.4435 | 39649.5194 | 2076.0598 | 6130.6537 | 33518.8657 | 61137.8844 | 0.055627 | -472090.5374 | 472090.5374
C | Xist Rating 1053 | -87.52 | 248.202 | 150.276 | 35.7 | 2367.22 | 8458.19 | 27311.3 | 1.08 | 4.16 | 11.959 | 54.079 | 1 | 1 | 1470 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 587548.7384 | 40152.2452 | 2104.5964 | 6172.6445 | 33979.6007 | 57012.0017 | 0.056008 | -440231.5646 | 440231.5646
C | Xist Rating 1054 | -87.35 | 251.413 | 150.276 | 35.7 | 2369.38 | 8513.26 | 27067.2 | 1.06 | 4.11 | 11.953 | 53.042 | 1 | 1 | 1480 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 595692.9339 | 40658.1159 | 2133.3277 | 6214.6353 | 34443.4807 | 55924.579 | 0.056389 | -431834.7749 | 431834.7749
C | Xist Rating 1055 | -87.18 | 254.156 | 150.276 | 35.7 | 2377.17 | 8638.33 | 26867.6 | 1.04 | 4.07 | 11.952 | 52.215 | 1 | 1 | 1490 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 604172.0185 | 41167.1316 | 2162.2539 | 6256.626 | 34910.5056 | 55055.3842 | 0.05677 | -425123.0831 | 425123.0831
C | Xist Rating 1056 | -87.03 | 256.991 | 150.276 | 35.7 | 2379.81 | 8696.96 | 26671.1 | 1.02 | 4.03 | 11.942 | 51.422 | 1 | 1 | 1500 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 611589.7517 | 41679.2923 | 2191.3748 | 6298.6168 | 35380.6755 | 54220.6685 | 0.057151 | -418677.6301 | 418677.6301
C | Xist Rating 1057 | -86.85 | 260.228 | 150.276 | 35.7 | 2384.65 | 8791.08 | 26439.6 | 1 | 3.99 | 11.94 | 50.471 | 1 | 1 | 1510 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 620552.7002 | 42194.5979 | 2220.6906 | 6340.6076 | 35853.9903 | 53222.2152 | 0.057532 | -410967.8385 | 410967.8385
C | Xist Rating 1058 | -86.36 | 270.224 | 150.277 | 35.7 | 2383.82 | 8879.89 | 25681.8 | 1.01 | 3.85 | 11.995 | 47.263 | 1 | 1 | 1520 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 644165.3757 | 42713.0484 | 2250.2011 | 6382.5984 | 36330.45 | 49907.9843 | 0.057913 | -385376.2259 | 385376.2259
C | Xist Rating 1059 | -86.24 | 273.806 | 150.276 | 35.7 | 2375.21 | 8790.31 | 25469.3 | 0.98 | 3.81 | 11.964 | 46.476 | 1 | 1 | 1530 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 650346.7493 | 43234.6439 | 2279.9064 | 6424.5891 | 36810.0547 | 49069.3539 | 0.058294 | -378900.5441 | 378900.5441
C | Xist Rating 1060 | -86.12 | 275.669 | 150.276 | 35.7 | 2381.02 | 8885.13 | 25364.5 | 0.96 | 3.79 | 11.957 | 46.107 | 1 | 1 | 1540 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 656373.4024 | 43759.3843 | 2309.8065 | 6466.5799 | 37292.8044 | 48674.4222 | 0.058675 | -375850.986 | 375850.986
C | Xist Rating 1061 | -85.87 | 280.915 | 150.276 | 35.7 | 2379.88 | 8918.45 | 25022.1 | 0.95 | 3.72 | 11.953 | 44.77 | 1 | 1 | 1550 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 668543.9902 | 44287.2697 | 2339.9013 | 6508.5707 | 37778.699 | 47282.5236 | 0.059056 | -365103.1139 | 365103.1139
C | Xist Rating 1062 | -85.72 | 282.554 | 150.277 | 35.7 | 2393.8 | 9132.55 | 24921.5 | 0.94 | 3.7 | 11.964 | 44.401 | 1 | 1 | 1560 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 676377.7652 | 44818.3001 | 2370.191 | 6550.5615 | 38267.7386 | 46896.7724 | 0.059437 | -362124.4454 | 362124.4454
C | Xist Rating 1063 | -85.25 | 294.638 | 150.277 | 35.7 | 2371.67 | 8932.75 | 24163 | 0.93 | 3.56 | 11.981 | 41.496 | 1 | 1 | 1570 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 698784.1055 | 45352.4753 | 2400.6755 | 6592.5523 | 38759.9231 | 43877.6685 | 0.059818 | -338811.7257 | 338811.7257
C | Xist Rating 1064 | -85.09 | 297.502 | 150.277 | 35.7 | 2375.55 | 9012.85 | 24008.5 | 0.91 | 3.53 | 11.974 | 40.959 | 1 | 1 | 1580 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 706730.8761 | 45889.7956 | 2431.3547 | 6634.543 | 39255.2525 | 43307.5677 | 0.0602 | -334409.5578 | 334409.5578
C | Xist Rating 1065 | -84.94 | 300.401 | 150.277 | 35.7 | 2378.47 | 9080.21 | 23855.9 | 0.89 | 3.5 | 11.967 | 40.437 | 1 | 1 | 1590 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 714494.7665 | 46430.2608 | 2462.2288 | 6676.5338 | 39753.7269 | 42752.8437 | 0.060581 | -330126.1263 | 330126.1263
C | Xist Rating 1066 | -84.75 | 304.133 | 150.277 | 35.7 | 2381.04 | 9153.61 | 23646 | 0.88 | 3.46 | 11.967 | 39.69 | 1 | 1 | 1600 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 724152.8383 | 46973.8709 | 2493.2976 | 6718.5246 | 40255.3463 | 41973.2768 | 0.060962 | -324106.5176 | 324106.5176
C | Xist Rating 1067 | -84.66 | 306.193 | 150.277 | 35.7 | 2380.84 | 9165.96 | 23557.3 | 0.86 | 3.45 | 11.953 | 39.426 | 1 | 1 | 1610 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 728996.5421 | 47520.626 | 2524.5612 | 6760.5154 | 40760.1106 | 41685.6922 | 0.061343 | -321885.8653 | 321885.8653
C | Xist Rating 1068 | -84.09 | 319.579 | 150.277 | 35.7 | 2367.2 | 9098.28 | 22805.7 | 0.87 | 3.31 | 11.991 | 36.733 | 1 | 1 | 1620 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 756507.4088 | 48070.526 | 2556.0196 | 6802.5062 | 41268.0199 | 38904.7042 | 0.061724 | -300411.8132 | 300411.8132
C | Xist Rating 1069 | -83.97 | 321.294 | 150.277 | 35.7 | 2374.21 | 9218.08 | 22724 | 0.86 | 3.29 | 11.991 | 36.476 | 1 | 1 | 1630 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 762819.4277 | 48623.571 | 2587.6728 | 6844.4969 | 41779.0741 | 38633.7251 | 0.062105 | -298319.3849 | 298319.3849
C | Xist Rating 1070 | -83.83 | 324.34 | 150.277 | 35.7 | 2373.69 | 9236.07 | 22589.1 | 0.84 | 3.27 | 11.98 | 36.059 | 1 | 1 | 1640 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 769882.6146 | 49179.7609 | 2619.5208 | 6886.4877 | 42293.2732 | 38186.9847 | 0.062486 | -294869.7739 | 294869.7739
C | Xist Rating 1071 | -83.66 | 328.43 | 150.277 | 35.7 | 2369.9 | 9214.63 | 22403.5 | 0.82 | 3.24 | 11.967 | 35.47 | 1 | 1 | 1650 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 778346.257 | 49739.0958 | 2651.5635 | 6928.4785 | 42810.6173 | 37561.3106 | 0.062867 | -290038.4837 | 290038.4837
C | Xist Rating 1072 | -83.48 | 332.276 | 150.277 | 35.6 | 2370.6 | 9261.07 | 22221.3 | 0.81 | 3.2 | 11.964 | 34.881 | 1 | 1 | 1660 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 787693.4856 | 50301.5756 | 2683.8011 | 6970.4693 | 43331.1064 | 36944.9483 | 0.063248 | -285279.0976 | 285279.0976
C | Xist Rating 1073 | -82.97 | 344.404 | 150.277 | 35.6 | 2358.5 | 9196.56 | 21633.6 | 0.81 | 3.1 | 11.997 | 32.943 | 1 | 1 | 1670 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 812276.834 | 50867.2004 | 2716.2334 | 7012.46 | 43854.7403 | 34938.6832 | 0.063629 | -269787.2501 | 269787.2501
C | Xist Rating 1074 | -82.86 | 346.23 | 150.277 | 35.6 | 2362.96 | 9280.21 | 21561 | 0.8 | 3.08 | 11.993 | 32.738 | 1 | 1 | 1680 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 818127.6408 | 51435.9701 | 2748.8606 | 7054.4508 | 44381.5193 | 34720.8715 | 0.06401 | -268105.3661 | 268105.3661
C | Xist Rating 1075 | -82.66 | 351.412 | 150.277 | 35.6 | 2357.35 | 9239.79 | 21346.7 | 0.79 | 3.04 | 11.979 | 32.092 | 1 | 1 | 1690 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 828401.0782 | 52007.8848 | 2781.6825 | 7096.4416 | 44911.4432 | 34044.3792 | 0.064391 | -262881.6719 | 262881.6719
C | Xist Rating 1076 | -82.49 | 354.806 | 150.277 | 35.6 | 2359.53 | 9304.17 | 21206.2 | 0.78 | 3.02 | 11.977 | 31.674 | 1 | 1 | 1700 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 837175.4012 | 52582.9444 | 2814.6992 | 7138.4324 | 45444.512 | 33605.2817 | 0.064772 | -259491.0774 | 259491.0774
C | Xist Rating 1077 | -82.31 | 358.844 | 150.277 | 35.6 | 2358.33 | 9321.46 | 21045.1 | 0.76 | 2.99 | 11.97 | 31.202 | 1 | 1 | 1710 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 846272.5705 | 53161.149 | 2847.9107 | 7180.4232 | 45980.7258 | 33100.5294 | 0.065153 | -255593.5142 | 255593.5142
C | Xist Rating 1078 | -81.84 | 370.084 | 150.277 | 35.6 | 2348.36 | 9275.54 | 20567.8 | 0.76 | 2.9 | 11.997 | 29.74 | 1 | 1 | 1720 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 869090.4622 | 53742.4985 | 2881.317 | 7222.4139 | 46520.0846 | 31587.9046 | 0.065534 | -243913.4262 | 243913.4262
C | Xist Rating 1079 | -81.63 | 375.136 | 150.277 | 35.6 | 2345.55 | 9277.11 | 20374.7 | 0.75 | 2.87 | 11.989 | 29.188 | 1 | 1 | 1730 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 879900.2448 | 54326.993 | 2914.9181 | 7264.4047 | 47062.5883 | 31008.9719 | 0.065915 | -239443.0614 | 239443.0614
C | Xist Rating 1080 | -81.52 | 377.578 | 150.277 | 35.6 | 2346.27 | 9308.79 | 20289.9 | 0.74 | 2.85 | 11.984 | 28.965 | 1 | 1 | 1740 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 885899.9341 | 54914.6324 | 2948.714 | 7306.3955 | 47608.2369 | 30771.7779 | 0.066296 | -237611.5121 | 237611.5121
C | Xist Rating 1081 | -81.34 | 382.293 | 150.277 | 35.6 | 2341.03 | 9267.03 | 20123.2 | 0.73 | 2.82 | 11.97 | 28.508 | 1 | 1 | 1750 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 894959.3818 | 55505.4168 | 2982.7046 | 7348.3863 | 48157.0305 | 30290.9569 | 0.066677 | -233898.74 | 233898.74
C | Xist Rating 1082 | -81.2 | 385.804 | 150.277 | 35.6 | 2338.6 | 9258.98 | 20000.6 | 0.72 | 2.8 | 11.965 | 28.175 | 1 | 1 | 1760 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 902241.2344 | 56099.3461 | 3016.8901 | 7390.3771 | 48708.969 | 29939.3264 | 0.067058 | -231183.5428 | 231183.5428
C | Xist Rating 1083 | -80.65 | 399.113 | 150.277 | 35.6 | 2328.49 | 9227.3 | 19497.4 | 0.72 | 2.71 | 12.003 | 26.732 | 1 | 1 | 1770 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 929330.6294 | 56696.4203 | 3051.2703 | 7432.3678 | 49264.0525 | 28446.8055 | 0.067439 | -219658.6918 | 219658.6918
C | Xist Rating 1084 | -80.49 | 402.733 | 150.277 | 35.6 | 2327.12 | 9235.32 | 19383 | 0.71 | 2.69 | 11.994 | 26.441 | 1 | 1 | 1780 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 937208.019 | 57296.6396 | 3085.8453 | 7474.3586 | 49822.2809 | 28138.3895 | 0.06782 | -217277.1851 | 217277.1851
C | Xist Rating 1085 | -80.41 | 404.818 | 150.277 | 35.6 | 2327.39 | 9254.61 | 19326.2 | 0.7 | 2.68 | 11.986 | 26.315 | 1 | 1 | 1790 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 942169.365 | 57900.0037 | 3120.6151 | 7516.3494 | 50383.6543 | 28001.283 | 0.068201 | -216218.4851 | 216218.4851
C | Xist Rating 1086 | -80.24 | 411.001 | 150.277 | 35.6 | 2313.52 | 9090.97 | 19122.9 | 0.69 | 2.65 | 12.079 | 25.768 | 1 | 1 | 1800 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 950859.0335 | 58506.5128 | 3155.5797 | 7558.3402 | 50948.1727 | 27432.4919 | 0.068582 | -211826.4313 | 211826.4313
C | Xist Rating 1087 | -80.08 | 414.494 | 150.277 | 35.6 | 2313.81 | 9124.19 | 19013.6 | 0.68 | 2.63 | 12.08 | 25.491 | 1 | 1 | 1810 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 959060.3621 | 59116.1669 | 3190.7391 | 7600.331 | 51515.8359 | 27138.819 | 0.068963 | -209558.7663 | 209558.7663
C | Xist Rating 1088 | -79.54 | 428.061 | 150.277 | 35.6 | 2302.47 | 9069.44 | 18563.7 | 0.68 | 2.55 | 12.114 | 24.292 | 1 | 1 | 1820 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 985597.6107 | 59728.9659 | 3226.0933 | 7642.3217 | 52086.6442 | 25899.2276 | 0.069344 | -199986.9703 | 199986.9703
C | Xist Rating 1089 | -79.43 | 425.874 | 150.277 | 35.6 | 2329.69 | 9486.41 | 18632.1 | 0.67 | 2.56 | 12.144 | 24.484 | 1 | 1 | 1830 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 992154.3991 | 60344.9099 | 3261.6423 | 7684.3125 | 52660.5974 | 26094.0235 | 0.069725 | -201491.1327 | 201491.1327
C | Xist Rating 1090 | -79.2 | 428.699 | 150.277 | 35.6 | 2339.91 | 9684.86 | 18546.5 | 0.66 | 2.55 | 12.162 | 24.273 | 1 | 1 | 1840 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 1003117.0771 | 60963.9988 | 3297.386 | 7726.3033 | 53237.6955 | 25869.5113 | 0.070106 | -199757.5087 | 199757.5087
C | Xist Rating 1091 | -79 | 433.531 | 150.277 | 35.6 | 2337.32 | 9683.34 | 18410.6 | 0.65 | 2.52 | 12.157 | 23.946 | 1 | 1 | 1850 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 1013300.6769 | 61586.2326 | 3333.3246 | 7768.2941 | 53817.9386 | 25523.1654 | 0.070487 | -197083.1177 | 197083.1177
C | Xist Rating 1092 | -78.8 | 438.925 | 150.277 | 35.6 | 2331.71 | 9635.26 | 18260.3 | 0.64 | 2.5 | 12.147 | 23.586 | 1 | 1 | 1860 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 1023445.8117 | 62211.6114 | 3369.4579 | 7810.2848 | 54401.3266 | 25142.1787 | 0.070868 | -194141.2393 | 194141.2393
C | Xist Rating 1093 | -78.28 | 451.332 | 150.277 | 35.6 | 2324.75 | 9640.28 | 17880.8 | 0.64 | 2.43 | 12.182 | 22.622 | 1 | 1 | 1870 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 1049234.067 | 62840.1352 | 3405.7861 | 7852.2756 | 54987.8596 | 24146.4285 | 0.071249 | -186452.3205 | 186452.3205
C | Xist Rating 1094 | -78.09 | 456.712 | 150.277 | 35.6 | 2319.31 | 9594.11 | 17740 | 0.63 | 2.41 | 12.169 | 22.297 | 1 | 1 | 1880 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 1059256.7087 | 63471.8039 | 3442.309 | 7894.2664 | 55577.5375 | 23801.4553 | 0.07163 | -183788.5287 | 183788.5287
C | Xist Rating 1095 | -77.88 | 460.253 | 150.277 | 35.6 | 2324.47 | 9715.01 | 17647.6 | 0.62 | 2.39 | 12.18 | 22.087 | 1 | 1 | 1890 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 1069844.2909 | 64106.6175 | 3479.0267 | 7936.2572 | 56170.3604 | 23577.0755 | 0.072011 | -182055.9272 | 182055.9272
C | Xist Rating 1096 | -77.74 | 464.252 | 150.277 | 35.6 | 2319.85 | 9666.42 | 17556.3 | 0.61 | 2.38 | 12.17 | 21.895 | 1 | 1 | 1900 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 1076995.0022 | 64744.5761 | 3515.9392 | 7978.248 | 56766.3282 | 23370.1759 | 0.072392 | -180458.3037 | 180458.3037
C | Xist Rating 1097 | -77.57 | 467.972 | 150.277 | 35.6 | 2319.57 | 9693.12 | 17466.4 | 0.6 | 2.36 | 12.176 | 21.698 | 1 | 1 | 1910 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 1085493.812 | 65385.6797 | 3553.0464 | 8020.2387 | 57365.441 | 23158.8082 | 0.072773 | -178826.1785 | 178826.1785
C | Xist Rating 1098 | -76.95 | 483.064 | 150.277 | 35.6 | 2310.32 | 9681.39 | 17051.6 | 0.6 | 2.29 | 12.213 | 20.704 | 1 | 1 | 1920 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 1116032.4205 | 66029.9282 | 3590.3485 | 8062.2295 | 57967.6987 | 22131.7261 | 0.073154 | -170895.3226 | 170895.3226
C | Xist Rating 1099 | -76.74 | 488.521 | 150.277 | 35.6 | 2307.39 | 9677.25 | 16924.9 | 0.59 | 2.27 | 12.206 | 20.432 | 1 | 1 | 1930 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 1127208.4702 | 66677.3216 | 3627.8454 | 8104.2203 | 58573.1013 | 21841.6163 | 0.073535 | -168655.1712 | 168655.1712
C | Xist Rating 1100 | -76.59 | 490.244 | 150.277 | 35.6 | 2315.02 | 9829 | 16883.3 | 0.59 | 2.26 | 12.235 | 20.346 | 1 | 1 | 1940 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 1134924.6649 | 67327.86 | 3665.537 | 8146.2111 | 59181.649 | 21757.0213 | 0.073916 | -168001.9517 | 168001.9517
C | Xist Rating 1101 | -76.42 | 495.647 | 150.277 | 35.6 | 2308.23 | 9750.07 | 16773.3 | 0.57 | 2.24 | 12.221 | 20.127 | 1 | 1 | 1950 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 1144067.2748 | 67981.5434 | 3703.4235 | 8188.2019 | 59793.3415 | 21510.7397 | 0.074297 | -166100.2297 | 166100.2297
C | Xist Rating 1102 | -76.18 | 501.546 | 150.277 | 35.6 | 2305.38 | 9752.21 | 16638.2 | 0.56 | 2.22 | 12.226 | 19.836 | 1 | 1 | 1960 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 8 | E | Rod | 1156254.1175 | 68638.3717 | 3741.5047 | 8230.1926 | 60408.179 | 21201.1682 | 0.074678 | -163709.8007 | 163709.8007
C | Xist Rating 1103 | -75.62 | 515.242 | 150.277 | 35.6 | 2297.5 | 9745.33 | 16304.1 | 0.57 | 2.16 | 12.262 | 19.088 | 1 | 1 | 1970 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1183768.495 | 69298.3449 | 3779.7807 | 8272.1834 | 61026.1615 | 20440.0484 | 0.075059 | -157832.6358 | 157832.6358
C | Xist Rating 1104 | -75.44 | 519.505 | 150.277 | 35.6 | 2296.96 | 9772.52 | 16215 | 0.56 | 2.15 | 12.261 | 18.909 | 1 | 1 | 1980 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1193282.2048 | 69961.4631 | 3818.2515 | 8314.1742 | 61647.2889 | 20246.3576 | 0.07544 | -156337.0065 | 156337.0065
C | Xist Rating 1105 | -75.23 | 525.157 | 150.277 | 35.6 | 2292.86 | 9745.77 | 16102 | 0.55 | 2.13 | 12.254 | 18.686 | 1 | 1 | 1990 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1204111.479 | 70627.7262 | 3856.9171 | 8356.165 | 62271.5613 | 20006.5698 | 0.075821 | -154485.4288 | 154485.4288
C | Xist Rating 1106 | -75.05 | 529.545 | 150.277 | 35.6 | 2291.1 | 9750.65 | 16015.6 | 0.54 | 2.12 | 12.251 | 18.517 | 1 | 1 | 2000 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1213240.5495 | 71297.1343 | 3895.7775 | 8398.1557 | 62898.9786 | 19822.9538 | 0.076202 | -153067.5944 | 153067.5944
C | Xist Rating 1107 | -74.92 | 532.842 | 150.277 | 35.6 | 2290.2 | 9760.59 | 15954.3 | 0.53 | 2.11 | 12.249 | 18.404 | 1 | 1 | 2010 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1220314.7484 | 71969.6874 | 3934.8326 | 8440.1465 | 63529.5409 | 19697.4355 | 0.076583 | -152098.3755 | 152098.3755
C | Xist Rating 1108 | -74.32 | 548.382 | 150.277 | 35.6 | 2280.23 | 9727.95 | 15615.4 | 0.53 | 2.05 | 12.285 | 17.688 | 1 | 1 | 2020 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1250437.0879 | 72645.3854 | 3974.0826 | 8482.1373 | 64163.2481 | 18958.5082 | 0.076964 | -146392.5751 | 146392.5751
C | Xist Rating 1109 | -74.07 | 554.225 | 150.277 | 35.6 | 2278.95 | 9756.35 | 15500.5 | 0.53 | 2.03 | 12.283 | 17.462 | 1 | 1 | 2030 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1263051.0637 | 73324.2283 | 4013.5273 | 8524.1281 | 64800.1002 | 18726.6297 | 0.077345 | -144602.0705 | 144602.0705
C | Xist Rating 1110 | -73.91 | 558.423 | 150.277 | 35.6 | 2276.43 | 9741.38 | 15432.3 | 0.52 | 2.02 | 12.279 | 17.345 | 1 | 1 | 2040 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1271210.8699 | 74006.2162 | 4053.1669 | 8566.1189 | 65440.0973 | 18596.6214 | 0.077726 | -143598.1809 | 143598.1809
C | Xist Rating 1111 | -73.75 | 561.807 | 150.277 | 35.6 | 2277.95 | 9800.48 | 15364.8 | 0.52 | 2.01 | 12.277 | 17.215 | 1 | 1 | 2050 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1279768.2556 | 74691.349 | 4093.0012 | 8608.1096 | 66083.2394 | 18464.3831 | 0.078107 | -142577.0721 | 142577.0721
C | Xist Rating 1112 | -73.55 | 567.853 | 150.277 | 35.6 | 2271.56 | 9729.61 | 15264.8 | 0.5 | 1.99 | 12.272 | 17.037 | 1 | 1 | 2060 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1289912.1607 | 75379.6268 | 4133.0303 | 8650.1004 | 66729.5264 | 18259.4883 | 0.078488 | -140994.9287 | 140994.9287
C | Xist Rating 1113 | -72.91 | 584.586 | 150.277 | 35.6 | 2261.33 | 9697.83 | 14936.8 | 0.51 | 1.94 | 12.31 | 16.383 | 1 | 1 | 2070 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1321941.8594 | 76071.0495 | 4173.2542 | 8692.0912 | 67378.9583 | 17596.2458 | 0.078869 | -135873.546 | 135873.546
C | Xist Rating 1114 | -72.77 | 588.586 | 150.277 | 35.6 | 2258.87 | 9683.23 | 14874 | 0.5 | 1.93 | 12.306 | 16.277 | 1 | 1 | 2080 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1329539.2578 | 76765.6172 | 4213.6729 | 8734.082 | 68031.5352 | 17477.3154 | 0.07925 | -134955.1967 | 134955.1967
C | Xist Rating 1115 | -72.58 | 593.618 | 150.277 | 35.6 | 2256.69 | 9683.64 | 14791.3 | 0.49 | 1.91 | 12.302 | 16.132 | 1 | 1 | 2090 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1339611.8044 | 77463.3299 | 4254.2864 | 8776.0728 | 68687.2571 | 17317.7789 | 0.079631 | -133723.298 | 133723.298
C | Xist Rating 1116 | -72.39 | 598.658 | 150.277 | 35.6 | 2254.17 | 9677.63 | 14709.7 | 0.49 | 1.9 | 12.298 | 15.989 | 1 | 1 | 2100 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1349476.9039 | 78164.1874 | 4295.0947 | 8818.0635 | 69346.1239 | 17171.7911 | 0.080012 | -132596.0193 | 132596.0193
C | Xist Rating 1117 | -72.23 | 603.14 | 150.277 | 35.6 | 2252.21 | 9676.72 | 14639.1 | 0.48 | 1.89 | 12.295 | 15.869 | 1 | 1 | 2110 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1358397.9394 | 78868.19 | 4336.0977 | 8860.0543 | 70008.1356 | 17038.1048 | 0.080393 | -131563.729 | 131563.729
C | Xist Rating 1118 | -71.63 | 619.119 | 150.277 | 35.6 | 2242.19 | 9634.4 | 14359.4 | 0.48 | 1.84 | 12.333 | 15.344 | 1 | 1 | 2120 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1388182.4306 | 79575.3374 | 4377.2956 | 8902.0451 | 70673.2923 | 16497.2718 | 0.080774 | -127387.5601 | 127387.5601
C | Xist Rating 1119 | -71.41 | 625.305 | 150.277 | 35.6 | 2238.67 | 9619.02 | 14264 | 0.47 | 1.83 | 12.327 | 15.181 | 1 | 1 | 2130 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1399851.5443 | 80285.6299 | 4418.6882 | 8944.0359 | 71341.594 | 16318.6058 | 0.081155 | -126007.9481 | 126007.9481
C | Xist Rating 1120 | -71.22 | 631.518 | 150.277 | 35.6 | 2232.76 | 9559.45 | 14170.1 | 0.47 | 1.81 | 12.324 | 15.022 | 1 | 1 | 2140 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1410028.1297 | 80999.0672 | 4460.2756 | 8986.0266 | 72013.0406 | 16155.9463 | 0.081536 | -124751.9346 | 124751.9346
C | Xist Rating 1121 | -71.09 | 634.965 | 150.277 | 35.6 | 2231.38 | 9558.65 | 14123.7 | 0.46 | 1.81 | 12.321 | 14.951 | 1 | 1 | 2150 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1416848.2017 | 81715.6496 | 4502.0578 | 9028.0174 | 72687.6321 | 16072.7992 | 0.081917 | -124109.8953 | 124109.8953
C | Xist Rating 1122 | -70.93 | 639.393 | 150.277 | 35.6 | 2229.52 | 9558.54 | 14059.2 | 0.46 | 1.79 | 12.317 | 14.846 | 1 | 1 | 2160 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1425539.4814 | 82435.3768 | 4544.0348 | 9070.0082 | 73365.3686 | 15966.1193 | 0.082298 | -123286.1408 | 123286.1408
C | Xist Rating 1123 | -70.3 | 656.778 | 150.277 | 35.6 | 2218.7 | 9507.14 | 13786.1 | 0.46 | 1.75 | 12.356 | 14.362 | 1 | 1 | 2170 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1457193.3486 | 83158.2491 | 4586.2066 | 9111.999 | 74046.2501 | 15467.7707 | 0.082679 | -119438.0255 | 119438.0255
C | Xist Rating 1124 | -70.08 | 662.739 | 150.277 | 35.6 | 2216.59 | 9516.17 | 13699.1 | 0.45 | 1.74 | 12.351 | 14.218 | 1 | 1 | 2180 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1469020.64 | 83884.2662 | 4628.5732 | 9153.9898 | 74730.2765 | 15308.4808 | 0.08306 | -118208.031 | 118208.031
C | Xist Rating 1125 | -69.92 | 667.401 | 150.277 | 35.6 | 2214.13 | 9504.38 | 13639 | 0.45 | 1.73 | 12.348 | 14.127 | 1 | 1 | 2190 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1477712.5761 | 84613.4284 | 4671.1346 | 9195.9805 | 75417.4478 | 15216.3363 | 0.083441 | -117496.5153 | 117496.5153
C | Xist Rating 1126 | -69.74 | 672.468 | 150.277 | 35.6 | 2211.02 | 9480.47 | 13579.4 | 0.44 | 1.72 | 12.343 | 14.042 | 1 | 1 | 2200 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1486840.1974 | 85345.7354 | 4713.8907 | 9237.9713 | 76107.7641 | 15118.1608 | 0.083822 | -116738.4303 | 116738.4303
C | Xist Rating 1127 | -69.52 | 678.687 | 150.277 | 35.6 | 2208.14 | 9474.78 | 13495.3 | 0.43 | 1.7 | 12.34 | 13.908 | 1 | 1 | 2210 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1498635.9122 | 86081.1874 | 4756.8417 | 9279.9621 | 76801.2253 | 14969.0813 | 0.084203 | -115587.2781 | 115587.2781
C | Xist Rating 1128 | -68.89 | 695.938 | 150.277 | 35.6 | 2198.59 | 9442.35 | 13246.2 | 0.43 | 1.66 | 12.379 | 13.487 | 1 | 1 | 2220 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1530082.3274 | 86819.7844 | 4799.9874 | 9321.9529 | 77497.8315 | 14535.9208 | 0.084584 | -112242.5271 | 112242.5271
C | Xist Rating 1129 | -68.69 | 700.941 | 150.277 | 35.6 | 2198.61 | 9480.24 | 13182.4 | 0.43 | 1.65 | 12.374 | 13.39 | 1 | 1 | 2230 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1541095.892 | 87561.5263 | 4843.3279 | 9363.9437 | 78197.5827 | 14437.3575 | 0.084965 | -111481.4478 | 111481.4478
C | Xist Rating 1130 | -68.48 | 706.956 | 150.277 | 35.6 | 2195.57 | 9466.11 | 13111.6 | 0.43 | 1.64 | 12.369 | 13.287 | 1 | 1 | 2240 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1552171.3849 | 88306.4132 | 4886.8633 | 9405.9344 | 78900.4787 | 14332.5613 | 0.085346 | -110672.2395 | 110672.2395
C | Xist Rating 1131 | -68.25 | 713.483 | 150.277 | 35.6 | 2192.33 | 9452.55 | 13034 | 0.42 | 1.63 | 12.366 | 13.172 | 1 | 1 | 2250 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1564190.1854 | 89054.445 | 4930.5934 | 9447.9252 | 79606.5198 | 14202.9162 | 0.085727 | -109671.1542 | 109671.1542
C | Xist Rating 1132 | -68.13 | 716.893 | 150.277 | 35.6 | 2191.73 | 9464.82 | 12995.6 | 0.42 | 1.62 | 12.361 | 13.119 | 1 | 1 | 2260 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1571235.8949 | 89805.6218 | 4974.5182 | 9489.916 | 80315.7058 | 14149.9911 | 0.086108 | -109262.4807 | 109262.4807
C | Xist Rating 1133 | -67.47 | 735.645 | 150.278 | 35.6 | 2180.93 | 9414.11 | 12751.9 | 0.41 | 1.59 | 12.4 | 12.729 | 1 | 1 | 2270 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1604390.2498 | 90559.9435 | 5018.6379 | 9531.9068 | 81028.0367 | 13736.3533 | 0.086489 | -106068.4792 | 106068.4792
C | Xist Rating 1134 | -67.27 | 741.605 | 150.277 | 35.6 | 2177.32 | 9388.18 | 12686.2 | 0.41 | 1.58 | 12.395 | 12.637 | 1 | 1 | 2280 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1614711.3986 | 91317.4101 | 5062.9524 | 9573.8976 | 81743.5126 | 13642.8808 | 0.08687 | -105346.7095 | 105346.7095
C | Xist Rating 1135 | -67.04 | 748.437 | 150.277 | 35.6 | 2174.06 | 9377.76 | 12606.9 | 0.41 | 1.56 | 12.391 | 12.521 | 1 | 1 | 2290 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1627146.9442 | 92078.0217 | 5107.4617 | 9615.8883 | 82462.1334 | 13524.5246 | 0.087251 | -104432.7943 | 104432.7943
C | Xist Rating 1136 | -66.88 | 753.262 | 150.277 | 35.6 | 2171.51 | 9362.22 | 12557 | 0.4 | 1.56 | 12.386 | 12.454 | 1 | 1 | 2300 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1635715.9656 | 92841.7783 | 5152.1657 | 9657.8791 | 83183.8992 | 13444.2416 | 0.087632 | -103812.8698 | 103812.8698
| Xist Rating 1137 | -66.73 | 758.353 | 150.277 | 35.6 | 2168.18 | 9331.95 | 12507.6 | 0.4 | 1.55 | 12.383 | 12.391 | 1 | 1 | 2310 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1644245.8075 | 93608.6798 | 5197.0645 | 9699.8699 | 83908.8099 | 13380.9127 | 0.088013 | -103323.8611 | 103323.8611
| Xist Rating 1138 | -66.05 | 777.501 | 150.278 | 35.6 | 2158.68 | 9305.69 | 12277.1 | 0.4 | 1.51 | 12.422 | 12.037 | 1 | 1 | 2320 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1678375.8587 | 94378.7263 | 5242.1582 | 9741.8607 | 84636.8656 | 13017.1268 | 0.088394 | -100514.8029 | 100514.8029
| Xist Rating 1139 | -65.86 | 783.493 | 150.278 | 35.6 | 2155.43 | 9285.4 | 12216.8 | 0.39 | 1.5 | 12.419 | 11.957 | 1 | 1 | 2330 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1688764.317 | 95151.9177 | 5287.4466 | 9783.8514 | 85368.0662 | 12923.1783 | 0.088775 | -99789.3571 | 99789.3571
| Xist Rating 1140 | -65.67 | 789.461 | 150.278 | 35.6 | 2152.28 | 9266.63 | 12157.2 | 0.39 | 1.49 | 12.412 | 11.877 | 1 | 1 | 2340 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1699141.1211 | 95928.254 | 5332.9298 | 9825.8422 | 86102.4118 | 12841.9831 | 0.089156 | -99162.3895 | 99162.3895
| Xist Rating 1141 | -65.5 | 794.964 | 150.277 | 35.6 | 2149.38 | 9248.07 | 12104.7 | 0.38 | 1.49 | 12.408 | 11.81 | 1 | 1 | 2350 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1708679.7223 | 96707.7353 | 5378.6078 | 9867.833 | 86839.9023 | 12761.3389 | 0.089537 | -98539.6761 | 98539.6761
| Xist Rating 1142 | -65.28 | 801.541 | 150.277 | 35.6 | 2146.07 | 9230.43 | 12039.8 | 0.38 | 1.48 | 12.404 | 11.724 | 1 | 1 | 2360 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1720163.0939 | 97490.3616 | 5424.4805 | 9909.8238 | 87580.5378 | 12673.9807 | 0.089918 | -97865.1195 | 97865.1195
| Xist Rating 1143 | -64.67 | 819.221 | 150.278 | 35.6 | 2137.69 | 9207.64 | 11846.8 | 0.38 | 1.45 | 12.44 | 11.443 | 1 | 1 | 2370 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1751240.5395 | 98276.1328 | 5470.5481 | 9951.8146 | 88324.3182 | 12385.7288 | 0.090299 | -95639.3144 | 95639.3144
| Xist Rating 1144 | -64.48 | 825.428 | 150.278 | 35.6 | 2134.38 | 9184.98 | 11791.1 | 0.37 | 1.44 | 12.435 | 11.373 | 1 | 1 | 2380 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1761777.0146 | 99065.0489 | 5516.8105 | 9993.8053 | 89071.2436 | 12301.6841 | 0.09068 | -94990.3441 | 94990.3441
| Xist Rating 1145 | -64.27 | 831.56 | 150.278 | 35.6 | 2132.21 | 9187.6 | 11730 | 0.37 | 1.43 | 12.428 | 11.292 | 1 | 1 | 2390 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1773060.5476 | 99857.11 | 5563.2676 | 10035.7961 | 89821.3139 | 12219.3507 | 0.091061 | -94354.5868 | 94354.5868
C | Xist Rating 1146 | -60.75 | 954.002 | 150.278 | 35.6 | 2043.11 | 8459.97 | 10538.2 | 0.4 | 1.25 | 12.431 | 9.663 | 1 | 1 | 2400 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1949131.0262 | 100652.3161 | 5609.9196 | 10077.7869 | 90574.5292 | 10569.9368 | 0.091442 | -81618.2505 | 81618.2505
C | Xist Rating 1147 | -60.41 | 955.448 | 150.278 | 35.6 | 2058.27 | 8726.34 | 10538 | 0.39 | 1.25 | 12.424 | 9.672 | 1 | 1 | 2410 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1966569.955 | 101450.6671 | 5656.7663 | 10119.7777 | 91330.8894 | 10567.7884 | 0.091823 | -81601.6607 | 81601.6607
C | Xist Rating 1148 | -60.38 | 956.849 | 150.278 | 35.6 | 2057.95 | 8720.5 | 10538 | 0.39 | 1.25 | 12.464 | 9.683 | 1 | 1 | 2420 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1969147.3995 | 102252.163 | 5703.8078 | 10161.7685 | 92090.3946 | 10583.076 | 0.092204 | -81719.7076 | 81719.7076
C | Xist Rating 1149 | -60.01 | 958.206 | 150.278 | 35.6 | 2074.84 | 9032.23 | 10537.9 | 0.39 | 1.25 | 12.458 | 9.692 | 1 | 1 | 2430 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1988124.137 | 103056.8039 | 5751.0441 | 10203.7592 | 92853.0447 | 10594.3465 | 0.092585 | -81806.7355 | 81806.7355
C | Xist Rating 1150 | -60 | 959.577 | 150.278 | 35.6 | 2073.63 | 9009.2 | 10537.9 | 0.38 | 1.25 | 12.451 | 9.703 | 1 | 1 | 2440 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1989807.6545 | 103864.5897 | 5798.4752 | 10245.75 | 93618.8397 | 10594.0313 | 0.092966 | -81804.3019 | 81804.3019
C | Xist Rating 1151 | -59.98 | 960.903 | 150.278 | 35.6 | 2072.79 | 8993.36 | 10537.9 | 0.38 | 1.25 | 12.449 | 9.714 | 1 | 1 | 2450 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1991750.1294 | 104675.5205 | 5846.1011 | 10287.7408 | 94387.7798 | 10607.4922 | 0.093347 | -81908.2429 | 81908.2429
C | Xist Rating 1152 | -59.96 | 962.375 | 150.278 | 35.6 | 2071.61 | 8971.33 | 10537.9 | 0.37 | 1.25 | 12.445 | 9.725 | 1 | 1 | 2460 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1993665.6738 | 105489.5963 | 5893.9217 | 10329.7316 | 95159.8647 | 10607.1456 | 0.093728 | -81905.5668 | 81905.5668
C | Xist Rating 1153 | -59.91 | 963.729 | 150.278 | 35.6 | 2072.02 | 8978.91 | 10537.8 | 0.36 | 1.25 | 12.481 | 9.736 | 1 | 1 | 2470 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1996865.7626 | 106306.817 | 5941.9372 | 10371.7223 | 95935.0946 | 10608.2893 | 0.094109 | -81914.3979 | 81914.3979
C | Xist Rating 1154 | -59.89 | 965.076 | 150.278 | 35.6 | 2071.34 | 8966.29 | 10537.9 | 0.36 | 1.25 | 12.475 | 9.746 | 1 | 1 | 2480 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 1999000.5218 | 107127.1826 | 5990.1474 | 10413.7131 | 96713.4695 | 10620.4482 | 0.09449 | -82008.2858 | 82008.2858
C | Xist Rating 1155 | -59.87 | 966.474 | 150.278 | 35.6 | 2070.69 | 8954.11 | 10537.8 | 0.35 | 1.25 | 12.469 | 9.757 | 1 | 1 | 2490 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2001268.0471 | 107950.6932 | 6038.5525 | 10455.7039 | 97494.9893 | 10619.7266 | 0.094871 | -82002.7138 | 82002.7138
C | Xist Rating 1156 | -59.85 | 967.459 | 150.278 | 35.6 | 2070.74 | 8954.98 | 10537.8 | 0.35 | 1.25 | 12.465 | 9.765 | 1 | 1 | 2500 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2003356.0497 | 108777.3487 | 6087.1523 | 10497.6947 | 98279.6541 | 10629.8339 | 0.095252 | -82080.7598 | 82080.7598
C | Xist Rating 1157 | -59.82 | 969.309 | 150.278 | 35.6 | 2069.11 | 8924.66 | 10537.8 | 0.34 | 1.25 | 12.461 | 9.778 | 1 | 1 | 2510 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2005606.945 | 109607.1492 | 6135.9469 | 10539.6855 | 99067.4638 | 10631.1126 | 0.095633 | -82090.6336 | 82090.6336
C | Xist Rating 1158 | -59.8 | 970.763 | 150.278 | 35.6 | 2068.4 | 8911.46 | 10537.8 | 0.34 | 1.25 | 12.507 | 9.789 | 1 | 1 | 2520 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2007926.1892 | 110440.0947 | 6184.9363 | 10581.6762 | 99858.4184 | 10646.2019 | 0.096014 | -82207.1488 | 82207.1488
C | Xist Rating 1159 | -59.77 | 972.101 | 150.278 | 35.6 | 2067.71 | 8898.69 | 10537.8 | 0.33 | 1.25 | 12.501 | 9.799 | 1 | 1 | 2530 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2010022.9587 | 111276.185 | 6234.1205 | 10623.667 | 100652.518 | 10644.0847 | 0.096395 | -82190.8005 | 82190.8005
C | Xist Rating 1160 | -59.75 | 973.252 | 150.278 | 35.6 | 2067.33 | 8891.43 | 10538 | 0.33 | 1.25 | 12.496 | 9.809 | 1 | 1 | 2540 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2012033.0572 | 112115.4204 | 6283.4995 | 10665.6578 | 101449.7626 | 10656.131 | 0.096776 | -82283.8187 | 82283.8187
C | Xist Rating 1161 | -59.75 | 974.798 | 150.278 | 35.6 | 2065.46 | 8856.97 | 10537.9 | 0.32 | 1.25 | 12.492 | 9.82 | 1 | 1 | 2550 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2013406.2771 | 112957.8007 | 6333.0732 | 10707.6486 | 102250.1521 | 10654.9733 | 0.097157 | -82274.8794 | 82274.8794
C | Xist Rating 1162 | -59.73 | 976.247 | 150.278 | 35.6 | 2064.22 | 8834.2 | 10537.9 | 0.32 | 1.25 | 12.489 | 9.83 | 1 | 1 | 2560 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2015188.5823 | 113803.3259 | 6382.8418 | 10749.6394 | 103053.6865 | 10667.04 | 0.097538 | -82368.055 | 82368.055
C | Xist Rating 1163 | -59.71 | 977.636 | 150.278 | 35.6 | 2063.47 | 8820.48 | 10537.9 | 0.31 | 1.25 | 12.49 | 9.841 | 1 | 1 | 2570 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2017322.5569 | 114651.9961 | 6432.8051 | 10791.6301 | 103860.3659 | 10665.9033 | 0.097919 | -82359.2781 | 82359.2781
C | Xist Rating 1164 | -59.69 | 979.002 | 150.278 | 35.6 | 2062.64 | 8805.53 | 10537.9 | 0.31 | 1.25 | 12.525 | 9.851 | 1 | 1 | 2580 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2019328.6853 | 115503.8112 | 6482.9633 | 10833.6209 | 104670.1903 | 10679.2786 | 0.0983 | -82462.5588 | 82462.5588
C | Xist Rating 1165 | -59.67 | 980.362 | 150.278 | 35.6 | 2061.54 | 8785.47 | 10537.9 | 0.3 | 1.25 | 12.52 | 9.861 | 1 | 1 | 2590 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2021055.4775 | 116358.7713 | 6533.3162 | 10875.6117 | 105483.1596 | 10676.6889 | 0.098681 | -82442.5616 | 82442.5616
C | Xist Rating 1166 | -59.66 | 981.539 | 150.278 | 35.6 | 2060.65 | 8769.24 | 10537.9 | 0.3 | 1.25 | 12.514 | 9.87 | 1 | 1 | 2600 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2022608.3403 | 117216.8763 | 6583.8639 | 10917.6025 | 106299.2738 | 10687.5092 | 0.099062 | -82526.1132 | 82526.1132
C | Xist Rating 1167 | -59.64 | 983.226 | 150.278 | 35.6 | 2059.21 | 8743.35 | 10537.8 | 0.3 | 1.25 | 12.511 | 9.882 | 1 | 1 | 2610 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2024668.8115 | 118078.1263 | 6634.6064 | 10959.5932 | 107118.533 | 10701.5487 | 0.099443 | -82634.5225 | 82634.5225
C | Xist Rating 1168 | -59.62 | 984.623 | 150.278 | 35.6 | 2058.38 | 8728.41 | 10537.9 | 0.29 | 1.25 | 12.509 | 9.892 | 1 | 1 | 2620 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2026728.2907 | 118942.5212 | 6685.5437 | 11001.584 | 107940.9372 | 10698.855 | 0.099824 | -82613.7223 | 82613.7223
C | Xist Rating 1169 | -59.6 | 986.049 | 150.278 | 35.6 | 2057.48 | 8712.24 | 10537.9 | 0.29 | 1.25 | 12.545 | 9.902 | 1 | 1 | 2630 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2028776.0965 | 119810.0611 | 6736.6758 | 11043.5748 | 108766.4863 | 10712.0968 | 0.10021 | -82715.972 | 82715.972
C | Xist Rating 1170 | -59.56 | 987.295 | 150.278 | 35.6 | 2057.61 | 8714.45 | 10537.8 | 0.28 | 1.25 | 12.541 | 9.912 | 1 | 1 | 2640 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2031468.065 | 120680.7459 | 6788.0027 | 11085.5656 | 109595.1803 | 10709.1346 | 0.10059 | -82693.0987 | 82693.0987
C | Xist Rating 1171 | -59.54 | 988.798 | 150.278 | 35.6 | 2056.49 | 8694.44 | 10537.8 | 0.28 | 1.25 | 12.537 | 9.922 | 1 | 1 | 2650 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2033453.199 | 121554.5757 | 6839.5243 | 11127.5564 | 110427.0193 | 10720.9606 | 0.10097 | -82784.4156 | 82784.4156
C | Xist Rating 1172 | -59.51 | 990.139 | 150.278 | 35.6 | 2056.35 | 8691.91 | 10537.8 | 0.28 | 1.25 | 12.535 | 9.932 | 1 | 1 | 2660 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2036072.3326 | 122431.5504 | 6891.2408 | 11169.5471 | 111262.0032 | 10732.8523 | 0.10135 | -82876.2403 | 82876.2403
C | Xist Rating 1173 | -59.5 | 991.526 | 150.278 | 35.6 | 2054.92 | 8666.54 | 10537.8 | 0.27 | 1.25 | 12.531 | 9.942 | 1 | 1 | 2670 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2037506.6079 | 123311.67 | 6943.152 | 11211.5379 | 112100.1321 | 10729.6791 | 0.10173 | -82851.7382 | 82851.7382
C | Xist Rating 1174 | -59.43 | 992.943 | 150.278 | 35.6 | 2056.72 | 8698.7 | 10537.8 | 0.27 | 1.25 | 12.57 | 9.952 | 1 | 1 | 2680 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2042205.727 | 124194.9347 | 6995.258 | 11253.5287 | 112941.406 | 10742.8457 | 0.10211 | -82953.4067 | 82953.4067
C | Xist Rating 1175 | -59.41 | 994.32 | 150.278 | 35.6 | 2056.38 | 8692.61 | 10537.7 | 0.27 | 1.25 | 12.561 | 9.962 | 1 | 1 | 2690 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2044699.7616 | 125081.3442 | 7047.5588 | 11295.5195 | 113785.8247 | 10754.459 | 0.10249 | -83043.0814 | 83043.0814
C | Xist Rating 1176 | -59.36 | 995.52 | 150.278 | 35.6 | 2057.05 | 8704.46 | 10537.8 | 0.26 | 1.25 | 12.559 | 9.971 | 1 | 1 | 2700 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2047834.416 | 125970.8987 | 7100.0544 | 11337.5103 | 114633.3885 | 10750.0606 | 0.10287 | -83009.1183 | 83009.1183
C | Xist Rating 1177 | -59.3 | 997.177 | 150.278 | 35.6 | 2057.67 | 8715.63 | 10537.8 | 0.26 | 1.25 | 12.559 | 9.982 | 1 | 1 | 2710 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2051861.1976 | 126863.5982 | 7152.7448 | 11379.501 | 115484.0972 | 10762.9477 | 0.10325 | -83108.6296 | 83108.6296
C | Xist Rating 1178 | -59.28 | 998.521 | 150.278 | 35.6 | 2056.85 | 8700.97 | 10537.8 | 0.26 | 1.25 | 12.555 | 9.992 | 1 | 1 | 2720 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2053807.9188 | 127759.4426 | 7205.63 | 11421.4918 | 116337.9508 | 10774.6696 | 0.10363 | -83199.1427 | 83199.1427
C | Xist Rating 1179 | -59.19 | 999.843 | 150.278 | 35.6 | 2059.95 | 8756.64 | 10537.9 | 0.25 | 1.25 | 12.6 | 10.001 | 1 | 1 | 2730 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2059626.5878 | 128658.432 | 7258.71 | 11463.4826 | 117194.9494 | 10771.4923 | 0.10402 | -83174.6081 | 83174.6081
C | Xist Rating 1180 | -59.11 | 1001.13 | 150.278 | 35.6 | 2062.09 | 8795.38 | 10538 | 0.25 | 1.25 | 12.601 | 10.011 | 1 | 1 | 2740 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2064420.1617 | 129560.5663 | 7311.9847 | 11505.4734 | 118055.0929 | 10783.3199 | 0.1044 | -83265.9382 | 83265.9382
C | Xist Rating 1181 | -58.92 | 1002.67 | 150.278 | 35.6 | 2069.74 | 8936.03 | 10538.2 | 0.24 | 1.25 | 12.616 | 10.022 | 1 | 1 | 2750 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2075266.2058 | 130465.8456 | 7365.4543 | 11547.4642 | 118918.3814 | 10781.0663 | 0.10478 | -83248.5362 | 83248.5362
C | Xist Rating 1182 | -59.11 | 1004.1 | 150.278 | 35.6 | 2057.94 | 8720.27 | 10538 | 0.24 | 1.25 | 12.587 | 10.031 | 1 | 1 | 2760 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2066377.554 | 131374.2698 | 7419.1186 | 11589.4549 | 119784.8148 | 10790.9089 | 0.10516 | -83324.5384 | 83324.5384
C | Xist Rating 1183 | -58.74 | 1005.33 | 150.278 | 35.6 | 2075.29 | 9040.32 | 10538.2 | 0.24 | 1.25 | 12.623 | 10.041 | 1 | 1 | 2770 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2086351.2957 | 132285.8389 | 7472.9777 | 11631.4457 | 120654.3932 | 10803.7208 | 0.10554 | -83423.4682 | 83423.4682
C | Xist Rating 1184 | -58.48 | 1006.88 | 150.278 | 35.6 | 2086.55 | 9257.92 | 10538.3 | 0.23 | 1.25 | 12.691 | 10.052 | 1 | 1 | 2780 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2100905.464 | 133200.553 | 7527.0316 | 11673.4365 | 121527.1165 | 10802.7214 | 0.10592 | -83415.7508 | 83415.7508
C | Xist Rating 1185 | -58.34 | 1008.29 | 150.278 | 35.6 | 2091.86 | 9363.34 | 10538.3 | 0.23 | 1.25 | 12.706 | 10.062 | 1 | 1 | 2790 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2109201.5194 | 134118.4121 | 7581.2803 | 11715.4273 | 122402.9848 | 10814.8462 | 0.1063 | -83509.3756 | 83509.3756
C | Xist Rating 1186 | -58.22 | 1009.27 | 150.278 | 35.6 | 2097.01 | 9467.44 | 10538.4 | 0.23 | 1.25 | 12.719 | 10.07 | 1 | 1 | 2800 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2116449.2827 | 135039.4161 | 7635.7238 | 11757.418 | 123281.998 | 10824.8394 | 0.10668 | -83586.5405 | 83586.5405
C | Xist Rating 1187 | -58.15 | 1011.01 | 150.278 | 35.6 | 2097.88 | 9485.32 | 10538.4 | 0.22 | 1.25 | 12.725 | 10.081 | 1 | 1 | 2810 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2120977.6588 | 135963.565 | 7690.3621 | 11799.4088 | 124164.1562 | 10821.7199 | 0.10706 | -83562.4528 | 83562.4528
C | Xist Rating 1188 | -58.07 | 1012.49 | 150.278 | 35.6 | 2099.49 | 9518.13 | 10538.4 | 0.22 | 1.25 | 12.732 | 10.091 | 1 | 1 | 2820 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2125712.6301 | 136890.8589 | 7745.1952 | 11841.3996 | 125049.4593 | 10833.5544 | 0.10744 | -83653.8358 | 83653.8358
C | Xist Rating 1189 | -58.01 | 1013.86 | 150.278 | 35.6 | 2100.96 | 9548.67 | 10538.3 | 0.22 | 1.25 | 12.777 | 10.101 | 1 | 1 | 2830 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2130079.3056 | 137821.2978 | 7800.223 | 11883.3904 | 125937.9074 | 10846.4508 | 0.10783 | -83753.4183 | 83753.4183
C | Xist Rating 1190 | -57.94 | 1015.17 | 150.278 | 35.6 | 2102.74 | 9585.54 | 10538.3 | 0.21 | 1.25 | 12.78 | 10.11 | 1 | 1 | 2840 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2134638.5658 | 138754.8816 | 7855.4457 | 11925.3812 | 126829.5004 | 10840.8721 | 0.10821 | -83710.3411 | 83710.3411
C | Xist Rating 1191 | -57.87 | 1016.62 | 150.278 | 35.6 | 2104.15 | 9614.92 | 10538.3 | 0.21 | 1.25 | 12.784 | 10.12 | 1 | 1 | 2850 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2139120.973 | 139691.6103 | 7910.8631 | 11967.3719 | 127724.2384 | 10852.5674 | 0.10859 | -83800.6491 | 83800.6491
C | Xist Rating 1192 | -57.82 | 1018.02 | 150.278 | 35.6 | 2104.88 | 9630.17 | 10538.3 | 0.21 | 1.25 | 12.784 | 10.129 | 1 | 1 | 2860 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2142809.9376 | 140631.484 | 7966.4753 | 12009.3627 | 128622.1213 | 10863.1173 | 0.10897 | -83882.1123 | 83882.1123
C | Xist Rating 1193 | -57.76 | 1019.21 | 150.278 | 35.6 | 2106.37 | 9661.36 | 10538.2 | 0.21 | 1.25 | 12.789 | 10.138 | 1 | 1 | 2870 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2146833.3677 | 141574.5027 | 8022.2824 | 12051.3535 | 129523.1492 | 10873.8022 | 0.10935 | -83964.6186 | 83964.6186
C | Xist Rating 1194 | -57.7 | 1020.72 | 150.278 | 35.5 | 2107.24 | 9679.75 | 10538.2 | 0.2 | 1.25 | 12.833 | 10.148 | 1 | 1 | 2880 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2150902.0128 | 142520.6663 | 8078.2842 | 12093.3443 | 130427.322 | 10870.0172 | 0.10973 | -83935.3912 | 83935.3912
C | Xist Rating 1195 | -57.64 | 1022.07 | 150.278 | 35.5 | 2108.47 | 9705.84 | 10538.2 | 0.2 | 1.25 | 12.832 | 10.157 | 1 | 1 | 2890 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2155003.9329 | 143469.9748 | 8134.4807 | 12135.3351 | 131334.6398 | 10880.4882 | 0.11011 | -84016.2458 | 84016.2458
C | Xist Rating 1196 | -57.58 | 1023.45 | 150.278 | 35.5 | 2109.74 | 9732.78 | 10538.1 | 0.2 | 1.25 | 12.832 | 10.166 | 1 | 1 | 2900 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2159213.403 | 144422.4283 | 8190.8721 | 12177.3258 | 132245.1025 | 10890.9851 | 0.11049 | -84097.2999 | 84097.2999
C | Xist Rating 1197 | -57.51 | 1024.99 | 150.278 | 35.5 | 2111.13 | 9762.42 | 10538.1 | 0.2 | 1.25 | 12.832 | 10.176 | 1 | 1 | 2910 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2163887.1387 | 145378.0268 | 8247.4583 | 12219.3166 | 133158.7102 | 10902.5204 | 0.11087 | -84186.3729 | 84186.3729
C | Xist Rating 1198 | -57.41 | 1026.38 | 150.278 | 35.5 | 2114.19 | 9828.44 | 10538 | 0.2 | 1.25 | 12.835 | 10.186 | 1 | 1 | 2920 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2169962.3322 | 146336.7702 | 8304.2393 | 12261.3074 | 134075.4628 | 10914.1343 | 0.11125 | -84276.0523 | 84276.0523
C | Xist Rating 1199 | -57.35 | 1027.77 | 150.278 | 35.5 | 2115.48 | 9856.13 | 10538 | 0.19 | 1.25 | 12.877 | 10.195 | 1 | 1 | 2930 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2174226.8796 | 147298.6585 | 8361.215 | 12303.2982 | 134995.3603 | 10908.8225 | 0.11164 | -84235.036 | 84235.036
C | Xist Rating 1200 | -57.32 | 1029.13 | 150.278 | 35.5 | 2114.79 | 9841.21 | 10538 | 0.19 | 1.25 | 12.872 | 10.204 | 1 | 1 | 2940 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2176393.8327 | 148263.6918 | 8418.3855 | 12345.2889 | 135918.4028 | 10919.1405 | 0.11202 | -84314.7087 | 84314.7087
C | Xist Rating 1201 | -57.3 | 1030.54 | 150.278 | 35.5 | 2114.06 | 9825.5 | 10538 | 0.19 | 1.25 | 12.868 | 10.213 | 1 | 1 | 2950 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2178623.3924 | 149231.87 | 8475.7509 | 12387.2797 | 136844.5903 | 10929.4828 | 0.1124 | -84394.5688 | 84394.5688
C | Xist Rating 1204 | -57.3 | 1034.52 | 150.278 | 35.5 | 2110.66 | 9753.57 | 10536.9 | 0.18 | 1.25 | 12.917 | 10.238 | 1 | 1 | 2980 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2183519.9832 | 152155.2744 | 8649.0156 | 12513.2521 | 139642.0224 | 10942.7224 | 0.11354 | -84496.8019 | 84496.8019
C | Xist Rating 1205 | -57.29 | 1036.08 | 150.278 | 35.5 | 2109.43 | 9727.85 | 10536.5 | 0.18 | 1.25 | 12.918 | 10.248 | 1 | 1 | 2990 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2185538.2344 | 153136.0325 | 8707.16 | 12555.2428 | 140580.7896 | 10954.1737 | 0.11392 | -84585.2259 | 84585.2259
C | Xist Rating 1206 | -57.31 | 1037.51 | 150.278 | 35.5 | 2107.8 | 9693.88 | 10535.7 | 0.18 | 1.25 | 12.927 | 10.257 | 1 | 1 | 3000 | 152.4 | 2 | 1.5 | 19.05 | 1.3333 | 7 | E | Rod | 2186863.578 | 154119.9355 | 8765.4993 | 12597.2336 | 141522.7018 | 10964.7803 | 0.1143 | -84667.1273 | 84667.1273
C | Xist Rating 1207 | -95.12 | 91.561 | 150.28 | 35.8 | 2413.58 | 7538.53 | 58745.8 | 2.44 | 10.95 | 13.292 | 328.538 | 1 | 1 | 1000 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 220989.7984 | 21252.0774 | 973.9444 | 4479.0164 | 16773.061 | 342639.9681 | 0.038101 | -2645775.0099 | 2645775.0099
C | Xist Rating 1208 | -95.08 | 92.55 | 150.28 | 35.8 | 2410.48 | 7517.21 | 58284.2 | 2.42 | 10.85 | 13.298 | 322.428 | 1 | 1 | 1010 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 223089.924 | 21634.006 | 993.5206 | 4523.8066 | 17110.1995 | 336297.9025 | 0.038482 | -2596803.2606 | 2596803.2606
C | Xist Rating 1209 | -94.7 | 99.84 | 150.28 | 35.8 | 2404.88 | 7529.91 | 54967.5 | 2.43 | 10.07 | 13.352 | 279.408 | 1 | 1 | 1020 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 240103.2192 | 22019.2893 | 1013.2917 | 4568.5967 | 17450.6926 | 291648.2052 | 0.038863 | -2252030.1329 | 2252030.1329
C | Xist Rating 1210 | -94.64 | 101.964 | 150.279 | 35.8 | 2385.76 | 7361.98 | 54179.3 | 2.35 | 9.89 | 13.141 | 270.215 | 1 | 1 | 1030 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 243261.6326 | 22407.9273 | 1033.2576 | 4613.3869 | 17794.5404 | 282043.6233 | 0.039244 | -2177866.0979 | 2177866.0979
C | Xist Rating 1211 | -94.55 | 103.028 | 150.279 | 35.8 | 2401.13 | 7518.92 | 53795.3 | 2.28 | 9.8 | 13.099 | 265.832 | 1 | 1 | 1040 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 247383.6216 | 22799.9198 | 1053.4182 | 4658.1771 | 18141.7427 | 277458.381 | 0.039625 | -2142460.0717 | 2142460.0717
C | Xist Rating 1212 | -94.43 | 105.03 | 150.279 | 35.8 | 2410.14 | 7625.53 | 53044.9 | 2.23 | 9.63 | 13.068 | 257.111 | 1 | 1 | 1050 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 253137.0042 | 23195.2669 | 1073.7737 | 4702.9672 | 18492.2997 | 268380.944 | 0.040006 | -2072366.5095 | 2072366.5095
C | Xist Rating 1213 | -94.35 | 106.075 | 150.279 | 35.8 | 2421.23 | 7746.72 | 52677.9 | 2.18 | 9.54 | 13.05 | 253.007 | 1 | 1 | 1060 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 256831.9723 | 23593.9687 | 1094.3239 | 4747.7574 | 18846.2113 | 264099.0989 | 0.040387 | -2039303.237 | 2039303.237
C | Xist Rating 1214 | -93.98 | 114.014 | 150.279 | 35.8 | 2401.51 | 7619.43 | 49858.7 | 2.17 | 8.9 | 13.005 | 221.454 | 1 | 1 | 1070 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 273805.7611 | 23996.025 | 1115.0689 | 4792.5475 | 19203.4775 | 231333.1679 | 0.040768 | -1786293.4026 | 1786293.4026
C | Xist Rating 1215 | -93.89 | 115.584 | 150.279 | 35.8 | 2405.75 | 7675.44 | 49381.6 | 2.12 | 8.79 | 12.951 | 216.572 | 1 | 1 | 1080 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 278066.208 | 24401.436 | 1136.0087 | 4837.3377 | 19564.0983 | 226238.8474 | 0.041149 | -1746956.4105 | 1746956.4105
C | Xist Rating 1216 | -93.79 | 117.667 | 150.279 | 35.8 | 2403.05 | 7665.29 | 48761.8 | 2.06 | 8.65 | 12.876 | 210.29 | 1 | 1 | 1090 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 282759.6844 | 24810.2016 | 1157.1433 | 4882.1279 | 19928.0737 | 219681.7925 | 0.04153 | -1696324.5705 | 1696324.5705
C | Xist Rating 1217 | -93.7 | 119.205 | 150.279 | 35.8 | 2408.99 | 7739.32 | 48308.7 | 2.03 | 8.55 | 12.86 | 205.743 | 1 | 1 | 1100 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 287163.6529 | 25222.3218 | 1178.4727 | 4926.918 | 20295.4038 | 214950.9819 | 0.041911 | -1659794.5049 | 1659794.5049
C | Xist Rating 1218 | -93.66 | 120.437 | 150.278 | 35.8 | 2401.37 | 7669.92 | 48010.6 | 1.96 | 8.49 | 12.723 | 203.052 | 1 | 1 | 1110 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 289213.7987 | 25637.7966 | 1199.9969 | 4971.7082 | 20666.0884 | 212109.9344 | 0.042292 | -1637856.6892 | 1637856.6892
C | Xist Rating 1219 | -93.21 | 129.191 | 150.279 | 35.8 | 2399.27 | 7728.36 | 45447.9 | 2 | 7.92 | 12.857 | 177.673 | 1 | 1 | 1120 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 309964.0906 | 26056.626 | 1221.7158 | 5016.4984 | 21040.1277 | 185804.0652 | 0.042673 | -1434729.7399 | 1434729.7399
C | Xist Rating 1220 | -93.16 | 130.376 | 150.278 | 35.8 | 2398.63 | 7730.44 | 45189.8 | 1.94 | 7.86 | 12.77 | 175.492 | 1 | 1 | 1130 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 312723.7849 | 26478.8101 | 1243.6296 | 5061.2885 | 21417.5215 | 183503.0034 | 0.043054 | -1416961.5513 | 1416961.5513
C | Xist Rating 1221 | -93.05 | 132.53 | 150.278 | 35.8 | 2398.17 | 7742.9 | 44682.1 | 1.88 | 7.75 | 12.653 | 171.01 | 1 | 1 | 1140 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 317829.4701 | 26904.3487 | 1265.7381 | 5106.0787 | 21798.27 | 178809.1654 | 0.043435 | -1380716.9783 | 1380716.9783
C | Xist Rating 1222 | -92.92 | 134.62 | 150.278 | 35.8 | 2406.58 | 7849.02 | 44187.9 | 1.83 | 7.64 | 12.626 | 166.656 | 1 | 1 | 1150 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 323973.7996 | 27333.242 | 1288.0414 | 5150.8689 | 22182.3731 | 174263.047 | 0.043816 | -1345613.0566 | 1345613.0566
C | Xist Rating 1223 | -92.82 | 136.789 | 150.278 | 35.8 | 2404.61 | 7845.66 | 43705.3 | 1.78 | 7.53 | 12.56 | 162.531 | 1 | 1 | 1160 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 328924.1973 | 27765.4898 | 1310.5395 | 5195.659 | 22569.8308 | 169950.664 | 0.044197 | -1312313.9783 | 1312313.9783
C | Xist Rating 1224 | -92.41 | 144.715 | 150.278 | 35.8 | 2404.94 | 7922.47 | 41833.8 | 1.8 | 7.13 | 12.644 | 146.236 | 1 | 1 | 1170 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 348030.8921 | 28201.0923 | 1333.2324 | 5240.4492 | 22960.6431 | 153059.4574 | 0.044578 | -1181884.5585 | 1181884.5585
C | Xist Rating 1225 | -92.35 | 145.401 | 150.278 | 35.8 | 2412.05 | 8004.65 | 41726.3 | 1.75 | 7.11 | 12.602 | 145.513 | 1 | 1 | 1180 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 350714.4821 | 28640.0494 | 1356.1201 | 5285.2394 | 23354.8101 | 152281.4981 | 0.044959 | -1175877.3631 | 1175877.3631
C | Xist Rating 1226 | -92.18 | 149.567 | 150.278 | 35.8 | 2399.73 | 7905.79 | 40887 | 1.7 | 6.93 | 12.527 | 138.792 | 1 | 1 | 1190 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 358920.4169 | 29082.3611 | 1379.2026 | 5330.0295 | 23752.3316 | 145271.2243 | 0.04534 | -1121745.8866 | 1121745.8866
C | Xist Rating 1227 | -92.09 | 150.645 | 150.278 | 35.8 | 2411.05 | 8039.04 | 40683.5 | 1.67 | 6.88 | 12.532 | 137.239 | 1 | 1 | 1200 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 363212.6273 | 29528.0275 | 1402.4799 | 5374.8197 | 24153.2078 | 143648.2165 | 0.045721 | -1109213.4509 | 1109213.4509
C | Xist Rating 1228 | -92 | 152.883 | 150.278 | 35.8 | 2405.84 | 7999.41 | 40282.6 | 1.63 | 6.8 | 12.464 | 134.228 | 1 | 1 | 1210 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 367812.0367 | 29977.0484 | 1425.9519 | 5419.6098 | 24557.4385 | 140497.4788 | 0.046102 | -1084884.2896 | 1084884.2896
C | Xist Rating 1229 | -91.57 | 161.991 | 150.278 | 35.8 | 2393.12 | 7941.07 | 38539.1 | 1.63 | 6.43 | 12.494 | 120.786 | 1 | 1 | 1220 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 387663.9019 | 30429.4239 | 1449.6188 | 5464.4 | 24965.0239 | 126549.7639 | 0.046483 | -977183.7325 | 977183.7325
C | Xist Rating 1230 | -91.45 | 164.079 | 150.278 | 35.8 | 2398.86 | 8022.57 | 38184.2 | 1.6 | 6.35 | 12.488 | 118.242 | 1 | 1 | 1230 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 393602.5499 | 30885.1541 | 1473.4804 | 5509.1902 | 25375.9639 | 123895.7579 | 0.046864 | -956690.201 | 956690.201
C | Xist Rating 1231 | -91.35 | 166.307 | 150.278 | 35.8 | 2395.63 | 8004.15 | 37836.5 | 1.56 | 6.28 | 12.439 | 115.85 | 1 | 1 | 1240 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 398410.0384 | 31344.2389 | 1497.5369 | 5553.9803 | 25790.2585 | 121388.6126 | 0.047245 | -937330.6902 | 937330.6902
C | Xist Rating 1232 | -91.29 | 167.529 | 150.278 | 35.8 | 2396.63 | 8024.28 | 37665.3 | 1.53 | 6.24 | 12.402 | 114.751 | 1 | 1 | 1250 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 401505.0273 | 31806.6782 | 1521.7881 | 5598.7705 | 26207.9077 | 120231.9201 | 0.047626 | -928399.017 | 928399.017
C | Xist Rating 1233 | -91.14 | 170.685 | 150.277 | 35.8 | 2394.15 | 8023.03 | 37162.2 | 1.5 | 6.14 | 12.378 | 111.253 | 1 | 1 | 1260 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 408645.4928 | 32272.4722 | 1546.2341 | 5643.5607 | 26628.9116 | 116584.7113 | 0.048007 | -900236.2374 | 900236.2374
C | Xist Rating 1234 | -90.72 | 179.323 | 150.278 | 35.8 | 2388.96 | 8041.73 | 35778.4 | 1.5 | 5.85 | 12.43 | 101.674 | 1 | 1 | 1270 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 428395.4741 | 32741.6208 | 1570.8749 | 5688.3508 | 27053.27 | 106649.6979 | 0.048388 | -823520.6971 | 823520.6971
C | Xist Rating 1235 | -90.61 | 181.62 | 150.277 | 35.7 | 2389.21 | 8062.19 | 35478.4 | 1.46 | 5.79 | 12.394 | 99.814 | 1 | 1 | 1280 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 433928.3202 | 33214.1241 | 1595.7105 | 5733.141 | 27480.9831 | 104694.9056 | 0.048769 | -808426.3092 | 808426.3092
C | Xist Rating 1236 | -90.48 | 183.865 | 150.277 | 35.7 | 2393.41 | 8128.13 | 35184 | 1.42 | 5.73 | 12.387 | 97.988 | 1 | 1 | 1290 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 440064.3296 | 33689.9819 | 1620.7408 | 5777.9312 | 27912.0507 | 102777.4771 | 0.04915 | -793620.4348 | 793620.4348
C | Xist Rating 1237 | -90.29 | 186.999 | 150.277 | 35.7 | 2401.63 | 8251.17 | 34753 | 1.4 | 5.64 | 12.39 | 95.251 | 1 | 1 | 1300 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 449102.4084 | 34169.1943 | 1645.966 | 5822.7213 | 28346.473 | 99928.7998 | 0.049531 | -771623.7038 | 771623.7038
C | Xist Rating 1238 | -90.18 | 188.762 | 150.277 | 35.7 | 2407.11 | 8330.25 | 34541.8 | 1.36 | 5.59 | 12.366 | 94.011 | 1 | 1 | 1310 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 454370.8978 | 34651.7614 | 1671.3859 | 5867.5115 | 28784.2499 | 98617.8186 | 0.049912 | -761500.6548 | 761500.6548
C | Xist Rating 1239 | -89.76 | 197.498 | 150.277 | 35.7 | 2401.69 | 8346.75 | 33365 | 1.37 | 5.35 | 12.409 | 86.651 | 1 | 1 | 1320 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 474328.9716 | 35137.6831 | 1697.0007 | 5912.3016 | 29225.3814 | 90992.8112 | 0.050293 | -702622.3683 | 702622.3683
C | Xist Rating 1240 | -89.62 | 200.849 | 150.277 | 35.7 | 2395.96 | 8305.47 | 32981.9 | 1.33 | 5.28 | 12.346 | 84.459 | 1 | 1 | 1330 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 481226.17 | 35626.9593 | 1722.8102 | 5957.0918 | 29669.8675 | 88689.4563 | 0.050674 | -684836.4725 | 684836.4725
C | Xist Rating 1241 | -89.46 | 204.099 | 150.277 | 35.7 | 2396 | 8333.66 | 32608.7 | 1.31 | 5.2 | 12.327 | 82.325 | 1 | 1 | 1340 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 489021.204 | 36119.5902 | 1748.8145 | 6001.882 | 30117.7083 | 86464.3347 | 0.051055 | -667654.6732 | 667654.6732
C | Xist Rating 1242 | -89.36 | 205.878 | 150.277 | 35.7 | 2399.44 | 8389.34 | 32425.6 | 1.28 | 5.16 | 12.306 | 81.347 | 1 | 1 | 1350 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 493991.9083 | 36615.5757 | 1775.0136 | 6046.6721 | 30568.9036 | 85431.9167 | 0.051436 | -659682.615 | 659682.615
C | Xist Rating 1243 | -89.24 | 206.902 | 150.277 | 35.7 | 2415.67 | 8601.01 | 32304.7 | 1.27 | 5.14 | 12.329 | 80.668 | 1 | 1 | 1360 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 499806.9543 | 37114.9158 | 1801.4075 | 6091.4623 | 31023.4535 | 84728.1156 | 0.051817 | -654248.05 | 654248.05
C | Xist Rating 1244 | -88.72 | 219.505 | 150.277 | 35.7 | 2387.8 | 8369.33 | 30904.2 | 1.26 | 4.86 | 12.328 | 72.81 | 1 | 1 | 1370 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 524134.039 | 37617.6106 | 1827.9962 | 6136.2525 | 31481.3581 | 76566.965 | 0.052198 | -591229.8084 | 591229.8084
C | Xist Rating 1245 | -88.66 | 220.791 | 150.277 | 35.7 | 2388.21 | 8383.61 | 30795.8 | 1.23 | 4.84 | 12.307 | 72.304 | 1 | 1 | 1380 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 527295.2741 | 38123.6599 | 1854.7797 | 6181.0426 | 31942.6173 | 76023.9722 | 0.052579 | -587036.9617 | 587036.9617
C | Xist Rating 1246 | -88.52 | 223.617 | 150.277 | 35.7 | 2388.94 | 8415.67 | 30528.3 | 1.21 | 4.79 | 12.286 | 70.942 | 1 | 1 | 1390 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 534207.596 | 38633.0639 | 1881.7579 | 6225.8328 | 32407.2311 | 74599.4035 | 0.05296 | -576036.8196 | 576036.8196
C | Xist Rating 1247 | -88.39 | 226.44 | 150.277 | 35.7 | 2388.15 | 8429.06 | 30266.3 | 1.18 | 4.73 | 12.268 | 69.62 | 1 | 1 | 1400 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 540772.686 | 39145.8224 | 1908.931 | 6270.623 | 32875.1995 | 73208.7093 | 0.053341 | -565298.2475 | 565298.2475
C | Xist Rating 1248 | -88.24 | 229.751 | 150.277 | 35.7 | 2387.08 | 8443.5 | 29958.6 | 1.16 | 4.67 | 12.254 | 68.065 | 1 | 1 | 1410 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 548434.0171 | 39661.9356 | 1936.2988 | 6315.4131 | 33346.5225 | 71583.7993 | 0.053722 | -552751.1235 | 552751.1235
C | Xist Rating 1249 | -87.79 | 239.101 | 150.277 | 35.7 | 2382.38 | 8469.91 | 29052.8 | 1.17 | 4.49 | 12.304 | 63.406 | 1 | 1 | 1420 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 569629.4404 | 40181.4034 | 1963.8614 | 6360.2033 | 33821.2001 | 66763.3302 | 0.054103 | -515528.739 | 515528.739
C | Xist Rating 1250 | -87.72 | 241.121 | 150.277 | 35.7 | 2378.05 | 8429.16 | 28911.7 | 1.14 | 4.47 | 12.265 | 62.809 | 1 | 1 | 1430 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 573397.7941 | 40704.2258 | 1991.6188 | 6404.9934 | 34299.2324 | 66123.2893 | 0.054484 | -510586.5127 | 510586.5127
C | Xist Rating 1251 | -87.52 | 245.457 | 150.277 | 35.7 | 2375.27 | 8430.75 | 28543.2 | 1.12 | 4.4 | 12.253 | 61.043 | 1 | 1 | 1440 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 583026.6484 | 41230.4028 | 2019.571 | 6449.7836 | 34780.6192 | 64278.8675 | 0.054865 | -496344.3765 | 496344.3765
C | Xist Rating 1252 | -87.39 | 248.317 | 150.277 | 35.7 | 2374.59 | 8444.97 | 28318 | 1.1 | 4.35 | 12.238 | 60.013 | 1 | 1 | 1450 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 589651.065 | 41759.9344 | 2047.718 | 6494.5738 | 35265.3607 | 63198.3653 | 0.055246 | -488001.0248 | 488001.0248
C | Xist Rating 1253 | -87.27 | 249.979 | 150.277 | 35.7 | 2381.15 | 8542.51 | 28184.8 | 1.09 | 4.33 | 12.244 | 59.408 | 1 | 1 | 1460 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 595237.4959 | 42292.8207 | 2076.0598 | 6539.3639 | 35753.4567 | 62568.5269 | 0.055627 | -483137.5799 | 483137.5799
C | Xist Rating 1254 | -86.82 | 260.782 | 150.277 | 35.7 | 2365.02 | 8430.15 | 27311.4 | 1.08 | 4.16 | 12.257 | 55.337 | 1 | 1 | 1470 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 616754.6456 | 42829.0615 | 2104.5964 | 6584.1541 | 36244.9074 | 58339.6394 | 0.056008 | -450483.2315 | 450483.2315
C | Xist Rating 1255 | -86.65 | 264.136 | 150.277 | 35.7 | 2366.85 | 8480.79 | 27067.3 | 1.06 | 4.11 | 12.251 | 54.273 | 1 | 1 | 1480 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 625170.2916 | 43368.657 | 2133.3277 | 6628.9443 | 36739.7127 | 57223.9262 | 0.056389 | -441867.9895 | 441867.9895
C | Xist Rating 1256 | -86.47 | 266.999 | 150.277 | 35.7 | 2374.6 | 8604.41 | 26867.4 | 1.04 | 4.07 | 12.249 | 53.424 | 1 | 1 | 1490 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 634015.8254 | 43911.6071 | 2162.2539 | 6673.7344 | 37237.8726 | 56331.5585 | 0.05677 | -434977.3627 | 434977.3627
C | Xist Rating 1257 | -86.32 | 269.953 | 150.277 | 35.7 | 2376.62 | 8654.61 | 26671.1 | 1.02 | 4.03 | 12.238 | 52.61 | 1 | 1 | 1500 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 641575.6989 | 44457.9118 | 2191.3748 | 6718.5246 | 37739.3872 | 55474.7048 | 0.057151 | -428360.9661 | 428360.9661
C | Xist Rating 1258 | -86.13 | 273.335 | 150.277 | 35.7 | 2381.2 | 8744.44 | 26439.6 | 1 | 3.99 | 12.236 | 51.634 | 1 | 1 | 1510 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 650865.302 | 45007.5711 | 2220.6906 | 6763.3148 | 38244.2563 | 54450.0237 | 0.057532 | -420448.6502 | 420448.6502
C | Xist Rating 1259 | -85.61 | 283.821 | 150.277 | 35.7 | 2380.22 | 8830.17 | 25681.8 | 1.01 | 3.85 | 12.292 | 48.348 | 1 | 1 | 1520 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 675556.4206 | 45560.585 | 2250.2011 | 6808.1049 | 38752.48 | 51055.1931 | 0.057913 | -394234.668 | 394234.668
C | Xist Rating 1260 | -85.48 | 287.546 | 150.277 | 35.7 | 2372.37 | 8751.63 | 25469.2 | 0.98 | 3.81 | 12.26 | 47.539 | 1 | 1 | 1530 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 682165.504 | 46116.9535 | 2279.9064 | 6852.8951 | 39264.0584 | 50193.1719 | 0.058294 | -387578.3688 | 387578.3688
C | Xist Rating 1261 | -85.36 | 289.482 | 150.277 | 35.7 | 2377.72 | 8839.42 | 25364.5 | 0.96 | 3.79 | 12.252 | 47.16 | 1 | 1 | 1540 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 688307.141 | 46676.6766 | 2309.8065 | 6897.6853 | 39778.9914 | 49787.5103 | 0.058675 | -384445.9574 | 384445.9574
C | Xist Rating 1262 | -85.1 | 294.967 | 150.277 | 35.7 | 2376.4 | 8869.76 | 25022 | 0.95 | 3.72 | 12.247 | 45.789 | 1 | 1 | 1550 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 700959.5788 | 47239.7544 | 2339.9013 | 6942.4754 | 40297.279 | 48360.1587 | 0.059056 | -373424.3269 | 373424.3269
C | Xist Rating 1263 | -84.95 | 296.678 | 150.277 | 35.7 | 2388.29 | 9052.78 | 24921.5 | 0.94 | 3.7 | 12.258 | 45.41 | 1 | 1 | 1560 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 708553.1006 | 47806.1867 | 2370.191 | 6987.2656 | 40818.9211 | 47963.9422 | 0.059437 | -370364.8476 | 370364.8476
C | Xist Rating 1264 | -84.45 | 309.325 | 150.277 | 35.7 | 2367.91 | 8879.68 | 24162.8 | 0.93 | 3.56 | 12.274 | 42.433 | 1 | 1 | 1570 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 732453.7607 | 48375.9737 | 2400.6755 | 7032.0557 | 41343.918 | 44869.9179 | 0.059818 | -346473.6127 | 346473.6127
C | Xist Rating 1265 | -84.29 | 312.308 | 150.277 | 35.7 | 2370.82 | 8945.13 | 24008.3 | 0.91 | 3.53 | 12.267 | 41.882 | 1 | 1 | 1580 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 740426.0526 | 48949.1153 | 2431.3547 | 7076.8459 | 41872.2694 | 44284.9852 | 0.0602 | -341956.9172 | 341956.9172
C | Xist Rating 1266 | -84.13 | 315.327 | 150.277 | 35.7 | 2373.77 | 9012.08 | 23855.9 | 0.9 | 3.5 | 12.259 | 41.346 | 1 | 1 | 1590 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 9 | E | Rod | 748513.7728 | 49525.6115 | 2462.2288 | 7121.6361 | 42403.9754 | 43724.0978 | 0.060581 | -337625.8935 | 337625.8935
C | Xist Rating 1267 | -83.91 | 319.226 | 150.277 | 35.7 | 2378.99 | 9123.24 | 23646 | 0.89 | 3.46 | 12.242 | 40.579 | 1 | 1 | 1600 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 759435.4617 | 50105.4623 | 2493.2976 | 7166.4262 | 42939.0361 | 42922.6379 | 0.060962 | -331437.2323 | 331437.2323
C | Xist Rating 1268 | -83.82 | 321.358 | 150.277 | 35.7 | 2378.17 | 9126.47 | 23557.3 | 0.87 | 3.45 | 12.228 | 40.307 | 1 | 1 | 1610 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 764243.9549 | 50688.6677 | 2524.5612 | 7211.2164 | 43477.4513 | 42626.5016 | 0.061343 | -329150.5463 | 329150.5463
C | Xist Rating 1269 | -83.22 | 335.379 | 150.277 | 35.7 | 2364.7 | 9061.44 | 22805.7 | 0.87 | 3.31 | 12.266 | 37.548 | 1 | 1 | 1620 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 793070.7213 | 51275.2277 | 2556.0196 | 7256.0066 | 44019.2212 | 39768.4538 | 0.061724 | -307081.4584 | 307081.4584
C | Xist Rating 1270 | -83.09 | 337.165 | 150.277 | 35.7 | 2371.37 | 9175.55 | 22723.9 | 0.86 | 3.29 | 12.266 | 37.284 | 1 | 1 | 1630 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 799542.9661 | 51865.1424 | 2587.6728 | 7300.7967 | 44564.3457 | 39490.1115 | 0.062105 | -304932.1737 | 304932.1737
C | Xist Rating 1271 | -82.95 | 340.331 | 150.277 | 35.7 | 2369.67 | 9175.44 | 22589.3 | 0.84 | 3.27 | 12.253 | 36.856 | 1 | 1 | 1640 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 806472.1608 | 52458.4116 | 2619.5208 | 7345.5869 | 45112.8248 | 39031.5258 | 0.062486 | -301391.0964 | 301391.0964
C | Xist Rating 1272 | -82.78 | 344.588 | 150.277 | 35.7 | 2366.39 | 9161.75 | 22403.6 | 0.82 | 3.24 | 12.24 | 36.252 | 1 | 1 | 1650 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 815429.5973 | 53055.0355 | 2651.5635 | 7390.3771 | 45664.6585 | 38389.9732 | 0.062867 | -296437.1967 | 296437.1967
C | Xist Rating 1273 | -82.58 | 348.602 | 150.277 | 35.7 | 2368.21 | 9224.74 | 22221.3 | 0.81 | 3.2 | 12.24 | 35.648 | 1 | 1 | 1660 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 825562.7424 | 53655.014 | 2683.8011 | 7435.1672 | 46219.8468 | 37758.1114 | 0.063248 | -291558.1278 | 291558.1278
C | Xist Rating 1274 | -82.05 | 361.292 | 150.277 | 35.7 | 2355.66 | 9153.52 | 21633.5 | 0.81 | 3.1 | 12.271 | 33.661 | 1 | 1 | 1670 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 851081.1127 | 54258.3471 | 2716.2334 | 7479.9574 | 46778.3897 | 35700.9388 | 0.063629 | -275673.1863 | 275673.1863
C | Xist Rating 1275 | -81.93 | 363.19 | 150.277 | 35.6 | 2360.77 | 9246.47 | 21561 | 0.8 | 3.08 | 12.269 | 33.451 | 1 | 1 | 1680 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 857408.0563 | 54865.0348 | 2748.8606 | 7524.7475 | 47340.2872 | 35477.9483 | 0.06401 | -273951.3125 | 273951.3125
C | Xist Rating 1276 | -81.71 | 368.588 | 150.277 | 35.6 | 2354.95 | 9203.05 | 21346.7 | 0.79 | 3.04 | 12.254 | 32.788 | 1 | 1 | 1690 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 868006.3106 | 55475.0771 | 2781.6825 | 7569.5377 | 47905.5394 | 34783.6316 | 0.064391 | -268589.9829 | 268589.9829
C | Xist Rating 1277 | -81.53 | 372.125 | 150.278 | 35.6 | 2356.99 | 9264.76 | 21206.4 | 0.78 | 3.02 | 12.252 | 32.36 | 1 | 1 | 1700 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 877094.9037 | 56088.474 | 2814.6992 | 7614.3279 | 48474.1462 | 34334.0369 | 0.064772 | -265118.3321 | 265118.3321
C | Xist Rating 1278 | -81.34 | 376.332 | 150.277 | 35.6 | 2356.25 | 9289.07 | 21045.1 | 0.76 | 2.99 | 12.245 | 31.875 | 1 | 1 | 1710 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 886732.275 | 56705.2256 | 2847.9107 | 7659.118 | 49046.1075 | 33815.4587 | 0.065153 | -261114.0089 | 261114.0089
C | Xist Rating 1279 | -80.85 | 388.086 | 150.277 | 35.6 | 2346.46 | 9245.95 | 20567.6 | 0.76 | 2.9 | 12.273 | 30.377 | 1 | 1 | 1720 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 910628.2756 | 57325.3317 | 2881.317 | 7703.9082 | 49621.4235 | 32265.6002 | 0.065534 | -249146.4124 | 249146.4124
C | Xist Rating 1280 | -80.63 | 393.353 | 150.277 | 35.6 | 2343.51 | 9245.23 | 20374.8 | 0.75 | 2.87 | 12.264 | 29.811 | 1 | 1 | 1730 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 921826.689 | 57948.7925 | 2914.9181 | 7748.6984 | 50200.0941 | 31671.9504 | 0.065915 | -244562.4057 | 244562.4057
C | Xist Rating 1281 | -80.51 | 395.891 | 150.278 | 35.6 | 2344.16 | 9275.64 | 20290.3 | 0.74 | 2.85 | 12.26 | 29.582 | 1 | 1 | 1740 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 928031.8466 | 58575.6079 | 2948.714 | 7793.4885 | 50782.1194 | 31428.4611 | 0.066296 | -242682.2457 | 242682.2457
C | Xist Rating 1282 | -80.32 | 400.798 | 150.278 | 35.6 | 2339.49 | 9242.87 | 20123.5 | 0.73 | 2.82 | 12.247 | 29.112 | 1 | 1 | 1750 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 937662.913 | 59205.7779 | 2982.7046 | 7838.2787 | 51367.4992 | 30934.0719 | 0.066677 | -238864.7038 | 238864.7038
C | Xist Rating 1283 | -80.17 | 404.452 | 150.277 | 35.6 | 2337.11 | 9235.52 | 20001.1 | 0.72 | 2.8 | 12.242 | 28.772 | 1 | 1 | 1760 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 945248.8137 | 59839.3025 | 3016.8901 | 7883.0689 | 51956.2336 | 30575.0441 | 0.067058 | -236092.386 | 236092.386
C | Xist Rating 1284 | -79.61 | 418.371 | 150.278 | 35.6 | 2325.81 | 9185.34 | 19497.2 | 0.72 | 2.71 | 12.277 | 27.293 | 1 | 1 | 1770 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 973051.4555 | 60476.1817 | 3051.2703 | 7927.859 | 52548.3227 | 29045.0553 | 0.067439 | -224278.2177 | 224278.2177
C | Xist Rating 1285 | -79.45 | 422.135 | 150.278 | 35.6 | 2324.25 | 9190.42 | 19382.8 | 0.71 | 2.69 | 12.268 | 26.994 | 1 | 1 | 1780 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 981147.2737 | 61116.4155 | 3085.8453 | 7972.6492 | 53143.7663 | 28728.2011 | 0.06782 | -221831.5537 | 221831.5537
C | Xist Rating 1286 | -79.42 | 424.292 | 150.278 | 35.6 | 2316.62 | 9086.27 | 19327.6 | 0.7 | 2.68 | 12.37 | 26.858 | 1 | 1 | 1790 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 982923.333 | 61760.004 | 3120.6151 | 8017.4394 | 53742.5646 | 28586.7551 | 0.068201 | -220739.3456 | 220739.3456
C | Xist Rating 1287 | -79.08 | 430.738 | 150.277 | 35.6 | 2321.51 | 9215.91 | 19122 | 0.69 | 2.65 | 12.256 | 26.308 | 1 | 1 | 1800 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 999962.5744 | 62406.947 | 3155.5797 | 8062.2295 | 54344.7175 | 28003.1351 | 0.068582 | -216232.7862 | 216232.7862
C | Xist Rating 1288 | -79.01 | 434.375 | 150.278 | 35.6 | 2310.68 | 9075.74 | 19013.8 | 0.68 | 2.63 | 12.361 | 26.019 | 1 | 1 | 1810 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1003701.625 | 63057.2447 | 3190.7391 | 8107.0197 | 54950.225 | 27702.6489 | 0.068963 | -213912.512 | 213912.512
C | Xist Rating 1289 | -78.45 | 448.553 | 150.278 | 35.6 | 2300.19 | 9034.19 | 18563.7 | 0.68 | 2.55 | 12.394 | 24.791 | 1 | 1 | 1820 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1031757.1251 | 63710.897 | 3226.0933 | 8151.8098 | 55559.0871 | 26432.9713 | 0.069344 | -204108.3977 | 204108.3977
C | Xist Rating 1290 | -78.34 | 446.27 | 150.278 | 35.6 | 2325.13 | 9411.29 | 18632.1 | 0.67 | 2.56 | 12.423 | 24.987 | 1 | 1 | 1830 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1037635.7651 | 64367.9039 | 3261.6423 | 8196.6 | 56171.3038 | 26631.7219 | 0.069725 | -205643.0973 | 205643.0973
C | Xist Rating 1291 | -78.1 | 449.214 | 150.278 | 35.6 | 2335.8 | 9614.8 | 18546.4 | 0.66 | 2.55 | 12.443 | 24.77 | 1 | 1 | 1840 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1049274.0612 | 65028.2654 | 3297.386 | 8241.3902 | 56786.8752 | 26400.9412 | 0.070106 | -203861.07 | 203861.07
C | Xist Rating 1292 | -77.88 | 454.238 | 150.278 | 35.6 | 2334.45 | 9634.28 | 18410.6 | 0.65 | 2.52 | 12.442 | 24.435 | 1 | 1 | 1850 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1060395.8991 | 65691.9815 | 3333.3246 | 8286.1803 | 57405.8011 | 26046.3531 | 0.070487 | -201123.0344 | 201123.0344
C | Xist Rating 1293 | -77.68 | 459.848 | 150.278 | 35.6 | 2327.65 | 9566.49 | 18260.2 | 0.64 | 2.5 | 12.427 | 24.065 | 1 | 1 | 1860 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1070365.1972 | 66359.0522 | 3369.4579 | 8330.9705 | 58028.0817 | 25654.56 | 0.070868 | -198097.7122 | 198097.7122
C | Xist Rating 1294 | -77.13 | 472.817 | 150.278 | 35.6 | 2321.36 | 9582.31 | 17880.8 | 0.64 | 2.43 | 12.465 | 23.077 | 1 | 1 | 1870 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1097578.4711 | 67029.4775 | 3405.7861 | 8375.7607 | 58653.7169 | 24634.1272 | 0.071249 | -190218.2002 | 190218.2002
C | Xist Rating 1295 | -76.94 | 478.413 | 150.278 | 35.6 | 2315 | 9520.86 | 17739.9 | 0.63 | 2.41 | 12.448 | 22.744 | 1 | 1 | 1880 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1107526.095 | 67703.2575 | 3442.309 | 8420.5508 | 59282.7067 | 24280.4763 | 0.07163 | -187487.4018 | 187487.4018
C | Xist Rating 1296 | -76.72 | 482.097 | 150.278 | 35.6 | 2319.99 | 9637.17 | 17647.6 | 0.62 | 2.39 | 12.456 | 22.529 | 1 | 1 | 1890 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1118460.219 | 68380.392 | 3479.0267 | 8465.341 | 59915.051 | 24050.5888 | 0.072011 | -185712.2717 | 185712.2717
C | Xist Rating 1297 | -76.58 | 486.24 | 150.278 | 35.6 | 2314.9 | 9581.04 | 17556.2 | 0.61 | 2.38 | 12.451 | 22.331 | 1 | 1 | 1900 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1125596.976 | 69060.8812 | 3515.9392 | 8510.1312 | 60550.7501 | 23837.5597 | 0.072392 | -184067.3172 | 184067.3172
C | Xist Rating 1298 | -76.37 | 490.104 | 150.278 | 35.6 | 2318.01 | 9665.89 | 17466.4 | 0.6 | 2.36 | 12.459 | 22.129 | 1 | 1 | 1910 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1136065.973 | 69744.725 | 3553.0464 | 8554.9213 | 61189.8037 | 23620.9385 | 0.072773 | -182394.6258 | 182394.6258
C | Xist Rating 1299 | -75.73 | 505.877 | 150.278 | 35.6 | 2308.24 | 9645.02 | 17051.5 | 0.6 | 2.29 | 12.497 | 21.111 | 1 | 1 | 1920 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1167685.5265 | 70431.9234 | 3590.3485 | 8599.7115 | 61832.2119 | 22569.0602 | 0.073154 | -174272.3002 | 174272.3002
C | Xist Rating 1300 | -75.48 | 511.55 | 150.278 | 35.6 | 2306.57 | 9662.84 | 16925.1 | 0.59 | 2.27 | 12.491 | 20.832 | 1 | 1 | 1930 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1179925.8835 | 71122.4764 | 3627.8454 | 8644.5016 | 62477.9748 | 22271.5625 | 0.073535 | -171975.1025 | 171975.1025
C | Xist Rating 1301 | -75.35 | 513.345 | 150.278 | 35.6 | 2312.16 | 9777.77 | 16883.3 | 0.59 | 2.26 | 12.519 | 20.744 | 1 | 1 | 1940 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1186935.7752 | 71816.384 | 3665.537 | 8689.2918 | 63127.0922 | 22184.9147 | 0.073916 | -171306.0308 | 171306.0308
C | Xist Rating 1302 | -75.17 | 518.939 | 150.278 | 35.6 | 2305.35 | 9698.86 | 16773.5 | 0.57 | 2.24 | 12.509 | 20.518 | 1 | 1 | 1950 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1196336.0236 | 72513.6463 | 3703.4235 | 8734.082 | 63779.5643 | 21931.1414 | 0.074297 | -169346.4609 | 169346.4609
C | Xist Rating 1303 | -74.92 | 525.078 | 150.278 | 35.6 | 2302.47 | 9700.43 | 16638 | 0.56 | 2.22 | 12.515 | 20.22 | 1 | 1 | 1960 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1208976.3427 | 73214.2631 | 3741.5047 | 8778.8721 | 64435.391 | 21614.1702 | 0.074678 | -166898.8932 | 166898.8932
C | Xist Rating 1304 | -74.36 | 539.384 | 150.278 | 35.6 | 2292.82 | 9661.77 | 16304 | 0.57 | 2.16 | 12.558 | 19.454 | 1 | 1 | 1970 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1236710.4229 | 73918.2346 | 3779.7807 | 8823.6623 | 65094.5723 | 20835.0376 | 0.075059 | -160882.6375 | 160882.6375
C | Xist Rating 1305 | -74.17 | 543.815 | 150.278 | 35.6 | 2292.33 | 9689.39 | 16214.8 | 0.56 | 2.15 | 12.556 | 19.27 | 1 | 1 | 1980 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1246603.439 | 74625.5606 | 3818.2515 | 8868.4525 | 65757.1082 | 20635.9175 | 0.07544 | -159345.0847 | 159345.0847
C | Xist Rating 1306 | -73.92 | 549.682 | 150.278 | 35.6 | 2290.77 | 9708.18 | 16102.1 | 0.55 | 2.13 | 12.549 | 19.041 | 1 | 1 | 1990 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1259195.0351 | 75336.2413 | 3856.9171 | 8913.2426 | 66422.9987 | 20389.7096 | 0.075821 | -157443.9329 | 157443.9329
C | Xist Rating 1307 | -73.73 | 554.237 | 150.278 | 35.6 | 2289.17 | 9715.75 | 16015.6 | 0.54 | 2.12 | 12.547 | 18.868 | 1 | 1 | 2000 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1268742.7133 | 76050.2766 | 3895.7775 | 8958.0328 | 67092.2438 | 20201.7962 | 0.076202 | -155992.9157 | 155992.9157
C | Xist Rating 1308 | -73.6 | 557.655 | 150.278 | 35.6 | 2287.87 | 9718.32 | 15954.3 | 0.53 | 2.11 | 12.545 | 18.752 | 1 | 1 | 2010 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1275842.1448 | 76767.6665 | 3934.8326 | 9002.823 | 67764.8436 | 20072.9674 | 0.076583 | -154998.1337 | 154998.1337
C | Xist Rating 1309 | -72.96 | 573.877 | 150.278 | 35.6 | 2277.8 | 9683.77 | 15615.4 | 0.53 | 2.05 | 12.581 | 18.018 | 1 | 1 | 2020 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1307177.0306 | 77488.4111 | 3974.0826 | 9047.6131 | 68440.7979 | 19315.4175 | 0.076964 | -149148.5341 | 149148.5341
C | Xist Rating 1310 | -72.7 | 579.959 | 150.278 | 35.6 | 2276.9 | 9718.87 | 15500.6 | 0.53 | 2.03 | 12.581 | 17.786 | 1 | 1 | 2030 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1320508.6471 | 78212.5102 | 4013.5273 | 9092.4033 | 69120.1069 | 19077.4748 | 0.077345 | -147311.2033 | 147311.2033
C | Xist Rating 1311 | -72.54 | 584.301 | 150.278 | 35.6 | 2273.94 | 9695.97 | 15432.3 | 0.52 | 2.02 | 12.575 | 17.666 | 1 | 1 | 2040 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1328665.4159 | 78939.9639 | 4053.1669 | 9137.1935 | 69802.7705 | 18944.0542 | 0.077726 | -146280.9648 | 146280.9648
C | Xist Rating 1312 | -72.37 | 587.828 | 150.278 | 35.6 | 2275.69 | 9758.94 | 15364.8 | 0.52 | 2.01 | 12.573 | 17.533 | 1 | 1 | 2050 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1337714.3013 | 79670.7723 | 4093.0012 | 9181.9836 | 70488.7887 | 18808.7694 | 0.078107 | -145236.3317 | 145236.3317
C | Xist Rating 1313 | -72.17 | 594.09 | 150.278 | 35.6 | 2268.95 | 9681.86 | 15264.8 | 0.5 | 1.99 | 12.568 | 17.35 | 1 | 1 | 2060 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1347960.5055 | 80404.9353 | 4133.0303 | 9226.7738 | 71178.1615 | 18598.2045 | 0.078488 | -143610.405 | 143610.405
C | Xist Rating 1314 | -71.5 | 611.553 | 150.278 | 35.6 | 2258.57 | 9647.41 | 14936.7 | 0.51 | 1.94 | 12.607 | 16.68 | 1 | 1 | 2070 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1381235.2592 | 81142.4528 | 4173.2542 | 9271.5639 | 71870.8889 | 17918.7343 | 0.078869 | -138363.7166 | 138363.7166
C | Xist Rating 1315 | -71.34 | 615.697 | 150.278 | 35.6 | 2256.65 | 9642.52 | 14874 | 0.5 | 1.93 | 12.601 | 16.572 | 1 | 1 | 2080 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1389412.6351 | 81883.325 | 4213.6729 | 9316.3541 | 72566.9709 | 17797.4246 | 0.07925 | -137426.9954 | 137426.9954
C | Xist Rating 1316 | -71.15 | 620.92 | 150.278 | 35.6 | 2254.21 | 9638.05 | 14791.3 | 0.49 | 1.91 | 12.597 | 16.422 | 1 | 1 | 2090 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1399684.0732 | 82627.5518 | 4254.2864 | 9361.1443 | 73266.4076 | 17632.4854 | 0.079631 | -136153.3781 | 136153.3781
C | Xist Rating 1317 | -70.95 | 626.151 | 150.278 | 35.6 | 2251.55 | 9629.45 | 14709.7 | 0.49 | 1.9 | 12.594 | 16.276 | 1 | 1 | 2100 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1409810.284 | 83375.1333 | 4295.0947 | 9405.9344 | 73969.1988 | 17483.493 | 0.080012 | -135002.8989 | 135002.8989
C | Xist Rating 1318 | -70.77 | 630.801 | 150.278 | 35.6 | 2249.97 | 9635.59 | 14639 | 0.48 | 1.89 | 12.591 | 16.152 | 1 | 1 | 2110 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1419283.326 | 84126.0693 | 4336.0977 | 9450.7246 | 74675.3447 | 17345.4378 | 0.080393 | -133936.8728 | 133936.8728
C | Xist Rating 1319 | -70.15 | 647.463 | 150.278 | 35.6 | 2239.6 | 9586.87 | 14359.4 | 0.48 | 1.84 | 12.629 | 15.614 | 1 | 1 | 2120 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1450058.1348 | 84880.3599 | 4377.2956 | 9495.5148 | 75384.8452 | 16791.168 | 0.080774 | -129656.9485 | 129656.9485
C | Xist Rating 1320 | -69.92 | 653.888 | 150.278 | 35.6 | 2236.43 | 9577.84 | 14264 | 0.47 | 1.83 | 12.624 | 15.447 | 1 | 1 | 2130 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1462374.7398 | 85638.0052 | 4418.6882 | 9540.3049 | 76097.7003 | 16608.1739 | 0.081155 | -128243.9166 | 128243.9166
C | Xist Rating 1321 | -69.71 | 660.34 | 150.278 | 35.6 | 2230.87 | 9524.91 | 14170.1 | 0.47 | 1.81 | 12.62 | 15.284 | 1 | 1 | 2140 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1473132.6958 | 86399.0051 | 4460.2756 | 9585.0951 | 76813.91 | 16441.3779 | 0.081536 | -126955.962 | 126955.962
C | Xist Rating 1322 | -69.58 | 663.907 | 150.278 | 35.6 | 2229.41 | 9522.52 | 14123.7 | 0.46 | 1.81 | 12.616 | 15.211 | 1 | 1 | 2150 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1480120.9049 | 87163.3595 | 4502.0578 | 9629.8853 | 77533.4743 | 16355.8866 | 0.081917 | -126295.8212 | 126295.8212
C | Xist Rating 1323 | -69.41 | 668.502 | 150.278 | 35.6 | 2227.75 | 9526.05 | 14059.2 | 0.46 | 1.79 | 12.613 | 15.103 | 1 | 1 | 2160 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1489255.3305 | 87931.0686 | 4544.0348 | 9674.6754 | 78256.3932 | 16246.1965 | 0.082298 | -125448.8233 | 125448.8233
C | Xist Rating 1324 | -68.75 | 686.618 | 150.278 | 35.6 | 2216.88 | 9473.82 | 13786.1 | 0.46 | 1.75 | 12.651 | 14.608 | 1 | 1 | 2170 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1522149.7118 | 88702.1323 | 4586.2066 | 9719.4656 | 78982.6667 | 15736.4408 | 0.082679 | -121512.6247 | 121512.6247
C | Xist Rating 1325 | -68.52 | 692.818 | 150.278 | 35.6 | 2214.81 | 9483.4 | 13699.2 | 0.45 | 1.74 | 12.647 | 14.46 | 1 | 1 | 2180 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1534460.2346 | 89476.5506 | 4628.5732 | 9764.2557 | 79712.2949 | 15572.8134 | 0.08306 | -120249.1375 | 120249.1375
C | Xist Rating 1326 | -68.35 | 697.647 | 150.278 | 35.6 | 2212.26 | 9469.93 | 13639 | 0.45 | 1.73 | 12.642 | 14.366 | 1 | 1 | 2190 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1543376.5522 | 90254.3236 | 4671.1346 | 9809.0459 | 80445.2777 | 15477.5247 | 0.083441 | -119513.3435 | 119513.3435
C | Xist Rating 1327 | -68.17 | 702.882 | 150.278 | 35.6 | 2208.76 | 9438.97 | 13579.5 | 0.44 | 1.72 | 12.639 | 14.279 | 1 | 1 | 2200 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1552497.6463 | 91035.4511 | 4713.8907 | 9853.8361 | 81181.615 | 15377.1284 | 0.083822 | -118738.1097 | 118738.1097
C | Xist Rating 1328 | -67.92 | 709.34 | 150.278 | 35.6 | 2207.51 | 9463.33 | 13495.4 | 0.43 | 1.7 | 12.635 | 14.142 | 1 | 1 | 2210 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1565875.1434 | 91819.9333 | 4756.8417 | 9898.6262 | 81921.307 | 15224.656 | 0.084203 | -117560.7582 | 117560.7582
C | Xist Rating 1329 | -67.28 | 727.321 | 150.278 | 35.6 | 2197.28 | 9418.22 | 13246.1 | 0.43 | 1.66 | 12.674 | 13.71 | 1 | 1 | 2220 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1598127.8869 | 92607.77 | 4799.9874 | 9943.4164 | 82664.3536 | 14780.1289 | 0.084584 | -114128.2372 | 114128.2372
C | Xist Rating 1330 | -67.08 | 732.516 | 150.278 | 35.6 | 2196.04 | 9432.74 | 13182.4 | 0.43 | 1.65 | 12.669 | 13.611 | 1 | 1 | 2230 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1608634.4366 | 93398.9614 | 4843.3279 | 9988.2066 | 83410.7548 | 14679.5455 | 0.084965 | -113351.5589 | 113351.5589
C | Xist Rating 1331 | -66.85 | 738.746 | 150.278 | 35.6 | 2193.47 | 9427.17 | 13111.7 | 0.43 | 1.64 | 12.664 | 13.505 | 1 | 1 | 2240 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1620417.1886 | 94193.5074 | 4886.8633 | 10032.9967 | 84160.5107 | 14571.6907 | 0.085346 | -112518.7327 | 112518.7327
C | Xist Rating 1332 | -66.61 | 745.512 | 150.278 | 35.6 | 2190.58 | 9420.08 | 13034 | 0.42 | 1.63 | 12.66 | 13.387 | 1 | 1 | 2250 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1633103.677 | 94991.408 | 4930.5934 | 10077.7869 | 84913.6211 | 14438.647 | 0.085727 | -111491.4049 | 111491.4049
C | Xist Rating 1333 | -66.5 | 749.042 | 150.278 | 35.6 | 2188.72 | 9408.86 | 12995.6 | 0.42 | 1.62 | 12.656 | 13.333 | 1 | 1 | 2260 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1639443.2062 | 95792.6632 | 4974.5182 | 10122.5771 | 85670.0861 | 14384.7813 | 0.086108 | -111075.4683 | 111075.4683
C | Xist Rating 1334 | -65.8 | 768.572 | 150.278 | 35.6 | 2178.37 | 9366.54 | 12751.9 | 0.41 | 1.59 | 12.696 | 12.933 | 1 | 1 | 2270 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1674234.1876 | 96597.273 | 5018.6379 | 10167.3672 | 86429.9058 | 13960.5556 | 0.086489 | -107799.7099 | 107799.7099
C | Xist Rating 1335 | -65.59 | 774.748 | 150.278 | 35.6 | 2175.15 | 9348.02 | 12686.2 | 0.41 | 1.58 | 12.69 | 12.839 | 1 | 1 | 2280 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1685193.1122 | 97405.2375 | 5062.9524 | 10212.1574 | 87193.0801 | 13865.0186 | 0.08687 | -107061.9987 | 107061.9987
C | Xist Rating 1336 | -65.35 | 781.844 | 150.278 | 35.6 | 2171.9 | 9337.77 | 12606.9 | 0.41 | 1.56 | 12.685 | 12.72 | 1 | 1 | 2290 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1698086.9836 | 98216.5565 | 5107.4617 | 10256.9476 | 87959.609 | 13743.5591 | 0.087251 | -106124.1201 | 106124.1201
C | Xist Rating 1337 | -65.19 | 786.836 | 150.278 | 35.6 | 2169.36 | 9322.29 | 12557 | 0.4 | 1.56 | 12.683 | 12.651 | 1 | 1 | 2300 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1706930.545 | 99031.2302 | 5152.1657 | 10301.7377 | 88729.4925 | 13661.0737 | 0.087632 | -105487.1896 | 105487.1896
| Xist Rating 1338 | -65.03 | 792.094 | 150.278 | 35.6 | 2165.92 | 9290.34 | 12507.6 | 0.4 | 1.55 | 12.678 | 12.586 | 1 | 1 | 2310 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1715612.2365 | 99849.2585 | 5197.0645 | 10346.5279 | 89502.7306 | 13595.6382 | 0.088013 | -104981.9144 | 104981.9144
| Xist Rating 1339 | -64.32 | 812.044 | 150.278 | 35.6 | 2156.29 | 9261.45 | 12277.1 | 0.4 | 1.51 | 12.715 | 12.224 | 1 | 1 | 2320 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1751002.3568 | 100670.6413 | 5242.1582 | 10391.318 | 90279.3233 | 13223.514 | 0.088394 | -102108.4702 | 102108.4702
| Xist Rating 1340 | -64.12 | 818.252 | 150.278 | 35.6 | 2153.1 | 9242.27 | 12216.9 | 0.39 | 1.5 | 12.711 | 12.141 | 1 | 1 | 2330 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1761778.3812 | 101495.3788 | 5287.4466 | 10436.1082 | 91059.2706 | 13126.1558 | 0.088775 | -101356.6956 | 101356.6956
| Xist Rating 1341 | -63.91 | 824.436 | 150.278 | 35.6 | 2150.43 | 9232.5 | 12157.2 | 0.39 | 1.49 | 12.707 | 12.06 | 1 | 1 | 2340 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1772891.9075 | 102323.471 | 5332.9298 | 10480.8984 | 91842.5726 | 13044.0959 | 0.089156 | -100723.0507 | 100723.0507
| Xist Rating 1342 | -63.73 | 830.129 | 150.278 | 35.6 | 2147.57 | 9214.63 | 12104.7 | 0.38 | 1.49 | 12.702 | 11.991 | 1 | 1 | 2350 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1782760.1365 | 103154.9177 | 5378.6078 | 10525.6885 | 92629.2291 | 12961.0754 | 0.089537 | -100081.9889 | 100081.9889
| Xist Rating 1343 | -63.51 | 836.946 | 150.278 | 35.6 | 2144.29 | 9197.69 | 12039.8 | 0.38 | 1.48 | 12.698 | 11.902 | 1 | 1 | 2360 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1794654.9383 | 103989.719 | 5424.4805 | 10570.4787 | 93419.2403 | 12870.6519 | 0.089918 | -99383.762 | 99383.762
| Xist Rating 1344 | -62.87 | 855.356 | 150.278 | 35.6 | 2135.91 | 9174.69 | 11846.8 | 0.38 | 1.45 | 12.734 | 11.614 | 1 | 1 | 2370 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1826963.434 | 104827.875 | 5470.5481 | 10615.2689 | 94212.6061 | 12575.1805 | 0.090299 | -97102.2105 | 97102.2105
| Xist Rating 1345 | -62.66 | 861.778 | 150.278 | 35.6 | 2132.62 | 9152.56 | 11791.1 | 0.37 | 1.44 | 12.728 | 11.543 | 1 | 1 | 2380 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1837844.9984 | 105669.3855 | 5516.8105 | 10660.059 | 95009.3265 | 12489.7943 | 0.09068 | -96442.8812 | 96442.8812
| Xist Rating 1346 | -62.45 | 868.15 | 150.278 | 35.6 | 2130.55 | 9156.84 | 11730 | 0.37 | 1.43 | 12.722 | 11.459 | 1 | 1 | 2390 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 1849636.9825 | 106514.2507 | 5563.2676 | 10704.8492 | 95809.4015 | 12404.4336 | 0.091061 | -95783.7481 | 95783.7481
C | Xist Rating 1347 | -58.76 | 995.895 | 150.278 | 35.6 | 2041.12 | 8425.88 | 10538.2 | 0.4 | 1.25 | 12.72 | 9.793 | 1 | 1 | 2400 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2032741.2024 | 107362.4705 | 5609.9196 | 10749.6394 | 96612.8311 | 10717.3778 | 0.091442 | -82756.7504 | 82756.7504
C | Xist Rating 1348 | -58.4 | 997.341 | 150.278 | 35.6 | 2056.6 | 8696.41 | 10538 | 0.39 | 1.25 | 12.718 | 9.802 | 1 | 1 | 2410 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2051131.5006 | 108214.0449 | 5656.7663 | 10794.4295 | 97419.6154 | 10715.1796 | 0.091823 | -82739.7766 | 82739.7766
C | Xist Rating 1349 | -58.37 | 998.742 | 150.278 | 35.6 | 2056.35 | 8691.77 | 10538 | 0.39 | 1.25 | 12.757 | 9.813 | 1 | 1 | 2420 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2053763.1117 | 109068.9739 | 5703.8078 | 10839.2197 | 98229.7542 | 10730.4763 | 0.092204 | -82857.8937 | 82857.8937
C | Xist Rating 1350 | -57.98 | 1000.1 | 150.278 | 35.6 | 2072.84 | 8994.35 | 10537.9 | 0.39 | 1.25 | 12.75 | 9.823 | 1 | 1 | 2430 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2073047.284 | 109927.2575 | 5751.0441 | 10884.0098 | 99043.2477 | 10742.7941 | 0.092585 | -82953.0081 | 82953.0081
C | Xist Rating 1351 | -57.96 | 1001.47 | 150.278 | 35.6 | 2072 | 8978.52 | 10537.9 | 0.38 | 1.25 | 12.745 | 9.833 | 1 | 1 | 2440 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2075045.84 | 110788.8957 | 5798.4752 | 10928.8 | 99860.0957 | 10741.2552 | 0.092966 | -82941.1254 | 82941.1254
C | Xist Rating 1352 | -57.95 | 1002.8 | 150.278 | 35.6 | 2071.17 | 8962.91 | 10537.9 | 0.38 | 1.25 | 12.742 | 9.844 | 1 | 1 | 2450 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2076969.276 | 111653.8886 | 5846.1011 | 10973.5902 | 100680.2984 | 10754.7244 | 0.093347 | -83045.1309 | 83045.1309
C | Xist Rating 1353 | -57.93 | 1004.27 | 150.278 | 35.6 | 2070.05 | 8942.05 | 10537.9 | 0.37 | 1.25 | 12.739 | 9.855 | 1 | 1 | 2460 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2078889.1135 | 112522.236 | 5893.9217 | 11018.3803 | 101503.8557 | 10754.1454 | 0.093728 | -83040.6604 | 83040.6604
C | Xist Rating 1354 | -57.9 | 1005.62 | 150.278 | 35.6 | 2069.44 | 8930.71 | 10537.9 | 0.36 | 1.25 | 12.776 | 9.866 | 1 | 1 | 2470 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2081070.2528 | 113393.9381 | 5941.9372 | 11063.1705 | 102330.7676 | 10755.0522 | 0.094109 | -83047.6624 | 83047.6624
C | Xist Rating 1355 | -57.86 | 1006.97 | 150.278 | 35.6 | 2069.66 | 8934.85 | 10537.8 | 0.36 | 1.25 | 12.768 | 9.876 | 1 | 1 | 2480 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2084085.5302 | 114268.9948 | 5990.1474 | 11107.9607 | 103161.0341 | 10767.1787 | 0.09449 | -83141.2998 | 83141.2998
C | Xist Rating 1356 | -57.84 | 1008.37 | 150.278 | 35.6 | 2068.96 | 8921.73 | 10537.9 | 0.35 | 1.25 | 12.763 | 9.887 | 1 | 1 | 2490 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2086277.1952 | 115147.4061 | 6038.5525 | 11152.7508 | 103994.6552 | 10766.2164 | 0.094871 | -83133.8693 | 83133.8693
C | Xist Rating 1357 | -57.82 | 1009.35 | 150.278 | 35.6 | 2069.06 | 8923.74 | 10537.8 | 0.35 | 1.25 | 12.757 | 9.896 | 1 | 1 | 2500 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2088405.711 | 116029.172 | 6087.1523 | 11197.541 | 104831.631 | 10777.3299 | 0.095252 | -83219.6848 | 83219.6848
C | Xist Rating 1358 | -57.79 | 1011.2 | 150.278 | 35.6 | 2067.53 | 8895.26 | 10537.8 | 0.34 | 1.25 | 12.754 | 9.908 | 1 | 1 | 2510 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2090686.336 | 116914.2925 | 6135.9469 | 11242.3312 | 105671.9613 | 10777.3256 | 0.095633 | -83219.6518 | 83219.6518
C | Xist Rating 1359 | -57.77 | 1012.66 | 150.278 | 35.6 | 2066.86 | 8882.94 | 10537.8 | 0.34 | 1.25 | 12.8 | 9.919 | 1 | 1 | 2520 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2093026.4476 | 117802.7676 | 6184.9363 | 11287.1213 | 106515.6463 | 10792.4595 | 0.096014 | -83336.5119 | 83336.5119
C | Xist Rating 1360 | -57.75 | 1013.99 | 150.278 | 35.6 | 2066.18 | 8870.32 | 10537.8 | 0.33 | 1.25 | 12.795 | 9.929 | 1 | 1 | 2530 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2095085.8582 | 118694.5974 | 6234.1205 | 11331.9115 | 107362.6859 | 10790.0922 | 0.096395 | -83318.2316 | 83318.2316
C | Xist Rating 1361 | -57.74 | 1015.14 | 150.279 | 35.6 | 2065.2 | 8852.36 | 10537.8 | 0.33 | 1.25 | 12.789 | 9.939 | 1 | 1 | 2540 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2096467.128 | 119589.7817 | 6283.4995 | 11376.7017 | 108213.0801 | 10802.1444 | 0.096776 | -83411.2955 | 83411.2955
C | Xist Rating 1362 | -57.71 | 1016.69 | 150.279 | 35.6 | 2064.79 | 8844.69 | 10537.9 | 0.32 | 1.25 | 12.786 | 9.95 | 1 | 1 | 2550 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2099251.3451 | 120488.3207 | 6333.0732 | 11421.4918 | 109066.8289 | 10800.7317 | 0.097157 | -83400.3872 | 83400.3872
C | Xist Rating 1363 | -57.69 | 1018.14 | 150.279 | 35.6 | 2063.83 | 8827.14 | 10537.9 | 0.32 | 1.25 | 12.783 | 9.961 | 1 | 1 | 2560 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2101267.8762 | 121390.2143 | 6382.8418 | 11466.282 | 109923.9323 | 10813.879 | 0.097538 | -83501.9074 | 83501.9074
C | Xist Rating 1364 | -57.68 | 1019.53 | 150.279 | 35.6 | 2062.15 | 8796.56 | 10537.9 | 0.31 | 1.25 | 12.78 | 9.971 | 1 | 1 | 2570 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2102423.7895 | 122295.4625 | 6432.8051 | 11511.0721 | 110784.3903 | 10811.2645 | 0.097919 | -83481.7189 | 83481.7189
C | Xist Rating 1365 | -57.66 | 1020.89 | 150.279 | 35.6 | 2061.46 | 8783.9 | 10537.9 | 0.31 | 1.25 | 12.819 | 9.981 | 1 | 1 | 2580 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2104523.8994 | 123204.0653 | 6482.9633 | 11555.8623 | 111648.203 | 10824.8235 | 0.0983 | -83586.4181 | 83586.4181
C | Xist Rating 1366 | -57.64 | 1022.25 | 150.279 | 35.6 | 2060.77 | 8771.46 | 10537.9 | 0.3 | 1.25 | 12.813 | 9.991 | 1 | 1 | 2590 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2106622.1325 | 124116.0227 | 6533.3162 | 11600.6525 | 112515.3702 | 10821.8985 | 0.098681 | -83563.8318 | 83563.8318
C | Xist Rating 1367 | -57.63 | 1023.43 | 150.279 | 35.6 | 2059.8 | 8753.91 | 10537.9 | 0.3 | 1.25 | 12.808 | 10 | 1 | 1 | 2600 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2108061.114 | 125031.3347 | 6583.8639 | 11645.4426 | 113385.8921 | 10832.7932 | 0.099062 | -83647.9576 | 83647.9576
C | Xist Rating 1368 | -57.61 | 1025.12 | 150.279 | 35.6 | 2058.33 | 8727.48 | 10537.8 | 0.3 | 1.25 | 12.805 | 10.012 | 1 | 1 | 2610 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2110035.2496 | 125950.0014 | 6634.6064 | 11690.2328 | 114259.7686 | 10846.8722 | 0.099443 | -83756.6722 | 83756.6722
C | Xist Rating 1369 | -57.59 | 1026.52 | 150.279 | 35.6 | 2057.43 | 8711.22 | 10537.8 | 0.29 | 1.25 | 12.802 | 10.022 | 1 | 1 | 2620 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2111993.0436 | 126872.0226 | 6685.5437 | 11735.023 | 115136.9996 | 10843.8387 | 0.099824 | -83733.2482 | 83733.2482
C | Xist Rating 1370 | -57.56 | 1027.94 | 150.279 | 35.6 | 2056.86 | 8701.19 | 10537.8 | 0.29 | 1.25 | 12.838 | 10.032 | 1 | 1 | 2630 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2114328.6684 | 127797.3985 | 6736.6758 | 11779.8131 | 116017.5853 | 10857.1186 | 0.10021 | -83835.792 | 83835.792
C | Xist Rating 1371 | -57.54 | 1029.19 | 150.279 | 35.6 | 2056.64 | 8697.22 | 10537.8 | 0.28 | 1.25 | 12.834 | 10.042 | 1 | 1 | 2640 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2116673.3216 | 128726.1289 | 6788.0027 | 11824.6033 | 116901.5257 | 10853.8478 | 0.10059 | -83810.5355 | 83810.5355
C | Xist Rating 1372 | -57.51 | 1030.69 | 150.279 | 35.6 | 2055.94 | 8684.62 | 10537.8 | 0.28 | 1.25 | 12.831 | 10.052 | 1 | 1 | 2650 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 8 | E | Rod | 2119036.7986 | 129658.214 | 6839.5243 | 11869.3935 | 117788.8206 | 10865.7438 | 0.10097 | -83902.3931 | 83902.3931
C | Xist Rating 1373 | -57.48 | 1032.03 | 150.279 | 35.6 | 2055.84 | 8683 | 10537.8 | 0.28 | 1.25 | 12.824 | 10.062 | 1 | 1 | 2660 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2121688.5552 | 130593.6537 | 6891.2408 | 11914.1836 | 118679.4701 | 10877.5055 | 0.10135 | -83993.2138 | 83993.2138
C | Xist Rating 1374 | -57.44 | 1033.42 | 150.279 | 35.6 | 2056.07 | 8687 | 10537.8 | 0.27 | 1.25 | 12.823 | 10.072 | 1 | 1 | 2670 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2124783.8594 | 131532.448 | 6943.152 | 11958.9738 | 119573.4743 | 10874.1197 | 0.10173 | -83967.0696 | 83967.0696
C | Xist Rating 1375 | -57.41 | 1034.84 | 150.279 | 35.6 | 2055.61 | 8678.83 | 10537.7 | 0.27 | 1.25 | 12.858 | 10.082 | 1 | 1 | 2680 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2127227.4524 | 132474.597 | 6995.258 | 12003.7639 | 120470.833 | 10887.1918 | 0.10211 | -84068.0091 | 84068.0091
C | Xist Rating 1376 | -57.35 | 1036.21 | 150.279 | 35.6 | 2056.85 | 8700.98 | 10537.7 | 0.27 | 1.25 | 12.855 | 10.092 | 1 | 1 | 2690 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2131328.5385 | 133420.1005 | 7047.5588 | 12048.5541 | 121371.5464 | 10899.0353 | 0.10249 | -84159.4613 | 84159.4613
C | Xist Rating 1377 | -57.33 | 1037.41 | 150.279 | 35.6 | 2056.22 | 8689.7 | 10537.8 | 0.26 | 1.25 | 12.848 | 10.101 | 1 | 1 | 2700 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2133143.1902 | 134368.9587 | 7100.0544 | 12093.3443 | 122275.6144 | 10894.1593 | 0.10287 | -84121.8105 | 84121.8105
C | Xist Rating 1378 | -57.29 | 1039.07 | 150.279 | 35.6 | 2056.03 | 8686.22 | 10537.8 | 0.26 | 1.25 | 12.848 | 10.112 | 1 | 1 | 2710 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2136359.0921 | 135321.1714 | 7152.7448 | 12138.1344 | 123183.037 | 10907.0802 | 0.10325 | -84221.5818 | 84221.5818
C | Xist Rating 1379 | -57.28 | 1040.41 | 150.279 | 35.6 | 2054.69 | 8662.44 | 10537.8 | 0.26 | 1.25 | 12.843 | 10.122 | 1 | 1 | 2720 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2137720.0229 | 136276.7388 | 7205.63 | 12182.9246 | 124093.8142 | 10918.804 | 0.10363 | -84312.1102 | 84312.1102
C | Xist Rating 1380 | -57.2 | 1041.73 | 150.279 | 35.6 | 2056.76 | 8699.35 | 10537.9 | 0.25 | 1.25 | 12.886 | 10.131 | 1 | 1 | 2730 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2142588.5948 | 137235.6608 | 7258.71 | 12227.7148 | 125007.946 | 10915.2466 | 0.10402 | -84284.641 | 84284.641
C | Xist Rating 1381 | -57.17 | 1043.02 | 150.279 | 35.6 | 2056.98 | 8703.2 | 10537.9 | 0.25 | 1.25 | 12.883 | 10.141 | 1 | 1 | 2740 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2145471.2796 | 138197.9374 | 7311.9847 | 12272.5049 | 125925.4324 | 10926.9835 | 0.1044 | -84375.2702 | 84375.2702
C | Xist Rating 1382 | -57.04 | 1044.57 | 150.279 | 35.6 | 2061.04 | 8776.16 | 10538 | 0.25 | 1.25 | 12.891 | 10.151 | 1 | 1 | 2750 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2152900.5528 | 139163.5686 | 7365.4543 | 12317.2951 | 126846.2735 | 10939.0587 | 0.10478 | -84468.5118 | 84468.5118
C | Xist Rating 1383 | -57.14 | 1045.99 | 150.279 | 35.6 | 2054.64 | 8661.51 | 10537.8 | 0.24 | 1.25 | 12.873 | 10.161 | 1 | 1 | 2760 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2149132.8936 | 140132.5544 | 7419.1186 | 12362.0853 | 127770.4692 | 10934.4056 | 0.10516 | -84432.5816 | 84432.5816
C | Xist Rating 1384 | -56.89 | 1047.23 | 150.279 | 35.6 | 2065.07 | 8849.7 | 10538.1 | 0.24 | 1.25 | 12.894 | 10.17 | 1 | 1 | 2770 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2162603.2561 | 141104.8948 | 7472.9777 | 12406.8754 | 128698.0194 | 10945.7627 | 0.10554 | -84520.2784 | 84520.2784
C | Xist Rating 1385 | -56.58 | 1048.77 | 150.279 | 35.6 | 2077.88 | 9089.7 | 10538.3 | 0.23 | 1.25 | 12.966 | 10.182 | 1 | 1 | 2780 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2179218.2076 | 142080.5899 | 7527.0316 | 12451.6656 | 129628.9243 | 10945.6079 | 0.10592 | -84519.0827 | 84519.0827
C | Xist Rating 1386 | -56.36 | 1050.18 | 150.279 | 35.6 | 2087.17 | 9270.28 | 10538.3 | 0.23 | 1.25 | 12.991 | 10.192 | 1 | 1 | 2790 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2191904.1906 | 143059.6396 | 7581.2803 | 12496.4558 | 130563.1838 | 10958.0487 | 0.1063 | -84615.1476 | 84615.1476
C | Xist Rating 1387 | -56.2 | 1051.16 | 150.279 | 35.6 | 2093.95 | 9405.31 | 10538.3 | 0.23 | 1.25 | 13.012 | 10.2 | 1 | 1 | 2800 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2201076.482 | 144042.0438 | 7635.7238 | 12541.2459 | 131500.7979 | 10968.3022 | 0.10668 | -84694.3226 | 84694.3226
C | Xist Rating 1388 | -56.12 | 1052.9 | 150.279 | 35.6 | 2094.95 | 9425.66 | 10538.3 | 0.22 | 1.25 | 13.019 | 10.211 | 1 | 1 | 2810 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2205772.855 | 145027.8027 | 7690.3621 | 12586.0361 | 132441.7666 | 10964.8716 | 0.10706 | -84667.8323 | 84667.8323
C | Xist Rating 1389 | -56.05 | 1054.38 | 150.279 | 35.6 | 2096.71 | 9461.35 | 10538.3 | 0.22 | 1.25 | 13.027 | 10.221 | 1 | 1 | 2820 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2210729.0898 | 146016.9162 | 7745.1952 | 12630.8262 | 133386.09 | 10976.763 | 0.10744 | -84759.6539 | 84759.6539
C | Xist Rating 1390 | -55.96 | 1055.75 | 150.279 | 35.6 | 2098.97 | 9507.51 | 10538.3 | 0.22 | 1.25 | 13.075 | 10.231 | 1 | 1 | 2830 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2215987.5775 | 147009.3843 | 7800.223 | 12675.6164 | 134333.7679 | 10989.7722 | 0.10783 | -84860.1076 | 84860.1076
C | Xist Rating 1391 | -55.89 | 1057.07 | 150.279 | 35.6 | 2100.87 | 9546.64 | 10538.3 | 0.21 | 1.25 | 13.079 | 10.24 | 1 | 1 | 2840 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2220766.6509 | 148005.207 | 7855.4457 | 12720.4066 | 135284.8005 | 10983.8702 | 0.10821 | -84814.5344 | 84814.5344
C | Xist Rating 1392 | -55.83 | 1058.51 | 150.279 | 35.6 | 2101.74 | 9564.8 | 10538.3 | 0.21 | 1.25 | 13.083 | 10.25 | 1 | 1 | 2850 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2224712.8074 | 149004.3844 | 7910.8631 | 12765.1967 | 136239.1876 | 10995.5937 | 0.10859 | -84905.0597 | 84905.0597
C | Xist Rating 1393 | -55.76 | 1059.92 | 150.279 | 35.6 | 2103.23 | 9595.66 | 10538.3 | 0.21 | 1.25 | 13.088 | 10.259 | 1 | 1 | 2860 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2229255.5416 | 150006.9163 | 7966.4753 | 12809.9869 | 137196.9294 | 11006.3063 | 0.10897 | -84987.7797 | 84987.7797
C | Xist Rating 1394 | -55.71 | 1061.11 | 150.279 | 35.6 | 2104.6 | 9624.3 | 10538.2 | 0.21 | 1.25 | 13.089 | 10.268 | 1 | 1 | 2870 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2233212.106 | 151012.8029 | 8022.2824 | 12854.7771 | 138158.0258 | 11016.9118 | 0.10935 | -85069.6726 | 85069.6726
C | Xist Rating 1395 | -55.64 | 1062.62 | 150.279 | 35.5 | 2105.57 | 9644.7 | 10538.2 | 0.2 | 1.25 | 13.132 | 10.278 | 1 | 1 | 2880 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2237420.7934 | 152022.044 | 8078.2842 | 12899.5672 | 139122.4768 | 11012.7418 | 0.10973 | -85037.4733 | 85037.4733
C | Xist Rating 1396 | -55.58 | 1063.96 | 150.279 | 35.5 | 2106.81 | 9670.62 | 10538.2 | 0.2 | 1.25 | 13.131 | 10.287 | 1 | 1 | 2890 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2241561.5676 | 153034.6398 | 8134.4807 | 12944.3574 | 140090.2824 | 11023.2397 | 0.11011 | -85118.5349 | 85118.5349
C | Xist Rating 1397 | -55.52 | 1065.34 | 150.279 | 35.5 | 2108.1 | 9697.95 | 10538.2 | 0.2 | 1.25 | 13.132 | 10.296 | 1 | 1 | 2900 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2245843.254 | 154050.5902 | 8190.8721 | 12989.1476 | 141061.4427 | 11033.7894 | 0.11049 | -85199.9967 | 85199.9967
C | Xist Rating 1398 | -55.45 | 1066.88 | 150.279 | 35.5 | 2109.45 | 9726.73 | 10538.1 | 0.2 | 1.25 | 13.131 | 10.306 | 1 | 1 | 2910 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2250530.016 | 155069.8952 | 8247.4583 | 13033.9377 | 142035.9575 | 11045.3255 | 0.11087 | -85289.0759 | 85289.0759
C | Xist Rating 1399 | -55.35 | 1068.27 | 150.279 | 35.5 | 2112.19 | 9785.34 | 10538 | 0.2 | 1.25 | 13.135 | 10.316 | 1 | 1 | 2920 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2256389.2113 | 156092.5548 | 8304.2393 | 13078.7279 | 143013.827 | 11056.9924 | 0.11125 | -85379.1645 | 85379.1645
C | Xist Rating 1400 | -55.27 | 1069.66 | 150.279 | 35.5 | 2114.54 | 9835.87 | 10538 | 0.19 | 1.25 | 13.178 | 10.325 | 1 | 1 | 2930 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2261838.8564 | 157118.5691 | 8361.215 | 13123.518 | 143995.051 | 11051.3384 | 0.11164 | -85335.5061 | 85335.5061
C | Xist Rating 1401 | -55.25 | 1071.03 | 150.279 | 35.5 | 2113.8 | 9819.85 | 10538 | 0.19 | 1.25 | 13.173 | 10.334 | 1 | 1 | 2940 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2263943.214 | 158147.9379 | 8418.3855 | 13168.3082 | 144979.6297 | 11061.6821 | 0.11202 | -85415.3767 | 85415.3767
C | Xist Rating 1402 | -55.22 | 1072.43 | 150.279 | 35.5 | 2113.07 | 9804.26 | 10538 | 0.19 | 1.25 | 13.169 | 10.343 | 1 | 1 | 2950 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2266119.6601 | 159180.6614 | 8475.7509 | 13213.0984 | 145967.563 | 11072.05 | 0.1124 | -85495.4349 | 85495.4349
C | Xist Rating 1403 | -55.23 | 1073.81 | 150.279 | 35.5 | 2111.95 | 9780.53 | 10537.5 | 0.19 | 1.25 | 13.175 | 10.352 | 1 | 1 | 2960 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2267833.0295 | 160216.7394 | 8533.311 | 13257.8885 | 146958.8509 | 11082.6693 | 0.11278 | -85577.4343 | 85577.4343
C | Xist Rating 1404 | -55.22 | 1075.19 | 150.279 | 35.5 | 2110.97 | 9759.82 | 10537.4 | 0.18 | 1.25 | 13.174 | 10.361 | 1 | 1 | 2970 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2269693.8343 | 161256.1721 | 8591.0659 | 13302.6787 | 147953.4934 | 11075.5741 | 0.11316 | -85522.6472 | 85522.6472
C | Xist Rating 1406 | -55.2 | 1077.97 | 150.279 | 35.5 | 2108.95 | 9717.23 | 10536.8 | 0.18 | 1.25 | 13.216 | 10.379 | 1 | 1 | 2990 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2273384.8315 | 163345.1013 | 8707.16 | 13392.259 | 149952.8423 | 11097.4062 | 0.11392 | -85691.2287 | 85691.2287
C | Xist Rating 1407 | -55.19 | 1079.4 | 150.279 | 35.5 | 2107.78 | 9692.9 | 10536.5 | 0.18 | 1.25 | 13.212 | 10.388 | 1 | 1 | 3000 | 152.4 | 2 | 1.6 | 19.05 | 1.3333 | 7 | E | Rod | 2275137.732 | 164394.5978 | 8765.4993 | 13437.0492 | 150957.5486 | 11107.7221 | 0.1143 | -85770.8861 | 85770.8861
C | Xist Rating 1408 | -94.85 | 96.336 | 150.28 | 35.8 | 2412.39 | 7527.01 | 58745.8 | 2.44 | 10.95 | 13.691 | 336.609 | 1 | 1 | 1000 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 232400.003 | 22580.3322 | 973.9444 | 4758.9549 | 17821.3773 | 351065.3283 | 0.038101 | -2710833.4083 | 2710833.4083
C | Xist Rating 1409 | -94.8 | 97.374 | 150.28 | 35.8 | 2409.34 | 7506.08 | 58284.2 | 2.42 | 10.85 | 13.701 | 330.344 | 1 | 1 | 1010 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 234607.0732 | 22986.1314 | 993.5206 | 4806.5445 | 18179.587 | 344562.8089 | 0.038482 | -2660622.6765 | 2660622.6765
C | Xist Rating 1410 | -94.41 | 105.035 | 150.281 | 35.8 | 2403.51 | 7516.48 | 54967.5 | 2.43 | 10.07 | 13.753 | 286.269 | 1 | 1 | 1020 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 252452.6729 | 23395.4949 | 1013.2917 | 4854.134 | 18541.3609 | 298817.8949 | 0.038863 | -2307392.5764 | 2307392.5764
C | Xist Rating 1411 | -94.34 | 107.254 | 150.28 | 35.8 | 2382.86 | 7334.47 | 54179.1 | 2.35 | 9.89 | 13.523 | 276.834 | 1 | 1 | 1030 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 255571.2664 | 23808.4227 | 1033.2576 | 4901.7236 | 18906.6991 | 288958.8906 | 0.039244 | -2231263.9589 | 2231263.9589
C | Xist Rating 1412 | -94.25 | 108.366 | 150.28 | 35.8 | 2397.88 | 7487.21 | 53794.9 | 2.28 | 9.8 | 13.478 | 272.337 | 1 | 1 | 1040 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 259848.6641 | 24224.9148 | 1053.4182 | 4949.3131 | 19275.6017 | 284254.0964 | 0.039625 | -2194934.785 | 2194934.785
C | Xist Rating 1413 | -94.13 | 110.465 | 150.28 | 35.8 | 2405.47 | 7579.06 | 53044.9 | 2.23 | 9.63 | 13.447 | 263.4 | 1 | 1 | 1050 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 265720.2436 | 24644.9711 | 1073.7737 | 4996.9027 | 19648.0684 | 274951.8392 | 0.040006 | -2123105.2207 | 2123105.2207
C | Xist Rating 1414 | -94.04 | 111.557 | 150.28 | 35.8 | 2419.49 | 7728.96 | 52677.9 | 2.18 | 9.54 | 13.43 | 259.193 | 1 | 1 | 1060 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 269911.0459 | 25068.5917 | 1094.3239 | 5044.4922 | 20024.0995 | 270562.6109 | 0.040387 | -2089212.7628 | 2089212.7628
C | Xist Rating 1415 | -93.65 | 119.891 | 150.28 | 35.8 | 2398.26 | 7586.85 | 49858.6 | 2.17 | 8.9 | 13.375 | 226.862 | 1 | 1 | 1070 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 287529.7897 | 25495.7766 | 1115.0689 | 5092.0818 | 20403.6948 | 236987.8763 | 0.040768 | -1829957.5623 | 1829957.5623
C | Xist Rating 1416 | -93.56 | 121.533 | 150.28 | 35.8 | 2402.75 | 7644.97 | 49381.7 | 2.12 | 8.79 | 13.319 | 221.854 | 1 | 1 | 1080 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 292013.4157 | 25926.5258 | 1136.0087 | 5139.6713 | 20786.8544 | 231761.9641 | 0.041149 | -1789604.4535 | 1789604.4535
C | Xist Rating 1417 | -93.45 | 123.711 | 150.279 | 35.8 | 2400.4 | 7638.43 | 48761.8 | 2.07 | 8.65 | 13.238 | 215.413 | 1 | 1 | 1090 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 296955.8844 | 26360.8392 | 1157.1433 | 5187.2609 | 21173.5783 | 225044.9229 | 0.04153 | -1737737.2416 | 1737737.2416
C | Xist Rating 1418 | -93.36 | 125.321 | 150.279 | 35.8 | 2406.1 | 7709.6 | 48308.2 | 2.03 | 8.55 | 13.222 | 210.747 | 1 | 1 | 1100 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 301534.8581 | 26798.7169 | 1178.4727 | 5234.8504 | 21563.8665 | 220183.8618 | 0.041911 | -1700201.4165 | 1700201.4165
C | Xist Rating 1419 | -93.32 | 126.601 | 150.279 | 35.8 | 2398.48 | 7640.56 | 48010.6 | 1.96 | 8.49 | 13.075 | 207.984 | 1 | 1 | 1110 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 303649.9665 | 27240.1589 | 1199.9969 | 5282.44 | 21957.7189 | 217266.1358 | 0.042292 | -1677671.5098 | 1677671.5098
C | Xist Rating 1420 | -92.84 | 135.798 | 150.279 | 35.8 | 2396.38 | 7698.49 | 45447.9 | 2 | 7.92 | 13.216 | 181.988 | 1 | 1 | 1120 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 325423.6112 | 27685.1652 | 1221.7158 | 5330.0295 | 22355.1356 | 190321.232 | 0.042673 | -1469610.1051 | 1469610.1051
C | Xist Rating 1421 | -92.78 | 137.031 | 150.279 | 35.8 | 2395.51 | 7698.09 | 45189.6 | 1.94 | 7.86 | 13.123 | 179.749 | 1 | 1 | 1130 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 328259.1308 | 28133.7357 | 1243.6296 | 5377.6191 | 22756.1166 | 187958.5786 | 0.043054 | -1451366.3217 | 1451366.3217
C | Xist Rating 1422 | -92.67 | 139.28 | 150.279 | 35.8 | 2395.66 | 7716.78 | 44682 | 1.88 | 7.75 | 12.996 | 175.152 | 1 | 1 | 1140 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 333667.5248 | 28585.8705 | 1265.7381 | 5425.2086 | 23160.6619 | 183143.5773 | 0.043435 | -1414186.1576 | 1414186.1576
C | Xist Rating 1423 | -92.54 | 141.466 | 150.279 | 35.8 | 2402.34 | 7804.08 | 44187.3 | 1.84 | 7.64 | 12.964 | 170.681 | 1 | 1 | 1150 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 339849.4304 | 29041.5696 | 1288.0414 | 5472.7982 | 23568.7714 | 178481.5705 | 0.043816 | -1378187.3775 | 1378187.3775
C | Xist Rating 1424 | -92.43 | 143.731 | 150.279 | 35.8 | 2400.09 | 7797.81 | 43705.3 | 1.78 | 7.53 | 12.895 | 166.454 | 1 | 1 | 1160 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 344967.3358 | 29500.833 | 1310.5395 | 5520.3877 | 23980.4453 | 174055.6988 | 0.044197 | -1344011.9694 | 1344011.9694
C | Xist Rating 1425 | -92 | 152.052 | 150.279 | 35.8 | 2400.26 | 7871.89 | 41834.2 | 1.8 | 7.13 | 12.985 | 149.765 | 1 | 1 | 1170 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 364964.3335 | 29963.6606 | 1333.2324 | 5567.9773 | 24395.6833 | 156756.509 | 0.044578 | -1210432.2107 | 1210432.2107
C | Xist Rating 1426 | -91.94 | 152.762 | 150.279 | 35.8 | 2408.83 | 7969.26 | 41726.6 | 1.75 | 7.11 | 12.94 | 149.022 | 1 | 1 | 1180 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 367977.6885 | 30430.0525 | 1356.1201 | 5615.5668 | 24814.4857 | 155956.8753 | 0.044959 | -1204257.6517 | 1204257.6517
C | Xist Rating 1427 | -91.76 | 157.119 | 150.279 | 35.8 | 2396.98 | 7875.98 | 40886.9 | 1.7 | 6.93 | 12.857 | 142.13 | 1 | 1 | 1190 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 376611.1006 | 30900.0087 | 1379.2026 | 5663.1564 | 25236.8523 | 148767.6565 | 0.04534 | -1148744.4093 | 1148744.4093
C | Xist Rating 1428 | -91.67 | 158.245 | 150.279 | 35.8 | 2408.09 | 8006.24 | 40683.4 | 1.68 | 6.88 | 12.863 | 140.537 | 1 | 1 | 1200 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 381068.2021 | 31373.5292 | 1402.4799 | 5710.7459 | 25662.7833 | 147109.8365 | 0.045721 | -1135943.1631 | 1135943.1631
C | Xist Rating 1429 | -91.57 | 160.579 | 150.278 | 35.8 | 2403.1 | 7969.24 | 40282.5 | 1.63 | 6.8 | 12.791 | 137.448 | 1 | 1 | 1210 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 385887.3949 | 31850.6139 | 1425.9519 | 5758.3355 | 26092.2785 | 143870.353 | 0.046102 | -1110928.7302 | 1110928.7302
C | Xist Rating 1430 | -91.12 | 170.13 | 150.278 | 35.8 | 2390.59 | 7913.38 | 38539.1 | 1.63 | 6.43 | 12.82 | 123.678 | 1 | 1 | 1220 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 406711.0767 | 32331.2629 | 1449.6188 | 5805.925 | 26525.3379 | 129582.1604 | 0.046483 | -1000599.0945 | 1000599.0945
C | Xist Rating 1431 | -90.99 | 172.314 | 150.278 | 35.8 | 2396.35 | 7994.51 | 38184.2 | 1.6 | 6.35 | 12.814 | 121.07 | 1 | 1 | 1230 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 10 | E | Rod | 412924.6539 | 32815.4762 | 1473.4804 | 5853.5146 | 26961.9617 | 126861.3894 | 0.046864 | -979590.0221 | 979590.0221
C | Xist Rating 1432 | -90.88 | 174.638 | 150.278 | 35.8 | 2393.3 | 7978.27 | 37836.5 | 1.56 | 6.28 | 12.706 | 118.616 | 1 | 1 | 1240 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 417961.1254 | 33303.2538 | 1497.5369 | 5901.1041 | 27402.1497 | 124284.2505 | 0.047245 | -959690.0383 | 959690.0383
C | Xist Rating 1433 | -90.82 | 175.908 | 150.278 | 35.8 | 2394.04 | 7995.31 | 37665.2 | 1.53 | 6.24 | 12.668 | 117.486 | 1 | 1 | 1250 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 421130.7883 | 33794.5956 | 1521.7881 | 5948.6937 | 27845.902 | 123095.0167 | 0.047626 | -950507.09 | 950507.09
C | Xist Rating 1434 | -90.67 | 179.207 | 150.278 | 35.8 | 2391.57 | 7994.14 | 37162.2 | 1.5 | 6.14 | 12.644 | 113.901 | 1 | 1 | 1260 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 428586.085 | 34289.5018 | 1546.2341 | 5996.2832 | 28293.2186 | 119357.1902 | 0.048007 | -921644.585 | 921644.585
C | Xist Rating 1435 | -90.22 | 188.264 | 150.278 | 35.8 | 2385.75 | 8005.5 | 35778.3 | 1.51 | 5.85 | 12.697 | 104.089 | 1 | 1 | 1270 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 449150.838 | 34787.9721 | 1570.8749 | 6043.8728 | 28744.0994 | 109187.699 | 0.048388 | -843118.4691 | 843118.4691
C | Xist Rating 1436 | -90.11 | 190.657 | 150.278 | 35.8 | 2385.73 | 8022.69 | 35478.1 | 1.46 | 5.79 | 12.66 | 102.18 | 1 | 1 | 1280 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 454856.1246 | 35290.0068 | 1595.7105 | 6091.4623 | 29198.5445 | 107174.2752 | 0.048769 | -827571.3443 | 827571.3443
C | Xist Rating 1437 | -89.97 | 192.998 | 150.278 | 35.7 | 2390.29 | 8092.26 | 35184 | 1.43 | 5.73 | 12.655 | 100.307 | 1 | 1 | 1290 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 461321.1894 | 35795.6058 | 1620.7408 | 6139.0519 | 29656.5539 | 105215.0779 | 0.04915 | -812442.9425 | 812442.9425
C | Xist Rating 1438 | -89.77 | 196.275 | 150.278 | 35.7 | 2398.55 | 8215.03 | 34752.9 | 1.4 | 5.64 | 12.66 | 97.502 | 1 | 1 | 1300 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 470775.4013 | 36304.769 | 1645.966 | 6186.6414 | 30118.1276 | 102288.4866 | 0.049531 | -789844.5796 | 789844.5796
C | Xist Rating 1439 | -89.67 | 198.11 | 150.278 | 35.7 | 2402.85 | 8279.48 | 34541.7 | 1.37 | 5.59 | 12.635 | 96.228 | 1 | 1 | 1310 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 476028.6135 | 36817.4965 | 1671.3859 | 6234.2309 | 30583.2655 | 100949.0712 | 0.049912 | -779501.9689 | 779501.9689
C | Xist Rating 1440 | -89.22 | 207.265 | 150.278 | 35.7 | 2396.87 | 8288.86 | 33364.8 | 1.37 | 5.35 | 12.678 | 88.689 | 1 | 1 | 1320 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 496787.2605 | 37333.7883 | 1697.0007 | 6281.8205 | 31051.9678 | 93131.0763 | 0.050293 | -719133.4851 | 719133.4851
C | Xist Rating 1441 | -89.07 | 210.76 | 150.278 | 35.7 | 2391.4 | 8250.94 | 32981.7 | 1.34 | 5.28 | 12.615 | 86.441 | 1 | 1 | 1330 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 504011.464 | 37853.6443 | 1722.8102 | 6329.41 | 31524.2342 | 90776.6099 | 0.050674 | -700952.9195 | 700952.9195
C | Xist Rating 1442 | -88.89 | 214.153 | 150.278 | 35.7 | 2393.76 | 8306.52 | 32608.6 | 1.31 | 5.2 | 12.597 | 84.255 | 1 | 1 | 1340 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 512630.8853 | 38377.0646 | 1748.8145 | 6376.9996 | 32000.065 | 88489.8816 | 0.051055 | -683295.4099 | 683295.4099
C | Xist Rating 1443 | -88.79 | 216.004 | 150.278 | 35.7 | 2396.74 | 8356.4 | 32425.6 | 1.28 | 5.16 | 12.576 | 83.25 | 1 | 1 | 1350 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 517705.427 | 38904.0492 | 1775.0136 | 6424.5891 | 32479.4601 | 87429.0925 | 0.051436 | -675104.2777 | 675104.2777
C | Xist Rating 1444 | -88.67 | 217.076 | 150.278 | 35.7 | 2413.13 | 8568.82 | 32304.7 | 1.27 | 5.14 | 12.6 | 82.554 | 1 | 1 | 1360 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 523832.6079 | 39434.5981 | 1801.4075 | 6472.1787 | 32962.4194 | 86707.7048 | 0.051817 | -669533.9126 | 669533.9126
C | Xist Rating 1445 | -88.12 | 230.266 | 150.278 | 35.7 | 2385.76 | 8344.36 | 30904.2 | 1.26 | 4.86 | 12.599 | 74.505 | 1 | 1 | 1370 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 549359.4122 | 39968.7112 | 1827.9962 | 6519.7682 | 33448.943 | 78348.1888 | 0.052198 | -604983.9464 | 604983.9464
C | Xist Rating 1446 | -88.07 | 231.599 | 150.278 | 35.7 | 2384.79 | 8341.52 | 30795.8 | 1.23 | 4.84 | 12.577 | 73.984 | 1 | 1 | 1380 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 552314.9792 | 40506.3887 | 1854.7797 | 6567.3578 | 33939.0309 | 77789.1926 | 0.052579 | -600667.5257 | 600667.5257
C | Xist Rating 1447 | -87.92 | 234.545 | 150.278 | 35.7 | 2385.68 | 8375.37 | 30528.7 | 1.21 | 4.79 | 12.558 | 72.588 | 1 | 1 | 1390 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 559549.3156 | 41047.6304 | 1881.7579 | 6614.9473 | 34432.683 | 76329.2781 | 0.05296 | -589394.453 | 589394.453
C | Xist Rating 1448 | -87.77 | 237.488 | 150.278 | 35.7 | 2385.75 | 8399.1 | 30266.7 | 1.18 | 4.73 | 12.541 | 71.232 | 1 | 1 | 1400 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 566586.996 | 41592.4363 | 1908.931 | 6662.5369 | 34929.8994 | 74902.9845 | 0.053341 | -578380.9914 | 578380.9914
C | Xist Rating 1449 | -87.61 | 240.942 | 150.278 | 35.7 | 2384.82 | 8415.2 | 29958.8 | 1.16 | 4.67 | 12.525 | 69.638 | 1 | 1 | 1410 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 574603.3004 | 42140.8066 | 1936.2988 | 6710.1264 | 35430.6801 | 73237.2257 | 0.053722 | -565518.4442 | 565518.4442
C | Xist Rating 1450 | -87.14 | 250.735 | 150.278 | 35.7 | 2380.12 | 8441.37 | 29053.3 | 1.17 | 4.49 | 12.576 | 64.866 | 1 | 1 | 1420 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 596779.3882 | 42692.7411 | 1963.8614 | 6757.716 | 35935.0251 | 68299.7942 | 0.054103 | -527392.9066 | 527392.9066
C | Xist Rating 1451 | -87.07 | 252.827 | 150.278 | 35.7 | 2374.93 | 8390.11 | 28911.6 | 1.14 | 4.47 | 12.536 | 64.253 | 1 | 1 | 1430 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 600446.4271 | 43248.2399 | 1991.6188 | 6805.3055 | 36442.9344 | 67642.6838 | 0.054484 | -522318.8746 | 522318.8746
C | Xist Rating 1452 | -86.86 | 257.354 | 150.278 | 35.7 | 2372.37 | 8394.32 | 28542.8 | 1.12 | 4.39 | 12.524 | 62.442 | 1 | 1 | 1440 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 610538.909 | 43807.303 | 2019.571 | 6852.8951 | 36954.4079 | 65751.3183 | 0.054865 | -507714.2508 | 507714.2508
C | Xist Rating 1453 | -86.72 | 260.335 | 150.278 | 35.7 | 2371.6 | 8407.24 | 28317.7 | 1.1 | 4.35 | 12.51 | 61.386 | 1 | 1 | 1450 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 617410.486 | 44369.9303 | 2047.718 | 6900.4846 | 37469.4457 | 64643.6704 | 0.055246 | -499161.2873 | 499161.2873
C | Xist Rating 1454 | -86.6 | 262.068 | 150.278 | 35.7 | 2378.84 | 8512.77 | 28185 | 1.09 | 4.33 | 12.516 | 60.765 | 1 | 1 | 1460 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 623417.8411 | 44936.122 | 2076.0598 | 6948.0742 | 37988.0478 | 63997.1721 | 0.055627 | -494169.1993 | 494169.1993
C | Xist Rating 1455 | -86.13 | 273.361 | 150.278 | 35.7 | 2362.1 | 8393.23 | 27311 | 1.08 | 4.16 | 12.529 | 56.595 | 1 | 1 | 1470 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 645706.0181 | 45505.8779 | 2104.5964 | 6995.6637 | 38510.2141 | 59665.4269 | 0.056008 | -460720.6113 | 460720.6113
C | Xist Rating 1456 | -85.95 | 276.859 | 150.278 | 35.7 | 2363.43 | 8436.95 | 27067.1 | 1.06 | 4.11 | 12.523 | 55.504 | 1 | 1 | 1480 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 654336.8664 | 46079.1981 | 2133.3277 | 7043.2533 | 39035.9448 | 58521.445 | 0.056389 | -451887.086 | 451887.086
C | Xist Rating 1457 | -85.76 | 279.842 | 150.278 | 35.7 | 2371.7 | 8566.43 | 26867.4 | 1.04 | 4.07 | 12.521 | 54.633 | 1 | 1 | 1490 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 663701.2714 | 46656.0825 | 2162.2539 | 7090.8428 | 39565.2397 | 57605.9963 | 0.05677 | -444818.2334 | 444818.2334
C | Xist Rating 1458 | -85.6 | 282.916 | 150.278 | 35.7 | 2373.67 | 8615.6 | 26671.1 | 1.02 | 4.03 | 12.509 | 53.798 | 1 | 1 | 1500 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 671549.2217 | 47236.5312 | 2191.3748 | 7138.4324 | 40098.0989 | 56727.0266 | 0.057151 | -438031.0628 | 438031.0628
C | Xist Rating 1459 | -85.4 | 286.441 | 150.278 | 35.7 | 2378.17 | 8703.72 | 26439.6 | 1 | 3.99 | 12.508 | 52.798 | 1 | 1 | 1510 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 681205.393 | 47820.5442 | 2220.6906 | 7186.0219 | 40634.5223 | 55677.2463 | 0.057532 | -429924.9373 | 429924.9373
C | Xist Rating 1460 | -84.86 | 297.418 | 150.278 | 35.7 | 2376.77 | 8782.86 | 25681.8 | 1.01 | 3.85 | 12.564 | 49.433 | 1 | 1 | 1520 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 706894.1799 | 48408.1215 | 2250.2011 | 7233.6115 | 41174.51 | 52200.6815 | 0.057913 | -403079.8258 | 403079.8258
C | Xist Rating 1461 | -84.73 | 301.287 | 150.278 | 35.7 | 2369.01 | 8706.05 | 25469.1 | 0.98 | 3.81 | 12.532 | 48.602 | 1 | 1 | 1530 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 713751.9159 | 48999.2631 | 2279.9064 | 7281.201 | 41718.062 | 51315.3769 | 0.058294 | -396243.7381 | 396243.7381
C | Xist Rating 1462 | -84.6 | 303.295 | 150.278 | 35.7 | 2374.86 | 8800.04 | 25364.3 | 0.96 | 3.79 | 12.525 | 48.213 | 1 | 1 | 1540 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 720283.1637 | 49593.9689 | 2309.8065 | 7328.7906 | 42265.1783 | 50899.1405 | 0.058675 | -393029.6712 | 393029.6712
C | Xist Rating 1463 | -84.33 | 309.019 | 150.278 | 35.7 | 2372.88 | 8820.92 | 25021.9 | 0.95 | 3.72 | 12.519 | 46.808 | 1 | 1 | 1550 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 733265.0047 | 50192.239 | 2339.9013 | 7376.3801 | 42815.8589 | 49436.3418 | 0.059056 | -381734.3272 | 381734.3272
C | Xist Rating 1464 | -84.16 | 310.802 | 150.278 | 35.7 | 2385.66 | 9015.21 | 24921.4 | 0.94 | 3.7 | 12.532 | 46.419 | 1 | 1 | 1560 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 741467.8993 | 50794.0734 | 2370.191 | 7423.9697 | 43370.1037 | 49029.7973 | 0.059437 | -378595.0986 | 378595.0986
C | Xist Rating 1465 | -83.65 | 324.011 | 150.278 | 35.7 | 2364.39 | 8830.36 | 24162.8 | 0.93 | 3.56 | 12.546 | 43.37 | 1 | 1 | 1570 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 766088.3683 | 51399.4721 | 2400.6755 | 7471.5592 | 43927.9128 | 45860.793 | 0.059818 | -354124.8868 | 354124.8868
C | Xist Rating 1466 | -83.47 | 327.114 | 150.278 | 35.7 | 2368.16 | 8907.51 | 24008.1 | 0.91 | 3.53 | 12.54 | 42.804 | 1 | 1 | 1580 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 774658.2902 | 52008.435 | 2431.3547 | 7519.1488 | 44489.2862 | 45260.0753 | 0.0602 | -349486.3043 | 349486.3043
C | Xist Rating 1467 | -83.31 | 330.252 | 150.278 | 35.7 | 2370.68 | 8967.74 | 23855.8 | 0.9 | 3.5 | 12.532 | 42.254 | 1 | 1 | 1590 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 782921.8114 | 52620.9622 | 2462.2288 | 7566.7383 | 45054.2239 | 44684.5657 | 0.060581 | -345042.372 | 345042.372
C | Xist Rating 1468 | -83.09 | 334.32 | 150.278 | 35.7 | 2374.45 | 9056.85 | 23646 | 0.89 | 3.46 | 12.534 | 41.469 | 1 | 1 | 1600 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 793826.124 | 53237.0537 | 2493.2976 | 7614.3279 | 45622.7258 | 43865.5399 | 0.060962 | -338718.0719 | 338718.0719
C | Xist Rating 1469 | -82.98 | 336.523 | 150.278 | 35.7 | 2375.59 | 9088.63 | 23557.3 | 0.87 | 3.45 | 12.521 | 41.189 | 1 | 1 | 1610 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 799440.6736 | 53856.7094 | 2524.5612 | 7661.9174 | 46194.792 | 43560.8535 | 0.061343 | -336365.3638 | 336365.3638
C | Xist Rating 1470 | -82.36 | 351.178 | 150.278 | 35.7 | 2360.77 | 9004.09 | 22805.6 | 0.87 | 3.31 | 12.557 | 38.364 | 1 | 1 | 1620 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 829050.4871 | 54479.9295 | 2556.0196 | 7709.507 | 46770.4225 | 40634.2526 | 0.061724 | -313766.9279 | 313766.9279
C | Xist Rating 1471 | -82.21 | 353.036 | 150.278 | 35.7 | 2369.35 | 9145.36 | 22723.9 | 0.86 | 3.29 | 12.56 | 38.093 | 1 | 1 | 1630 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 836465.8466 | 55106.7138 | 2587.6728 | 7757.0965 | 47349.6173 | 40348.7303 | 0.062105 | -311562.2002 | 311562.2002
C | Xist Rating 1472 | -82.07 | 356.322 | 150.278 | 35.7 | 2367.75 | 9146.73 | 22589.2 | 0.84 | 3.27 | 12.546 | 37.653 | 1 | 1 | 1640 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 843681.4155 | 55737.0624 | 2619.5208 | 7804.6861 | 47932.3763 | 39877.302 | 0.062486 | -307921.9554 | 307921.9554
C | Xist Rating 1473 | -81.89 | 360.747 | 150.278 | 35.7 | 2363.9 | 9124.48 | 22403.6 | 0.83 | 3.24 | 12.532 | 37.033 | 1 | 1 | 1650 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 852769.8333 | 56370.9752 | 2651.5635 | 7852.2756 | 48518.6996 | 39228.0183 | 0.062867 | -302908.3593 | 302908.3593
C | Xist Rating 1474 | -81.68 | 364.928 | 150.278 | 35.7 | 2364.58 | 9169.88 | 22221.3 | 0.82 | 3.2 | 12.53 | 36.414 | 1 | 1 | 1660 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 862901.4502 | 57008.4524 | 2683.8011 | 7899.8652 | 49108.5872 | 38580.4033 | 0.063248 | -297907.6478 | 297907.6478
C | Xist Rating 1475 | -81.12 | 378.181 | 150.278 | 35.7 | 2353.17 | 9116.06 | 21633.4 | 0.81 | 3.1 | 12.562 | 34.38 | 1 | 1 | 1670 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 889924.1838 | 57649.4938 | 2716.2334 | 7947.4547 | 49702.0391 | 36465.2638 | 0.063629 | -281575.101 | 281575.101
C | Xist Rating 1476 | -81 | 380.151 | 150.278 | 35.6 | 2357.78 | 9200.76 | 21561 | 0.8 | 3.08 | 12.56 | 34.163 | 1 | 1 | 1680 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 896312.4248 | 58294.0995 | 2748.8606 | 7995.0443 | 50299.0552 | 36234.8903 | 0.06401 | -279796.2178 | 279796.2178
C | Xist Rating 1477 | -80.77 | 385.764 | 150.278 | 35.6 | 2352.26 | 9162.04 | 21346.7 | 0.79 | 3.04 | 12.544 | 33.484 | 1 | 1 | 1690 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 907417.2266 | 58942.2694 | 2781.6825 | 8042.6338 | 50899.6356 | 35523.7816 | 0.064391 | -274305.2255 | 274305.2255
C | Xist Rating 1478 | -80.59 | 389.445 | 150.278 | 35.6 | 2353.71 | 9214.2 | 21206.5 | 0.78 | 3.02 | 12.541 | 33.045 | 1 | 1 | 1700 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 916640.5909 | 59594.0037 | 2814.6992 | 8090.2234 | 51503.7803 | 35062.5858 | 0.064772 | -270743.9932 | 270743.9932
C | Xist Rating 1479 | -80.38 | 393.819 | 150.278 | 35.6 | 2353.96 | 9253.51 | 21045.4 | 0.77 | 2.99 | 12.535 | 32.548 | 1 | 1 | 1710 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 927034.1732 | 60249.3022 | 2847.9107 | 8137.8129 | 52111.4893 | 34540.87 | 0.065153 | -266715.4421 | 266715.4421
C | Xist Rating 1480 | -79.87 | 406.087 | 150.278 | 35.6 | 2343.66 | 9202.61 | 20567.8 | 0.76 | 2.9 | 12.561 | 31.014 | 1 | 1 | 1720 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 951729.8584 | 60908.165 | 2881.317 | 8185.4025 | 52722.7625 | 32943.999 | 0.065534 | -254384.828 | 254384.828
C | Xist Rating 1481 | -79.63 | 411.57 | 150.278 | 35.6 | 2341.51 | 9214.34 | 20374.7 | 0.75 | 2.87 | 12.553 | 30.433 | 1 | 1 | 1730 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 963695.2707 | 61570.592 | 2914.9181 | 8232.992 | 53337.6 | 32334.7047 | 0.065915 | -249680.0184 | 249680.0184
C | Xist Rating 1482 | -79.51 | 414.204 | 150.278 | 35.6 | 2342.27 | 9246.27 | 20289.9 | 0.74 | 2.85 | 12.548 | 30.197 | 1 | 1 | 1740 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 970177.6031 | 62236.5834 | 2948.714 | 8280.5816 | 53956.0018 | 32083.7599 | 0.066296 | -247742.2893 | 247742.2893
C | Xist Rating 1483 | -79.31 | 419.302 | 150.278 | 35.6 | 2338.24 | 9223.41 | 20123.5 | 0.73 | 2.82 | 12.537 | 29.717 | 1 | 1 | 1750 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 980428.7085 | 62906.139 | 2982.7046 | 8328.1711 | 54577.9679 | 31578.9699 | 0.066677 | -243844.4349 | 243844.4349
C | Xist Rating 1484 | -79.15 | 423.1 | 150.278 | 35.6 | 2335.32 | 9207.67 | 20001.1 | 0.72 | 2.8 | 12.531 | 29.367 | 1 | 1 | 1760 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 988073.892 | 63579.2589 | 3016.8901 | 8375.7607 | 55203.4982 | 31209.3664 | 0.067058 | -240990.4545 | 240990.4545
C | Xist Rating 1485 | -78.64 | 437.63 | 150.278 | 35.6 | 2315.52 | 9026.57 | 19498.7 | 0.72 | 2.71 | 12.679 | 27.848 | 1 | 1 | 1770 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1013341.0176 | 64255.9431 | 3051.2703 | 8423.3502 | 55832.5928 | 29644.3859 | 0.067439 | -228906.0903 | 228906.0903
C | Xist Rating 1486 | -78.38 | 441.538 | 150.278 | 35.6 | 2323.16 | 9173.17 | 19383.3 | 0.71 | 2.69 | 12.558 | 27.547 | 1 | 1 | 1780 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1025763.4201 | 64936.1915 | 3085.8453 | 8470.9398 | 56465.2517 | 29318.919 | 0.06782 | -226392.9211 | 226392.9211
C | Xist Rating 1487 | -78.28 | 443.766 | 150.278 | 35.6 | 2323.78 | 9197.64 | 19326.7 | 0.7 | 2.68 | 12.55 | 27.413 | 1 | 1 | 1790 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1031214.5555 | 65620.0042 | 3120.6151 | 8518.5293 | 57101.4749 | 29173.2315 | 0.068201 | -225267.9607 | 225267.9607
C | Xist Rating 1488 | -78.1 | 450.476 | 150.278 | 35.6 | 2310.95 | 9051.53 | 19122.7 | 0.69 | 2.65 | 12.654 | 26.837 | 1 | 1 | 1800 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1041027.5122 | 66307.3812 | 3155.5797 | 8566.1189 | 57741.2623 | 28574.6583 | 0.068582 | -220645.9369 | 220645.9369
C | Xist Rating 1489 | -77.94 | 454.256 | 150.278 | 35.6 | 2308.27 | 9038.62 | 19013.9 | 0.68 | 2.63 | 12.653 | 26.547 | 1 | 1 | 1810 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1048545.4971 | 66998.3225 | 3190.7391 | 8613.7084 | 58384.6141 | 28267.0858 | 0.068963 | -218270.9438 | 218270.9438
C | Xist Rating 1490 | -77.35 | 469.044 | 150.278 | 35.6 | 2297.9 | 8998.9 | 18563.7 | 0.68 | 2.55 | 12.686 | 25.289 | 1 | 1 | 1820 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1077816.2076 | 67692.828 | 3226.0933 | 8661.298 | 59031.5301 | 26966.3422 | 0.069344 | -208226.9465 | 208226.9465
C | Xist Rating 1491 | -77.24 | 466.666 | 150.278 | 35.6 | 2322.64 | 9370.57 | 18632.1 | 0.67 | 2.56 | 12.717 | 25.489 | 1 | 1 | 1830 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1083897.1182 | 68390.8978 | 3261.6423 | 8708.8875 | 59682.0103 | 27169.2062 | 0.069725 | -209793.4085 | 209793.4085
C | Xist Rating 1492 | -76.99 | 469.73 | 150.278 | 35.6 | 2333.25 | 9571.79 | 18546.4 | 0.66 | 2.55 | 12.738 | 25.267 | 1 | 1 | 1840 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1095997.5225 | 69092.5319 | 3297.386 | 8756.4771 | 60336.0549 | 26933.1333 | 0.070106 | -207970.516 | 207970.516
C | Xist Rating 1493 | -76.77 | 474.945 | 150.278 | 35.6 | 2330.92 | 9574.56 | 18410.5 | 0.65 | 2.52 | 12.734 | 24.923 | 1 | 1 | 1850 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1107058.7994 | 69797.7303 | 3333.3246 | 8804.0666 | 60993.6637 | 26568.8796 | 0.070487 | -205157.8456 | 205157.8456
C | Xist Rating 1494 | -76.56 | 480.77 | 150.278 | 35.6 | 2324.48 | 9513.12 | 18260.1 | 0.64 | 2.5 | 12.716 | 24.544 | 1 | 1 | 1860 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1117540.2496 | 70506.493 | 3369.4579 | 8851.6562 | 61654.8368 | 26167.4216 | 0.070868 | -202057.8933 | 202057.8933
C | Xist Rating 1495 | -75.98 | 494.302 | 150.278 | 35.6 | 2318.36 | 9531.29 | 17880.7 | 0.64 | 2.43 | 12.757 | 23.533 | 1 | 1 | 1870 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1145969.9847 | 71218.8199 | 3405.7861 | 8899.2457 | 62319.5742 | 25123.3471 | 0.071249 | -193995.827 | 193995.827
C | Xist Rating 1496 | -75.77 | 500.113 | 150.278 | 35.6 | 2312.35 | 9476.2 | 17739.9 | 0.63 | 2.41 | 12.74 | 23.191 | 1 | 1 | 1880 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1156436.2955 | 71934.7111 | 3442.309 | 8946.8353 | 62987.8758 | 24760.1875 | 0.07163 | -191191.6043 | 191191.6043
C | Xist Rating 1497 | -75.55 | 503.941 | 150.278 | 35.6 | 2316.58 | 9578.6 | 17647.5 | 0.62 | 2.39 | 12.749 | 22.971 | 1 | 1 | 1890 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1167419.6418 | 72654.1665 | 3479.0267 | 8994.4248 | 63659.7417 | 24524.9951 | 0.072011 | -189375.5113 | 189375.5113
C | Xist Rating 1498 | -75.4 | 508.227 | 150.278 | 35.6 | 2312.75 | 9544.47 | 17556.1 | 0.61 | 2.38 | 12.739 | 22.767 | 1 | 1 | 1900 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1175401.9942 | 73377.1863 | 3515.9392 | 9042.0144 | 64335.1719 | 24305.3071 | 0.072392 | -187679.1387 | 187679.1387
C | Xist Rating 1499 | -75.19 | 512.235 | 150.278 | 35.6 | 2313.69 | 9591.26 | 17466.5 | 0.6 | 2.36 | 12.748 | 22.56 | 1 | 1 | 1910 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1185152.9971 | 74103.7703 | 3553.0464 | 9089.6039 | 65014.1664 | 24083.377 | 0.072773 | -185965.4531 | 185965.4531
C | Xist Rating 1500 | -74.51 | 528.691 | 150.278 | 35.6 | 2305.08 | 9590.12 | 17051.6 | 0.6 | 2.29 | 12.79 | 21.518 | 1 | 1 | 1920 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1218675.0503 | 74833.9186 | 3590.3485 | 9137.1935 | 65696.7252 | 23006.859 | 0.073154 | -177652.8664 | 177652.8664
C | Xist Rating 1501 | -74.29 | 534.579 | 150.278 | 35.6 | 2301.14 | 9568.45 | 16924.4 | 0.59 | 2.27 | 12.78 | 21.231 | 1 | 1 | 1930 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1230141.1201 | 75567.6312 | 3627.8454 | 9184.783 | 66382.8482 | 22700.6745 | 0.073535 | -175288.5913 | 175288.5913
C | Xist Rating 1502 | -74.13 | 536.446 | 150.279 | 35.6 | 2307.62 | 9697.17 | 16883.2 | 0.59 | 2.26 | 12.809 | 21.141 | 1 | 1 | 1940 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1237913.5185 | 76304.908 | 3665.537 | 9232.3726 | 67072.5355 | 22612.0774 | 0.073916 | -174604.4679 | 174604.4679
C | Xist Rating 1503 | -73.95 | 542.232 | 150.279 | 35.6 | 2300.42 | 9612.41 | 16773.2 | 0.57 | 2.24 | 12.8 | 20.91 | 1 | 1 | 1950 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1247361.3374 | 77045.7492 | 3703.4235 | 9279.9621 | 67765.7871 | 22352.7312 | 0.074297 | -172601.8653 | 172601.8653
C | Xist Rating 1504 | -73.68 | 548.61 | 150.279 | 35.6 | 2298.39 | 9628.42 | 16638 | 0.57 | 2.22 | 12.806 | 20.604 | 1 | 1 | 1960 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1260919.7379 | 77790.1546 | 3741.5047 | 9327.5516 | 68462.6029 | 22038.5216 | 0.074678 | -170175.6217 | 170175.6217
C | Xist Rating 1505 | -73.07 | 563.526 | 150.279 | 35.6 | 2290.21 | 9615.63 | 16304 | 0.57 | 2.16 | 12.852 | 19.819 | 1 | 1 | 1970 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1290592.8805 | 78538.1242 | 3779.7807 | 9375.1412 | 69162.983 | 21228.8876 | 0.075059 | -163923.8428 | 163923.8428
C | Xist Rating 1506 | -72.86 | 568.124 | 150.279 | 35.6 | 2290.22 | 9651.7 | 16215 | 0.56 | 2.15 | 12.85 | 19.631 | 1 | 1 | 1980 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1301128.9473 | 79289.6582 | 3818.2515 | 9422.7307 | 69866.9274 | 21025.4277 | 0.07544 | -162352.7792 | 162352.7792
C | Xist Rating 1507 | -72.62 | 574.207 | 150.279 | 35.6 | 2287.48 | 9649.35 | 16102.2 | 0.55 | 2.13 | 12.844 | 19.396 | 1 | 1 | 1990 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1313487.0284 | 80044.7564 | 3856.9171 | 9470.3203 | 70574.4361 | 20772.8494 | 0.075821 | -160402.4369 | 160402.4369
C | Xist Rating 1508 | -72.42 | 578.93 | 150.279 | 35.6 | 2286.81 | 9673.4 | 16015.5 | 0.54 | 2.12 | 12.842 | 19.218 | 1 | 1 | 2000 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1323902.9133 | 80803.4189 | 3895.7775 | 9517.9098 | 71285.5091 | 20579.5518 | 0.076202 | -158909.8441 | 158909.8441
C | Xist Rating 1509 | -72.27 | 582.467 | 150.279 | 35.6 | 2285.9 | 9682.9 | 15954.4 | 0.53 | 2.11 | 12.842 | 19.099 | 1 | 1 | 2010 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1331461.3153 | 81565.6457 | 3934.8326 | 9565.4994 | 72000.1463 | 20447.5086 | 0.076583 | -157890.2416 | 157890.2416
C | Xist Rating 1510 | -71.61 | 599.371 | 150.279 | 35.6 | 2275.55 | 9643.24 | 15615.4 | 0.53 | 2.05 | 12.877 | 18.348 | 1 | 1 | 2020 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1363898.6791 | 82331.4367 | 3974.0826 | 9613.0889 | 72718.3478 | 19672.3268 | 0.076964 | -151904.4932 | 151904.4932
C | Xist Rating 1511 | -71.35 | 605.693 | 150.279 | 35.6 | 2273.67 | 9660.4 | 15500.4 | 0.53 | 2.03 | 12.875 | 18.111 | 1 | 1 | 2030 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1377146.0033 | 83100.7921 | 4013.5273 | 9660.6785 | 73440.1136 | 19429.1654 | 0.077345 | -150026.8654 | 150026.8654
C | Xist Rating 1512 | -71.17 | 610.179 | 150.279 | 35.6 | 2271.24 | 9646.89 | 15432.4 | 0.52 | 2.02 | 12.87 | 17.987 | 1 | 1 | 2040 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1385862.952 | 83873.7117 | 4053.1669 | 9708.268 | 74165.4436 | 19291.4394 | 0.077726 | -148963.3816 | 148963.3816
C | Xist Rating 1513 | -70.99 | 613.849 | 150.279 | 35.6 | 2273.25 | 9714.26 | 15364.8 | 0.52 | 2.01 | 12.871 | 17.851 | 1 | 1 | 2050 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1395432.2393 | 84650.1956 | 4093.0012 | 9755.8576 | 74894.338 | 19153.2513 | 0.078107 | -147896.3293 | 147896.3293
C | Xist Rating 1514 | -70.79 | 620.326 | 150.279 | 35.6 | 2266.56 | 9638.54 | 15264.7 | 0.51 | 1.99 | 12.864 | 17.663 | 1 | 1 | 2060 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1406006.0986 | 85430.2437 | 4133.0303 | 9803.4471 | 75626.7966 | 18948.7991 | 0.078488 | -146317.6036 | 146317.6036
C | Xist Rating 1515 | -70.08 | 638.519 | 150.279 | 35.6 | 2256.35 | 9606.95 | 14936.6 | 0.51 | 1.94 | 12.902 | 16.977 | 1 | 1 | 2070 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1440722.3457 | 86213.8561 | 4173.2542 | 9851.0367 | 76362.8195 | 18241.1281 | 0.078869 | -140853.1563 | 140853.1563
C | Xist Rating 1516 | -69.91 | 642.807 | 150.279 | 35.6 | 2254.98 | 9612.05 | 14874.1 | 0.5 | 1.93 | 12.898 | 16.866 | 1 | 1 | 2080 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1449516.9289 | 87001.0329 | 4213.6729 | 9898.6262 | 77102.4066 | 18116.5886 | 0.07925 | -139891.495 | 139891.495
C | Xist Rating 1517 | -69.71 | 648.222 | 150.279 | 35.6 | 2252.14 | 9600.45 | 14791.3 | 0.49 | 1.91 | 12.892 | 16.712 | 1 | 1 | 2090 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1459886.6951 | 87791.7738 | 4254.2864 | 9946.2158 | 77845.558 | 17947.1919 | 0.079631 | -138583.4583 | 138583.4583
C | Xist Rating 1518 | -69.51 | 653.645 | 150.279 | 35.6 | 2249.47 | 9591.49 | 14709.7 | 0.49 | 1.9 | 12.889 | 16.562 | 1 | 1 | 2100 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1470354.8181 | 88586.0791 | 4295.0947 | 9993.8053 | 78592.2738 | 17794.1103 | 0.080012 | -137401.4033 | 137401.4033
C | Xist Rating 1519 | -69.33 | 658.462 | 150.279 | 35.6 | 2247.27 | 9586.31 | 14639 | 0.48 | 1.89 | 12.887 | 16.435 | 1 | 1 | 2110 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1479741.8987 | 89383.9486 | 4336.0977 | 10041.3949 | 79342.5537 | 17652.7708 | 0.080393 | -136310.0166 | 136310.0166
C | Xist Rating 1520 | -68.67 | 675.806 | 150.279 | 35.6 | 2237.5 | 9548.39 | 14359.4 | 0.48 | 1.84 | 12.924 | 15.885 | 1 | 1 | 2120 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1512115.925 | 90185.3824 | 4377.2956 | 10088.9844 | 80096.398 | 17086.0571 | 0.080774 | -131934.0038 | 131934.0038
C | Xist Rating 1521 | -68.43 | 682.471 | 150.279 | 35.6 | 2233.9 | 9531.58 | 14264 | 0.47 | 1.83 | 12.919 | 15.713 | 1 | 1 | 2130 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1524571.9669 | 90990.3805 | 4418.6882 | 10136.574 | 80853.8065 | 16897.6523 | 0.081155 | -130479.1921 | 130479.1921
C | Xist Rating 1522 | -68.22 | 689.162 | 150.279 | 35.6 | 2228.29 | 9478.15 | 14170.1 | 0.47 | 1.81 | 12.915 | 15.546 | 1 | 1 | 2140 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1535652.793 | 91798.9429 | 4460.2756 | 10184.1635 | 81614.7793 | 16726.7645 | 0.081536 | -129159.6413 | 129159.6413
C | Xist Rating 1523 | -68.08 | 692.848 | 150.279 | 35.6 | 2227.45 | 9486.87 | 14123.7 | 0.46 | 1.8 | 12.911 | 15.471 | 1 | 1 | 2150 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1543284.2776 | 92611.0695 | 4502.0578 | 10231.7531 | 82379.3164 | 16638.9741 | 0.081917 | -128481.7471 | 128481.7471
C | Xist Rating 1524 | -67.9 | 697.611 | 150.279 | 35.6 | 2225.93 | 9492.99 | 14059.2 | 0.46 | 1.79 | 12.909 | 15.361 | 1 | 1 | 2160 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1552833.2532 | 93426.7604 | 4544.0348 | 10279.3426 | 83147.4178 | 16527.3123 | 0.082298 | -127619.5248 | 127619.5248
C | Xist Rating 1525 | -67.21 | 716.457 | 150.279 | 35.6 | 2214.92 | 9438.06 | 13786.1 | 0.46 | 1.75 | 12.947 | 14.853 | 1 | 1 | 2170 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1586894.9384 | 94246.0156 | 4586.2066 | 10326.9322 | 83919.0834 | 16004.1171 | 0.082679 | -123579.5503 | 123579.5503
C | Xist Rating 1526 | -66.96 | 722.896 | 150.279 | 35.6 | 2212.91 | 9448.78 | 13699.2 | 0.45 | 1.74 | 12.943 | 14.702 | 1 | 1 | 2180 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1599703.7874 | 95068.8351 | 4628.5732 | 10374.5217 | 84694.3133 | 15837.1461 | 0.08306 | -122290.2439 | 122290.2439
C | Xist Rating 1527 | -66.79 | 727.893 | 150.279 | 35.6 | 2210.45 | 9436.88 | 13639 | 0.45 | 1.73 | 12.937 | 14.606 | 1 | 1 | 2190 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1608971.0818 | 95895.2188 | 4671.1346 | 10422.1113 | 85473.1075 | 15739.7959 | 0.083441 | -121538.5318 | 121538.5318
C | Xist Rating 1528 | -66.6 | 733.296 | 150.279 | 35.6 | 2207.63 | 9418.52 | 13579.4 | 0.44 | 1.72 | 12.933 | 14.516 | 1 | 1 | 2200 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1618846.2485 | 96725.1668 | 4713.8907 | 10469.7008 | 86255.466 | 15636.0093 | 0.083822 | -120737.1191 | 120737.1191
C | Xist Rating 1529 | -66.35 | 739.994 | 150.279 | 35.6 | 2204.96 | 9416.59 | 13495.4 | 0.43 | 1.7 | 12.931 | 14.375 | 1 | 1 | 2210 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1631657.1702 | 97558.6791 | 4756.8417 | 10517.2904 | 87041.3887 | 15479.2348 | 0.084203 | -119526.5483 | 119526.5483
C | Xist Rating 1530 | -65.66 | 758.705 | 150.279 | 35.6 | 2195.83 | 9391.65 | 13246.1 | 0.44 | 1.66 | 12.969 | 13.934 | 1 | 1 | 2220 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1665987.2001 | 98395.7557 | 4799.9874 | 10564.8799 | 87830.8757 | 15038.281 | 0.084584 | -116121.6195 | 116121.6195
C | Xist Rating 1531 | -65.45 | 764.091 | 150.279 | 35.6 | 2194.44 | 9403.27 | 13182.5 | 0.43 | 1.65 | 12.963 | 13.832 | 1 | 1 | 2230 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1676751.854 | 99236.3965 | 4843.3279 | 10612.4695 | 88623.927 | 14921.6904 | 0.084965 | -115221.3381 | 115221.3381
C | Xist Rating 1532 | -65.23 | 770.537 | 150.279 | 35.6 | 2190.97 | 9381.17 | 13111.7 | 0.43 | 1.64 | 12.959 | 13.723 | 1 | 1 | 2240 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1688223.4509 | 100080.6016 | 4886.8633 | 10660.059 | 89420.5426 | 14810.82 | 0.085346 | -114365.2258 | 114365.2258
C | Xist Rating 1533 | -64.98 | 777.542 | 150.279 | 35.6 | 2187.53 | 9363.86 | 13034.1 | 0.42 | 1.63 | 12.956 | 13.602 | 1 | 1 | 2250 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1700896.4513 | 100928.371 | 4930.5934 | 10707.6486 | 90220.7224 | 14674.4625 | 0.085727 | -113312.3097 | 113312.3097
C | Xist Rating 1534 | -64.85 | 781.192 | 150.279 | 35.6 | 2186.78 | 9373.17 | 12995.6 | 0.42 | 1.62 | 12.952 | 13.546 | 1 | 1 | 2260 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1708295.0418 | 101779.7047 | 4974.5182 | 10755.2381 | 91024.4665 | 14618.5756 | 0.086108 | -112880.7654 | 112880.7654
C | Xist Rating 1535 | -64.13 | 801.5 | 150.279 | 35.6 | 2175.82 | 9319.51 | 12752 | 0.41 | 1.59 | 12.993 | 13.138 | 1 | 1 | 2270 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1743919.73 | 102634.6026 | 5018.6379 | 10802.8277 | 91831.7749 | 14185.8381 | 0.086489 | -109539.2817 | 109539.2817
C | Xist Rating 1536 | -63.91 | 807.891 | 150.279 | 35.6 | 2173.11 | 9310.38 | 12686.2 | 0.41 | 1.58 | 12.985 | 13.04 | 1 | 1 | 2280 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1755636.011 | 103493.0648 | 5062.9524 | 10850.4172 | 92642.6476 | 14086.1179 | 0.08687 | -108769.2688 | 108769.2688
C | Xist Rating 1537 | -63.66 | 815.25 | 150.279 | 35.6 | 2169.91 | 9301.14 | 12606.9 | 0.41 | 1.56 | 12.981 | 12.918 | 1 | 1 | 2290 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 9 | E | Rod | 1769019.1275 | 104355.0913 | 5107.4617 | 10898.0068 | 93457.0845 | 13961.6392 | 0.087251 | -107808.0769 | 107808.0769
C | Xist Rating 1538 | -63.5 | 820.41 | 150.279 | 35.6 | 2167.03 | 9279.52 | 12557 | 0.4 | 1.56 | 12.969 | 12.848 | 1 | 1 | 2300 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 1777853.0823 | 105220.6821 | 5152.1657 | 10945.5963 | 94275.0857 | 13877.4521 | 0.087632 | -107158.0066 | 107158.0066
| Xist Rating 1539 | -63.33 | 825.836 | 150.279 | 35.6 | 2163.82 | 9251.73 | 12507.7 | 0.4 | 1.55 | 12.968 | 12.781 | 1 | 1 | 2310 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 1786960.4535 | 106089.8371 | 5197.0645 | 10993.1859 | 95096.6512 | 13810.1566 | 0.088013 | -106638.3687 | 106638.3687
| Xist Rating 1540 | -62.58 | 846.588 | 150.279 | 35.6 | 2154.43 | 9227.25 | 12277.1 | 0.4 | 1.51 | 13.005 | 12.411 | 1 | 1 | 2320 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 1823914.5848 | 106962.5564 | 5242.1582 | 11040.7754 | 95921.781 | 13429.7764 | 0.088394 | -103701.1738 | 103701.1738
| Xist Rating 1541 | -62.37 | 853.011 | 150.279 | 35.6 | 2151.31 | 9209.29 | 12216.9 | 0.39 | 1.5 | 13.001 | 12.326 | 1 | 1 | 2330 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 1835091.0944 | 107838.84 | 5287.4466 | 11088.365 | 96750.4751 | 13330.0903 | 0.088775 | -102931.424 | 102931.424
| Xist Rating 1542 | -62.16 | 859.41 | 150.279 | 35.6 | 2148.42 | 9195.59 | 12157.2 | 0.39 | 1.49 | 12.996 | 12.242 | 1 | 1 | 2340 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 1846373.6322 | 108718.6879 | 5332.9298 | 11135.9545 | 97582.7334 | 13244.9247 | 0.089156 | -102273.7977 | 102273.7977
| Xist Rating 1543 | -61.97 | 865.295 | 150.279 | 35.6 | 2145.59 | 9178.33 | 12104.8 | 0.38 | 1.49 | 12.992 | 12.171 | 1 | 1 | 2350 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 1856568.2991 | 109602.1 | 5378.6078 | 11183.5441 | 98418.556 | 13159.6134 | 0.089537 | -101615.0464 | 101615.0464
| Xist Rating 1544 | -61.73 | 872.351 | 150.279 | 35.6 | 2142.59 | 9166.48 | 12039.8 | 0.38 | 1.48 | 12.988 | 12.08 | 1 | 1 | 2360 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 1869090.5291 | 110489.0765 | 5424.4805 | 11231.1336 | 99257.9428 | 13067.1622 | 0.089918 | -100901.1629 | 100901.1629
| Xist Rating 1545 | -61.06 | 891.492 | 150.279 | 35.6 | 2134.27 | 9144.51 | 11846.8 | 0.38 | 1.45 | 13.024 | 11.786 | 1 | 1 | 2370 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 1902684.6308 | 111379.6171 | 5470.5481 | 11278.7232 | 100100.894 | 12765.5093 | 0.090299 | -98571.8787 | 98571.8787
| Xist Rating 1546 | -60.85 | 898.129 | 150.279 | 35.6 | 2130.94 | 9121.6 | 11791.1 | 0.37 | 1.44 | 13.018 | 11.713 | 1 | 1 | 2380 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 1913859.0113 | 112273.7221 | 5516.8105 | 11326.3127 | 100947.4094 | 12677.7861 | 0.09068 | -97894.5039 | 97894.5039
| Xist Rating 1547 | -60.62 | 904.741 | 150.279 | 35.6 | 2128.87 | 9126.1 | 11730 | 0.37 | 1.43 | 13.012 | 11.627 | 1 | 1 | 2390 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 1926075.9727 | 113171.3914 | 5563.2676 | 11373.9023 | 101797.4891 | 12590.3965 | 0.091061 | -97219.7042 | 97219.7042
C | Xist Rating 1548 | -56.77 | 1037.79 | 150.279 | 35.6 | 2039.26 | 8394.41 | 10538.1 | 0.4 | 1.25 | 13.01 | 9.923 | 1 | 1 | 2400 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2116323.6354 | 114072.6249 | 5609.9196 | 11421.4918 | 102651.1331 | 10864.8618 | 0.091442 | -83895.5826 | 83895.5826
C | Xist Rating 1549 | -56.36 | 1039.23 | 150.279 | 35.6 | 2056.27 | 8690.41 | 10537.9 | 0.39 | 1.25 | 13.009 | 9.933 | 1 | 1 | 2410 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2136937.4721 | 114977.4227 | 5656.7663 | 11469.0814 | 103508.3413 | 10863.4829 | 0.091823 | -83884.9355 | 83884.9355
C | Xist Rating 1550 | -56.36 | 1040.63 | 150.279 | 35.6 | 2054.82 | 8664.55 | 10538 | 0.39 | 1.25 | 13.048 | 9.944 | 1 | 1 | 2420 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2138307.3366 | 115885.7847 | 5703.8078 | 11516.6709 | 104369.1138 | 10878.8305 | 0.092204 | -84003.4455 | 84003.4455
C | Xist Rating 1551 | -55.96 | 1041.99 | 150.279 | 35.6 | 2071.24 | 8964.29 | 10537.9 | 0.39 | 1.25 | 13.039 | 9.953 | 1 | 1 | 2430 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2158211.3676 | 116797.7111 | 5751.0441 | 11564.2605 | 105233.4506 | 10890.0757 | 0.092585 | -84090.2777 | 84090.2777
C | Xist Rating 1552 | -55.94 | 1043.36 | 150.279 | 35.6 | 2070.3 | 8946.66 | 10537.9 | 0.38 | 1.25 | 13.036 | 9.964 | 1 | 1 | 2440 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2160068.208 | 117713.2017 | 5798.4752 | 11611.85 | 106101.3517 | 10889.3929 | 0.092966 | -84085.0052 | 84085.0052
C | Xist Rating 1553 | -55.92 | 1044.69 | 150.279 | 35.6 | 2069.61 | 8933.88 | 10537.9 | 0.38 | 1.25 | 13.032 | 9.974 | 1 | 1 | 2450 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2162100.8709 | 118632.2566 | 5846.1011 | 11659.4396 | 106972.8171 | 10901.8314 | 0.093347 | -84181.0522 | 84181.0522
C | Xist Rating 1554 | -55.9 | 1046.16 | 150.279 | 35.6 | 2068.57 | 8914.56 | 10537.9 | 0.37 | 1.25 | 13.028 | 9.985 | 1 | 1 | 2460 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2164055.1912 | 119554.8758 | 5893.9217 | 11707.0291 | 107847.8467 | 10900.9412 | 0.093728 | -84174.1788 | 84174.1788
C | Xist Rating 1555 | -55.88 | 1047.51 | 150.279 | 35.6 | 2067.86 | 8901.42 | 10537.9 | 0.36 | 1.25 | 13.065 | 9.996 | 1 | 1 | 2470 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2166104.0286 | 120481.0592 | 5941.9372 | 11754.6187 | 108726.4406 | 10901.576 | 0.094109 | -84179.0801 | 84179.0801
C | Xist Rating 1556 | -55.84 | 1048.86 | 150.279 | 35.6 | 2067.89 | 8901.99 | 10537.9 | 0.36 | 1.25 | 13.058 | 10.007 | 1 | 1 | 2480 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2168927.1054 | 121410.807 | 5990.1474 | 11802.2082 | 109608.5987 | 10914.8276 | 0.09449 | -84281.4057 | 84281.4057
C | Xist Rating 1557 | -55.81 | 1050.26 | 150.279 | 35.6 | 2067.41 | 8893.09 | 10537.8 | 0.35 | 1.25 | 13.052 | 10.017 | 1 | 1 | 2490 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2171318.0266 | 122344.119 | 6038.5525 | 11849.7978 | 110494.3212 | 10912.5109 | 0.094871 | -84263.5166 | 84263.5166
C | Xist Rating 1558 | -55.79 | 1051.24 | 150.279 | 35.6 | 2067.62 | 8897.05 | 10537.7 | 0.35 | 1.25 | 13.047 | 10.026 | 1 | 1 | 2500 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2173564.8488 | 123280.9952 | 6087.1523 | 11897.3873 | 111383.6079 | 10923.709 | 0.095252 | -84349.985 | 84349.985
C | Xist Rating 1559 | -55.77 | 1053.09 | 150.279 | 35.6 | 2066.02 | 8867.49 | 10537.8 | 0.34 | 1.25 | 13.044 | 10.039 | 1 | 1 | 2510 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2175705.0018 | 124221.4358 | 6135.9469 | 11944.9769 | 112276.4589 | 10924.4624 | 0.095633 | -84355.803 | 84355.803
C | Xist Rating 1560 | -55.74 | 1054.55 | 150.279 | 35.6 | 2065.49 | 8857.68 | 10537.8 | 0.34 | 1.25 | 13.091 | 10.049 | 1 | 1 | 2520 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2178162.4795 | 125165.4406 | 6184.9363 | 11992.5664 | 113172.8742 | 10938.6404 | 0.096014 | -84465.2818 | 84465.2818
C | Xist Rating 1561 | -55.72 | 1055.89 | 150.279 | 35.6 | 2064.8 | 8845 | 10537.8 | 0.33 | 1.25 | 13.086 | 10.06 | 1 | 1 | 2530 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2180201.672 | 126113.0097 | 6234.1205 | 12040.156 | 114072.8538 | 10937.0259 | 0.096395 | -84452.8147 | 84452.8147
C | Xist Rating 1562 | -55.7 | 1057.04 | 150.279 | 35.6 | 2064.47 | 8838.96 | 10537.8 | 0.33 | 1.25 | 13.081 | 10.069 | 1 | 1 | 2540 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2182227.3688 | 127064.1431 | 6283.4995 | 12087.7455 | 114976.3976 | 10948.1202 | 0.096776 | -84538.4821 | 84538.4821
C | Xist Rating 1563 | -55.68 | 1058.58 | 150.279 | 35.6 | 2063.42 | 8819.69 | 10537.8 | 0.32 | 1.25 | 13.075 | 10.08 | 1 | 1 | 2550 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2184295.1436 | 128018.8407 | 6333.0732 | 12135.3351 | 115883.5057 | 10946.3072 | 0.097157 | -84524.4828 | 84524.4828
C | Xist Rating 1564 | -55.66 | 1060.03 | 150.279 | 35.6 | 2062.49 | 8802.67 | 10537.8 | 0.32 | 1.25 | 13.072 | 10.091 | 1 | 1 | 2560 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2186301.2747 | 128977.1027 | 6382.8418 | 12182.9246 | 116794.1781 | 10959.496 | 0.097538 | -84626.3231 | 84626.3231
C | Xist Rating 1565 | -55.64 | 1061.42 | 150.279 | 35.6 | 2061.78 | 8789.78 | 10537.8 | 0.31 | 1.25 | 13.07 | 10.101 | 1 | 1 | 2570 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2188414.5276 | 129938.9289 | 6432.8051 | 12230.5142 | 117708.4147 | 10956.6257 | 0.097919 | -84604.1597 | 84604.1597
C | Xist Rating 1566 | -55.62 | 1062.79 | 150.279 | 35.6 | 2060.54 | 8767.16 | 10537.9 | 0.31 | 1.25 | 13.11 | 10.111 | 1 | 1 | 2580 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2189921.3066 | 130904.3193 | 6482.9633 | 12278.1037 | 118626.2156 | 10970.2609 | 0.0983 | -84709.4469 | 84709.4469
C | Xist Rating 1567 | -55.62 | 1064.15 | 150.279 | 35.6 | 2059.5 | 8748.45 | 10537.9 | 0.3 | 1.25 | 13.105 | 10.121 | 1 | 1 | 2590 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2191616.925 | 131873.2741 | 6533.3162 | 12325.6933 | 119547.5809 | 10967.0733 | 0.098681 | -84684.833 | 84684.833
C | Xist Rating 1568 | -55.6 | 1065.32 | 150.279 | 35.6 | 2059.04 | 8740.22 | 10537.9 | 0.3 | 1.25 | 13.1 | 10.131 | 1 | 1 | 2600 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2193536.4928 | 132845.7931 | 6583.8639 | 12373.2828 | 120472.5103 | 10979.0458 | 0.099062 | -84777.2811 | 84777.2811
C | Xist Rating 1569 | -55.58 | 1067.01 | 150.279 | 35.6 | 2057.62 | 8714.65 | 10537.8 | 0.3 | 1.25 | 13.096 | 10.142 | 1 | 1 | 2610 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2195501.1162 | 133821.8764 | 6634.6064 | 12420.8723 | 121401.0041 | 10992.0905 | 0.099443 | -84878.0088 | 84878.0088
C | Xist Rating 1570 | -55.56 | 1068.41 | 150.279 | 35.6 | 2056.65 | 8697.27 | 10537.8 | 0.29 | 1.25 | 13.094 | 10.152 | 1 | 1 | 2620 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2197345.4265 | 134801.524 | 6685.5437 | 12468.4619 | 122333.0621 | 10988.7884 | 0.099824 | -84852.511 | 84852.511
C | Xist Rating 1571 | -55.54 | 1069.83 | 150.279 | 35.6 | 2056.03 | 8686.23 | 10537.8 | 0.29 | 1.25 | 13.13 | 10.163 | 1 | 1 | 2630 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2199602.5749 | 135784.7359 | 6736.6758 | 12516.0514 | 123268.6844 | 11003.1447 | 0.10021 | -84963.367 | 84963.367
C | Xist Rating 1572 | -55.51 | 1071.08 | 150.279 | 35.6 | 2056.09 | 8687.32 | 10537.8 | 0.28 | 1.25 | 13.124 | 10.172 | 1 | 1 | 2640 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2202236.8772 | 136771.512 | 6788.0027 | 12563.641 | 124207.871 | 10998.4615 | 0.10059 | -84927.2046 | 84927.2046
C | Xist Rating 1573 | -55.48 | 1072.58 | 150.279 | 35.6 | 2055.49 | 8676.69 | 10537.7 | 0.28 | 1.25 | 13.12 | 10.183 | 1 | 1 | 2650 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2204677.4642 | 137761.8524 | 6839.5243 | 12611.2305 | 125150.6219 | 11011.3992 | 0.10097 | -85027.1055 | 85027.1055
C | Xist Rating 1574 | -55.46 | 1073.92 | 150.279 | 35.6 | 2054.85 | 8665.27 | 10537.7 | 0.28 | 1.25 | 13.115 | 10.192 | 1 | 1 | 2660 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2206744.512 | 138755.7571 | 6891.2408 | 12658.8201 | 126096.937 | 11022.2254 | 0.10135 | -85110.7029 | 85110.7029
C | Xist Rating 1575 | -55.43 | 1075.31 | 150.279 | 35.6 | 2054.57 | 8660.39 | 10537.8 | 0.27 | 1.25 | 13.116 | 10.202 | 1 | 1 | 2670 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2209299.6667 | 139753.2261 | 6943.152 | 12706.4096 | 127046.8164 | 11018.5925 | 0.10173 | -85082.6504 | 85082.6504
C | Xist Rating 1576 | -55.4 | 1076.73 | 150.279 | 35.6 | 2054.1 | 8651.99 | 10537.7 | 0.27 | 1.25 | 13.15 | 10.212 | 1 | 1 | 2680 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2211711.093 | 140754.2593 | 6995.258 | 12753.9992 | 128000.2601 | 11031.6676 | 0.10211 | -85183.6133 | 85183.6133
C | Xist Rating 1577 | -55.33 | 1078.11 | 150.279 | 35.6 | 2055.55 | 8677.84 | 10537.7 | 0.27 | 1.25 | 13.146 | 10.222 | 1 | 1 | 2690 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2216109.0105 | 141758.8568 | 7047.5588 | 12801.5887 | 128957.268 | 11043.5139 | 0.10249 | -85275.087 | 85275.087
C | Xist Rating 1578 | -55.32 | 1079.31 | 150.279 | 35.6 | 2055.01 | 8668.13 | 10537.7 | 0.26 | 1.25 | 13.14 | 10.231 | 1 | 1 | 2700 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2217992.8431 | 142767.0186 | 7100.0544 | 12849.1783 | 129917.8403 | 11038.3524 | 0.10287 | -85235.2316 | 85235.2316
C | Xist Rating 1579 | -55.29 | 1080.96 | 150.279 | 35.6 | 2054.07 | 8651.43 | 10537.7 | 0.26 | 1.25 | 13.138 | 10.242 | 1 | 1 | 2710 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2220367.5072 | 143778.7446 | 7152.7448 | 12896.7678 | 130881.9768 | 11051.2442 | 0.10325 | -85334.778 | 85334.778
C | Xist Rating 1580 | -55.24 | 1082.31 | 150.279 | 35.6 | 2054.62 | 8661.24 | 10537.8 | 0.26 | 1.25 | 13.139 | 10.252 | 1 | 1 | 2720 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2223735.7722 | 144794.035 | 7205.63 | 12944.3574 | 131849.6776 | 11063.192 | 0.10363 | -85427.036 | 85427.036
C | Xist Rating 1581 | -55.22 | 1083.63 | 150.279 | 35.6 | 2054.05 | 8651.09 | 10537.8 | 0.25 | 1.25 | 13.175 | 10.261 | 1 | 1 | 2730 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2225830.2015 | 145812.8896 | 7258.71 | 12991.9469 | 132820.9426 | 11059.0927 | 0.10402 | -85395.3826 | 85395.3826
C | Xist Rating 1582 | -55.12 | 1084.91 | 150.279 | 35.6 | 2056.93 | 8702.37 | 10537.9 | 0.25 | 1.25 | 13.179 | 10.271 | 1 | 1 | 2740 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2231583.9263 | 146835.3085 | 7311.9847 | 13039.5365 | 133795.772 | 11071.0769 | 0.1044 | -85487.9215 | 85487.9215
C | Xist Rating 1583 | -55.11 | 1086.46 | 150.279 | 35.6 | 2055.69 | 8680.09 | 10537.9 | 0.25 | 1.25 | 13.174 | 10.281 | 1 | 1 | 2750 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2233424.9574 | 147861.2916 | 7365.4543 | 13087.126 | 134774.1656 | 11082.7847 | 0.10478 | -85578.3258 | 85578.3258
C | Xist Rating 1584 | -54.9 | 1087.88 | 150.279 | 35.6 | 2063.63 | 8823.25 | 10538.1 | 0.24 | 1.25 | 13.192 | 10.292 | 1 | 1 | 2760 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2244981.8044 | 148890.8391 | 7419.1186 | 13134.7156 | 135756.1235 | 11079.9206 | 0.10516 | -85556.2098 | 85556.2098
C | Xist Rating 1585 | -55.05 | 1089.12 | 150.279 | 35.6 | 2055.28 | 8672.75 | 10537.9 | 0.24 | 1.25 | 13.168 | 10.3 | 1 | 1 | 2770 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2238446.5536 | 149923.9508 | 7472.9777 | 13182.3051 | 136741.6456 | 11088.9326 | 0.10554 | -85625.798 | 85625.798
C | Xist Rating 1586 | -54.77 | 1090.67 | 150.28 | 35.6 | 2066.35 | 8873.17 | 10538.1 | 0.24 | 1.25 | 13.234 | 10.311 | 1 | 1 | 2780 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2253705.9545 | 150960.6268 | 7527.0316 | 13229.8947 | 137730.7321 | 11103.7465 | 0.10592 | -85740.1874 | 85740.1874
C | Xist Rating 1587 | -54.47 | 1092.08 | 150.28 | 35.6 | 2078.25 | 9096.87 | 10538.3 | 0.23 | 1.25 | 13.264 | 10.322 | 1 | 1 | 2790 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2269615.26 | 152000.867 | 7581.2803 | 13277.4842 | 138723.3828 | 11100.9061 | 0.1063 | -85718.2542 | 85718.2542
C | Xist Rating 1588 | -54.2 | 1093.05 | 150.28 | 35.6 | 2090.16 | 9329.47 | 10538.3 | 0.23 | 1.25 | 13.303 | 10.33 | 1 | 1 | 2800 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2284649.388 | 153044.6716 | 7635.7238 | 13325.0738 | 139719.5978 | 11111.7074 | 0.10668 | -85801.6589 | 85801.6589
C | Xist Rating 1589 | -54.12 | 1094.79 | 150.279 | 35.6 | 2091.25 | 9351.28 | 10538.3 | 0.22 | 1.25 | 13.311 | 10.341 | 1 | 1 | 2810 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2289479.5875 | 154092.0404 | 7690.3621 | 13372.6633 | 140719.377 | 11107.9679 | 0.10706 | -85772.7839 | 85772.7839
C | Xist Rating 1590 | -54.02 | 1096.27 | 150.279 | 35.6 | 2093.9 | 9404.49 | 10538.3 | 0.22 | 1.25 | 13.323 | 10.351 | 1 | 1 | 2820 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2295479.753 | 155142.9735 | 7745.1952 | 13420.2529 | 141722.7206 | 11119.9993 | 0.10744 | -85865.6868 | 85865.6868
C | Xist Rating 1591 | -53.94 | 1097.64 | 150.28 | 35.6 | 2096.12 | 9449.39 | 10538.3 | 0.22 | 1.25 | 13.372 | 10.361 | 1 | 1 | 2830 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2300785.1568 | 156197.4708 | 7800.223 | 13467.8424 | 142729.6284 | 11133.0656 | 0.10783 | -85966.5814 | 85966.5814
C | Xist Rating 1592 | -53.86 | 1098.96 | 150.28 | 35.6 | 2098.42 | 9496.28 | 10538.3 | 0.21 | 1.25 | 13.379 | 10.37 | 1 | 1 | 2840 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2306079.6432 | 157255.5325 | 7855.4457 | 13515.432 | 143740.1005 | 11126.895 | 0.10821 | -85918.9341 | 85918.9341
C | Xist Rating 1593 | -53.78 | 1100.4 | 150.28 | 35.6 | 2099.92 | 9527.07 | 10538.3 | 0.21 | 1.25 | 13.384 | 10.38 | 1 | 1 | 2850 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2310751.968 | 158317.1584 | 7910.8631 | 13563.0215 | 144754.1369 | 11138.6736 | 0.10859 | -86009.8847 | 86009.8847
C | Xist Rating 1594 | -53.72 | 1101.81 | 150.28 | 35.6 | 2100.93 | 9547.94 | 10538.3 | 0.21 | 1.25 | 13.39 | 10.39 | 1 | 1 | 2860 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2314825.6833 | 159382.3486 | 7966.4753 | 13610.6111 | 145771.7375 | 11150.4799 | 0.10897 | -86101.0504 | 86101.0504
C | Xist Rating 1595 | -53.65 | 1103 | 150.28 | 35.6 | 2102.89 | 9588.7 | 10538.2 | 0.21 | 1.25 | 13.39 | 10.398 | 1 | 1 | 2870 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2319487.67 | 160451.103 | 8022.2824 | 13658.2006 | 146792.9024 | 11160.0483 | 0.10935 | -86174.9351 | 86174.9351
C | Xist Rating 1596 | -53.59 | 1104.51 | 150.28 | 35.5 | 2103.87 | 9609.04 | 10538.2 | 0.2 | 1.25 | 13.432 | 10.408 | 1 | 1 | 2880 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2323745.4537 | 161523.4218 | 8078.2842 | 13705.7902 | 147817.6316 | 11155.4923 | 0.10973 | -86139.7548 | 86139.7548
C | Xist Rating 1597 | -53.53 | 1105.85 | 150.28 | 35.5 | 2105.15 | 9635.74 | 10538.2 | 0.2 | 1.25 | 13.431 | 10.417 | 1 | 1 | 2890 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2327980.1275 | 162599.3048 | 8134.4807 | 13753.3797 | 148845.9251 | 11166.0171 | 0.11011 | -86221.0241 | 86221.0241
C | Xist Rating 1598 | -53.46 | 1107.24 | 150.28 | 35.5 | 2106.48 | 9663.7 | 10538.2 | 0.2 | 1.25 | 13.432 | 10.427 | 1 | 1 | 2900 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2332378.9152 | 163678.7521 | 8190.8721 | 13800.9693 | 149877.7828 | 11177.6321 | 0.11049 | -86310.7125 | 86310.7125
C | Xist Rating 1599 | -53.39 | 1108.78 | 150.28 | 35.5 | 2107.57 | 9686.88 | 10538.1 | 0.2 | 1.25 | 13.434 | 10.437 | 1 | 1 | 2910 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2336831.4646 | 164761.7637 | 8247.4583 | 13848.5588 | 150913.2048 | 11189.2735 | 0.11087 | -86400.6038 | 86400.6038
C | Xist Rating 1600 | -53.3 | 1110.17 | 150.28 | 35.5 | 2110.16 | 9741.78 | 10538 | 0.2 | 1.25 | 13.435 | 10.446 | 1 | 1 | 2920 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2342636.3272 | 165848.3395 | 8304.2393 | 13896.1484 | 151952.1911 | 11199.8505 | 0.11125 | -86482.2767 | 86482.2767
C | Xist Rating 1601 | -53.19 | 1111.55 | 150.28 | 35.5 | 2113.59 | 9815.43 | 10538 | 0.19 | 1.25 | 13.48 | 10.455 | 1 | 1 | 2930 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2349360.9645 | 166938.4796 | 8361.215 | 13943.7379 | 152994.7417 | 11193.8793 | 0.11164 | -86436.1688 | 86436.1688
C | Xist Rating 1602 | -53.17 | 1112.92 | 150.28 | 35.5 | 2112.87 | 9799.96 | 10538 | 0.19 | 1.25 | 13.475 | 10.465 | 1 | 1 | 2940 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2351455.2804 | 168032.184 | 8418.3855 | 13991.3275 | 154040.8566 | 11205.2871 | 0.11202 | -86524.2571 | 86524.2571
C | Xist Rating 1603 | -53.15 | 1114.33 | 150.28 | 35.5 | 2112.16 | 9784.59 | 10538 | 0.19 | 1.25 | 13.472 | 10.474 | 1 | 1 | 2950 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2353643.2528 | 169129.4527 | 8475.7509 | 14038.917 | 155090.5357 | 11215.7059 | 0.1124 | -86604.7079 | 86604.7079
C | Xist Rating 1604 | -53.12 | 1115.7 | 150.28 | 35.5 | 2111.48 | 9769.98 | 10538 | 0.19 | 1.25 | 13.468 | 10.483 | 1 | 1 | 2960 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2355778.236 | 170230.2856 | 8533.311 | 14086.5066 | 156143.7791 | 11226.0989 | 0.11278 | -86684.96 | 86684.96
C | Xist Rating 1605 | -53.13 | 1117.08 | 150.28 | 35.5 | 2110.3 | 9745.41 | 10537.5 | 0.18 | 1.25 | 13.475 | 10.491 | 1 | 1 | 2970 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2357373.924 | 171334.6829 | 8591.0659 | 14134.0961 | 157200.5867 | 11217.7918 | 0.11316 | -86620.8149 | 86620.8149
C | Xist Rating 1608 | -53.1 | 1121.3 | 150.28 | 35.5 | 2107.47 | 9685.92 | 10536.8 | 0.18 | 1.25 | 13.515 | 10.518 | 1 | 1 | 3000 | 152.4 | 2 | 1.7 | 19.05 | 1.3333 | 8 | E | Rod | 2363106.111 | 174669.2602 | 8765.4993 | 14276.8648 | 160392.3954 | 11250.0611 | 0.1143 | -86869.9901 | 86869.9901
C | Xist Rating 1609 | -94.57 | 101.112 | 150.281 | 35.8 | 2411.11 | 7514.55 | 58745.8 | 2.44 | 10.95 | 13.957 | 344.679 | 1 | 1 | 1000 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 243792.1543 | 23908.587 | 973.9444 | 5038.8934 | 18869.6936 | 359475.1036 | 0.038101 | -2775771.4634 | 2775771.4634
C | Xist Rating 1610 | -94.53 | 102.197 | 150.281 | 35.8 | 2408.2 | 7495.06 | 58284.3 | 2.42 | 10.85 | 13.967 | 338.261 | 1 | 1 | 1010 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 246110.8154 | 24338.2568 | 993.5206 | 5089.2824 | 19248.9744 | 352813.7439 | 0.038482 | -2724334.2099 | 2724334.2099
C | Xist Rating 1611 | -94.11 | 110.229 | 150.281 | 35.8 | 2402.37 | 7505.31 | 54967.8 | 2.43 | 10.07 | 14.021 | 293.13 | 1 | 1 | 1020 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 264810.8427 | 24771.7005 | 1013.2917 | 5139.6713 | 19632.0292 | 305972.808 | 0.038863 | -2362640.9187 | 2362640.9187
C | Xist Rating 1612 | -94.05 | 112.545 | 150.281 | 35.8 | 2382.07 | 7327.05 | 54178.4 | 2.35 | 9.89 | 13.787 | 283.452 | 1 | 1 | 1030 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 268090.0682 | 25208.9182 | 1033.2576 | 5190.0603 | 20018.8579 | 295860.3167 | 0.039244 | -2284554.9413 | 2284554.9413
C | Xist Rating 1613 | -93.96 | 113.705 | 150.281 | 35.8 | 2394.39 | 7453.23 | 53794.8 | 2.29 | 9.8 | 13.742 | 278.845 | 1 | 1 | 1040 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 272254.1149 | 25649.9098 | 1053.4182 | 5240.4492 | 20409.4606 | 291047.1104 | 0.039625 | -2247388.6384 | 2247388.6384
C | Xist Rating 1614 | -93.82 | 115.899 | 150.28 | 35.8 | 2401.95 | 7544.2 | 53044.8 | 2.23 | 9.63 | 13.71 | 269.689 | 1 | 1 | 1050 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 278383.603 | 26094.6753 | 1073.7737 | 5290.8381 | 20803.8372 | 281510.5594 | 0.040006 | -2173749.9198 | 2173749.9198
C | Xist Rating 1615 | -93.73 | 117.039 | 150.28 | 35.8 | 2416.14 | 7694.87 | 52677.9 | 2.19 | 9.54 | 13.694 | 265.377 | 1 | 1 | 1060 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 282782.6095 | 26543.2148 | 1094.3239 | 5341.2271 | 21201.9877 | 277018.537 | 0.040387 | -2139063.7131 | 2139063.7131
C | Xist Rating 1616 | -93.33 | 125.768 | 150.28 | 35.8 | 2394.76 | 7551.92 | 49858.6 | 2.17 | 8.9 | 13.64 | 232.269 | 1 | 1 | 1070 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 301184.1757 | 26995.5282 | 1115.0689 | 5391.616 | 21603.9122 | 242630.618 | 0.040768 | -1873529.3181 | 1873529.3181
C | Xist Rating 1617 | -93.23 | 127.482 | 150.28 | 35.8 | 2399.67 | 7613.87 | 49381.6 | 2.12 | 8.79 | 13.583 | 227.137 | 1 | 1 | 1080 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 305914.7309 | 27451.6155 | 1136.0087 | 5442.0049 | 22009.6106 | 237275.4457 | 0.041149 | -1832178.097 | 1832178.097
C | Xist Rating 1618 | -93.12 | 129.756 | 150.28 | 35.8 | 2397.75 | 7611.63 | 48761.3 | 2.07 | 8.65 | 13.502 | 220.532 | 1 | 1 | 1090 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 311122.449 | 27911.4768 | 1157.1433 | 5492.3939 | 22419.0829 | 230387.6967 | 0.04153 | -1778992.7247 | 1778992.7247
C | Xist Rating 1619 | -93.01 | 131.438 | 150.28 | 35.8 | 2403.34 | 7681.35 | 48308.7 | 2.03 | 8.55 | 13.488 | 215.758 | 1 | 1 | 1100 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 315890.2029 | 28375.112 | 1178.4727 | 5542.7828 | 22832.3292 | 225414.4022 | 0.041911 | -1740590.2633 | 1740590.2633
C | Xist Rating 1620 | -92.97 | 132.765 | 150.28 | 35.8 | 2395.79 | 7613.27 | 48010.7 | 1.96 | 8.49 | 13.339 | 212.917 | 1 | 1 | 1110 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 318077.0593 | 28842.5212 | 1199.9969 | 5593.1717 | 23249.3495 | 222414.7939 | 0.042292 | -1717428.083 | 1717428.083
C | Xist Rating 1621 | -92.47 | 142.405 | 150.28 | 35.8 | 2393.97 | 7673.62 | 45448 | 2 | 7.92 | 13.483 | 186.305 | 1 | 1 | 1120 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 340913.2978 | 29313.7043 | 1221.7158 | 5643.5607 | 23670.1436 | 194831.2384 | 0.042673 | -1504435.1791 | 1504435.1791
C | Xist Rating 1622 | -92.42 | 143.686 | 150.28 | 35.8 | 2391.87 | 7660.62 | 45189.6 | 1.94 | 7.86 | 13.387 | 184.006 | 1 | 1 | 1130 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 343678.2328 | 29788.6613 | 1243.6296 | 5693.9496 | 24094.7117 | 192405.4082 | 0.043054 | -1485703.5614 | 1485703.5614
C | Xist Rating 1623 | -92.29 | 146.031 | 150.28 | 35.8 | 2392.5 | 7684.14 | 44682.1 | 1.88 | 7.75 | 13.261 | 179.293 | 1 | 1 | 1140 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 349379.1675 | 30267.3923 | 1265.7381 | 5744.3385 | 24523.0538 | 187469.4573 | 0.043435 | -1447589.4565 | 1447589.4565
C | Xist Rating 1624 | -92.16 | 148.313 | 150.279 | 35.8 | 2399.21 | 7771.14 | 44187.2 | 1.84 | 7.64 | 13.228 | 174.711 | 1 | 1 | 1150 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 355834.0327 | 30749.8972 | 1288.0414 | 5794.7275 | 24955.1698 | 182691.7593 | 0.043816 | -1410697.3391 | 1410697.3391
C | Xist Rating 1625 | -92.05 | 150.674 | 150.279 | 35.8 | 2396.9 | 7764.19 | 43705 | 1.78 | 7.53 | 13.158 | 170.376 | 1 | 1 | 1160 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 361150.5106 | 31236.1761 | 1310.5395 | 5845.1164 | 25391.0597 | 178153.0313 | 0.044197 | -1375650.4847 | 1375650.4847
C | Xist Rating 1626 | -91.59 | 159.389 | 150.279 | 35.8 | 2397.01 | 7837 | 41834 | 1.8 | 7.13 | 13.25 | 153.292 | 1 | 1 | 1170 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 382057.0269 | 31726.2289 | 1333.2324 | 5895.5053 | 25830.7235 | 160444.3091 | 0.044578 | -1238908.4256 | 1238908.4256
C | Xist Rating 1627 | -91.53 | 160.123 | 150.279 | 35.8 | 2406.03 | 7938.74 | 41726.6 | 1.75 | 7.11 | 13.207 | 152.529 | 1 | 1 | 1180 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 385260.7417 | 32220.0556 | 1356.1201 | 5945.8943 | 26274.1613 | 159623.6036 | 0.044959 | -1232571.1554 | 1232571.1554
C | Xist Rating 1628 | -91.33 | 164.672 | 150.279 | 35.8 | 2394.14 | 7845.46 | 40887.4 | 1.71 | 6.93 | 13.126 | 145.47 | 1 | 1 | 1190 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 394247.8221 | 32717.6563 | 1379.2026 | 5996.2832 | 26721.3731 | 152267.6358 | 0.04534 | -1175770.3217 | 1175770.3217
C | Xist Rating 1629 | -91.24 | 165.846 | 150.279 | 35.8 | 2405.59 | 7978.75 | 40683.2 | 1.68 | 6.88 | 13.13 | 143.835 | 1 | 1 | 1200 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 398957.4791 | 33219.0309 | 1402.4799 | 6046.6721 | 27172.3588 | 150558.9322 | 0.045721 | -1162576.1653 | 1162576.1653
C | Xist Rating 1630 | -91.13 | 168.275 | 150.279 | 35.8 | 2400.58 | 7941.57 | 40282.5 | 1.63 | 6.8 | 13.058 | 140.667 | 1 | 1 | 1210 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 403957.5995 | 33724.1794 | 1425.9519 | 6097.0611 | 27627.1184 | 147236.8843 | 0.046102 | -1136924.1922 | 1136924.1922
C | Xist Rating 1631 | -90.66 | 178.269 | 150.279 | 35.8 | 2388.14 | 7886.6 | 38539.1 | 1.63 | 6.43 | 13.087 | 126.569 | 1 | 1 | 1220 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 425731.3297 | 34233.1019 | 1449.6188 | 6147.45 | 28085.6519 | 132608.2593 | 0.046483 | -1023965.8278 | 1023965.8278
C | Xist Rating 1632 | -90.53 | 180.549 | 150.279 | 35.8 | 2393.84 | 7966.63 | 38184.2 | 1.61 | 6.35 | 13.081 | 123.897 | 1 | 1 | 1230 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 432205.4182 | 34745.7984 | 1473.4804 | 6197.8389 | 28547.9594 | 129827.99 | 0.046864 | -1002497.325 | 1002497.325
C | Xist Rating 1633 | -90.42 | 182.969 | 150.279 | 35.8 | 2390.97 | 7952.42 | 37836.6 | 1.57 | 6.28 | 13.029 | 121.381 | 1 | 1 | 1240 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 437473.3899 | 35262.2687 | 1497.5369 | 6248.2279 | 29014.0408 | 127190.9474 | 0.047245 | -982134.7815 | 982134.7815
C | Xist Rating 1634 | -90.35 | 184.286 | 150.279 | 35.8 | 2391.77 | 7969.98 | 37665.3 | 1.53 | 6.24 | 12.99 | 120.221 | 1 | 1 | 1250 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 440769.7262 | 35782.513 | 1521.7881 | 6298.6168 | 29483.8962 | 125962.914 | 0.047626 | -972652.2329 | 972652.2329
C | Xist Rating 1635 | -90.19 | 187.729 | 150.279 | 35.8 | 2389.07 | 7966.33 | 37162.2 | 1.5 | 6.14 | 12.963 | 116.548 | 1 | 1 | 1260 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 448497.722 | 36306.5313 | 1546.2341 | 6349.0057 | 29957.5255 | 122133.1208 | 0.048007 | -943079.5848 | 943079.5848
C | Xist Rating 1636 | -89.73 | 197.205 | 150.279 | 35.8 | 2382.7 | 7971.21 | 35778.3 | 1.51 | 5.85 | 13.016 | 106.503 | 1 | 1 | 1270 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 469880.3535 | 36834.3235 | 1570.8749 | 6399.3947 | 30434.9288 | 111722.0555 | 0.048388 | -862688.0982 | 862688.0982
C | Xist Rating 1637 | -89.61 | 199.694 | 150.279 | 35.8 | 2382.46 | 7985.81 | 35478.1 | 1.47 | 5.79 | 12.975 | 104.546 | 1 | 1 | 1280 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 475762.9672 | 37365.8896 | 1595.7105 | 6449.7836 | 30916.106 | 109665.194 | 0.048769 | -846805.5586 | 846805.5586
C | Xist Rating 1638 | -89.47 | 202.13 | 150.279 | 35.7 | 2387.12 | 8056.02 | 35183.8 | 1.43 | 5.73 | 12.97 | 102.626 | 1 | 1 | 1290 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 482508.5656 | 37901.2296 | 1620.7408 | 6500.1725 | 31401.0571 | 107649.4025 | 0.04915 | -831240.1515 | 831240.1515
C | Xist Rating 1639 | -89.26 | 205.551 | 150.279 | 35.8 | 2394.88 | 8172.09 | 34752.9 | 1.4 | 5.64 | 12.975 | 99.753 | 1 | 1 | 1300 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 492269.9789 | 38440.3436 | 1645.966 | 6550.5615 | 31889.7821 | 104651.8445 | 0.049531 | -808093.8029 | 808093.8029
C | Xist Rating 1640 | -89.14 | 207.458 | 150.279 | 35.7 | 2399.65 | 8241.67 | 34541.5 | 1.37 | 5.59 | 12.949 | 98.446 | 1 | 1 | 1310 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 497826.5897 | 38983.2316 | 1671.3859 | 6600.9504 | 32382.2811 | 103277.721 | 0.049912 | -797483.1853 | 797483.1853
C | Xist Rating 1641 | -88.68 | 217.032 | 150.279 | 35.7 | 2394.19 | 8256.87 | 33364.4 | 1.37 | 5.35 | 12.993 | 90.729 | 1 | 1 | 1320 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 519615.8441 | 39529.8934 | 1697.0007 | 6651.3394 | 32878.5541 | 95275.1473 | 0.050293 | -735689.4327 | 735689.4327
C | Xist Rating 1642 | -88.52 | 220.67 | 150.279 | 35.7 | 2388.65 | 8218.32 | 32981.4 | 1.34 | 5.28 | 12.925 | 88.424 | 1 | 1 | 1330 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 527103.3955 | 40080.3293 | 1722.8102 | 6701.7283 | 33378.601 | 92860.7171 | 0.050674 | -717045.8427 | 717045.8427
C | Xist Rating 1643 | -88.34 | 224.207 | 150.279 | 35.7 | 2389.92 | 8260.48 | 32608.5 | 1.31 | 5.2 | 12.905 | 86.183 | 1 | 1 | 1340 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 535836.7934 | 40634.539 | 1748.8145 | 6752.1172 | 33882.4218 | 90516.3416 | 0.051055 | -698943.1968 | 698943.1968
C | Xist Rating 1644 | -88.22 | 226.13 | 150.279 | 35.7 | 2394.63 | 8330.87 | 32425.6 | 1.28 | 5.16 | 12.884 | 85.153 | 1 | 1 | 1350 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 541497.6819 | 41192.5227 | 1775.0136 | 6802.5062 | 34390.0165 | 89429.2118 | 0.051436 | -690548.6684 | 690548.6684
C | Xist Rating 1645 | -88.1 | 227.25 | 150.279 | 35.7 | 2409.97 | 8529.18 | 32304.8 | 1.27 | 5.14 | 12.91 | 84.44 | 1 | 1 | 1360 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 547665.6825 | 41754.2803 | 1801.4075 | 6852.8951 | 34901.3852 | 88690.3134 | 0.051817 | -684843.0905 | 684843.0905
C | Xist Rating 1646 | -87.52 | 241.026 | 150.279 | 35.7 | 2383.43 | 8315.85 | 30904.3 | 1.26 | 4.86 | 12.906 | 76.2 | 1 | 1 | 1370 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 574468.5992 | 42319.8119 | 1827.9962 | 6903.284 | 35416.5279 | 80132.1982 | 0.052198 | -618759.5937 | 618759.5937
C | Xist Rating 1647 | -87.46 | 242.408 | 150.279 | 35.7 | 2382.87 | 8318.15 | 30796.1 | 1.23 | 4.84 | 12.884 | 75.665 | 1 | 1 | 1380 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 577626.751 | 42889.1174 | 1854.7797 | 6953.673 | 35935.4444 | 79558.2667 | 0.052579 | -614327.8466 | 614327.8466
C | Xist Rating 1648 | -87.32 | 245.473 | 150.278 | 35.7 | 2382.01 | 8330.39 | 30528.1 | 1.21 | 4.79 | 12.86 | 74.232 | 1 | 1 | 1390 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 584719.1407 | 43462.1969 | 1881.7579 | 7004.0619 | 36458.135 | 78059.3375 | 0.05296 | -602753.5127 | 602753.5127
C | Xist Rating 1649 | -87.17 | 248.536 | 150.278 | 35.7 | 2382.3 | 8356.57 | 30266.1 | 1.19 | 4.73 | 12.842 | 72.843 | 1 | 1 | 1400 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 592087.3128 | 44039.0502 | 1908.931 | 7054.4508 | 36984.5994 | 76606.3535 | 0.053341 | -591533.9556 | 591533.9556
C | Xist Rating 1650 | -87 | 252.133 | 150.278 | 35.7 | 2381.23 | 8370.72 | 29958.4 | 1.17 | 4.67 | 12.828 | 71.21 | 1 | 1 | 1410 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 600386.6636 | 44619.6776 | 1936.2988 | 7104.8398 | 37514.8378 | 74900.0674 | 0.053722 | -578358.4668 | 578358.4668
C | Xist Rating 1651 | -86.5 | 262.37 | 150.279 | 35.7 | 2376.5 | 8396.07 | 29052.9 | 1.17 | 4.49 | 12.879 | 66.326 | 1 | 1 | 1420 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 623522.305 | 45204.0788 | 1963.8614 | 7155.2287 | 38048.8501 | 69838.5668 | 0.054103 | -539274.9008 | 539274.9008
C | Xist Rating 1652 | -86.43 | 264.533 | 150.278 | 35.7 | 2372.01 | 8353.86 | 28911.6 | 1.14 | 4.47 | 12.836 | 65.695 | 1 | 1 | 1430 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 627474.9213 | 45792.254 | 1991.6188 | 7205.6176 | 38586.6364 | 69162.1205 | 0.054484 | -534051.5617 | 534051.5617
C | Xist Rating 1653 | -86.2 | 269.251 | 150.278 | 35.7 | 2370.16 | 8366.74 | 28542.8 | 1.12 | 4.39 | 12.825 | 63.841 | 1 | 1 | 1440 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 638167.9502 | 46384.2032 | 2019.571 | 7256.0066 | 39128.1966 | 67225.9378 | 0.054865 | -519100.872 | 519100.872
C | Xist Rating 1654 | -86.06 | 272.352 | 150.278 | 35.7 | 2369.27 | 8378.09 | 28317.7 | 1.1 | 4.35 | 12.809 | 62.758 | 1 | 1 | 1450 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 645275.423 | 46979.9262 | 2047.718 | 7306.3955 | 39673.5307 | 66089.8673 | 0.055246 | -510328.4367 | 510328.4367
C | Xist Rating 1655 | -85.94 | 274.157 | 150.278 | 35.7 | 2375.91 | 8475.43 | 28184.3 | 1.09 | 4.33 | 12.815 | 62.122 | 1 | 1 | 1460 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 651372.3579 | 47579.4233 | 2076.0598 | 7356.7844 | 40222.6388 | 65427.7433 | 0.055627 | -505215.691 | 505215.691
C | Xist Rating 1656 | -85.44 | 285.941 | 150.278 | 35.7 | 2359.92 | 8365.84 | 27311 | 1.08 | 4.16 | 12.827 | 57.853 | 1 | 1 | 1470 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 674797.8847 | 48182.6942 | 2104.5964 | 7407.1734 | 40775.5209 | 60993.0647 | 0.056008 | -470972.2782 | 470972.2782
C | Xist Rating 1657 | -85.26 | 289.583 | 150.278 | 35.7 | 2360.55 | 8400.45 | 27067 | 1.06 | 4.11 | 12.82 | 56.735 | 1 | 1 | 1480 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 683575.1507 | 48789.7391 | 2133.3277 | 7457.5623 | 41332.1768 | 59820.7219 | 0.056389 | -461919.7576 | 461919.7576
C | Xist Rating 1658 | -85.05 | 292.685 | 150.278 | 35.7 | 2369.2 | 8533.87 | 26867.7 | 1.04 | 4.07 | 12.819 | 55.843 | 1 | 1 | 1490 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 693429.302 | 49400.558 | 2162.2539 | 7507.9512 | 41892.6067 | 58883.2785 | 0.05677 | -454681.0684 | 454681.0684
C | Xist Rating 1659 | -84.89 | 295.879 | 150.278 | 35.7 | 2370.8 | 8577.84 | 26671.2 | 1.02 | 4.03 | 12.806 | 54.986 | 1 | 1 | 1500 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 701469.9332 | 50015.1507 | 2191.3748 | 7558.3402 | 42456.8106 | 57981.1315 | 0.057151 | -447714.9283 | 447714.9283
C | Xist Rating 1660 | -84.68 | 299.548 | 150.278 | 35.7 | 2375.09 | 8662.56 | 26439.6 | 1 | 3.99 | 12.804 | 53.961 | 1 | 1 | 1510 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 711453.4593 | 50633.5174 | 2220.6906 | 7608.7291 | 43024.7883 | 56905.0548 | 0.057532 | -439405.749 | 439405.749
C | Xist Rating 1661 | -84.12 | 311.015 | 150.279 | 35.7 | 2373.56 | 8739.22 | 25681.8 | 1.01 | 3.85 | 12.861 | 50.517 | 1 | 1 | 1520 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 738212.7634 | 51255.6581 | 2250.2011 | 7659.118 | 43596.54 | 53346.8518 | 0.057913 | -411930.249 | 411930.249
C | Xist Rating 1662 | -83.97 | 315.028 | 150.278 | 35.7 | 2365.94 | 8664.71 | 25469.1 | 0.98 | 3.81 | 12.826 | 49.665 | 1 | 1 | 1530 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 745337.3463 | 51881.5727 | 2279.9064 | 7709.507 | 44172.0657 | 52439.0605 | 0.058294 | -404920.5248 | 404920.5248
C | Xist Rating 1663 | -83.84 | 317.107 | 150.278 | 35.7 | 2371.56 | 8754.86 | 25364.3 | 0.96 | 3.79 | 12.819 | 49.265 | 1 | 1 | 1540 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 752038.2769 | 52511.2612 | 2309.8065 | 7759.8959 | 44751.3653 | 52011.1239 | 0.058675 | -401616.1119 | 401616.1119
C | Xist Rating 1664 | -83.55 | 323.071 | 150.278 | 35.7 | 2370.21 | 8784.09 | 25021.8 | 0.95 | 3.72 | 12.815 | 47.826 | 1 | 1 | 1550 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 765746.1149 | 53144.7237 | 2339.9013 | 7810.2848 | 45334.4388 | 50513.0705 | 0.059056 | -390048.5405 | 390048.5405
C | Xist Rating 1665 | -83.38 | 324.926 | 150.278 | 35.7 | 2383.14 | 8979.36 | 24921.2 | 0.94 | 3.7 | 12.829 | 47.427 | 1 | 1 | 1560 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 774344.1476 | 53781.9601 | 2370.191 | 7860.6738 | 45921.2863 | 50096.1258 | 0.059437 | -386829.0044 | 386829.0044
C | Xist Rating 1666 | -82.84 | 338.697 | 150.278 | 35.7 | 2361.07 | 8784.2 | 24162.8 | 0.93 | 3.56 | 12.839 | 44.306 | 1 | 1 | 1570 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 799687.3258 | 54422.9704 | 2400.6755 | 7911.0627 | 46511.9077 | 46852.0039 | 0.059818 | -361778.7548 | 361778.7548
C | Xist Rating 1667 | -82.66 | 341.92 | 150.278 | 35.7 | 2364.76 | 8859.61 | 24008.1 | 0.92 | 3.53 | 12.833 | 43.726 | 1 | 1 | 1580 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 808558.7392 | 55067.7547 | 2431.3547 | 7961.4516 | 47106.303 | 46245.5431 | 0.0602 | -357095.8253 | 357095.8253
C | Xist Rating 1668 | -82.49 | 345.178 | 150.278 | 35.7 | 2367.94 | 8928.77 | 23855.6 | 0.9 | 3.5 | 12.826 | 43.162 | 1 | 1 | 1590 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 817360.7933 | 55716.3129 | 2462.2288 | 8011.8406 | 47704.4723 | 45646.3807 | 0.060581 | -352469.2519 | 352469.2519
C | Xist Rating 1669 | -82.25 | 349.413 | 150.278 | 35.7 | 2371.7 | 9017.06 | 23645.8 | 0.89 | 3.46 | 12.828 | 42.358 | 1 | 1 | 1600 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 828702.8121 | 56368.6451 | 2493.2976 | 8062.2295 | 48306.4156 | 44807.5311 | 0.060962 | -345991.8783 | 345991.8783
C | Xist Rating 1670 | -82.15 | 351.688 | 150.278 | 35.7 | 2371.76 | 9032.88 | 23557.2 | 0.87 | 3.45 | 12.812 | 42.07 | 1 | 1 | 1610 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 834119.5309 | 57024.7512 | 2524.5612 | 8112.6185 | 48912.1327 | 44494.0413 | 0.061343 | -343571.1926 | 343571.1926
C | Xist Rating 1671 | -81.49 | 366.978 | 150.279 | 35.7 | 2357.5 | 8956.68 | 22805.5 | 0.87 | 3.31 | 12.848 | 39.179 | 1 | 1 | 1620 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 865150.635 | 57684.6312 | 2556.0196 | 8163.0074 | 49521.6238 | 41499.013 | 0.061724 | -320444.3784 | 320444.3784
C | Xist Rating 1672 | -81.35 | 368.908 | 150.279 | 35.7 | 2365.17 | 9083.29 | 22723.9 | 0.86 | 3.29 | 12.853 | 38.901 | 1 | 1 | 1630 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 872530.1344 | 58348.2852 | 2587.6728 | 8213.3963 | 50134.8889 | 41206.2477 | 0.062105 | -318183.7225 | 318183.7225
C | Xist Rating 1673 | -81.19 | 372.313 | 150.279 | 35.7 | 2365.75 | 9116.97 | 22589 | 0.84 | 3.27 | 12.84 | 38.45 | 1 | 1 | 1640 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 880799.4797 | 59015.7131 | 2619.5208 | 8263.7853 | 50751.9278 | 40723.1398 | 0.062486 | -314453.2912 | 314453.2912
C | Xist Rating 1674 | -80.99 | 376.905 | 150.279 | 35.7 | 2361.93 | 9095.3 | 22403.4 | 0.83 | 3.24 | 12.825 | 37.814 | 1 | 1 | 1650 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 890223.2266 | 59686.915 | 2651.5635 | 8314.1742 | 51372.7408 | 40057.0721 | 0.062867 | -309310.0927 | 309310.0927
C | Xist Rating 1675 | -80.78 | 381.254 | 150.279 | 35.7 | 2363.03 | 9146.6 | 22221.3 | 0.82 | 3.2 | 12.823 | 37.18 | 1 | 1 | 1660 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 900914.6396 | 60361.8907 | 2683.8011 | 8364.5631 | 51997.3276 | 39393.7706 | 0.063248 | -304188.2543 | 304188.2543
C | Xist Rating 1676 | -80.19 | 395.07 | 150.279 | 35.7 | 2350.85 | 9081.39 | 21633.4 | 0.81 | 3.1 | 12.853 | 35.098 | 1 | 1 | 1670 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 928750.3095 | 61040.6405 | 2716.2334 | 8414.9521 | 52625.6884 | 37228.5502 | 0.063629 | -287468.9966 | 287468.9966
C | Xist Rating 1677 | -80.07 | 397.111 | 150.279 | 35.7 | 2355.29 | 9162.93 | 21561 | 0.8 | 3.08 | 12.85 | 34.876 | 1 | 1 | 1680 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 935311.5672 | 61723.1641 | 2748.8606 | 8465.341 | 53257.8232 | 36992.8105 | 0.06401 | -285648.6769 | 285648.6769
C | Xist Rating 1678 | -79.83 | 402.94 | 150.279 | 35.6 | 2350.12 | 9129.68 | 21346.6 | 0.79 | 3.04 | 12.835 | 34.18 | 1 | 1 | 1690 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 946957.3528 | 62409.4618 | 2781.6825 | 8515.7299 | 53893.7318 | 36263.9915 | 0.064391 | -280020.9302 | 280020.9302
C | Xist Rating 1679 | -79.64 | 406.764 | 150.279 | 35.6 | 2350.9 | 9171.31 | 21206.5 | 0.78 | 3.02 | 12.83 | 33.73 | 1 | 1 | 1700 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 956261.4876 | 63099.5333 | 2814.6992 | 8566.1189 | 54533.4144 | 35791.1346 | 0.064772 | -276369.6543 | 276369.6543
C | Xist Rating 1680 | -79.43 | 411.306 | 150.279 | 35.6 | 2351.1 | 9209.5 | 21045.1 | 0.77 | 2.99 | 12.825 | 33.22 | 1 | 1 | 1710 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 967021.5366 | 63793.3788 | 2847.9107 | 8616.5078 | 55176.871 | 35255.8569 | 0.065153 | -272236.3816 | 272236.3816
C | Xist Rating 1681 | -78.89 | 424.089 | 150.279 | 35.6 | 2340.39 | 9152.32 | 20567.8 | 0.76 | 2.9 | 12.848 | 31.65 | 1 | 1 | 1720 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 992533.6547 | 64490.9982 | 2881.317 | 8666.8967 | 55824.1015 | 33621.3007 | 0.065534 | -259614.7722 | 259614.7722
C | Xist Rating 1682 | -78.64 | 429.788 | 150.279 | 35.6 | 2338.12 | 9161.94 | 20375 | 0.75 | 2.87 | 12.84 | 31.056 | 1 | 1 | 1730 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1004895.9186 | 65192.3916 | 2914.9181 | 8717.2857 | 56475.1059 | 32998.3811 | 0.065915 | -254804.7518 | 254804.7518
C | Xist Rating 1683 | -78.52 | 432.517 | 150.279 | 35.6 | 2339.26 | 9199.41 | 20289.9 | 0.74 | 2.85 | 12.832 | 30.813 | 1 | 1 | 1740 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1011769.7174 | 65897.5589 | 2948.714 | 8767.6746 | 57129.8843 | 32739.8663 | 0.066296 | -252808.5693 | 252808.5693
C | Xist Rating 1684 | -78.29 | 437.807 | 150.279 | 35.6 | 2336.41 | 9194.83 | 20124 | 0.73 | 2.82 | 12.826 | 30.322 | 1 | 1 | 1750 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1022896.6529 | 66606.5001 | 2982.7046 | 8818.0635 | 57788.4366 | 32223.8106 | 0.066677 | -248823.7238 | 248823.7238
C | Xist Rating 1685 | -78.15 | 441.749 | 150.279 | 35.6 | 2332.47 | 9163.67 | 20000.5 | 0.72 | 2.8 | 12.815 | 29.962 | 1 | 1 | 1760 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1030366.29 | 67319.2153 | 3016.8901 | 8868.4525 | 58450.7628 | 31843.4046 | 0.067058 | -245886.3299 | 245886.3299
C | Xist Rating 1686 | -77.6 | 456.888 | 150.279 | 35.6 | 2313.81 | 9000.76 | 19497.9 | 0.72 | 2.71 | 12.973 | 28.408 | 1 | 1 | 1770 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1057152.0233 | 68035.7044 | 3051.2703 | 8918.8414 | 59116.863 | 30242.7397 | 0.067439 | -233526.4192 | 233526.4192
C | Xist Rating 1687 | -77.42 | 460.94 | 150.279 | 35.6 | 2313.06 | 9017.64 | 19383.9 | 0.71 | 2.69 | 12.964 | 28.093 | 1 | 1 | 1780 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1066181.8764 | 68755.9675 | 3085.8453 | 8969.2303 | 59786.7371 | 29908.9388 | 0.06782 | -230948.8975 | 230948.8975
C | Xist Rating 1688 | -77.22 | 463.24 | 150.279 | 35.6 | 2321.97 | 9169.24 | 19326.7 | 0.7 | 2.68 | 12.838 | 27.962 | 1 | 1 | 1790 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1075629.3828 | 69480.0045 | 3120.6151 | 9019.6193 | 60460.3852 | 29759.5427 | 0.068201 | -229795.3006 | 229795.3006
C | Xist Rating 1689 | -77.04 | 470.213 | 150.279 | 35.6 | 2308.55 | 9014.83 | 19122.8 | 0.69 | 2.65 | 12.949 | 27.372 | 1 | 1 | 1800 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1085510.2212 | 70207.8154 | 3155.5797 | 9070.0082 | 61137.8072 | 29146.6782 | 0.068582 | -225062.9234 | 225062.9234
C | Xist Rating 1690 | -76.88 | 474.137 | 150.279 | 35.6 | 2308.35 | 9040.22 | 19012.5 | 0.68 | 2.63 | 12.939 | 27.072 | 1 | 1 | 1810 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1094474.1439 | 70939.4003 | 3190.7391 | 9120.3971 | 61819.0031 | 28828.0761 | 0.068963 | -222602.7625 | 222602.7625
C | Xist Rating 1691 | -76.26 | 489.536 | 150.279 | 35.6 | 2295.57 | 8963.27 | 18563.5 | 0.68 | 2.55 | 12.977 | 25.787 | 1 | 1 | 1820 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1123764.1555 | 71674.7591 | 3226.0933 | 9170.7861 | 62503.973 | 27499.6576 | 0.069344 | -212345.0669 | 212345.0669
C | Xist Rating 1692 | -76.15 | 487.061 | 150.279 | 35.6 | 2319.26 | 9315.78 | 18632.1 | 0.67 | 2.56 | 13.008 | 25.992 | 1 | 1 | 1830 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1129621.0949 | 72413.8918 | 3261.6423 | 9221.175 | 63192.7168 | 27707.5641 | 0.069725 | -213950.4657 | 213950.4657
C | Xist Rating 1693 | -75.89 | 490.245 | 150.279 | 35.6 | 2329.95 | 9516.54 | 18546.3 | 0.66 | 2.55 | 13.031 | 25.764 | 1 | 1 | 1840 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1142246.3377 | 73156.7985 | 3297.386 | 9271.5639 | 63885.2346 | 27465.2165 | 0.070106 | -212079.1213 | 212079.1213
C | Xist Rating 1694 | -75.65 | 495.652 | 150.279 | 35.6 | 2327.6 | 9518.69 | 18410.5 | 0.65 | 2.52 | 13.027 | 25.412 | 1 | 1 | 1850 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1153679.5952 | 73903.4791 | 3333.3246 | 9321.9529 | 64581.5263 | 27092.4985 | 0.070487 | -209201.092 | 209201.092
C | Xist Rating 1695 | -75.43 | 501.692 | 150.279 | 35.6 | 2322.22 | 9475.4 | 18260.2 | 0.64 | 2.5 | 13.011 | 25.023 | 1 | 1 | 1860 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1165039.1962 | 74653.9337 | 3369.4579 | 9372.3418 | 65281.5919 | 26680.6033 | 0.070868 | -206020.5465 | 206020.5465
C | Xist Rating 1696 | -74.83 | 515.787 | 150.279 | 35.6 | 2315.11 | 9476.6 | 17880.7 | 0.64 | 2.43 | 13.049 | 23.989 | 1 | 1 | 1870 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1194103.6416 | 75408.1622 | 3405.7861 | 9422.7307 | 65985.4315 | 25612.5671 | 0.071249 | -197773.4537 | 197773.4537
C | Xist Rating 1697 | -74.62 | 521.813 | 150.279 | 35.6 | 2309.11 | 9422.06 | 17739.9 | 0.63 | 2.41 | 13.031 | 23.638 | 1 | 1 | 1880 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1204923.6164 | 76166.1647 | 3442.309 | 9473.1197 | 66693.045 | 25239.8455 | 0.07163 | -194895.3968 | 194895.3968
C | Xist Rating 1698 | -74.34 | 525.785 | 150.279 | 35.6 | 2316.17 | 9571.55 | 17647.9 | 0.62 | 2.39 | 13.06 | 23.413 | 1 | 1 | 1890 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1217807.4434 | 76927.941 | 3479.0267 | 9523.5086 | 67404.4324 | 25000.3468 | 0.072011 | -193046.0514 | 193046.0514
C | Xist Rating 1699 | -74.23 | 530.215 | 150.279 | 35.6 | 2309.28 | 9485.55 | 17556.1 | 0.61 | 2.38 | 13.035 | 23.203 | 1 | 1 | 1900 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1224414.8952 | 77693.4914 | 3515.9392 | 9573.8976 | 68119.5938 | 24773.4701 | 0.072392 | -191294.1696 | 191294.1696
C | Xist Rating 1700 | -74.02 | 534.366 | 150.279 | 35.6 | 2309.84 | 9525.49 | 17466.1 | 0.6 | 2.36 | 13.037 | 22.99 | 1 | 1 | 1910 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1234299.9614 | 78462.8156 | 3553.0464 | 9624.2865 | 68838.5291 | 24544.7769 | 0.072773 | -189528.2614 | 189528.2614
C | Xist Rating 1701 | -73.31 | 551.504 | 150.279 | 35.6 | 2300.95 | 9519.11 | 17051.4 | 0.6 | 2.29 | 13.079 | 21.924 | 1 | 1 | 1920 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 10 | E | Rod | 1268983.1288 | 79235.9138 | 3590.3485 | 9674.6754 | 69561.2384 | 23443.4127 | 0.073154 | -181023.8187 | 181023.8187
C | Xist Rating 1702 | -73.06 | 557.608 | 150.279 | 35.6 | 2298.08 | 9515.8 | 16924.5 | 0.59 | 2.27 | 13.065 | 21.631 | 1 | 1 | 1930 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1281427.7926 | 80012.786 | 3627.8454 | 9725.0644 | 70287.7216 | 23130.6208 | 0.073535 | -178608.5225 | 178608.5225
C | Xist Rating 1703 | -72.89 | 559.547 | 150.279 | 35.6 | 2305.99 | 9668.43 | 16883.2 | 0.59 | 2.26 | 13.092 | 21.539 | 1 | 1 | 1940 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1290309.7865 | 80793.432 | 3665.537 | 9775.4533 | 71017.9787 | 23039.9195 | 0.073916 | -177908.1508 | 177908.1508
C | Xist Rating 1704 | -72.7 | 565.524 | 150.279 | 35.6 | 2298.55 | 9579.72 | 16773.2 | 0.57 | 2.24 | 13.088 | 21.301 | 1 | 1 | 1950 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1299885.1902 | 81577.8521 | 3703.4235 | 9825.8422 | 71752.0098 | 22773.133 | 0.074297 | -175848.0965 | 175848.0965
C | Xist Rating 1705 | -72.43 | 572.141 | 150.279 | 35.6 | 2295.02 | 9569.55 | 16637.8 | 0.57 | 2.22 | 13.096 | 20.988 | 1 | 1 | 1960 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1313075.0378 | 82366.046 | 3741.5047 | 9876.2312 | 72489.8148 | 22451.8276 | 0.074678 | -173367.0614 | 173367.0614
C | Xist Rating 1706 | -71.79 | 587.668 | 150.279 | 35.6 | 2287.26 | 9563.88 | 16303.9 | 0.57 | 2.16 | 13.138 | 20.185 | 1 | 1 | 1970 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1344149.5097 | 83158.0139 | 3779.7807 | 9926.6201 | 73231.3938 | 21623.3734 | 0.075059 | -166969.9578 | 166969.9578
C | Xist Rating 1707 | -71.57 | 592.434 | 150.279 | 35.6 | 2287.94 | 9611.45 | 16215 | 0.56 | 2.15 | 13.137 | 19.992 | 1 | 1 | 1980 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1355453.446 | 83953.7557 | 3818.2515 | 9977.009 | 73976.7467 | 21414.5899 | 0.07544 | -165357.7871 | 165357.7871
C | Xist Rating 1708 | -71.33 | 598.732 | 150.279 | 35.6 | 2283.64 | 9581.41 | 16102.1 | 0.55 | 2.13 | 13.132 | 19.751 | 1 | 1 | 1990 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1367288.3445 | 84753.2715 | 3856.9171 | 10027.398 | 74725.8735 | 21155.6458 | 0.075821 | -163358.2891 | 163358.2891
C | Xist Rating 1709 | -71.11 | 603.623 | 150.279 | 35.6 | 2284.21 | 9627.1 | 16015.5 | 0.54 | 2.12 | 13.129 | 19.569 | 1 | 1 | 2000 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1378801.6928 | 85556.5612 | 3895.7775 | 10077.7869 | 75478.7743 | 20957.9586 | 0.076202 | -161831.8011 | 161831.8011
C | Xist Rating 1710 | -70.96 | 607.279 | 150.279 | 35.6 | 2283.34 | 9637.22 | 15954.3 | 0.53 | 2.11 | 13.128 | 19.446 | 1 | 1 | 2010 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1386624.4319 | 86363.6249 | 3934.8326 | 10128.1758 | 76235.449 | 20821.5246 | 0.076583 | -160778.2935 | 160778.2935
C | Xist Rating 1711 | -70.26 | 624.866 | 150.279 | 35.6 | 2273.14 | 9600.17 | 15615.5 | 0.53 | 2.05 | 13.166 | 18.678 | 1 | 1 | 2020 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1420407.8992 | 87174.4624 | 3974.0826 | 10178.5648 | 76995.8977 | 20028.9002 | 0.076964 | -154657.8583 | 154657.8583
C | Xist Rating 1712 | -69.99 | 631.427 | 150.279 | 35.6 | 2271.1 | 9614.06 | 15500.4 | 0.53 | 2.03 | 13.163 | 18.435 | 1 | 1 | 2030 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1434033.8597 | 87989.074 | 4013.5273 | 10228.9537 | 77760.1203 | 19779.5283 | 0.077345 | -152732.2742 | 152732.2742
C | Xist Rating 1713 | -69.82 | 636.056 | 150.279 | 35.6 | 2268.4 | 9595.95 | 15432.3 | 0.52 | 2.02 | 13.158 | 18.308 | 1 | 1 | 2040 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1442829.4304 | 88807.4594 | 4053.1669 | 10279.3426 | 78528.1168 | 19638.4918 | 0.077726 | -151643.2281 | 151643.2281
C | Xist Rating 1714 | -69.61 | 639.87 | 150.279 | 35.6 | 2271.37 | 9679.89 | 15364.9 | 0.52 | 2.01 | 13.159 | 18.168 | 1 | 1 | 2050 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1453381.5219 | 89629.6188 | 4093.0012 | 10329.7316 | 79299.8873 | 19496.2168 | 0.078107 | -150544.6181 | 150544.6181
C | Xist Rating 1715 | -69.4 | 646.563 | 150.279 | 35.6 | 2264.69 | 9604.9 | 15264.8 | 0.51 | 1.99 | 13.153 | 17.976 | 1 | 1 | 2060 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1464264.7605 | 90455.5522 | 4133.0303 | 10380.1205 | 80075.4317 | 19287.4589 | 0.078488 | -148932.6449 | 148932.6449
C | Xist Rating 1716 | -68.66 | 665.486 | 150.279 | 35.6 | 2254.39 | 9571.53 | 14936.7 | 0.51 | 1.94 | 13.191 | 17.274 | 1 | 1 | 2070 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1500264.9835 | 91285.2594 | 4173.2542 | 10430.5094 | 80854.75 | 18563.2381 | 0.078869 | -143340.4037 | 143340.4037
C | Xist Rating 1717 | -68.49 | 669.917 | 150.279 | 35.6 | 2252.5 | 9567.19 | 14874 | 0.5 | 1.93 | 13.186 | 17.16 | 1 | 1 | 2080 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1508988.0425 | 92118.7407 | 4213.6729 | 10480.8984 | 81637.8423 | 18435.333 | 0.07925 | -142352.7549 | 142352.7549
C | Xist Rating 1718 | -68.28 | 675.524 | 150.279 | 35.6 | 2250.26 | 9566.22 | 14791.4 | 0.49 | 1.91 | 13.182 | 17.003 | 1 | 1 | 2090 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1520104.6362 | 92955.9958 | 4254.2864 | 10531.2873 | 82424.7085 | 18262.7073 | 0.079631 | -141019.7851 | 141019.7851
C | Xist Rating 1719 | -68.07 | 681.138 | 150.279 | 35.6 | 2247.38 | 9553.72 | 14709.7 | 0.49 | 1.9 | 13.178 | 16.848 | 1 | 1 | 2100 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1530775.9184 | 93797.0249 | 4295.0947 | 10581.6762 | 83215.3487 | 18104.4509 | 0.080012 | -139797.7707 | 139797.7707
C | Xist Rating 1720 | -67.88 | 686.123 | 150.279 | 35.6 | 2245.19 | 9548.57 | 14639 | 0.48 | 1.89 | 13.175 | 16.718 | 1 | 1 | 2110 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1540476.4984 | 94641.828 | 4336.0977 | 10632.0652 | 84009.7628 | 17959.7406 | 0.080393 | -138680.356 | 138680.356
C | Xist Rating 1721 | -67.2 | 704.149 | 150.279 | 35.6 | 2235.34 | 9509.28 | 14359.4 | 0.48 | 1.84 | 13.213 | 16.155 | 1 | 1 | 2120 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1574012.4257 | 95490.4049 | 4377.2956 | 10682.4541 | 84807.9508 | 17379.634 | 0.080774 | -134200.9267 | 134200.9267
C | Xist Rating 1722 | -66.94 | 711.053 | 150.279 | 35.6 | 2231.88 | 9494.98 | 14264 | 0.47 | 1.83 | 13.208 | 15.979 | 1 | 1 | 2130 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1586984.9696 | 96342.7558 | 4418.6882 | 10732.843 | 85609.9128 | 17186.8615 | 0.081155 | -132712.3885 | 132712.3885
C | Xist Rating 1723 | -66.72 | 717.984 | 150.279 | 35.6 | 2226.33 | 9442.75 | 14170.1 | 0.47 | 1.81 | 13.205 | 15.808 | 1 | 1 | 2140 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1598469.3187 | 97198.8807 | 4460.2756 | 10783.232 | 86415.6487 | 17011.9256 | 0.081536 | -131361.58 | 131361.58
C | Xist Rating 1724 | -66.58 | 721.79 | 150.279 | 35.6 | 2225.07 | 9443.98 | 14123.7 | 0.46 | 1.8 | 13.201 | 15.731 | 1 | 1 | 2150 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1606033.2753 | 98058.7795 | 4502.0578 | 10833.6209 | 87225.1586 | 16921.8398 | 0.081917 | -130665.9615 | 130665.9615
C | Xist Rating 1725 | -66.39 | 726.72 | 150.279 | 35.6 | 2224.04 | 9458.64 | 14059.2 | 0.46 | 1.79 | 13.198 | 15.618 | 1 | 1 | 2160 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1616254.3488 | 98922.4522 | 4544.0348 | 10884.0098 | 88038.4424 | 16807.0778 | 0.082298 | -129779.7999 | 129779.7999
C | Xist Rating 1726 | -65.67 | 746.296 | 150.279 | 35.6 | 2212.45 | 9393.4 | 13786.1 | 0.46 | 1.75 | 13.235 | 15.099 | 1 | 1 | 2170 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1651142.5852 | 99789.8989 | 4586.2066 | 10934.3988 | 88855.5001 | 16272.474 | 0.082679 | -125651.731 | 125651.731
C | Xist Rating 1727 | -65.41 | 752.975 | 150.279 | 35.6 | 2211.03 | 9414.44 | 13699.2 | 0.45 | 1.74 | 13.232 | 14.944 | 1 | 1 | 2180 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1664850.3143 | 100661.1195 | 4628.5732 | 10984.7877 | 89676.3318 | 16101.1709 | 0.08306 | -124328.9735 | 124328.9735
C | Xist Rating 1728 | -65.23 | 758.14 | 150.279 | 35.6 | 2208.71 | 9405.31 | 13639 | 0.45 | 1.73 | 13.227 | 14.845 | 1 | 1 | 2190 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1674511.3994 | 101536.114 | 4671.1346 | 11035.1767 | 90500.9374 | 16000.8077 | 0.083441 | -123553.9956 | 123553.9956
C | Xist Rating 1729 | -65.02 | 763.71 | 150.279 | 35.6 | 2206.29 | 9394.04 | 13579.4 | 0.44 | 1.72 | 13.223 | 14.753 | 1 | 1 | 2200 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1684965.7359 | 102414.8825 | 4713.8907 | 11085.5656 | 91329.3169 | 15894.7166 | 0.083822 | -122734.7883 | 122734.7883
C | Xist Rating 1730 | -64.77 | 770.647 | 150.279 | 35.6 | 2203.43 | 9388.73 | 13495.4 | 0.44 | 1.7 | 13.219 | 14.609 | 1 | 1 | 2210 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1698066.7192 | 103297.4249 | 4756.8417 | 11135.9545 | 92161.4704 | 15747.6064 | 0.084203 | -121598.8426 | 121598.8426
C | Xist Rating 1731 | -64.05 | 790.088 | 150.279 | 35.6 | 2194.17 | 9361.37 | 13246.2 | 0.44 | 1.66 | 13.257 | 14.157 | 1 | 1 | 2220 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1733587.387 | 104183.7413 | 4799.9874 | 11186.3435 | 92997.3978 | 15282.4761 | 0.084584 | -118007.2297 | 118007.2297
C | Xist Rating 1732 | -63.83 | 795.666 | 150.279 | 35.6 | 2192.86 | 9374.18 | 13182.5 | 0.43 | 1.65 | 13.253 | 14.053 | 1 | 1 | 2230 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1744784.1448 | 105073.8316 | 4843.3279 | 11236.7324 | 93837.0992 | 15163.6635 | 0.084965 | -117089.7898 | 117089.7898
C | Xist Rating 1733 | -63.61 | 802.327 | 150.279 | 35.6 | 2188.89 | 9343 | 13111.8 | 0.43 | 1.64 | 13.249 | 13.941 | 1 | 1 | 2240 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1756205.547 | 105967.6958 | 4886.8633 | 11287.1213 | 94680.5745 | 15049.7334 | 0.085346 | -116210.052 | 116210.052
C | Xist Rating 1734 | -63.37 | 809.572 | 150.279 | 35.6 | 2184.95 | 9316.95 | 13034 | 0.42 | 1.63 | 13.246 | 13.817 | 1 | 1 | 2250 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1768874.3414 | 106865.334 | 4930.5934 | 11337.5103 | 95527.8237 | 14910.0239 | 0.085727 | -115131.2521 | 115131.2521
C | Xist Rating 1735 | -63.23 | 813.341 | 150.279 | 35.6 | 2184.04 | 9323.06 | 12995.7 | 0.42 | 1.62 | 13.245 | 13.76 | 1 | 1 | 2260 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1776369.2776 | 107766.7461 | 4974.5182 | 11387.8992 | 96378.8469 | 14853.2806 | 0.086108 | -114693.096 | 114693.096
C | Xist Rating 1736 | -62.47 | 834.427 | 150.279 | 35.6 | 2173.55 | 9278.19 | 12751.9 | 0.42 | 1.59 | 13.278 | 13.342 | 1 | 1 | 2270 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1813668.8059 | 108671.9322 | 5018.6379 | 11438.2881 | 97233.644 | 14423.0921 | 0.086489 | -111371.2944 | 111371.2944
C | Xist Rating 1737 | -62.26 | 841.034 | 150.279 | 35.6 | 2169.84 | 9250.78 | 12686.3 | 0.41 | 1.58 | 13.276 | 13.242 | 1 | 1 | 2280 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1824909.2146 | 109580.8922 | 5062.9524 | 11488.6771 | 98092.2151 | 14308.0881 | 0.08687 | -110483.2638 | 110483.2638
C | Xist Rating 1738 | -61.98 | 848.656 | 150.279 | 35.6 | 2167.1 | 9249.63 | 12607.1 | 0.41 | 1.56 | 13.272 | 13.117 | 1 | 1 | 2290 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1839122.4176 | 110493.6261 | 5107.4617 | 11539.066 | 98954.5601 | 14180.5473 | 0.087251 | -109498.4278 | 109498.4278
C | Xist Rating 1739 | -61.8 | 853.984 | 150.279 | 35.6 | 2165.18 | 9245.67 | 12557.1 | 0.4 | 1.56 | 13.266 | 13.045 | 1 | 1 | 2300 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1849029.0771 | 111410.134 | 5152.1657 | 11589.4549 | 99820.679 | 14094.2842 | 0.087632 | -108832.3264 | 108832.3264
| Xist Rating 1740 | -61.62 | 859.577 | 150.279 | 35.6 | 2162.08 | 9220.05 | 12507.7 | 0.4 | 1.55 | 13.262 | 12.976 | 1 | 1 | 2310 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1858474.2402 | 112330.4158 | 5197.0645 | 11639.8439 | 100690.5719 | 14024.8407 | 0.088013 | -108296.1022 | 108296.1022
| Xist Rating 1741 | -60.86 | 881.131 | 150.28 | 35.6 | 2151.72 | 9177.66 | 12277.2 | 0.4 | 1.51 | 13.303 | 12.598 | 1 | 1 | 2320 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1895947.1953 | 113254.4715 | 5242.1582 | 11690.2328 | 101564.2387 | 13636.3716 | 0.088394 | -105296.4472 | 105296.4472
| Xist Rating 1742 | -60.63 | 887.77 | 150.28 | 35.6 | 2149.61 | 9178.24 | 12216.9 | 0.39 | 1.5 | 13.296 | 12.51 | 1 | 1 | 2330 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1908359.2697 | 114182.3012 | 5287.4466 | 11740.6217 | 102441.6795 | 13533.19 | 0.088775 | -104499.706 | 104499.706
| Xist Rating 1743 | -60.41 | 894.384 | 150.279 | 35.6 | 2146.75 | 9165.03 | 12157.2 | 0.39 | 1.49 | 13.291 | 12.425 | 1 | 1 | 2340 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1920018.852 | 115113.9048 | 5332.9298 | 11791.0107 | 103322.8942 | 13447.0375 | 0.089156 | -103834.4589 | 103834.4589
| Xist Rating 1744 | -60.21 | 900.461 | 150.279 | 35.6 | 2144 | 9149.24 | 12104.7 | 0.38 | 1.49 | 13.286 | 12.352 | 1 | 1 | 2350 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1930588.384 | 116049.2824 | 5378.6078 | 11841.3996 | 104207.8828 | 13359.35 | 0.089537 | -103157.3592 | 103157.3592
| Xist Rating 1745 | -59.97 | 907.756 | 150.279 | 35.6 | 2140.71 | 9132.14 | 12039.9 | 0.38 | 1.48 | 13.282 | 12.258 | 1 | 1 | 2360 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1943242.3468 | 116988.4339 | 5424.4805 | 11891.7885 | 105096.6454 | 13263.8334 | 0.089918 | -102419.8054 | 102419.8054
| Xist Rating 1746 | -59.27 | 927.627 | 150.28 | 35.6 | 2132.37 | 9109.64 | 11846.8 | 0.38 | 1.45 | 13.318 | 11.958 | 1 | 1 | 2370 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1978043.986 | 117931.3593 | 5470.5481 | 11942.1775 | 105989.1819 | 12955.9995 | 0.090299 | -100042.7939 | 100042.7939
| Xist Rating 1747 | -59.05 | 934.48 | 150.28 | 35.6 | 2129.11 | 9088.18 | 11791.2 | 0.37 | 1.44 | 13.312 | 11.882 | 1 | 1 | 2380 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 1989610.7128 | 118878.0587 | 5516.8105 | 11992.5664 | 106885.4923 | 12864.8973 | 0.09068 | -99339.3268 | 99339.3268
| Xist Rating 1748 | -58.8 | 941.331 | 150.28 | 35.6 | 2127.3 | 9097.24 | 11729.9 | 0.37 | 1.43 | 13.306 | 11.795 | 1 | 1 | 2390 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2002493.4363 | 119828.532 | 5563.2676 | 12042.9553 | 107785.5767 | 12776.5179 | 0.091061 | -98656.8846 | 98656.8846
C | Xist Rating 1749 | -54.77 | 1079.68 | 150.28 | 35.6 | 2037.84 | 8370.41 | 10538.1 | 0.4 | 1.25 | 13.303 | 10.053 | 1 | 1 | 2400 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2200215.0912 | 120782.7793 | 5609.9196 | 12093.3443 | 108689.435 | 11012.4748 | 0.091442 | -85035.4116 | 85035.4116
C | Xist Rating 1750 | -54.34 | 1081.13 | 150.28 | 35.6 | 2054.84 | 8664.97 | 10538 | 0.39 | 1.25 | 13.302 | 10.063 | 1 | 1 | 2410 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2221549.1692 | 121740.8005 | 5656.7663 | 12143.7332 | 109597.0673 | 11010.832 | 0.091823 | -85022.7261 | 85022.7261
C | Xist Rating 1751 | -54.35 | 1082.53 | 150.28 | 35.6 | 2053.11 | 8634.21 | 10538 | 0.39 | 1.25 | 13.34 | 10.074 | 1 | 1 | 2420 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2222553.1683 | 122702.5956 | 5703.8078 | 12194.1221 | 110508.4735 | 11026.1885 | 0.092204 | -85141.3049 | 85141.3049
C | Xist Rating 1752 | -53.93 | 1083.88 | 150.28 | 35.6 | 2069.73 | 8936.05 | 10537.9 | 0.39 | 1.25 | 13.333 | 10.083 | 1 | 1 | 2430 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2243338.9524 | 123668.1647 | 5751.0441 | 12244.5111 | 111423.6536 | 11037.5697 | 0.092585 | -85229.1873 | 85229.1873
C | Xist Rating 1753 | -53.91 | 1085.25 | 150.28 | 35.6 | 2068.84 | 8919.6 | 10537.9 | 0.38 | 1.25 | 13.33 | 10.094 | 1 | 1 | 2440 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2245208.61 | 124637.5077 | 5798.4752 | 12294.9 | 112342.6077 | 11036.6167 | 0.092966 | -85221.8287 | 85221.8287
C | Xist Rating 1754 | -53.89 | 1086.58 | 150.28 | 35.6 | 2068.15 | 8906.65 | 10537.9 | 0.38 | 1.25 | 13.325 | 10.104 | 1 | 1 | 2450 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2247210.427 | 125610.6246 | 5846.1011 | 12345.2889 | 113265.3357 | 11049.0636 | 0.093347 | -85317.9402 | 85317.9402
C | Xist Rating 1755 | -53.87 | 1088.05 | 150.28 | 35.6 | 2067.12 | 8887.62 | 10537.9 | 0.37 | 1.25 | 13.321 | 10.116 | 1 | 1 | 2460 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2249129.916 | 126587.5155 | 5893.9217 | 12395.6779 | 114191.8377 | 11048.9388 | 0.093728 | -85316.9764 | 85316.9764
C | Xist Rating 1756 | -53.85 | 1089.41 | 150.28 | 35.6 | 2066.44 | 8875.13 | 10537.9 | 0.36 | 1.25 | 13.359 | 10.126 | 1 | 1 | 2470 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2251200.4004 | 127568.1804 | 5941.9372 | 12446.0668 | 115122.1135 | 11048.2991 | 0.094109 | -85312.0368 | 85312.0368
C | Xist Rating 1757 | -53.83 | 1090.75 | 150.28 | 35.6 | 2065.66 | 8860.74 | 10537.9 | 0.36 | 1.25 | 13.353 | 10.137 | 1 | 1 | 2480 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2253118.645 | 128552.6191 | 5990.1474 | 12496.4558 | 116056.1634 | 11061.6382 | 0.09449 | -85415.0377 | 85415.0377
C | Xist Rating 1758 | -53.79 | 1092.15 | 150.28 | 35.6 | 2065.72 | 8861.83 | 10537.9 | 0.35 | 1.25 | 13.346 | 10.147 | 1 | 1 | 2490 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2256076.098 | 129540.8318 | 6038.5525 | 12546.8447 | 116993.9872 | 11059.0007 | 0.094871 | -85394.6721 | 85394.6721
C | Xist Rating 1759 | -53.77 | 1093.14 | 150.28 | 35.6 | 2065.89 | 8864.99 | 10537.8 | 0.35 | 1.25 | 13.34 | 10.156 | 1 | 1 | 2500 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2258306.9946 | 130532.8185 | 6087.1523 | 12597.2336 | 117935.5849 | 11070.2057 | 0.095252 | -85481.1938 | 85481.1938
C | Xist Rating 1760 | -53.75 | 1094.99 | 150.28 | 35.6 | 2064.42 | 8838.03 | 10537.8 | 0.34 | 1.25 | 13.337 | 10.169 | 1 | 1 | 2510 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2260519.2558 | 131528.5791 | 6135.9469 | 12647.6226 | 118880.9565 | 11070.6754 | 0.095633 | -85484.8212 | 85484.8212
C | Xist Rating 1761 | -53.72 | 1096.44 | 150.28 | 35.6 | 2063.87 | 8827.92 | 10537.8 | 0.34 | 1.25 | 13.374 | 10.18 | 1 | 1 | 2520 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2262909.6228 | 132528.1136 | 6184.9363 | 12698.0115 | 119830.1021 | 11085.5525 | 0.096014 | -85599.6983 | 85599.6983
C | Xist Rating 1762 | -53.7 | 1097.78 | 150.28 | 35.6 | 2063.38 | 8819.04 | 10537.8 | 0.33 | 1.25 | 13.378 | 10.19 | 1 | 1 | 2530 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2265137.2964 | 133531.422 | 6234.1205 | 12748.4004 | 120783.0216 | 11082.9585 | 0.096395 | -85579.6678 | 85579.6678
C | Xist Rating 1763 | -53.68 | 1098.93 | 150.28 | 35.6 | 2063 | 8812.05 | 10537.8 | 0.33 | 1.25 | 13.373 | 10.199 | 1 | 1 | 2540 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2267092.59 | 134538.5044 | 6283.4995 | 12798.7894 | 121739.7151 | 11094.096 | 0.096776 | -85665.6687 | 85665.6687
C | Xist Rating 1764 | -53.66 | 1100.48 | 150.28 | 35.6 | 2062.06 | 8795.03 | 10537.8 | 0.32 | 1.25 | 13.37 | 10.21 | 1 | 1 | 2550 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2269255.7888 | 135549.3608 | 6333.0732 | 12849.1783 | 122700.1825 | 11092.1022 | 0.097157 | -85650.273 | 85650.273
C | Xist Rating 1765 | -53.65 | 1101.92 | 150.28 | 35.6 | 2060.67 | 8769.66 | 10537.8 | 0.32 | 1.25 | 13.366 | 10.221 | 1 | 1 | 2560 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2270693.4864 | 136563.9911 | 6382.8418 | 12899.5672 | 123664.4238 | 11105.2966 | 0.097538 | -85752.1565 | 85752.1565
C | Xist Rating 1766 | -53.62 | 1103.31 | 150.28 | 35.6 | 2060.5 | 8766.61 | 10537.8 | 0.31 | 1.25 | 13.363 | 10.231 | 1 | 1 | 2570 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2273370.255 | 137582.3953 | 6432.8051 | 12949.9562 | 124632.4391 | 11102.0941 | 0.097919 | -85727.4277 | 85727.4277
C | Xist Rating 1767 | -53.6 | 1104.68 | 150.28 | 35.6 | 2059.87 | 8755.32 | 10537.8 | 0.31 | 1.25 | 13.398 | 10.241 | 1 | 1 | 2580 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2275497.1916 | 138604.5734 | 6482.9633 | 13000.3451 | 125604.2283 | 11115.5907 | 0.0983 | -85831.6452 | 85831.6452
C | Xist Rating 1768 | -53.58 | 1106.04 | 150.28 | 35.6 | 2058.7 | 8734.14 | 10537.9 | 0.3 | 1.25 | 13.396 | 10.252 | 1 | 1 | 2590 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2277004.548 | 139630.5255 | 6533.3162 | 13050.734 | 126579.7915 | 11113.2518 | 0.098681 | -85813.5843 | 85813.5843
C | Xist Rating 1769 | -53.57 | 1107.22 | 150.28 | 35.6 | 2058.37 | 8728.19 | 10537.9 | 0.3 | 1.25 | 13.392 | 10.261 | 1 | 1 | 2600 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2279068.4314 | 140660.2516 | 6583.8639 | 13101.123 | 127559.1286 | 11124.2598 | 0.099062 | -85898.5856 | 85898.5856
C | Xist Rating 1770 | -53.55 | 1108.9 | 150.28 | 35.6 | 2056.91 | 8701.99 | 10537.8 | 0.3 | 1.25 | 13.388 | 10.272 | 1 | 1 | 2610 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2280907.499 | 141693.7515 | 6634.6064 | 13151.5119 | 128542.2396 | 11137.3438 | 0.099443 | -85999.6165 | 85999.6165
C | Xist Rating 1771 | -53.52 | 1110.3 | 150.28 | 35.6 | 2056.58 | 8696.14 | 10537.8 | 0.29 | 1.25 | 13.386 | 10.283 | 1 | 1 | 2620 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2283420.774 | 142731.0254 | 6685.5437 | 13201.9008 | 129529.1246 | 11134.7765 | 0.099824 | -85979.7929 | 85979.7929
C | Xist Rating 1772 | -53.51 | 1111.73 | 150.28 | 35.6 | 2055.58 | 8678.31 | 10537.7 | 0.29 | 1.25 | 13.421 | 10.293 | 1 | 1 | 2630 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2285249.9534 | 143772.0733 | 6736.6758 | 13252.2898 | 130519.7835 | 11148.0982 | 0.10021 | -86082.659 | 86082.659
C | Xist Rating 1773 | -53.48 | 1112.97 | 150.28 | 35.6 | 2055.32 | 8673.77 | 10537.7 | 0.28 | 1.25 | 13.416 | 10.302 | 1 | 1 | 2640 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2287509.5004 | 144816.8951 | 6788.0027 | 13302.6787 | 131514.2164 | 11143.1416 | 0.10059 | -86044.3855 | 86044.3855
C | Xist Rating 1774 | -53.45 | 1114.48 | 150.28 | 35.6 | 2054.76 | 8663.67 | 10537.7 | 0.28 | 1.25 | 13.414 | 10.313 | 1 | 1 | 2650 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2289988.9248 | 145865.4908 | 6839.5243 | 13353.0676 | 132512.4232 | 11156.1824 | 0.10097 | -86145.083 | 86145.083
C | Xist Rating 1775 | -53.43 | 1115.82 | 150.28 | 35.6 | 2054.51 | 8659.23 | 10537.7 | 0.28 | 1.25 | 13.411 | 10.323 | 1 | 1 | 2660 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2292463.3482 | 146917.8605 | 6891.2408 | 13403.4566 | 133514.4039 | 11168.1508 | 0.10135 | -86237.4999 | 86237.4999
C | Xist Rating 1776 | -53.42 | 1117.2 | 150.28 | 35.6 | 2053.19 | 8635.95 | 10537.7 | 0.27 | 1.25 | 13.407 | 10.333 | 1 | 1 | 2670 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2293823.868 | 147974.0041 | 6943.152 | 13453.8455 | 134520.1585 | 11164.0392 | 0.10173 | -86205.7512 | 86205.7512
C | Xist Rating 1777 | -53.36 | 1118.62 | 150.28 | 35.6 | 2053.97 | 8649.77 | 10537.7 | 0.27 | 1.25 | 13.446 | 10.343 | 1 | 1 | 2680 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2297611.9214 | 149033.9216 | 6995.258 | 13504.2344 | 135529.6872 | 11177.3117 | 0.10211 | -86308.2384 | 86308.2384
C | Xist Rating 1778 | -53.32 | 1120 | 150.28 | 35.6 | 2054.3 | 8655.55 | 10537.7 | 0.27 | 1.25 | 13.438 | 10.352 | 1 | 1 | 2690 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2300816 | 150097.6131 | 7047.5588 | 13554.6234 | 136542.9897 | 11188.0251 | 0.10249 | -86390.9641 | 86390.9641
C | Xist Rating 1779 | -53.28 | 1121.2 | 150.28 | 35.6 | 2054.51 | 8659.28 | 10537.7 | 0.26 | 1.25 | 13.436 | 10.362 | 1 | 1 | 2700 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2303516.612 | 151165.0785 | 7100.0544 | 13605.0123 | 137560.0662 | 11183.7099 | 0.10287 | -86357.6437 | 86357.6437
C | Xist Rating 1780 | -53.28 | 1122.85 | 150.28 | 35.6 | 2052.61 | 8625.69 | 10537.7 | 0.26 | 1.25 | 13.43 | 10.373 | 1 | 1 | 2710 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2304773.1385 | 152236.3178 | 7152.7448 | 13655.4012 | 138580.9166 | 11196.5098 | 0.10325 | -86456.4809 | 86456.4809
C | Xist Rating 1781 | -53.23 | 1124.2 | 150.28 | 35.6 | 2053.02 | 8632.89 | 10537.8 | 0.26 | 1.25 | 13.431 | 10.382 | 1 | 1 | 2720 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2308005.084 | 153311.3311 | 7205.63 | 13705.7902 | 139605.541 | 11207.4532 | 0.10363 | -86540.9827 | 86540.9827
C | Xist Rating 1782 | -53.21 | 1125.52 | 150.28 | 35.6 | 2052.45 | 8622.77 | 10537.8 | 0.25 | 1.25 | 13.466 | 10.392 | 1 | 1 | 2730 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2310073.524 | 154390.1184 | 7258.71 | 13756.1791 | 140633.9393 | 11204.0385 | 0.10402 | -86514.6157 | 86514.6157
C | Xist Rating 1783 | -53.15 | 1126.8 | 150.28 | 35.6 | 2053.75 | 8645.7 | 10537.8 | 0.25 | 1.25 | 13.467 | 10.401 | 1 | 1 | 2740 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2314165.5 | 155472.6796 | 7311.9847 | 13806.568 | 141666.1115 | 11214.9247 | 0.1044 | -86598.6761 | 86598.6761
C | Xist Rating 1784 | -53.14 | 1128.35 | 150.28 | 35.6 | 2052.36 | 8621.18 | 10537.8 | 0.25 | 1.25 | 13.461 | 10.411 | 1 | 1 | 2750 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2315780.406 | 156559.0147 | 7365.4543 | 13856.957 | 142702.0577 | 11226.634 | 0.10478 | -86689.0916 | 86689.0916
C | Xist Rating 1785 | -53.02 | 1129.78 | 150.28 | 35.6 | 2055.77 | 8681.58 | 10538 | 0.24 | 1.25 | 13.47 | 10.422 | 1 | 1 | 2760 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2322567.8306 | 157649.1237 | 7419.1186 | 13907.3459 | 143741.7778 | 11223.1797 | 0.10516 | -86662.4188 | 86662.4188
C | Xist Rating 1786 | -53.09 | 1131.01 | 150.28 | 35.6 | 2051.71 | 8609.66 | 10537.8 | 0.24 | 1.25 | 13.456 | 10.43 | 1 | 1 | 2770 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2320504.5271 | 158743.0067 | 7472.9777 | 13957.7349 | 144785.2719 | 11232.5196 | 0.10554 | -86734.539 | 86734.539
C | Xist Rating 1787 | -52.95 | 1132.56 | 150.28 | 35.6 | 2055.86 | 8683.03 | 10538 | 0.24 | 1.25 | 13.506 | 10.441 | 1 | 1 | 2780 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2328384.8016 | 159840.6636 | 7527.0316 | 14008.1238 | 145832.5398 | 11246.886 | 0.10592 | -86845.4726 | 86845.4726
C | Xist Rating 1788 | -52.64 | 1133.97 | 150.28 | 35.6 | 2067.86 | 8901.19 | 10538.2 | 0.23 | 1.25 | 13.534 | 10.451 | 1 | 1 | 2790 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2344891.2042 | 160942.0945 | 7581.2803 | 14058.5127 | 146883.5818 | 11242.6387 | 0.1063 | -86812.6756 | 86812.6756
C | Xist Rating 1789 | -52.21 | 1134.94 | 150.28 | 35.6 | 2086.47 | 9256.4 | 10538.3 | 0.23 | 1.25 | 13.593 | 10.46 | 1 | 1 | 2800 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2368018.2618 | 162047.2993 | 7635.7238 | 14108.9017 | 147938.3977 | 11255.0836 | 0.10668 | -86908.7722 | 86908.7722
C | Xist Rating 1790 | -52.11 | 1136.69 | 150.28 | 35.6 | 2088.3 | 9292.59 | 10538.3 | 0.22 | 1.25 | 13.606 | 10.471 | 1 | 1 | 2810 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2373749.727 | 163156.278 | 7690.3621 | 14159.2906 | 148996.9875 | 11251.1473 | 0.10706 | -86878.3775 | 86878.3775
C | Xist Rating 1791 | -52.01 | 1138.16 | 150.28 | 35.6 | 2091.04 | 9346.99 | 10538.3 | 0.22 | 1.25 | 13.619 | 10.482 | 1 | 1 | 2820 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2379938.0864 | 164269.0307 | 7745.1952 | 14209.6795 | 150059.3512 | 11264.2741 | 0.10744 | -86979.7387 | 86979.7387
C | Xist Rating 1792 | -51.9 | 1139.53 | 150.28 | 35.6 | 2094.09 | 9408.24 | 10538.3 | 0.22 | 1.25 | 13.672 | 10.491 | 1 | 1 | 2830 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2386278.3777 | 165385.5574 | 7800.223 | 14260.0685 | 151125.4889 | 11276.4427 | 0.10783 | -87073.7017 | 87073.7017
C | Xist Rating 1793 | -51.82 | 1140.85 | 150.28 | 35.6 | 2096.47 | 9456.54 | 10538.3 | 0.21 | 1.25 | 13.679 | 10.5 | 1 | 1 | 2840 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2391757.7995 | 166505.8579 | 7855.4457 | 14310.4574 | 152195.4005 | 11269.9199 | 0.10821 | -87023.3339 | 87023.3339
C | Xist Rating 1794 | -51.75 | 1142.3 | 150.28 | 35.6 | 2097.57 | 9478.9 | 10538.3 | 0.21 | 1.25 | 13.684 | 10.51 | 1 | 1 | 2850 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2396054.211 | 167629.9324 | 7910.8631 | 14360.8463 | 153269.0861 | 11281.7266 | 0.10859 | -87114.5025 | 87114.5025
C | Xist Rating 1795 | -51.67 | 1143.7 | 150.28 | 35.6 | 2099.27 | 9513.89 | 10538.2 | 0.21 | 1.25 | 13.689 | 10.52 | 1 | 1 | 2860 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2400935.099 | 168757.7809 | 7966.4753 | 14411.2353 | 154346.5456 | 11293.5343 | 0.10897 | -87205.6784 | 87205.6784
C | Xist Rating 1796 | -51.6 | 1144.89 | 150.28 | 35.6 | 2101.44 | 9558.65 | 10538.2 | 0.21 | 1.25 | 13.691 | 10.528 | 1 | 1 | 2870 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2405917.6416 | 169889.4032 | 8022.2824 | 14461.6242 | 155427.779 | 11303.1849 | 0.10935 | -87280.1976 | 87280.1976
C | Xist Rating 1797 | -51.54 | 1146.4 | 150.28 | 35.6 | 2102.22 | 9574.85 | 10538.2 | 0.2 | 1.25 | 13.732 | 10.538 | 1 | 1 | 2880 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2409985.008 | 171024.7995 | 8078.2842 | 14512.0131 | 156512.7864 | 11298.2428 | 0.10973 | -87242.0363 | 87242.0363
C | Xist Rating 1798 | -51.47 | 1147.74 | 150.28 | 35.5 | 2103.49 | 9601.12 | 10538.2 | 0.2 | 1.25 | 13.732 | 10.548 | 1 | 1 | 2890 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2414259.6126 | 172163.9698 | 8134.4807 | 14562.4021 | 157601.5677 | 11309.8589 | 0.11011 | -87331.7323 | 87331.7323
C | Xist Rating 1799 | -51.41 | 1149.13 | 150.28 | 35.5 | 2104.81 | 9628.69 | 10538.1 | 0.2 | 1.25 | 13.732 | 10.557 | 1 | 1 | 2900 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2418700.3153 | 173306.914 | 8190.8721 | 14612.791 | 158694.123 | 11320.4364 | 0.11049 | -87413.4093 | 87413.4093
C | Xist Rating 1800 | -51.34 | 1150.67 | 150.28 | 35.5 | 2105.96 | 9652.8 | 10538.1 | 0.2 | 1.25 | 13.735 | 10.567 | 1 | 1 | 2910 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2423264.9932 | 174453.6321 | 8247.4583 | 14663.1799 | 159790.4522 | 11332.1307 | 0.11087 | -87503.7097 | 87503.7097
C | Xist Rating 1801 | -51.24 | 1152.06 | 150.28 | 35.5 | 2108.44 | 9705.35 | 10538 | 0.2 | 1.25 | 13.736 | 10.576 | 1 | 1 | 2920 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2429049.3864 | 175604.1242 | 8304.2393 | 14713.5689 | 160890.5553 | 11342.7347 | 0.11125 | -87585.591 | 87585.591
C | Xist Rating 1802 | -51.1 | 1153.44 | 150.28 | 35.5 | 2113.4 | 9811.37 | 10538 | 0.19 | 1.25 | 13.784 | 10.586 | 1 | 1 | 2930 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2437680.096 | 176758.3902 | 8361.215 | 14763.9578 | 161994.4324 | 11337.5086 | 0.11164 | -87545.236 | 87545.236
C | Xist Rating 1803 | -51.08 | 1154.81 | 150.28 | 35.5 | 2112.74 | 9797.05 | 10538 | 0.19 | 1.25 | 13.778 | 10.595 | 1 | 1 | 2940 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2439813.2794 | 177916.4301 | 8418.3855 | 14814.3467 | 163102.0834 | 11347.8788 | 0.11202 | -87625.3119 | 87625.3119
C | Xist Rating 1804 | -51.08 | 1156.22 | 150.28 | 35.5 | 2110.86 | 9756.88 | 10537.9 | 0.19 | 1.25 | 13.773 | 10.604 | 1 | 1 | 2950 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2440618.5492 | 179078.244 | 8475.7509 | 14864.7357 | 164213.5084 | 11358.2731 | 0.1124 | -87705.5739 | 87705.5739
C | Xist Rating 1805 | -51.06 | 1157.59 | 150.28 | 35.5 | 2110.13 | 9741.38 | 10537.9 | 0.19 | 1.25 | 13.77 | 10.613 | 1 | 1 | 2960 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2442665.3867 | 180243.8319 | 8533.311 | 14915.1246 | 165328.7073 | 11368.7169 | 0.11278 | -87786.2186 | 87786.2186
C | Xist Rating 1806 | -51.02 | 1158.97 | 150.28 | 35.5 | 2110.06 | 9739.71 | 10537.9 | 0.18 | 1.25 | 13.768 | 10.622 | 1 | 1 | 2970 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2445496.2382 | 181413.1936 | 8591.0659 | 14965.5135 | 166447.6801 | 11360.8563 | 0.11316 | -87725.5212 | 87725.5212
C | Xist Rating 1807 | -51.04 | 1160.2 | 150.28 | 35.5 | 2109 | 9717.85 | 10537.4 | 0.18 | 1.25 | 13.814 | 10.63 | 1 | 1 | 2980 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 9 | E | Rod | 2446861.8 | 182586.3293 | 8649.0156 | 15015.9025 | 167570.4268 | 11371.3812 | 0.11354 | -87806.7915 | 87806.7915
C | Xist Rating 1808 | -51.02 | 1161.76 | 150.28 | 35.5 | 2108.06 | 9697.97 | 10537.3 | 0.18 | 1.25 | 13.811 | 10.64 | 1 | 1 | 2990 | 152.4 | 2 | 1.8 | 19.05 | 1.3333 | 8 | E | Rod | 2449059.7856 | 183763.239 | 8707.16 | 15066.2914 | 168696.9476 | 11382.8084 | 0.11392 | -87895.0292 | 87895.0292
C | Xist Rating 1810 | -94.3 | 105.888 | 150.282 | 35.8 | 2409.96 | 7503.39 | 58745.9 | 2.44 | 10.95 | 14.356 | 352.751 | 1 | 1 | 1000 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 255185.8445 | 25236.8419 | 973.9444 | 5318.832 | 19918.0099 | 367901.5023 | 0.038101 | -2840837.8808 | 2840837.8808
C | Xist Rating 1811 | -94.25 | 107.021 | 150.282 | 35.8 | 2406.86 | 7482.02 | 58284.4 | 2.42 | 10.85 | 14.369 | 346.178 | 1 | 1 | 1010 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 257584.5641 | 25690.3822 | 993.5206 | 5372.0203 | 20318.3619 | 361079.5792 | 0.038482 | -2788160.7988 | 2788160.7988
C | Xist Rating 1812 | -93.82 | 115.424 | 150.282 | 35.8 | 2400.55 | 7487.6 | 54967.8 | 2.43 | 10.07 | 14.422 | 299.989 | 1 | 1 | 1020 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 277081.0832 | 26147.9061 | 1013.2917 | 5425.2086 | 20722.6975 | 313140.4207 | 0.038863 | -2417987.3241 | 2417987.3241
C | Xist Rating 1813 | -93.75 | 117.835 | 150.282 | 35.8 | 2380.64 | 7313.52 | 54179 | 2.35 | 9.89 | 14.173 | 290.078 | 1 | 1 | 1030 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 280522.7144 | 26609.4136 | 1033.2576 | 5478.3969 | 21131.0167 | 302783.2874 | 0.039244 | -2338012.2866 | 2338012.2866
C | Xist Rating 1814 | -93.66 | 119.043 | 150.281 | 35.8 | 2390.97 | 7420.2 | 53794.8 | 2.29 | 9.8 | 14.122 | 285.353 | 1 | 1 | 1040 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 284628.2417 | 27074.9047 | 1053.4182 | 5531.5853 | 21543.3195 | 297846.2248 | 0.039625 | -2299889.5974 | 2299889.5974
C | Xist Rating 1815 | -93.52 | 121.333 | 150.281 | 35.8 | 2398.62 | 7511.45 | 53044.7 | 2.24 | 9.63 | 14.088 | 275.976 | 1 | 1 | 1050 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 291031.7605 | 27544.3795 | 1073.7737 | 5584.7736 | 21959.6059 | 288085.9034 | 0.040006 | -2224522.9826 | 2224522.9826
C | Xist Rating 1816 | -93.42 | 122.521 | 150.281 | 35.8 | 2412.83 | 7661.45 | 52677.8 | 2.19 | 9.54 | 14.073 | 271.56 | 1 | 1 | 1060 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 295622.3444 | 28017.8378 | 1094.3239 | 5637.9619 | 22379.8759 | 283479.0099 | 0.040387 | -2188949.7726 | 2188949.7726
C | Xist Rating 1817 | -93 | 131.645 | 150.281 | 35.8 | 2391.59 | 7520.51 | 49858.6 | 2.18 | 8.9 | 14.009 | 237.676 | 1 | 1 | 1070 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 314840.8656 | 28495.2797 | 1115.0689 | 5691.1502 | 22804.1295 | 248290.9029 | 0.040768 | -1917236.5378 | 1917236.5378
C | Xist Rating 1818 | -92.89 | 133.43 | 150.281 | 35.8 | 2396.68 | 7583.8 | 49381.6 | 2.12 | 8.79 | 13.95 | 232.419 | 1 | 1 | 1080 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 319789.0124 | 28976.7053 | 1136.0087 | 5744.3385 | 23232.3667 | 242798.4598 | 0.041149 | -1874825.3475 | 1874825.3475
C | Xist Rating 1819 | -92.78 | 135.8 | 150.281 | 35.8 | 2394.79 | 7581.9 | 48761.8 | 2.07 | 8.65 | 13.866 | 225.658 | 1 | 1 | 1090 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 325212.482 | 29462.1144 | 1157.1433 | 5797.5269 | 23664.5875 | 235747.8538 | 0.04153 | -1820382.4368 | 1820382.4368
C | Xist Rating 1820 | -92.67 | 137.554 | 150.281 | 35.8 | 2400.81 | 7655.56 | 48308.2 | 2.03 | 8.55 | 13.85 | 220.762 | 1 | 1 | 1100 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 330241.0187 | 29951.5071 | 1178.4727 | 5850.7152 | 24100.792 | 230647.2821 | 0.041911 | -1780997.1749 | 1780997.1749
C | Xist Rating 1821 | -92.63 | 138.929 | 150.28 | 35.8 | 2393.52 | 7590.4 | 48010.7 | 1.96 | 8.49 | 13.691 | 217.85 | 1 | 1 | 1110 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 332529.3401 | 30444.8835 | 1199.9969 | 5903.9035 | 24540.98 | 227572.0338 | 0.042292 | -1757250.9226 | 1757250.9226
C | Xist Rating 1822 | -92.1 | 149.012 | 150.281 | 35.8 | 2391.25 | 7645.83 | 45447.9 | 2 | 7.92 | 13.842 | 190.62 | 1 | 1 | 1120 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 356324.945 | 30942.2434 | 1221.7158 | 5957.0918 | 24985.1516 | 199348.4053 | 0.042673 | -1539315.5443 | 1539315.5443
C | Xist Rating 1823 | -92.05 | 150.341 | 150.28 | 35.8 | 2389.05 | 7631.81 | 45188.9 | 1.94 | 7.86 | 13.737 | 188.258 | 1 | 1 | 1130 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 359172.1661 | 31443.587 | 1243.6296 | 6010.2801 | 25433.3068 | 196855.4961 | 0.043054 | -1520065.9604 | 1520065.9604
C | Xist Rating 1824 | -91.92 | 152.782 | 150.28 | 35.8 | 2389.03 | 7648.44 | 44681.9 | 1.88 | 7.75 | 13.602 | 183.434 | 1 | 1 | 1140 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 365000.7815 | 31948.9141 | 1265.7381 | 6063.4684 | 25885.4457 | 191802.6385 | 0.043435 | -1481049.1332 | 1481049.1332
C | Xist Rating 1825 | -91.77 | 155.159 | 150.28 | 35.8 | 2396.8 | 7745.94 | 44187.2 | 1.84 | 7.64 | 13.569 | 178.742 | 1 | 1 | 1150 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 371885.0912 | 32458.2248 | 1288.0414 | 6116.6568 | 26341.5681 | 186910.2899 | 0.043816 | -1443271.7143 | 1443271.7143
C | Xist Rating 1826 | -91.66 | 157.616 | 150.28 | 35.8 | 2395.01 | 7744.42 | 43704.5 | 1.79 | 7.53 | 13.492 | 174.298 | 1 | 1 | 1160 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 377491.8962 | 32971.5192 | 1310.5395 | 6169.8451 | 26801.6741 | 182263.9505 | 0.044197 | -1407393.9131 | 1407393.9131
C | Xist Rating 1827 | -91.18 | 166.726 | 150.28 | 35.8 | 2394.69 | 7812.24 | 41833.9 | 1.8 | 7.13 | 13.588 | 156.821 | 1 | 1 | 1170 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 399257.0849 | 33488.7971 | 1333.2324 | 6223.0334 | 27265.7637 | 164141.0774 | 0.044578 | -1267453.891 | 1267453.891
C | Xist Rating 1828 | -91.11 | 167.484 | 150.28 | 35.8 | 2402.81 | 7903.84 | 41726.6 | 1.75 | 7.11 | 13.542 | 156.035 | 1 | 1 | 1180 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 402432.23 | 34010.0587 | 1356.1201 | 6276.2217 | 27733.837 | 163295.5876 | 0.044959 | -1260925.2427 | 1260925.2427
C | Xist Rating 1829 | -90.92 | 172.224 | 150.28 | 35.8 | 2389.39 | 7794.7 | 40887.3 | 1.71 | 6.93 | 13.455 | 148.806 | 1 | 1 | 1190 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 411510.3034 | 34535.3039 | 1379.2026 | 6329.41 | 28205.8938 | 155762.0758 | 0.04534 | -1202753.4613 | 1202753.4613
C | Xist Rating 1830 | -90.81 | 173.446 | 150.28 | 35.8 | 2402.9 | 7949.24 | 40683.2 | 1.68 | 6.88 | 13.462 | 147.133 | 1 | 1 | 1200 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 416773.3934 | 35064.5326 | 1402.4799 | 6382.5984 | 28681.9342 | 154013.9016 | 0.045721 | -1189254.5237 | 1189254.5237
C | Xist Rating 1831 | -90.7 | 175.971 | 150.28 | 35.8 | 2397.92 | 7912.53 | 40282.2 | 1.63 | 6.8 | 13.384 | 143.886 | 1 | 1 | 1210 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 421964.3803 | 35597.745 | 1425.9519 | 6435.7867 | 29161.9583 | 150608.6316 | 0.046102 | -1162959.9312 | 1162959.9312
C | Xist Rating 1832 | -90.21 | 186.408 | 150.28 | 35.8 | 2385.54 | 7858.31 | 38539.1 | 1.63 | 6.43 | 13.412 | 129.461 | 1 | 1 | 1220 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 444683.7403 | 36134.9409 | 1449.6188 | 6488.975 | 29645.9659 | 135640.5667 | 0.046483 | -1047380.5015 | 1047380.5015
C | Xist Rating 1833 | -90.06 | 188.783 | 150.28 | 35.8 | 2391.69 | 7942.89 | 38184.2 | 1.61 | 6.35 | 13.408 | 126.725 | 1 | 1 | 1230 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 451510.4133 | 36676.1205 | 1473.4804 | 6542.1633 | 30133.9572 | 132793.8901 | 0.046864 | -1025399.2194 | 1025399.2194
C | Xist Rating 1834 | -89.95 | 191.299 | 150.28 | 35.8 | 2388.6 | 7926.25 | 37836.5 | 1.57 | 6.28 | 13.352 | 124.147 | 1 | 1 | 1240 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 456936.7914 | 37221.2837 | 1497.5369 | 6595.3516 | 30625.932 | 130091.6205 | 0.047245 | -1004533.0103 | 1004533.0103
C | Xist Rating 1835 | -89.88 | 192.665 | 150.28 | 35.8 | 2389.51 | 7945.03 | 37665.3 | 1.53 | 6.24 | 13.311 | 122.957 | 1 | 1 | 1250 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 460374.9441 | 37770.4304 | 1521.7881 | 6648.54 | 31121.8904 | 128831.7641 | 0.047626 | -994804.7328 | 994804.7328
C | Xist Rating 1836 | -89.71 | 196.252 | 150.279 | 35.8 | 2386.99 | 7943.19 | 37162.2 | 1.5 | 6.14 | 13.283 | 119.196 | 1 | 1 | 1260 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 468451.5615 | 38323.5608 | 1546.2341 | 6701.7283 | 31621.8325 | 124910.1746 | 0.048007 | -964523.2578 | 964523.2578
C | Xist Rating 1837 | -89.23 | 206.146 | 150.28 | 35.8 | 2380.36 | 7945.16 | 35778.3 | 1.51 | 5.85 | 13.335 | 108.918 | 1 | 1 | 1270 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 490701.6926 | 38880.6748 | 1570.8749 | 6754.9166 | 32125.7581 | 114257.4505 | 0.048388 | -882265.7463 | 882265.7463
C | Xist Rating 1838 | -89.11 | 208.73 | 150.279 | 35.8 | 2379.37 | 7951.33 | 35478.1 | 1.47 | 5.79 | 13.29 | 106.912 | 1 | 1 | 1280 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 496645.9001 | 39441.7723 | 1595.7105 | 6808.1049 | 32633.6674 | 112148.849 | 0.048769 | -865983.6843 | 865983.6843
C | Xist Rating 1839 | -88.96 | 211.263 | 150.279 | 35.7 | 2383.97 | 8020.32 | 35183.8 | 1.43 | 5.73 | 13.285 | 104.945 | 1 | 1 | 1290 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 503644.6541 | 40006.8535 | 1620.7408 | 6861.2932 | 33145.5603 | 110083.7271 | 0.04915 | -850037.3605 | 850037.3605
C | Xist Rating 1840 | -88.75 | 214.828 | 150.279 | 35.8 | 2391.23 | 8129.75 | 34752.8 | 1.41 | 5.64 | 13.29 | 102.003 | 1 | 1 | 1300 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 513703.1584 | 40575.9183 | 1645.966 | 6914.4816 | 33661.4367 | 107021.9082 | 0.049531 | -826394.8071 | 826394.8071
C | Xist Rating 1841 | -88.63 | 216.806 | 150.279 | 35.7 | 2396.44 | 8203.85 | 34541.5 | 1.37 | 5.59 | 13.263 | 100.663 | 1 | 1 | 1310 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 519562.5706 | 41148.9667 | 1671.3859 | 6967.6699 | 34181.2968 | 105605.3322 | 0.049912 | -815456.3827 | 815456.3827
C | Xist Rating 1842 | -88.13 | 226.799 | 150.279 | 35.7 | 2390.92 | 8218.11 | 33364.4 | 1.37 | 5.35 | 13.308 | 92.768 | 1 | 1 | 1320 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 542258.2651 | 41725.9986 | 1697.0007 | 7020.8582 | 34705.1404 | 97418.1797 | 0.050293 | -752237.3613 | 752237.3613
C | Xist Rating 1843 | -87.97 | 230.581 | 150.279 | 35.7 | 2385.58 | 8182.17 | 32981.4 | 1.34 | 5.28 | 13.234 | 90.408 | 1 | 1 | 1330 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 550069.422 | 42307.0142 | 1722.8102 | 7074.0465 | 35232.9677 | 94945.7829 | 0.050674 | -733146.1681 | 733146.1681
C | Xist Rating 1844 | -87.78 | 234.261 | 150.279 | 35.7 | 2386.44 | 8219.07 | 32608.5 | 1.31 | 5.2 | 13.213 | 88.113 | 1 | 1 | 1340 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 559049.8208 | 42892.0134 | 1748.8145 | 7127.2348 | 35764.7786 | 92544.8786 | 0.051055 | -714607.0217 | 714607.0217
C | Xist Rating 1845 | -87.67 | 236.256 | 150.279 | 35.7 | 2390.04 | 8275.51 | 32425.6 | 1.28 | 5.16 | 13.19 | 87.056 | 1 | 1 | 1350 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 564661.2902 | 43480.9962 | 1775.0136 | 7180.4232 | 36300.573 | 91429.1761 | 0.051436 | -705991.8628 | 705991.8628
C | Xist Rating 1846 | -87.53 | 237.424 | 150.279 | 35.7 | 2407.1 | 8493.29 | 32304.8 | 1.27 | 5.14 | 13.22 | 86.326 | 1 | 1 | 1360 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 571503.3104 | 44073.9626 | 1801.4075 | 7233.6115 | 36840.3511 | 90672.9219 | 0.051817 | -700152.2683 | 700152.2683
C | Xist Rating 1847 | -86.93 | 251.786 | 150.279 | 35.7 | 2379 | 8262.23 | 30903.8 | 1.26 | 4.86 | 13.211 | 77.894 | 1 | 1 | 1370 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 598998.894 | 44670.9126 | 1827.9962 | 7286.7998 | 37384.1128 | 81915.0143 | 0.052198 | -632526.027 | 632526.027
C | Xist Rating 1848 | -86.87 | 253.216 | 150.279 | 35.7 | 2379.46 | 8276.72 | 30795.6 | 1.24 | 4.84 | 13.189 | 77.346 | 1 | 1 | 1380 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 602517.3434 | 45271.8462 | 1854.7797 | 7339.9881 | 37931.858 | 81335.347 | 0.052579 | -628049.9898 | 628049.9898
C | Xist Rating 1849 | -86.71 | 256.401 | 150.279 | 35.7 | 2379.79 | 8303.3 | 30528.1 | 1.21 | 4.79 | 13.164 | 75.878 | 1 | 1 | 1390 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 610180.5358 | 45876.7633 | 1881.7579 | 7393.1764 | 38483.5869 | 79791.6246 | 0.05296 | -616129.7748 | 616129.7748
C | Xist Rating 1850 | -86.55 | 259.583 | 150.279 | 35.7 | 2379.73 | 8325.06 | 30266.1 | 1.19 | 4.73 | 13.145 | 74.454 | 1 | 1 | 1400 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 617737.4526 | 46485.6641 | 1908.931 | 7446.3648 | 39039.2994 | 78302.0018 | 0.053341 | -604627.3027 | 604627.3027
C | Xist Rating 1851 | -86.38 | 263.325 | 150.279 | 35.7 | 2378.44 | 8336.36 | 29958.3 | 1.17 | 4.67 | 13.129 | 72.782 | 1 | 1 | 1410 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 626302.713 | 47098.5485 | 1936.2988 | 7499.5531 | 39598.9955 | 76554.845 | 0.053722 | -591136.221 | 591136.221
C | Xist Rating 1852 | -85.86 | 274.004 | 150.279 | 35.7 | 2373.81 | 8362.56 | 29052.8 | 1.17 | 4.49 | 13.181 | 67.786 | 1 | 1 | 1420 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 650433.4352 | 47715.4165 | 1963.8614 | 7552.7414 | 40162.6751 | 71377.265 | 0.054103 | -551156.3199 | 551156.3199
C | Xist Rating 1853 | -85.78 | 276.239 | 150.279 | 35.7 | 2369.52 | 8322.96 | 28911.6 | 1.14 | 4.47 | 13.136 | 67.138 | 1 | 1 | 1430 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 654553.8353 | 48336.2681 | 1991.6188 | 7605.9297 | 40730.3384 | 70682.5957 | 0.054484 | -545792.2679 | 545792.2679
C | Xist Rating 1854 | -85.55 | 281.149 | 150.279 | 35.7 | 2366.72 | 8324.02 | 28542.8 | 1.12 | 4.39 | 13.124 | 65.24 | 1 | 1 | 1440 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 665400.9613 | 48961.1033 | 2019.571 | 7659.118 | 41301.9853 | 68700.4127 | 0.054865 | -530486.3768 | 530486.3768
C | Xist Rating 1855 | -85.4 | 284.369 | 150.279 | 35.7 | 2366.75 | 8346.7 | 28317.6 | 1.1 | 4.35 | 13.108 | 64.13 | 1 | 1 | 1450 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 673030.3308 | 49589.9222 | 2047.718 | 7712.3064 | 41877.6158 | 67536.0642 | 0.055246 | -521495.586 | 521495.586
C | Xist Rating 1856 | -85.27 | 286.246 | 150.279 | 35.7 | 2373.54 | 8445.34 | 28184.3 | 1.09 | 4.33 | 13.114 | 63.479 | 1 | 1 | 1460 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 679416.3308 | 50222.7246 | 2076.0598 | 7765.4947 | 42457.2299 | 66858.3145 | 0.055627 | -516262.1826 | 516262.1826
C | Xist Rating 1857 | -84.75 | 298.521 | 150.279 | 35.7 | 2357.15 | 8331.07 | 27311 | 1.08 | 4.16 | 13.124 | 59.11 | 1 | 1 | 1470 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 703658.7752 | 50859.5106 | 2104.5964 | 7818.683 | 43040.8276 | 62319.5928 | 0.056008 | -481215.3766 | 481215.3766
C | Xist Rating 1858 | -84.56 | 302.306 | 150.279 | 35.7 | 2357.86 | 8366.39 | 27067 | 1.06 | 4.11 | 13.117 | 57.966 | 1 | 1 | 1480 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 712795.2252 | 51500.2802 | 2133.3277 | 7871.8713 | 43628.4089 | 61119.9987 | 0.056389 | -471952.4291 | 471952.4291
C | Xist Rating 1859 | -84.35 | 305.528 | 150.279 | 35.7 | 2365.62 | 8487.67 | 26867.3 | 1.04 | 4.07 | 13.115 | 57.052 | 1 | 1 | 1490 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 722763.1474 | 52145.0334 | 2162.2539 | 7925.0596 | 44219.9738 | 60159.3833 | 0.05677 | -464534.8116 | 464534.8116
C | Xist Rating 1860 | -84.18 | 308.842 | 150.279 | 35.7 | 2367.69 | 8537.29 | 26670.8 | 1.02 | 4.03 | 13.102 | 56.174 | 1 | 1 | 1500 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 731242.115 | 52793.7702 | 2191.3748 | 7978.248 | 44815.5222 | 59235.1678 | 0.057151 | -457398.2643 | 457398.2643
C | Xist Rating 1861 | -83.96 | 312.654 | 150.279 | 35.7 | 2372.18 | 8623.99 | 26439.6 | 1.01 | 3.99 | 13.1 | 55.124 | 1 | 1 | 1510 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 741671.5657 | 53446.4906 | 2220.6906 | 8031.4363 | 45415.0543 | 58141.73 | 0.057532 | -448955.0275 | 448955.0275
C | Xist Rating 1862 | -83.37 | 324.612 | 150.279 | 35.7 | 2370.83 | 8702.24 | 25681.8 | 1.01 | 3.85 | 13.159 | 51.602 | 1 | 1 | 1520 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 769599.868 | 54103.1946 | 2250.2011 | 8084.6246 | 46018.57 | 54494.1294 | 0.057913 | -420789.2224 | 420789.2224
C | Xist Rating 1863 | -83.22 | 328.769 | 150.279 | 35.7 | 2363.07 | 8626.43 | 25469.2 | 0.99 | 3.81 | 13.122 | 50.728 | 1 | 1 | 1530 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 776904.1608 | 54763.8823 | 2279.9064 | 8137.8129 | 46626.0693 | 53571.8778 | 0.058294 | -413667.8397 | 413667.8397
C | Xist Rating 1864 | -83.08 | 330.92 | 150.279 | 35.7 | 2368.48 | 8713.08 | 25364.3 | 0.96 | 3.79 | 13.113 | 50.318 | 1 | 1 | 1540 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 783777.4016 | 55428.5535 | 2309.8065 | 8191.0012 | 47237.5522 | 53124.1457 | 0.058675 | -410210.5716 | 410210.5716
C | Xist Rating 1865 | -82.78 | 337.123 | 150.279 | 35.7 | 2367.05 | 8740.91 | 25021.8 | 0.95 | 3.72 | 13.109 | 48.845 | 1 | 1 | 1550 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 797986.9972 | 56097.2083 | 2339.9013 | 8244.1896 | 47853.0188 | 51590.7056 | 0.059056 | -398369.7535 | 398369.7535
C | Xist Rating 1866 | -82.6 | 339.049 | 150.279 | 35.7 | 2379.73 | 8931.13 | 24921.2 | 0.94 | 3.7 | 13.123 | 48.436 | 1 | 1 | 1560 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 11 | E | Rod | 806845.0768 | 56769.8467 | 2370.191 | 8297.3779 | 48472.4689 | 51163.2956 | 0.059437 | -395069.4066 | 395069.4066
C | Xist Rating 1867 | -82.04 | 353.384 | 150.279 | 35.7 | 2358.25 | 8745.3 | 24162.8 | 0.93 | 3.56 | 13.112 | 45.243 | 1 | 1 | 1570 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 833367.818 | 57446.4688 | 2400.6755 | 8350.5662 | 49095.9026 | 47842.9443 | 0.059818 | -369430.5343 | 369430.5343
C | Xist Rating 1868 | -81.85 | 356.726 | 150.279 | 35.7 | 2361.66 | 8816.18 | 24008.1 | 0.92 | 3.53 | 13.106 | 44.649 | 1 | 1 | 1580 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 842465.5252 | 58127.0744 | 2431.3547 | 8403.7545 | 49723.3199 | 47221.865 | 0.0602 | -364634.7244 | 364634.7244
C | Xist Rating 1869 | -81.67 | 360.104 | 150.279 | 35.7 | 2364.35 | 8877.84 | 23855.6 | 0.9 | 3.5 | 13.098 | 44.071 | 1 | 1 | 1590 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 851411.8924 | 58811.6636 | 2462.2288 | 8456.9428 | 50354.7208 | 46607.8229 | 0.060581 | -359893.2541 | 359893.2541
C | Xist Rating 1870 | -81.43 | 364.506 | 150.279 | 35.7 | 2368.63 | 8972.8 | 23645.7 | 0.89 | 3.46 | 13.101 | 43.248 | 1 | 1 | 1600 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 863379.8468 | 59500.2365 | 2493.2976 | 8510.1312 | 50990.1053 | 45749.2204 | 0.060962 | -353263.3532 | 353263.3532
C | Xist Rating 1871 | -81.32 | 366.853 | 150.279 | 35.7 | 2368.56 | 8986.52 | 23557.1 | 0.87 | 3.45 | 13.085 | 42.951 | 1 | 1 | 1610 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 868913.3417 | 60192.7929 | 2524.5612 | 8563.3195 | 51629.4734 | 45426.0989 | 0.061343 | -350768.2948 | 350768.2948
C | Xist Rating 1872 | -80.63 | 382.777 | 150.279 | 35.7 | 2354.45 | 8912.82 | 22805.5 | 0.87 | 3.31 | 13.121 | 39.994 | 1 | 1 | 1620 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 901229.3076 | 60889.3329 | 2556.0196 | 8616.5078 | 52272.8251 | 42362.6362 | 0.061724 | -327113.048 | 327113.048
C | Xist Rating 1873 | -80.48 | 384.779 | 150.279 | 35.7 | 2362.78 | 9048.21 | 22723.8 | 0.86 | 3.29 | 13.127 | 39.71 | 1 | 1 | 1630 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 909148.1256 | 61589.8566 | 2587.6728 | 8669.6961 | 52920.1605 | 42063.6098 | 0.062105 | -324804.0451 | 324804.0451
C | Xist Rating 1874 | -80.32 | 388.304 | 150.279 | 35.7 | 2362.13 | 9063.45 | 22588.9 | 0.84 | 3.27 | 13.113 | 39.246 | 1 | 1 | 1640 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 917224.5275 | 62294.3638 | 2619.5208 | 8722.8844 | 53571.4794 | 41566.6424 | 0.062486 | -320966.5948 | 320966.5948
C | Xist Rating 1875 | -80.12 | 393.064 | 150.279 | 35.7 | 2357.96 | 9036.7 | 22403.5 | 0.83 | 3.24 | 13.096 | 38.596 | 1 | 1 | 1650 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 926829.1894 | 63002.8547 | 2651.5635 | 8776.0728 | 54226.7819 | 40885.8138 | 0.062867 | -315709.4167 | 315709.4167
C | Xist Rating 1876 | -79.88 | 397.58 | 150.279 | 35.7 | 2360.48 | 9108.53 | 22221.2 | 0.82 | 3.2 | 13.098 | 37.946 | 1 | 1 | 1660 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 938479.6384 | 63715.3291 | 2683.8011 | 8829.2611 | 54886.068 | 40206.0396 | 0.063248 | -310460.3802 | 310460.3802
C | Xist Rating 1877 | -79.28 | 411.958 | 150.279 | 35.7 | 2346.71 | 9019.94 | 21633.5 | 0.82 | 3.1 | 13.123 | 35.817 | 1 | 1 | 1670 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 966745.9582 | 64431.7872 | 2716.2334 | 8882.4494 | 55549.3378 | 38001.4253 | 0.063629 | -293436.9335 | 293436.9335
C | Xist Rating 1878 | -79.13 | 414.071 | 150.28 | 35.7 | 2353.48 | 9135.61 | 21561 | 0.8 | 3.08 | 13.126 | 35.589 | 1 | 1 | 1680 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 974507.8171 | 65152.2288 | 2748.8606 | 8935.6377 | 56216.5911 | 37749.8873 | 0.06401 | -291494.6233 | 291494.6233
C | Xist Rating 1879 | -78.89 | 420.115 | 150.279 | 35.6 | 2347.63 | 9092.22 | 21346.7 | 0.79 | 3.04 | 13.108 | 34.876 | 1 | 1 | 1690 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 986274.5775 | 65876.6541 | 2781.6825 | 8988.826 | 56887.828 | 37003.1242 | 0.064391 | -285728.3169 | 285728.3169
C | Xist Rating 1880 | -78.69 | 424.084 | 150.279 | 35.6 | 2349.41 | 9148.73 | 21206.4 | 0.78 | 3.02 | 13.106 | 34.415 | 1 | 1 | 1700 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 996347.1904 | 66605.0629 | 2814.6992 | 9042.0144 | 57563.0486 | 36518.9108 | 0.064772 | -281989.3489 | 281989.3489
C | Xist Rating 1881 | -78.48 | 428.793 | 150.279 | 35.6 | 2348.4 | 9168.15 | 21045.2 | 0.77 | 2.99 | 13.093 | 33.893 | 1 | 1 | 1710 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1006977.4812 | 67337.4554 | 2847.9107 | 9095.2027 | 58242.2527 | 35970.5838 | 0.065153 | -277755.3137 | 277755.3137
C | Xist Rating 1882 | -77.91 | 442.091 | 150.279 | 35.6 | 2338.53 | 9123.95 | 20567.8 | 0.76 | 2.9 | 13.123 | 32.287 | 1 | 1 | 1720 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1033843.0662 | 68073.8314 | 2881.317 | 9148.391 | 58925.4405 | 34298.9378 | 0.065534 | -264847.3059 | 264847.3059
C | Xist Rating 1883 | -77.67 | 448.005 | 150.28 | 35.6 | 2335.73 | 9125.64 | 20374 | 0.75 | 2.87 | 13.111 | 31.676 | 1 | 1 | 1730 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1046418.7187 | 68814.1911 | 2914.9181 | 9201.5793 | 59612.6118 | 33658.0115 | 0.065915 | -259898.2427 | 259898.2427
C | Xist Rating 1884 | -77.53 | 450.83 | 150.28 | 35.6 | 2336.87 | 9162.68 | 20289.9 | 0.74 | 2.85 | 13.106 | 31.429 | 1 | 1 | 1740 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1053531.1021 | 69558.5344 | 2948.714 | 9254.7676 | 60303.7667 | 33395.3956 | 0.066296 | -257870.3925 | 257870.3925
C | Xist Rating 1885 | -77.28 | 456.311 | 150.28 | 35.6 | 2334.03 | 9158.09 | 20123.9 | 0.73 | 2.82 | 13.1 | 30.926 | 1 | 1 | 1750 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1065043.5633 | 70306.8612 | 2982.7046 | 9307.956 | 60998.9053 | 32866.7538 | 0.066677 | -253788.361 | 253788.361
C | Xist Rating 1886 | -77.14 | 460.397 | 150.279 | 35.6 | 2329.96 | 9125.05 | 20000.5 | 0.72 | 2.8 | 13.089 | 30.558 | 1 | 1 | 1760 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1072706.5941 | 71059.1717 | 3016.8901 | 9361.1443 | 61698.0274 | 32477.9134 | 0.067058 | -250785.8383 | 250785.8383
C | Xist Rating 1887 | -76.49 | 476.147 | 150.28 | 35.6 | 2318.57 | 9073.52 | 19497.1 | 0.72 | 2.71 | 13.127 | 28.973 | 1 | 1 | 1770 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1103980.1498 | 71815.4658 | 3051.2703 | 9414.3326 | 62401.1332 | 30838.2884 | 0.067439 | -238125.0891 | 238125.0891
C | Xist Rating 1888 | -76.39 | 480.342 | 150.28 | 35.6 | 2309.98 | 8971.02 | 19383.9 | 0.71 | 2.69 | 13.242 | 28.645 | 1 | 1 | 1780 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1109580.4132 | 72575.7434 | 3085.8453 | 9467.5209 | 63108.2225 | 30497.9385 | 0.06782 | -235496.9967 | 235496.9967
C | Xist Rating 1889 | -76.27 | 482.714 | 150.279 | 35.6 | 2311.46 | 9007.49 | 19327 | 0.7 | 2.68 | 13.235 | 28.503 | 1 | 1 | 1790 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1115774.1024 | 73340.0047 | 3120.6151 | 9520.7092 | 63819.2955 | 30343.668 | 0.068201 | -234305.7611 | 234305.7611
C | Xist Rating 1890 | -75.98 | 489.95 | 150.279 | 35.6 | 2305.59 | 8969.85 | 19123 | 0.69 | 2.65 | 13.23 | 27.908 | 1 | 1 | 1800 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1129623.8205 | 74108.2496 | 3155.5797 | 9573.8976 | 64534.352 | 29718.9573 | 0.068582 | -229481.9105 | 229481.9105
C | Xist Rating 1891 | -75.81 | 494.018 | 150.279 | 35.6 | 2306.12 | 9006.01 | 19012.5 | 0.68 | 2.63 | 13.219 | 27.6 | 1 | 1 | 1810 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1139264.7902 | 74880.4781 | 3190.7391 | 9627.0859 | 65253.3922 | 29391.851 | 0.068963 | -226956.0822 | 226956.0822
C | Xist Rating 1892 | -75.16 | 510.027 | 150.28 | 35.6 | 2295.3 | 8959.43 | 18562.8 | 0.68 | 2.55 | 13.256 | 26.284 | 1 | 1 | 1820 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1170664.9731 | 75656.6901 | 3226.0933 | 9680.2742 | 65976.416 | 28031.2689 | 0.069344 | -216450.0279 | 216450.0279
C | Xist Rating 1893 | -75.06 | 507.457 | 150.28 | 35.6 | 2316.21 | 9266.87 | 18632.1 | 0.67 | 2.56 | 13.288 | 26.495 | 1 | 1 | 1830 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1175376.978 | 76436.8858 | 3261.6423 | 9733.4625 | 66703.4233 | 28245.3175 | 0.069725 | -218102.8546 | 218102.8546
C | Xist Rating 1894 | -74.78 | 510.76 | 150.28 | 35.6 | 2326.86 | 9465.25 | 18546.3 | 0.66 | 2.55 | 13.307 | 26.261 | 1 | 1 | 1840 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1188467.0136 | 77221.0651 | 3297.386 | 9786.6508 | 67434.4143 | 27996.3743 | 0.070106 | -216180.581 | 216180.581
C | Xist Rating 1895 | -74.55 | 516.359 | 150.28 | 35.6 | 2323.98 | 9458.51 | 18410.4 | 0.65 | 2.52 | 13.301 | 25.9 | 1 | 1 | 1850 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1200007.9888 | 78009.228 | 3333.3246 | 9839.8392 | 68169.3888 | 27614.0548 | 0.070487 | -213228.4114 | 213228.4114
C | Xist Rating 1896 | -74.31 | 522.614 | 150.28 | 35.6 | 2319.13 | 9424.14 | 18260.2 | 0.64 | 2.5 | 13.291 | 25.502 | 1 | 1 | 1860 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1212009.8058 | 78801.3745 | 3369.4579 | 9893.0275 | 68908.347 | 27192.9846 | 0.070868 | -209977.0194 | 209977.0194
C | Xist Rating 1897 | -73.67 | 537.272 | 150.28 | 35.6 | 2312.63 | 9435.32 | 17880.7 | 0.64 | 2.43 | 13.332 | 24.444 | 1 | 1 | 1870 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1242511.3454 | 79597.5046 | 3405.7861 | 9946.2158 | 69651.2888 | 26100.2657 | 0.071249 | -201539.3334 | 201539.3334
C | Xist Rating 1898 | -73.46 | 543.514 | 150.28 | 35.6 | 2306.14 | 9372.87 | 17739.8 | 0.63 | 2.41 | 13.312 | 24.085 | 1 | 1 | 1880 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1253419.376 | 80397.6183 | 3442.309 | 9999.4041 | 70398.2141 | 25718.9727 | 0.07163 | -198595.0898 | 198595.0898
C | Xist Rating 1899 | -73.22 | 547.629 | 150.28 | 35.6 | 2310.48 | 9475.27 | 17647.5 | 0.62 | 2.39 | 13.321 | 23.854 | 1 | 1 | 1890 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1265285.8519 | 81201.7155 | 3479.0267 | 10052.5924 | 71149.1231 | 25472.0338 | 0.072011 | -196688.2931 | 196688.2931
C | Xist Rating 1900 | -73.06 | 552.203 | 150.28 | 35.6 | 2306.2 | 9433.72 | 17556.1 | 0.61 | 2.38 | 13.316 | 23.639 | 1 | 1 | 1900 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1273490.5586 | 82009.7964 | 3515.9392 | 10105.7807 | 71904.0157 | 25240.8539 | 0.072392 | -194903.1831 | 194903.1831
C | Xist Rating 1901 | -72.85 | 556.497 | 150.28 | 35.6 | 2306.89 | 9475.54 | 17466 | 0.6 | 2.36 | 13.319 | 23.421 | 1 | 1 | 1910 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1283777.3643 | 82821.8609 | 3553.0464 | 10158.9691 | 72662.8919 | 25006.8558 | 0.072773 | -193096.3121 | 193096.3121
C | Xist Rating 1902 | -72.1 | 574.318 | 150.28 | 35.6 | 2298.06 | 9469.96 | 17051.3 | 0.6 | 2.29 | 13.36 | 22.331 | 1 | 1 | 1920 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1319817.2231 | 83637.909 | 3590.3485 | 10212.1574 | 73425.7517 | 23880.5918 | 0.073154 | -184399.6001 | 184399.6001
C | Xist Rating 1903 | -71.84 | 580.636 | 150.28 | 35.6 | 2295.25 | 9467.38 | 16924.5 | 0.59 | 2.27 | 13.356 | 22.031 | 1 | 1 | 1930 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1332704.779 | 84457.9407 | 3627.8454 | 10265.3457 | 74192.595 | 23560.8733 | 0.073535 | -181930.8186 | 181930.8186
C | Xist Rating 1904 | -71.66 | 582.647 | 150.28 | 35.6 | 2302.42 | 9605.89 | 16883.2 | 0.59 | 2.26 | 13.388 | 21.936 | 1 | 1 | 1940 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1341498.1057 | 85281.956 | 3665.537 | 10318.534 | 74963.422 | 23467.39 | 0.073916 | -181208.965 | 181208.965
C | Xist Rating 1905 | -71.47 | 588.816 | 150.28 | 35.6 | 2294.79 | 9514.79 | 16773.1 | 0.57 | 2.24 | 13.378 | 21.692 | 1 | 1 | 1950 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1351209.0686 | 86109.9549 | 3703.4235 | 10371.7223 | 75738.2326 | 23193.6344 | 0.074297 | -179095.0971 | 179095.0971
C | Xist Rating 1906 | -71.19 | 595.673 | 150.28 | 35.6 | 2291.69 | 9511.92 | 16637.7 | 0.57 | 2.22 | 13.387 | 21.372 | 1 | 1 | 1960 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1365097.8574 | 86941.9375 | 3741.5047 | 10424.9107 | 76517.0268 | 22865.1837 | 0.074678 | -176558.8878 | 176558.8878
C | Xist Rating 1907 | -70.51 | 611.81 | 150.28 | 35.6 | 2284.83 | 9521.56 | 16304 | 0.57 | 2.16 | 13.433 | 20.551 | 1 | 1 | 1970 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1397881.8423 | 87777.9036 | 3779.7807 | 10478.099 | 77299.8046 | 22018.3122 | 0.075059 | -170019.5708 | 170019.5708
C | Xist Rating 1908 | -70.29 | 616.744 | 150.28 | 35.6 | 2284.94 | 9558.69 | 16215 | 0.56 | 2.15 | 13.433 | 20.353 | 1 | 1 | 1980 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1409223.0354 | 88617.8533 | 3818.2515 | 10531.2873 | 78086.566 | 21804.1995 | 0.07544 | -168366.2492 | 168366.2492
C | Xist Rating 1909 | -70.03 | 623.257 | 150.28 | 35.6 | 2281.33 | 9540.79 | 16102.1 | 0.55 | 2.13 | 13.427 | 20.106 | 1 | 1 | 1990 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1421854.8918 | 89461.7866 | 3856.9171 | 10584.4756 | 78877.311 | 21538.7856 | 0.075821 | -166316.7932 | 166316.7932
C | Xist Rating 1910 | -69.81 | 628.315 | 150.28 | 35.6 | 2280.71 | 9565.24 | 16015.5 | 0.54 | 2.12 | 13.425 | 19.919 | 1 | 1 | 2000 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1433004.3037 | 90309.7035 | 3895.7775 | 10637.6639 | 79672.0396 | 21335.7626 | 0.076202 | -164749.1034 | 164749.1034
C | Xist Rating 1911 | -69.64 | 632.092 | 150.28 | 35.6 | 2281.51 | 9604.65 | 15954.3 | 0.53 | 2.11 | 13.422 | 19.794 | 1 | 1 | 2010 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1442124.2189 | 91161.604 | 3934.8326 | 10690.8523 | 80470.7517 | 21196.961 | 0.076583 | -163677.3143 | 163677.3143
C | Xist Rating 1912 | -68.93 | 650.36 | 150.28 | 35.6 | 2270.18 | 9547.64 | 15615.3 | 0.53 | 2.05 | 13.461 | 19.008 | 1 | 1 | 2020 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1476434.2648 | 92017.4881 | 3974.0826 | 10744.0406 | 81273.4475 | 20385.7615 | 0.076964 | -157413.4467 | 157413.4467
C | Xist Rating 1913 | -68.64 | 657.161 | 150.28 | 35.6 | 2268.35 | 9565.09 | 15500.2 | 0.53 | 2.03 | 13.461 | 18.76 | 1 | 1 | 2030 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1490671.1543 | 92877.3559 | 4013.5273 | 10797.2289 | 82080.1269 | 20131.4118 | 0.077345 | -155449.426 | 155449.426
C | Xist Rating 1914 | -68.47 | 661.934 | 150.28 | 35.6 | 2265.28 | 9540.54 | 15432.1 | 0.52 | 2.02 | 13.452 | 18.629 | 1 | 1 | 2040 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1499465.8515 | 93741.2072 | 4053.1669 | 10850.4172 | 82890.7899 | 19985.8295 | 0.077726 | -154325.2777 | 154325.2777
C | Xist Rating 1915 | -68.24 | 665.892 | 150.28 | 35.6 | 2268.78 | 9633.06 | 15364.9 | 0.52 | 2.01 | 13.457 | 18.486 | 1 | 1 | 2050 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1510762.4518 | 94609.0421 | 4093.0012 | 10903.6055 | 83705.4366 | 19840.6986 | 0.078107 | -153204.6157 | 153204.6157
C | Xist Rating 1916 | -68.01 | 672.8 | 150.28 | 35.6 | 2262.77 | 9570.3 | 15264.8 | 0.51 | 1.99 | 13.449 | 18.288 | 1 | 1 | 2060 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1522391.656 | 95480.8606 | 4133.0303 | 10956.7939 | 84524.0668 | 19625.4098 | 0.078488 | -151542.2127 | 151542.2127
C | Xist Rating 1917 | -67.27 | 692.453 | 150.28 | 35.6 | 2251.19 | 9514.29 | 14936.4 | 0.51 | 1.94 | 13.472 | 17.57 | 1 | 1 | 2070 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1558843.2691 | 96356.6628 | 4173.2542 | 11009.9822 | 85346.6806 | 18883.9309 | 0.078869 | -145816.7088 | 145816.7088
C | Xist Rating 1918 | -67.1 | 697.028 | 150.28 | 35.6 | 2249.08 | 9505.96 | 14873.7 | 0.5 | 1.93 | 13.468 | 17.453 | 1 | 1 | 2080 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1567671.7342 | 97236.4485 | 4213.6729 | 11063.1705 | 86173.278 | 18752.7592 | 0.07925 | -144803.8359 | 144803.8359
C | Xist Rating 1919 | -66.88 | 702.826 | 150.28 | 35.6 | 2246.87 | 9505.45 | 14790.9 | 0.5 | 1.91 | 13.463 | 17.292 | 1 | 1 | 2090 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1579158.6546 | 98120.2178 | 4254.2864 | 11116.3588 | 87003.859 | 18588.3453 | 0.079631 | -143534.2749 | 143534.2749
C | Xist Rating 1920 | -66.66 | 708.632 | 150.28 | 35.6 | 2244.25 | 9497.54 | 14709.4 | 0.49 | 1.9 | 13.463 | 17.135 | 1 | 1 | 2100 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1590347.366 | 99007.9707 | 4295.0947 | 11169.5471 | 87838.4236 | 18415.6454 | 0.080012 | -142200.7325 | 142200.7325
C | Xist Rating 1921 | -66.44 | 713.784 | 150.28 | 35.6 | 2243.18 | 9512.26 | 14639 | 0.48 | 1.89 | 13.471 | 17.001 | 1 | 1 | 2110 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1601145.9931 | 99899.7073 | 4336.0977 | 11222.7355 | 88676.9718 | 18267.0735 | 0.080393 | -141053.4998 | 141053.4998
C | Xist Rating 1922 | -65.75 | 732.492 | 150.28 | 35.6 | 2232.15 | 9451.92 | 14359.1 | 0.48 | 1.84 | 13.498 | 16.426 | 1 | 1 | 2120 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1635032.0178 | 100795.4274 | 4377.2956 | 11275.9238 | 89519.5036 | 17674.0669 | 0.080774 | -136474.4598 | 136474.4598
C | Xist Rating 1923 | -65.46 | 739.636 | 150.28 | 35.6 | 2229.94 | 9459.99 | 14264 | 0.47 | 1.83 | 13.503 | 16.246 | 1 | 1 | 2130 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1649343.9018 | 101695.1312 | 4418.6882 | 11329.1121 | 90366.0191 | 17477.3784 | 0.081155 | -134955.6829 | 134955.6829
C | Xist Rating 1924 | -65.23 | 746.806 | 150.28 | 35.6 | 2224.27 | 9405.84 | 14170.1 | 0.47 | 1.81 | 13.5 | 16.07 | 1 | 1 | 2140 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1661098.1816 | 102598.8185 | 4460.2756 | 11382.3004 | 91216.5181 | 17297.3121 | 0.081536 | -133565.2593 | 133565.2593
C | Xist Rating 1925 | -65.08 | 750.732 | 150.28 | 35.6 | 2223.07 | 9408.05 | 14123.7 | 0.46 | 1.8 | 13.496 | 15.991 | 1 | 1 | 2150 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1668929.7872 | 103506.4894 | 4502.0578 | 11435.4887 | 92071.0007 | 17204.9272 | 0.081917 | -132851.8874 | 132851.8874
C | Xist Rating 1926 | -64.89 | 755.83 | 150.28 | 35.6 | 2221.59 | 9414.56 | 14059.2 | 0.46 | 1.79 | 13.493 | 15.875 | 1 | 1 | 2160 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1679144.3697 | 104418.144 | 4544.0348 | 11488.6771 | 92929.4669 | 17087.1106 | 0.082298 | -131942.1385 | 131942.1385
C | Xist Rating 1927 | -64.14 | 776.136 | 150.28 | 35.6 | 2210.62 | 9360.39 | 13786.1 | 0.46 | 1.75 | 13.531 | 15.345 | 1 | 1 | 2170 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1715741.7643 | 105333.7821 | 4586.2066 | 11541.8654 | 93791.9168 | 16541.1888 | 0.082679 | -127726.6756 | 127726.6756
C | Xist Rating 1928 | -63.87 | 783.054 | 150.28 | 35.6 | 2208.57 | 9370.04 | 13699.2 | 0.45 | 1.74 | 13.527 | 15.186 | 1 | 1 | 2180 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1729429.5728 | 106253.4039 | 4628.5732 | 11595.0537 | 94658.3502 | 16365.4595 | 0.08306 | -126369.7404 | 126369.7404
C | Xist Rating 1929 | -63.65 | 788.386 | 150.28 | 35.6 | 2208 | 9392.43 | 13639 | 0.45 | 1.73 | 13.523 | 15.085 | 1 | 1 | 2190 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1740756.288 | 107177.0092 | 4671.1346 | 11648.242 | 95528.7672 | 16263.123 | 0.083441 | -125579.5251 | 125579.5251
C | Xist Rating 1930 | -63.48 | 794.124 | 150.28 | 35.6 | 2203.62 | 9345.93 | 13579.4 | 0.44 | 1.72 | 13.512 | 14.99 | 1 | 1 | 2200 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1749947.5289 | 108104.5982 | 4713.8907 | 11701.4303 | 96403.1679 | 16153.3805 | 0.083822 | -124732.1225 | 124732.1225
C | Xist Rating 1931 | -63.2 | 801.3 | 150.28 | 35.6 | 2201 | 9344.83 | 13495.4 | 0.44 | 1.7 | 13.509 | 14.842 | 1 | 1 | 2210 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1763661.3 | 109036.1708 | 4756.8417 | 11754.6187 | 97281.5521 | 16002.2169 | 0.084203 | -123564.8774 | 123564.8774
C | Xist Rating 1932 | -62.46 | 821.472 | 150.28 | 35.6 | 2191.66 | 9315.82 | 13246.1 | 0.44 | 1.66 | 13.547 | 14.38 | 1 | 1 | 2220 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1800387.3235 | 109971.7269 | 4799.9874 | 11807.807 | 98163.9199 | 15526.7588 | 0.084584 | -119893.5161 | 119893.5161
C | Xist Rating 1933 | -62.22 | 827.241 | 150.28 | 35.6 | 2191.14 | 9342.91 | 13182.5 | 0.43 | 1.65 | 13.547 | 14.274 | 1 | 1 | 2230 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1812600.8447 | 110911.2667 | 4843.3279 | 11860.9953 | 99050.2714 | 15405.8084 | 0.084965 | -118959.569 | 118959.569
C | Xist Rating 1934 | -61.99 | 834.118 | 150.28 | 35.6 | 2187.03 | 9309.19 | 13111.8 | 0.43 | 1.64 | 13.544 | 14.159 | 1 | 1 | 2240 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1824241.0895 | 111854.79 | 4886.8633 | 11914.1836 | 99940.6064 | 15288.8627 | 0.085346 | -118056.5452 | 118056.5452
C | Xist Rating 1935 | -61.74 | 841.602 | 150.28 | 35.6 | 2183.03 | 9281.96 | 13034.1 | 0.42 | 1.63 | 13.542 | 14.032 | 1 | 1 | 2250 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1837242.4141 | 112802.297 | 4930.5934 | 11967.3719 | 100834.9251 | 15145.8394 | 0.085727 | -116952.157 | 116952.157
C | Xist Rating 1936 | -61.59 | 845.491 | 150.28 | 35.6 | 2182.48 | 9294.6 | 12995.7 | 0.42 | 1.62 | 13.539 | 13.974 | 1 | 1 | 2260 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1845267.1977 | 113753.7876 | 4974.5182 | 12020.5603 | 101733.2273 | 15088.0283 | 0.086108 | -116505.7551 | 116505.7551
C | Xist Rating 1937 | -60.8 | 867.355 | 150.28 | 35.6 | 2172.07 | 9251.23 | 12751.9 | 0.41 | 1.59 | 13.578 | 13.546 | 1 | 1 | 2270 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1883955.7749 | 114709.2617 | 5018.6379 | 12073.7486 | 102635.5132 | 14633.9507 | 0.086489 | -112999.4881 | 112999.4881
C | Xist Rating 1938 | -60.58 | 874.177 | 150.28 | 35.6 | 2168.23 | 9221.51 | 12686.2 | 0.41 | 1.58 | 13.57 | 13.444 | 1 | 1 | 2280 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1895416.7967 | 115668.7195 | 5062.9524 | 12126.9369 | 103541.7826 | 14530.184 | 0.08687 | -112198.2294 | 112198.2294
C | Xist Rating 1939 | -60.3 | 882.062 | 150.28 | 35.6 | 2165.19 | 9214.94 | 12607 | 0.41 | 1.56 | 13.566 | 13.316 | 1 | 1 | 2290 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1909831.8218 | 116632.1609 | 5107.4617 | 12180.1252 | 104452.0357 | 14399.5818 | 0.087251 | -111189.7536 | 111189.7536
C | Xist Rating 1940 | -60.12 | 887.558 | 150.28 | 35.6 | 2162.7 | 9200.54 | 12557.1 | 0.4 | 1.56 | 13.562 | 13.242 | 1 | 1 | 2300 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1919521.6866 | 117599.5858 | 5152.1657 | 12233.3135 | 105366.2723 | 14311.075 | 0.087632 | -110506.3278 | 110506.3278
| Xist Rating 1941 | -59.93 | 893.318 | 150.28 | 35.6 | 2159.5 | 9173.2 | 12507.7 | 0.4 | 1.55 | 13.559 | 13.172 | 1 | 1 | 2310 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1929120.221 | 118570.9944 | 5197.0645 | 12286.5019 | 106284.4926 | 14240.6875 | 0.088013 | -109962.8142 | 109962.8142
| Xist Rating 1942 | -59.13 | 915.674 | 150.28 | 35.6 | 2150.18 | 9149.79 | 12277.2 | 0.4 | 1.51 | 13.597 | 12.784 | 1 | 1 | 2320 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1968863.9213 | 119546.3866 | 5242.1582 | 12339.6902 | 107206.6964 | 13841.7619 | 0.088394 | -106882.4166 | 106882.4166
| Xist Rating 1943 | -58.9 | 922.528 | 150.28 | 35.6 | 2147.08 | 9132.24 | 12216.9 | 0.39 | 1.5 | 13.592 | 12.695 | 1 | 1 | 2330 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1980741.4182 | 120525.7624 | 5287.4466 | 12392.8785 | 108132.8839 | 13737.3689 | 0.088775 | -106076.3216 | 106076.3216
| Xist Rating 1944 | -58.67 | 929.358 | 150.28 | 35.6 | 2144.18 | 9118.22 | 12157.3 | 0.39 | 1.49 | 13.587 | 12.607 | 1 | 1 | 2340 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 1992710.8364 | 121509.1218 | 5332.9298 | 12446.0668 | 109063.0549 | 13648.1526 | 0.089156 | -105387.417 | 105387.417
| Xist Rating 1945 | -58.45 | 935.627 | 150.28 | 35.6 | 2142.31 | 9118.54 | 12104.7 | 0.38 | 1.49 | 13.581 | 12.532 | 1 | 1 | 2350 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2004403.0784 | 122496.4647 | 5378.6078 | 12499.2551 | 109997.2096 | 13558.0881 | 0.089537 | -104691.9621 | 104691.9621
| Xist Rating 1946 | -58.2 | 943.162 | 150.28 | 35.6 | 2139.14 | 9103.61 | 12039.8 | 0.38 | 1.48 | 13.576 | 12.437 | 1 | 1 | 2360 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2017555.5607 | 123487.7913 | 5424.4805 | 12552.4435 | 110935.3479 | 13461.543 | 0.089918 | -103946.4669 | 103946.4669
| Xist Rating 1947 | -57.47 | 963.762 | 150.28 | 35.6 | 2130.69 | 9079.05 | 11846.8 | 0.38 | 1.45 | 13.612 | 12.129 | 1 | 1 | 2370 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2053478.0558 | 124483.1015 | 5470.5481 | 12605.6318 | 111877.4697 | 13145.4512 | 0.090299 | -101505.69 | 101505.69
| Xist Rating 1948 | -57.24 | 970.83 | 150.28 | 35.6 | 2127.57 | 9060.25 | 11791.1 | 0.37 | 1.44 | 13.605 | 12.052 | 1 | 1 | 2380 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2065508.7831 | 125482.3953 | 5516.8105 | 12658.8201 | 112823.5752 | 13053.0075 | 0.09068 | -100791.8639 | 100791.8639
| Xist Rating 1949 | -56.99 | 977.921 | 150.28 | 35.6 | 2125.51 | 9064.51 | 11730 | 0.37 | 1.43 | 13.6 | 11.962 | 1 | 1 | 2390 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2078580.8647 | 126485.6727 | 5563.2676 | 12712.0084 | 113773.6643 | 12961.6008 | 0.091061 | -100086.046 | 100086.046
C | Xist Rating 1950 | -52.76 | 1121.57 | 150.28 | 35.6 | 2036.66 | 8350.48 | 10538.2 | 0.4 | 1.25 | 13.603 | 10.184 | 1 | 1 | 2400 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2284256.7562 | 127492.9337 | 5609.9196 | 12765.1967 | 114727.737 | 11161.4276 | 0.091442 | -86185.5855 | 86185.5855
C | Xist Rating 1951 | -52.33 | 1123.02 | 150.28 | 35.6 | 2053.38 | 8639.02 | 10538 | 0.39 | 1.25 | 13.596 | 10.193 | 1 | 1 | 2410 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2305986.8076 | 128504.1783 | 5656.7663 | 12818.3851 | 115685.7932 | 11158.2232 | 0.091823 | -86160.842 | 86160.842
C | Xist Rating 1952 | -52.34 | 1124.42 | 150.28 | 35.6 | 2051.74 | 8609.99 | 10538 | 0.39 | 1.25 | 13.636 | 10.204 | 1 | 1 | 2420 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2307017.4908 | 129519.4065 | 5703.8078 | 12871.5734 | 116647.8331 | 11173.7157 | 0.092204 | -86280.471 | 86280.471
C | Xist Rating 1953 | -51.9 | 1125.78 | 150.28 | 35.6 | 2068.33 | 8910.05 | 10537.9 | 0.39 | 1.25 | 13.631 | 10.213 | 1 | 1 | 2430 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2328484.5474 | 130538.6183 | 5751.0441 | 12924.7617 | 117613.8566 | 11185.2336 | 0.092585 | -86369.409 | 86369.409
C | Xist Rating 1954 | -51.89 | 1127.15 | 150.28 | 35.6 | 2067.37 | 8892.19 | 10537.9 | 0.38 | 1.25 | 13.623 | 10.224 | 1 | 1 | 2440 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2330236.0955 | 131561.8137 | 5798.4752 | 12977.95 | 118583.8637 | 11183.799 | 0.092966 | -86358.3314 | 86358.3314
C | Xist Rating 1955 | -51.87 | 1128.47 | 150.28 | 35.6 | 2066.71 | 8880 | 10537.9 | 0.38 | 1.25 | 13.619 | 10.235 | 1 | 1 | 2450 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2332220.2337 | 132588.9927 | 5846.1011 | 13031.1383 | 119557.8544 | 11197.376 | 0.093347 | -86463.1694 | 86463.1694
C | Xist Rating 1956 | -51.85 | 1129.94 | 150.28 | 35.6 | 2065.72 | 8861.83 | 10537.9 | 0.37 | 1.25 | 13.615 | 10.246 | 1 | 1 | 2460 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2334139.6568 | 133620.1553 | 5893.9217 | 13084.3267 | 120535.8286 | 11195.9386 | 0.093728 | -86452.07 | 86452.07
C | Xist Rating 1957 | -51.83 | 1131.3 | 150.28 | 35.6 | 2065.05 | 8849.56 | 10537.9 | 0.36 | 1.25 | 13.652 | 10.257 | 1 | 1 | 2470 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2336191.065 | 134655.3015 | 5941.9372 | 13137.515 | 121517.7865 | 11196.0208 | 0.094109 | -86452.7047 | 86452.7047
C | Xist Rating 1958 | -51.81 | 1132.65 | 150.28 | 35.6 | 2064.3 | 8835.79 | 10537.9 | 0.36 | 1.25 | 13.646 | 10.267 | 1 | 1 | 2480 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2338129.395 | 135694.4313 | 5990.1474 | 13190.7033 | 122503.728 | 11208.3686 | 0.09449 | -86548.0517 | 86548.0517
C | Xist Rating 1959 | -51.79 | 1134.04 | 150.28 | 35.6 | 2063.44 | 8820.14 | 10537.9 | 0.35 | 1.25 | 13.641 | 10.278 | 1 | 1 | 2490 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2340023.4976 | 136737.5447 | 6038.5525 | 13243.8916 | 123493.6531 | 11206.5681 | 0.094871 | -86534.1482 | 86534.1482
C | Xist Rating 1960 | -51.75 | 1135.03 | 150.28 | 35.6 | 2064.32 | 8836.23 | 10537.8 | 0.35 | 1.25 | 13.634 | 10.286 | 1 | 1 | 2500 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2343065.1296 | 137784.6417 | 6087.1523 | 13297.0799 | 124487.5618 | 11216.7416 | 0.095252 | -86612.7054 | 86612.7054
C | Xist Rating 1961 | -51.73 | 1136.88 | 150.28 | 35.6 | 2062.94 | 8810.96 | 10537.8 | 0.34 | 1.25 | 13.63 | 10.299 | 1 | 1 | 2510 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2345315.2272 | 138835.7223 | 6135.9469 | 13350.2683 | 125485.4541 | 11216.8885 | 0.095633 | -86613.8394 | 86613.8394
C | Xist Rating 1962 | -51.7 | 1138.33 | 150.28 | 35.6 | 2062.42 | 8801.45 | 10537.8 | 0.34 | 1.25 | 13.667 | 10.31 | 1 | 1 | 2520 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2347714.5586 | 139890.7866 | 6184.9363 | 13403.4566 | 126487.33 | 11231.8102 | 0.096014 | -86729.0613 | 86729.0613
C | Xist Rating 1963 | -51.68 | 1139.67 | 150.28 | 35.6 | 2061.98 | 8793.51 | 10537.8 | 0.33 | 1.25 | 13.671 | 10.32 | 1 | 1 | 2530 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2349976.7466 | 140949.8344 | 6234.1205 | 13456.6449 | 127493.1895 | 11228.9286 | 0.096395 | -86706.8099 | 86706.8099
C | Xist Rating 1964 | -51.66 | 1140.82 | 150.28 | 35.6 | 2061.69 | 8788.2 | 10537.8 | 0.33 | 1.25 | 13.667 | 10.329 | 1 | 1 | 2540 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2352017.1858 | 142012.8658 | 6283.4995 | 13509.8332 | 128503.0326 | 11240.147 | 0.096776 | -86793.4356 | 86793.4356
C | Xist Rating 1965 | -51.64 | 1142.37 | 150.28 | 35.6 | 2060.72 | 8770.66 | 10537.8 | 0.32 | 1.25 | 13.662 | 10.341 | 1 | 1 | 2550 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2354104.7064 | 143079.8808 | 6333.0732 | 13563.0215 | 129516.8593 | 11238.826 | 0.097157 | -86783.2349 | 86783.2349
C | Xist Rating 1966 | -51.62 | 1143.82 | 150.28 | 35.6 | 2060.02 | 8757.91 | 10537.7 | 0.32 | 1.25 | 13.66 | 10.351 | 1 | 1 | 2560 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2356292.0764 | 144150.8795 | 6382.8418 | 13616.2099 | 130534.6696 | 11251.0972 | 0.097538 | -86877.9899 | 86877.9899
C | Xist Rating 1967 | -51.58 | 1145.21 | 150.28 | 35.6 | 2060.01 | 8757.86 | 10537.8 | 0.31 | 1.25 | 13.658 | 10.362 | 1 | 1 | 2570 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2359144.0521 | 145225.8617 | 6432.8051 | 13669.3982 | 131556.4635 | 11248.6724 | 0.097919 | -86859.2663 | 86859.2663
C | Xist Rating 1968 | -51.57 | 1146.57 | 150.281 | 35.6 | 2058.79 | 8735.84 | 10537.8 | 0.31 | 1.25 | 13.693 | 10.372 | 1 | 1 | 2580 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2360546.8503 | 146304.8275 | 6482.9633 | 13722.5865 | 132582.241 | 11262.21 | 0.0983 | -86963.8003 | 86963.8003
C | Xist Rating 1969 | -51.55 | 1147.93 | 150.281 | 35.6 | 2058.03 | 8722.01 | 10537.8 | 0.3 | 1.25 | 13.692 | 10.382 | 1 | 1 | 2590 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2362474.3779 | 147387.7769 | 6533.3162 | 13775.7748 | 133612.0021 | 11258.5659 | 0.098681 | -86935.6613 | 86935.6613
C | Xist Rating 1970 | -51.55 | 1149.11 | 150.281 | 35.6 | 2057.01 | 8703.75 | 10537.8 | 0.3 | 1.25 | 13.686 | 10.391 | 1 | 1 | 2600 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2363730.7611 | 148474.71 | 6583.8639 | 13828.9631 | 134645.7468 | 11269.5438 | 0.099062 | -87020.43 | 87020.43
C | Xist Rating 1971 | -51.52 | 1150.8 | 150.281 | 35.6 | 2056.33 | 8691.7 | 10537.8 | 0.3 | 1.25 | 13.682 | 10.403 | 1 | 1 | 2610 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2366424.564 | 149565.6266 | 6634.6064 | 13882.1514 | 135683.4752 | 11283.7058 | 0.099443 | -87129.7852 | 87129.7852
C | Xist Rating 1972 | -51.5 | 1152.19 | 150.281 | 35.6 | 2055.41 | 8675.29 | 10537.8 | 0.29 | 1.25 | 13.679 | 10.413 | 1 | 1 | 2620 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 10 | E | Rod | 2368222.8479 | 150660.5268 | 6685.5437 | 13935.3398 | 136725.1871 | 11279.7603 | 0.099824 | -87099.3188 | 87099.3188
C | Xist Rating 1973 | -51.46 | 1153.62 | 150.281 | 35.6 | 2055.43 | 8675.61 | 10537.7 | 0.29 | 1.25 | 13.712 | 10.423 | 1 | 1 | 2630 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2371185.1566 | 151759.4107 | 6736.6758 | 13988.5281 | 137770.8826 | 11293.0516 | 0.10021 | -87201.9509 | 87201.9509
C | Xist Rating 1974 | -51.44 | 1154.87 | 150.281 | 35.6 | 2055.15 | 8670.76 | 10537.7 | 0.28 | 1.25 | 13.708 | 10.432 | 1 | 1 | 2640 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2373431.0805 | 152862.2781 | 6788.0027 | 14041.7164 | 138820.5617 | 11287.8216 | 0.10059 | -87161.5664 | 87161.5664
C | Xist Rating 1975 | -51.42 | 1156.37 | 150.281 | 35.6 | 2054.4 | 8657.44 | 10537.7 | 0.28 | 1.25 | 13.704 | 10.443 | 1 | 1 | 2650 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2375646.528 | 153969.1292 | 6839.5243 | 14094.9047 | 139874.2244 | 11300.8325 | 0.10097 | -87262.0332 | 87262.0332
C | Xist Rating 1976 | -51.39 | 1157.71 | 150.281 | 35.6 | 2054.11 | 8652.12 | 10537.7 | 0.28 | 1.25 | 13.702 | 10.453 | 1 | 1 | 2660 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2378063.6881 | 155079.9638 | 6891.2408 | 14148.093 | 140931.8708 | 11312.8707 | 0.10135 | -87354.9889 | 87354.9889
C | Xist Rating 1977 | -51.4 | 1159.1 | 150.281 | 35.6 | 2052.08 | 8616.36 | 10537.7 | 0.27 | 1.25 | 13.698 | 10.463 | 1 | 1 | 2670 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2378565.928 | 156194.7821 | 6943.152 | 14201.2814 | 141993.5007 | 11308.4474 | 0.10173 | -87320.833 | 87320.833
C | Xist Rating 1978 | -51.35 | 1160.51 | 150.281 | 35.6 | 2052.79 | 8628.79 | 10537.7 | 0.27 | 1.25 | 13.737 | 10.473 | 1 | 1 | 2680 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2382283.3229 | 157313.5839 | 6995.258 | 14254.4697 | 143059.1142 | 11321.7551 | 0.10211 | -87423.5921 | 87423.5921
C | Xist Rating 1979 | -51.31 | 1161.89 | 150.281 | 35.6 | 2052.68 | 8627 | 10537.7 | 0.27 | 1.25 | 13.729 | 10.483 | 1 | 1 | 2690 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2384988.3652 | 158436.3694 | 7047.5588 | 14307.658 | 144128.7113 | 11333.5422 | 0.10249 | -87514.6088 | 87514.6088
C | Xist Rating 1980 | -51.27 | 1163.09 | 150.281 | 35.6 | 2053.11 | 8634.49 | 10537.7 | 0.26 | 1.25 | 13.726 | 10.492 | 1 | 1 | 2700 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2387951.7099 | 159563.1384 | 7100.0544 | 14360.8463 | 145202.2921 | 11327.8401 | 0.10287 | -87470.5789 | 87470.5789
C | Xist Rating 1981 | -51.27 | 1164.75 | 150.281 | 35.6 | 2051.39 | 8604.13 | 10537.7 | 0.26 | 1.25 | 13.72 | 10.503 | 1 | 1 | 2710 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2389356.5025 | 160693.8911 | 7152.7448 | 14414.0346 | 146279.8564 | 11340.6738 | 0.10325 | -87569.677 | 87569.677
C | Xist Rating 1982 | -51.24 | 1166.09 | 150.281 | 35.6 | 2051.26 | 8601.88 | 10537.7 | 0.26 | 1.25 | 13.719 | 10.512 | 1 | 1 | 2720 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2391953.7734 | 161828.6273 | 7205.63 | 14467.223 | 147361.4044 | 11351.5876 | 0.10363 | -87653.9503 | 87653.9503
C | Xist Rating 1983 | -51.18 | 1167.41 | 150.281 | 35.6 | 2052.17 | 8617.72 | 10537.8 | 0.25 | 1.25 | 13.761 | 10.522 | 1 | 1 | 2730 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2395723.7797 | 162967.3472 | 7258.71 | 14520.4113 | 148446.9359 | 11348.0682 | 0.10402 | -87626.7747 | 87626.7747
C | Xist Rating 1984 | -51.17 | 1168.7 | 150.281 | 35.6 | 2051.4 | 8604.21 | 10537.8 | 0.25 | 1.25 | 13.754 | 10.531 | 1 | 1 | 2740 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2397471.18 | 164110.0506 | 7311.9847 | 14573.5996 | 149536.451 | 11358.7418 | 0.1044 | -87709.1936 | 87709.1936
C | Xist Rating 1985 | -51.1 | 1170.24 | 150.281 | 35.6 | 2052.47 | 8623.06 | 10537.8 | 0.25 | 1.25 | 13.757 | 10.542 | 1 | 1 | 2750 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2401882.4928 | 165256.7377 | 7365.4543 | 14626.7879 | 150629.9498 | 11371.7991 | 0.10478 | -87810.0181 | 87810.0181
C | Xist Rating 1986 | -50.96 | 1171.67 | 150.281 | 35.6 | 2056.47 | 8693.96 | 10538 | 0.24 | 1.25 | 13.767 | 10.552 | 1 | 1 | 2760 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2409504.2049 | 166407.4084 | 7419.1186 | 14679.9762 | 151727.4321 | 11367.003 | 0.10516 | -87772.984 | 87772.984
C | Xist Rating 1987 | -50.83 | 1172.9 | 150.281 | 35.6 | 2060.75 | 8770.89 | 10538.1 | 0.24 | 1.25 | 13.775 | 10.561 | 1 | 1 | 2770 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2417053.675 | 167562.0626 | 7472.9777 | 14733.1646 | 152828.8981 | 11378.0689 | 0.10554 | -87858.4322 | 87858.4322
C | Xist Rating 1988 | -51.03 | 1174.45 | 150.281 | 35.6 | 2050.8 | 8593.71 | 10537.8 | 0.24 | 1.25 | 13.787 | 10.571 | 1 | 1 | 2780 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2408562.06 | 168720.7005 | 7527.0316 | 14786.3529 | 153934.3476 | 11390.2947 | 0.10592 | -87952.8363 | 87952.8363
C | Xist Rating 1989 | -50.83 | 1175.86 | 150.281 | 35.6 | 2057.69 | 8715.9 | 10538 | 0.23 | 1.25 | 13.803 | 10.581 | 1 | 1 | 2790 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2419555.3634 | 169883.322 | 7581.2803 | 14839.5412 | 155043.7808 | 11385.381 | 0.1063 | -87914.8938 | 87914.8938
C | Xist Rating 1990 | -50.24 | 1176.84 | 150.281 | 35.6 | 2081.81 | 9165.41 | 10538.3 | 0.23 | 1.25 | 13.878 | 10.59 | 1 | 1 | 2800 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2449957.2804 | 171049.927 | 7635.7238 | 14892.7295 | 156157.1975 | 11398.3155 | 0.10668 | -88014.7711 | 88014.7711
C | Xist Rating 1991 | -50.13 | 1178.58 | 150.281 | 35.6 | 2084.51 | 9217.99 | 10538.3 | 0.22 | 1.25 | 13.894 | 10.602 | 1 | 1 | 2810 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2456761.7958 | 172220.5157 | 7690.3621 | 14945.9178 | 157274.5979 | 11395.1713 | 0.10706 | -87990.4922 | 87990.4922
C | Xist Rating 1992 | -50.02 | 1180.06 | 150.281 | 35.6 | 2087.48 | 9276.26 | 10538.3 | 0.22 | 1.25 | 13.909 | 10.612 | 1 | 1 | 2820 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2463351.6488 | 173395.088 | 7745.1952 | 14999.1062 | 158395.9818 | 11407.3436 | 0.10744 | -88084.4832 | 88084.4832
C | Xist Rating 1993 | -49.89 | 1181.43 | 150.281 | 35.6 | 2091.45 | 9355.17 | 10538.3 | 0.22 | 1.25 | 13.967 | 10.621 | 1 | 1 | 2830 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2470901.7735 | 174573.6439 | 7800.223 | 15052.2945 | 159521.3494 | 11419.6803 | 0.10783 | -88179.7445 | 88179.7445
C | Xist Rating 1994 | -49.8 | 1182.74 | 150.281 | 35.6 | 2093.85 | 9403.48 | 10538.3 | 0.21 | 1.25 | 13.975 | 10.631 | 1 | 1 | 2840 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2476480.149 | 175756.1834 | 7855.4457 | 15105.4828 | 160650.7006 | 11413.8763 | 0.10821 | -88134.9269 | 88134.9269
C | Xist Rating 1995 | -49.71 | 1184.19 | 150.281 | 35.6 | 2095.69 | 9440.77 | 10538.3 | 0.21 | 1.25 | 13.984 | 10.64 | 1 | 1 | 2850 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2481695.1411 | 176942.7064 | 7910.8631 | 15158.6711 | 161784.0353 | 11424.7797 | 0.10859 | -88219.1203 | 88219.1203
C | Xist Rating 1996 | -49.63 | 1185.59 | 150.281 | 35.6 | 2097.49 | 9477.44 | 10538.2 | 0.21 | 1.25 | 13.987 | 10.65 | 1 | 1 | 2860 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2486763.1691 | 178133.2131 | 7966.4753 | 15211.8594 | 162921.3537 | 11436.5618 | 0.10897 | -88310.0985 | 88310.0985
C | Xist Rating 1997 | -49.56 | 1186.78 | 150.281 | 35.6 | 2099.2 | 9512.3 | 10538.2 | 0.21 | 1.25 | 13.99 | 10.659 | 1 | 1 | 2870 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2491288.576 | 179327.7034 | 8022.2824 | 15265.0478 | 164062.6556 | 11447.3059 | 0.10935 | -88393.062 | 88393.062
C | Xist Rating 1998 | -49.49 | 1188.29 | 150.281 | 35.5 | 2100.79 | 9545.13 | 10538.2 | 0.2 | 1.25 | 14.032 | 10.669 | 1 | 1 | 2880 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2496347.7491 | 180526.1773 | 8078.2842 | 15318.2361 | 165207.9412 | 11442.0318 | 0.10973 | -88352.3367 | 88352.3367
C | Xist Rating 1999 | -49.42 | 1189.64 | 150.281 | 35.5 | 2101.93 | 9568.72 | 10538.2 | 0.2 | 1.25 | 14.031 | 10.678 | 1 | 1 | 2890 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2500540.0052 | 181728.6348 | 8134.4807 | 15371.4244 | 166357.2104 | 11452.6104 | 0.11011 | -88434.0214 | 88434.0214
C | Xist Rating 2000 | -49.35 | 1191.02 | 150.281 | 35.5 | 2103.27 | 9596.61 | 10538.2 | 0.2 | 1.25 | 14.032 | 10.687 | 1 | 1 | 2900 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2505036.6354 | 182935.0759 | 8190.8721 | 15424.6127 | 167510.4632 | 11463.2407 | 0.11049 | -88516.1062 | 88516.1062
C | Xist Rating 2001 | -49.28 | 1192.56 | 150.281 | 35.5 | 2104.4 | 9620.25 | 10538.1 | 0.2 | 1.25 | 14.034 | 10.697 | 1 | 1 | 2910 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2509623.264 | 184145.5006 | 8247.4583 | 15477.801 | 168667.6995 | 11474.9358 | 0.11087 | -88606.4128 | 88606.4128
C | Xist Rating 2002 | -49.19 | 1193.95 | 150.281 | 35.5 | 2106.81 | 9670.87 | 10538.1 | 0.2 | 1.25 | 14.035 | 10.707 | 1 | 1 | 2920 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2515425.7995 | 185359.9089 | 8304.2393 | 15530.9894 | 169828.9195 | 11486.6051 | 0.11125 | -88696.52 | 88696.52
C | Xist Rating 2003 | -49.03 | 1195.34 | 150.281 | 35.5 | 2111.9 | 9779.2 | 10537.9 | 0.19 | 1.25 | 14.084 | 10.716 | 1 | 1 | 2930 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2524438.546 | 186578.3008 | 8361.215 | 15584.1777 | 170994.1231 | 11479.9995 | 0.11164 | -88645.5134 | 88645.5134
C | Xist Rating 2004 | -49.01 | 1196.7 | 150.281 | 35.5 | 2111.24 | 9765.08 | 10537.9 | 0.19 | 1.25 | 14.079 | 10.725 | 1 | 1 | 2940 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2526520.908 | 187800.6763 | 8418.3855 | 15637.366 | 172163.3103 | 11490.4203 | 0.11202 | -88725.9799 | 88725.9799
C | Xist Rating 2005 | -48.99 | 1198.11 | 150.281 | 35.5 | 2110.52 | 9749.66 | 10537.9 | 0.19 | 1.25 | 14.075 | 10.734 | 1 | 1 | 2950 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2528635.1172 | 189027.0354 | 8475.7509 | 15690.5543 | 173336.481 | 11500.8654 | 0.1124 | -88806.6339 | 88806.6339
C | Xist Rating 2006 | -48.97 | 1199.48 | 150.281 | 35.5 | 2109.84 | 9735.22 | 10537.9 | 0.19 | 1.25 | 14.072 | 10.743 | 1 | 1 | 2960 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2530710.8832 | 190257.3781 | 8533.311 | 15743.7426 | 174513.6354 | 11511.335 | 0.11278 | -88887.4772 | 88887.4772
C | Xist Rating 2007 | -48.95 | 1200.87 | 150.281 | 35.5 | 2109.14 | 9720.31 | 10537.9 | 0.18 | 1.25 | 14.069 | 10.752 | 1 | 1 | 2970 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2532802.9518 | 191491.7044 | 8591.0659 | 15796.931 | 175694.7734 | 11503.0741 | 0.11316 | -88823.6889 | 88823.6889
C | Xist Rating 2008 | -48.94 | 1202.09 | 150.281 | 35.5 | 2108.55 | 9707.71 | 10537.9 | 0.18 | 1.25 | 14.105 | 10.761 | 1 | 1 | 2980 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2534666.8695 | 192730.0143 | 8649.0156 | 15850.1193 | 176879.895 | 11514.4213 | 0.11354 | -88911.3091 | 88911.3091
C | Xist Rating 2009 | -48.93 | 1203.65 | 150.281 | 35.5 | 2107.48 | 9685.37 | 10537.5 | 0.18 | 1.25 | 14.108 | 10.77 | 1 | 1 | 2990 | 152.4 | 2 | 1.9 | 19.05 | 1.3333 | 9 | E | Rod | 2536668.302 | 193972.3078 | 8707.16 | 15903.3076 | 178069.0002 | 11524.9782 | 0.11392 | -88992.8268 | 88992.8268
C | Xist Rating 2011 | -94.03 | 110.664 | 150.283 | 35.8 | 2408.06 | 7484.98 | 58746 | 2.44 | 10.95 | 14.753 | 360.819 | 1 | 1 | 1000 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 266485.5518 | 26565.0967 | 973.9444 | 5598.7705 | 20966.3262 | 376323.5283 | 0.038101 | -2905870.533 | 2905870.533
C | Xist Rating 2012 | -93.98 | 111.845 | 150.283 | 35.8 | 2405.03 | 7464.43 | 58284.4 | 2.42 | 10.85 | 14.77 | 354.092 | 1 | 1 | 1010 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 268990.5804 | 27042.5076 | 993.5206 | 5654.7582 | 21387.7494 | 369342.1894 | 0.038482 | -2851962.4847 | 2851962.4847
C | Xist Rating 2013 | -93.53 | 120.619 | 150.283 | 35.8 | 2398.94 | 7471.95 | 54967.9 | 2.43 | 10.07 | 14.823 | 306.848 | 1 | 1 | 1020 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 289357.7439 | 27524.1117 | 1013.2917 | 5710.7459 | 21813.3658 | 320308.0334 | 0.038863 | -2473333.7295 | 2473333.7295
C | Xist Rating 2014 | -93.45 | 123.126 | 150.283 | 35.8 | 2379.49 | 7302.63 | 54179.1 | 2.35 | 9.89 | 14.558 | 296.702 | 1 | 1 | 1030 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 292977.0857 | 28009.9091 | 1033.2576 | 5766.7336 | 22243.1755 | 309704.0727 | 0.039244 | -2391452.7561 | 2391452.7561
C | Xist Rating 2015 | -93.36 | 124.381 | 150.282 | 35.8 | 2387.08 | 7382.91 | 53794.7 | 2.29 | 9.8 | 14.5 | 291.858 | 1 | 1 | 1040 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 296907.3975 | 28499.8997 | 1053.4182 | 5822.7213 | 22677.1784 | 304642.0101 | 0.039625 | -2352364.8507 | 2352364.8507
C | Xist Rating 2016 | -93.22 | 126.767 | 150.282 | 35.8 | 2395.34 | 7479.3 | 53044.5 | 2.24 | 9.63 | 14.466 | 282.264 | 1 | 1 | 1050 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 303650.0658 | 28994.0837 | 1073.7737 | 5878.709 | 23115.3746 | 294655.833 | 0.040006 | -2275254.2381 | 2275254.2381
C | Xist Rating 2017 | -93.12 | 128.003 | 150.282 | 35.8 | 2409.66 | 7629.57 | 52677.8 | 2.19 | 9.54 | 14.452 | 277.744 | 1 | 1 | 1060 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 308443.709 | 29492.4608 | 1094.3239 | 5934.6967 | 23557.7641 | 289940.5213 | 0.040387 | -2238843.851 | 2238843.851
C | Xist Rating 2018 | -92.67 | 137.522 | 150.282 | 35.8 | 2388.47 | 7489.69 | 49858.6 | 2.18 | 8.9 | 14.379 | 243.084 | 1 | 1 | 1070 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 328467.1713 | 29995.0313 | 1115.0689 | 5990.6844 | 24004.3469 | 253945.7888 | 0.040768 | -1960902.0678 | 1960902.0678
C | Xist Rating 2019 | -92.56 | 139.379 | 150.282 | 35.8 | 2393.44 | 7551.51 | 49382 | 2.13 | 8.79 | 14.318 | 237.705 | 1 | 1 | 1080 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 333595.2738 | 30501.795 | 1136.0087 | 6046.6721 | 24455.1229 | 248332.6619 | 0.041149 | -1917558.9892 | 1917558.9892
C | Xist Rating 2020 | -92.44 | 141.845 | 150.282 | 35.8 | 2391.97 | 7553.74 | 48761.8 | 2.07 | 8.65 | 14.227 | 230.78 | 1 | 1 | 1090 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 339288.9846 | 31012.752 | 1157.1433 | 6102.6598 | 24910.0922 | 241103.5534 | 0.04153 | -1861737.73 | 1861737.73
C | Xist Rating 2021 | -92.33 | 143.67 | 150.282 | 35.8 | 2397.83 | 7625.31 | 48308.7 | 2.04 | 8.55 | 14.213 | 225.772 | 1 | 1 | 1100 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 344496.2361 | 31527.9022 | 1178.4727 | 6158.6475 | 25369.2547 | 235893.5012 | 0.041911 | -1821507.0875 | 1821507.0875
C | Xist Rating 2022 | -92.28 | 145.093 | 150.281 | 35.8 | 2390.87 | 7563.82 | 48010.7 | 1.96 | 8.49 | 14.043 | 222.782 | 1 | 1 | 1110 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 346898.5009 | 32047.2458 | 1199.9969 | 6214.6353 | 25832.6105 | 232728.2353 | 0.042292 | -1797065.7432 | 1797065.7432
C | Xist Rating 2023 | -91.73 | 155.619 | 150.282 | 35.8 | 2388.77 | 7620.48 | 45448 | 2 | 7.92 | 14.202 | 194.936 | 1 | 1 | 1120 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 371737.9986 | 32570.7825 | 1221.7158 | 6270.623 | 26300.1596 | 203866.7111 | 0.042673 | -1574204.7038 | 1574204.7038
C | Xist Rating 2024 | -91.68 | 156.996 | 150.281 | 35.8 | 2386.39 | 7604.73 | 45188.8 | 1.94 | 7.86 | 14.089 | 192.514 | 1 | 1 | 1130 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 374653.6844 | 33098.5126 | 1243.6296 | 6326.6107 | 26771.9019 | 201309.9345 | 0.043054 | -1554461.9531 | 1554461.9531
C | Xist Rating 2025 | -91.55 | 159.532 | 150.281 | 35.8 | 2385.39 | 7611.26 | 44681.9 | 1.89 | 7.75 | 13.942 | 187.575 | 1 | 1 | 1140 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 380546.0375 | 33630.4359 | 1265.7381 | 6382.5984 | 27247.8375 | 196142.848 | 0.043435 | -1514563.0806 | 1514563.0806
C | Xist Rating 2026 | -91.39 | 162.006 | 150.281 | 35.8 | 2394.09 | 7717.67 | 44187 | 1.84 | 7.64 | 13.909 | 182.773 | 1 | 1 | 1150 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 387856.9445 | 34166.5525 | 1288.0414 | 6438.5861 | 27727.9664 | 191128.7257 | 0.043816 | -1475845.3572 | 1475845.3572
C | Xist Rating 2027 | -91.27 | 164.558 | 150.281 | 35.8 | 2392.53 | 7718.61 | 43704.5 | 1.79 | 7.53 | 13.827 | 178.223 | 1 | 1 | 1160 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 393709.9517 | 34706.8623 | 1310.5395 | 6494.5738 | 28212.2885 | 186371.2366 | 0.044197 | -1439109.2873 | 1439109.2873
C | Xist Rating 2028 | -90.77 | 174.064 | 150.281 | 35.8 | 2392.44 | 7788.45 | 41833.5 | 1.81 | 7.13 | 13.925 | 160.348 | 1 | 1 | 1170 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 416437.6762 | 35251.3654 | 1333.2324 | 6550.5615 | 28700.8039 | 167842.9773 | 0.044578 | -1296038.9808 | 1296038.9808
C | Xist Rating 2029 | -90.71 | 174.845 | 150.281 | 35.8 | 2399.06 | 7863.38 | 41726 | 1.76 | 7.11 | 13.875 | 159.536 | 1 | 1 | 1180 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 419463.6457 | 35800.0618 | 1356.1201 | 6606.5492 | 29193.5126 | 166969.5329 | 0.044959 | -1289294.4746 | 1289294.4746
C | Xist Rating 2030 | -90.5 | 179.777 | 150.281 | 35.8 | 2387.28 | 7772.22 | 40887.1 | 1.71 | 6.93 | 13.784 | 152.143 | 1 | 1 | 1190 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 12 | E | Rod | 429178.0366 | 36352.9514 | 1379.2026 | 6662.5369 | 29690.4145 | 159257.5543 | 0.04534 | -1229744.6199 | 1229744.6199
C | Xist Rating 2031 | -90.39 | 181.047 | 150.28 | 35.8 | 2399.83 | 7915.65 | 40683.2 | 1.68 | 6.88 | 13.728 | 150.43 | 1 | 1 | 1200 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 434482.022 | 36910.0343 | 1402.4799 | 6718.5246 | 30191.5097 | 157461.8684 | 0.045721 | -1215878.8092 | 1215878.8092
C | Xist Rating 2032 | -90.27 | 183.668 | 150.28 | 35.8 | 2395.44 | 7885.62 | 40282.2 | 1.63 | 6.8 | 13.651 | 147.106 | 1 | 1 | 1210 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 439965.6739 | 37471.3105 | 1425.9519 | 6774.5123 | 30696.7982 | 153976.2013 | 0.046102 | -1188963.4122 | 1188963.4122
C | Xist Rating 2033 | -89.76 | 194.547 | 150.28 | 35.8 | 2382.61 | 7826.54 | 38539.1 | 1.63 | 6.43 | 13.677 | 132.351 | 1 | 1 | 1220 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 463529.6277 | 38036.7799 | 1449.6188 | 6830.5 | 31206.2799 | 138665.4488 | 0.046483 | -1070737.8391 | 1070737.8391
C | Xist Rating 2034 | -89.61 | 197.018 | 150.28 | 35.8 | 2389.27 | 7916.3 | 38184.2 | 1.61 | 6.35 | 13.675 | 129.552 | 1 | 1 | 1230 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 470729.1969 | 38606.4426 | 1473.4804 | 6886.4877 | 31719.9549 | 135753.4257 | 0.046864 | -1048251.969 | 1048251.969
C | Xist Rating 2035 | -89.49 | 199.63 | 150.28 | 35.8 | 2386.28 | 7900.73 | 37836.5 | 1.57 | 6.28 | 13.618 | 126.912 | 1 | 1 | 1240 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 476373.0764 | 39180.2986 | 1497.5369 | 6942.4754 | 32237.8232 | 132986.2811 | 0.047245 | -1026884.8115 | 1026884.8115
C | Xist Rating 2036 | -89.42 | 201.043 | 150.28 | 35.8 | 2387.22 | 7919.74 | 37665.3 | 1.53 | 6.24 | 13.577 | 125.692 | 1 | 1 | 1250 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 479933.8705 | 39758.3478 | 1521.7881 | 6998.4631 | 32759.8847 | 131694.8607 | 0.047626 | -1016912.8058 | 1016912.8058
C | Xist Rating 2037 | -89.24 | 204.774 | 150.28 | 35.8 | 2384.74 | 7918.36 | 37162.2 | 1.5 | 6.14 | 13.549 | 121.843 | 1 | 1 | 1260 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 488332.7488 | 40340.5903 | 1546.2341 | 7054.4508 | 33286.1395 | 127681.615 | 0.048007 | -985923.5864 | 985923.5864
C | Xist Rating 2038 | -88.73 | 215.088 | 150.28 | 35.8 | 2378.09 | 7919.9 | 35778.3 | 1.51 | 5.85 | 13.602 | 111.333 | 1 | 1 | 1270 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 511498.6219 | 40927.0261 | 1570.8749 | 7110.4385 | 33816.5875 | 116788.3755 | 0.048388 | -901808.8787 | 901808.8787
C | Xist Rating 2039 | -88.61 | 217.767 | 150.28 | 35.8 | 2376.69 | 7921.39 | 35478.1 | 1.47 | 5.79 | 13.558 | 109.278 | 1 | 1 | 1280 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 517564.6512 | 41517.6551 | 1595.7105 | 7166.4262 | 34351.2288 | 114628.5399 | 0.048769 | -885131.2004 | 885131.2004
C | Xist Rating 2040 | -88.46 | 220.395 | 150.28 | 35.7 | 2380.81 | 7984.64 | 35183.5 | 1.43 | 5.73 | 13.552 | 107.263 | 1 | 1 | 1290 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 524718.6199 | 42112.4774 | 1620.7408 | 7222.4139 | 34890.0634 | 112513.0441 | 0.04915 | -868795.9027 | 868795.9027
C | Xist Rating 2041 | -88.23 | 224.104 | 150.28 | 35.7 | 2388.06 | 8093.3 | 34752.4 | 1.41 | 5.64 | 13.556 | 104.252 | 1 | 1 | 1300 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 535173.7982 | 42711.4929 | 1645.966 | 7278.4016 | 35433.0913 | 109379.3467 | 0.049531 | -844598.322 | 844598.322
C | Xist Rating 2042 | -88.11 | 226.154 | 150.28 | 35.7 | 2393.11 | 8164.98 | 34541.5 | 1.37 | 5.59 | 13.531 | 102.881 | 1 | 1 | 1310 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 541211.3989 | 43314.7017 | 1671.3859 | 7334.3894 | 35980.3124 | 107930.2815 | 0.049912 | -833409.0244 | 833409.0244
C | Xist Rating 2043 | -87.59 | 236.566 | 150.28 | 35.7 | 2387.61 | 8179.18 | 33364.5 | 1.37 | 5.35 | 13.576 | 94.807 | 1 | 1 | 1320 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 564827.3473 | 43922.1038 | 1697.0007 | 7390.3771 | 36531.7268 | 99557.4023 | 0.050293 | -768755.8711 | 768755.8711
C | Xist Rating 2044 | -87.42 | 240.491 | 150.28 | 35.7 | 2382.48 | 8145.75 | 32981.7 | 1.34 | 5.28 | 13.503 | 92.392 | 1 | 1 | 1330 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 572964.9977 | 44533.6992 | 1722.8102 | 7446.3648 | 37087.3344 | 97027.6532 | 0.050674 | -749221.8189 | 749221.8189
C | Xist Rating 2045 | -87.23 | 244.315 | 150.28 | 35.7 | 2382.24 | 8169.55 | 32608 | 1.31 | 5.2 | 13.481 | 90.043 | 1 | 1 | 1340 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 582016.9656 | 45149.4878 | 1748.8145 | 7502.3525 | 37647.1353 | 94570.2682 | 0.051055 | -730246.5431 | 730246.5431
C | Xist Rating 2046 | -87.11 | 246.382 | 150.28 | 35.7 | 2386.62 | 8234.72 | 32425.2 | 1.28 | 5.16 | 13.46 | 88.96 | 1 | 1 | 1350 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 588020.2088 | 45769.4697 | 1775.0136 | 7558.3402 | 38211.1295 | 93427.3905 | 0.051436 | -721421.5446 | 721421.5446
C | Xist Rating 2047 | -86.96 | 247.598 | 150.28 | 35.7 | 2404.88 | 8465.78 | 32304.9 | 1.27 | 5.14 | 13.493 | 88.214 | 1 | 1 | 1360 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 595443.4782 | 46393.6448 | 1801.4075 | 7614.3279 | 38779.3169 | 92654.7429 | 0.051817 | -715455.3647 | 715455.3647
C | Xist Rating 2048 | -86.34 | 262.547 | 150.28 | 35.7 | 2375.53 | 8220.53 | 30903.6 | 1.26 | 4.86 | 13.48 | 79.589 | 1 | 1 | 1370 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 623688.2749 | 47022.0132 | 1827.9962 | 7670.3156 | 39351.6976 | 83696.0833 | 0.052198 | -646278.9701 | 646278.9701
C | Xist Rating 2049 | -86.28 | 264.024 | 150.28 | 35.7 | 2375.55 | 8229.71 | 30795.3 | 1.24 | 4.84 | 13.457 | 79.025 | 1 | 1 | 1380 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 627202.2132 | 47654.5749 | 1854.7797 | 7726.3033 | 39928.2716 | 83099.5425 | 0.052579 | -641672.6398 | 641672.6398
C | Xist Rating 2050 | -86.11 | 267.329 | 150.28 | 35.7 | 2376.74 | 8266.19 | 30528.4 | 1.21 | 4.79 | 13.436 | 77.524 | 1 | 1 | 1390 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 635371.5275 | 48291.3298 | 1881.7579 | 7782.291 | 40509.0388 | 81521.4992 | 0.05296 | -629487.4082 | 629487.4082
C | Xist Rating 2051 | -85.94 | 270.631 | 150.28 | 35.7 | 2377.62 | 8299.26 | 30266 | 1.19 | 4.73 | 13.415 | 76.066 | 1 | 1 | 1400 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 643457.6782 | 48932.278 | 1908.931 | 7838.2787 | 41093.9993 | 79996.2243 | 0.053341 | -617709.6395 | 617709.6395
C | Xist Rating 2052 | -85.75 | 274.516 | 150.28 | 35.7 | 2376.58 | 8313.58 | 29958.3 | 1.17 | 4.67 | 13.4 | 74.354 | 1 | 1 | 1410 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 652409.2353 | 49577.4195 | 1936.2988 | 7894.2664 | 41683.1531 | 78207.4043 | 0.053722 | -603896.8452 | 603896.8452
C | Xist Rating 2053 | -85.21 | 285.638 | 150.28 | 35.7 | 2371.91 | 8339.11 | 29052.6 | 1.17 | 4.49 | 13.453 | 69.246 | 1 | 1 | 1420 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 677507.6286 | 50226.7543 | 1963.8614 | 7950.2541 | 42276.5001 | 72913.7289 | 0.054103 | -563020.4876 | 563020.4876
C | Xist Rating 2054 | -85.13 | 287.945 | 150.28 | 35.7 | 2367.8 | 8301.76 | 28911.4 | 1.14 | 4.47 | 13.408 | 68.581 | 1 | 1 | 1430 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 681796.171 | 50880.2823 | 1991.6188 | 8006.2418 | 42874.0404 | 72201.0248 | 0.054484 | -557517.175 | 557517.175
C | Xist Rating 2055 | -84.89 | 293.046 | 150.28 | 35.7 | 2365.11 | 8304.07 | 28542.8 | 1.12 | 4.39 | 13.395 | 66.638 | 1 | 1 | 1440 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 693086.0251 | 51538.0035 | 2019.571 | 8062.2295 | 43475.774 | 70171.825 | 0.054865 | -541848.2321 | 541848.2321
C | Xist Rating 2056 | -84.74 | 296.386 | 150.28 | 35.7 | 2364.21 | 8315.2 | 28317.6 | 1.1 | 4.35 | 13.378 | 65.503 | 1 | 1 | 1450 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 700718.7451 | 52199.9181 | 2047.718 | 8118.2172 | 44081.7008 | 68981.2263 | 0.055246 | -532654.7444 | 532654.7444
C | Xist Rating 2057 | -84.6 | 298.335 | 150.28 | 35.7 | 2370.77 | 8410.4 | 28184.5 | 1.09 | 4.33 | 13.385 | 64.836 | 1 | 1 | 1460 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 707283.6679 | 52866.0259 | 2076.0598 | 8174.2049 | 44691.8209 | 68286.8884 | 0.055627 | -527293.2512 | 527293.2512
C | Xist Rating 2058 | -84.06 | 311.1 | 150.28 | 35.7 | 2354.75 | 8301.19 | 27311 | 1.08 | 4.16 | 13.395 | 60.368 | 1 | 1 | 1470 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 732562.725 | 53536.3269 | 2104.5964 | 8230.1926 | 45306.1343 | 63645.3092 | 0.056008 | -491452.2069 | 491452.2069
C | Xist Rating 2059 | -83.86 | 315.029 | 150.28 | 35.7 | 2355.45 | 8336.19 | 27066.8 | 1.07 | 4.11 | 13.386 | 59.195 | 1 | 1 | 1480 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 742035.058 | 54210.8212 | 2133.3277 | 8286.1803 | 45924.6409 | 62424.11 | 0.056389 | -482022.4303 | 482022.4303
C | Xist Rating 2060 | -83.65 | 318.371 | 150.28 | 35.7 | 2362.42 | 8446.7 | 26867.3 | 1.05 | 4.07 | 13.386 | 58.261 | 1 | 1 | 1490 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 752126.0178 | 54889.5088 | 2162.2539 | 8342.168 | 46547.3408 | 61442.692 | 0.05677 | -474444.181 | 474444.181
C | Xist Rating 2061 | -83.47 | 321.804 | 150.28 | 35.7 | 2364.93 | 8501.62 | 26670.8 | 1.02 | 4.03 | 13.373 | 57.362 | 1 | 1 | 1500 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 761043.9337 | 55572.3897 | 2191.3748 | 8398.1557 | 47174.2339 | 60487.4896 | 0.057151 | -467068.361 | 467068.361
C | Xist Rating 2062 | -83.24 | 325.76 | 150.28 | 35.7 | 2369.57 | 8589.51 | 26439.8 | 1.01 | 3.99 | 13.372 | 56.288 | 1 | 1 | 1510 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 771911.1232 | 56259.4638 | 2220.6906 | 8454.1435 | 47805.3204 | 59369.1367 | 0.057532 | -458432.7362 | 458432.7362
C | Xist Rating 2063 | -82.62 | 338.209 | 150.28 | 35.7 | 2367.99 | 8664.18 | 25681.9 | 1.01 | 3.85 | 13.432 | 52.687 | 1 | 1 | 1520 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 800875.5299 | 56950.7312 | 2250.2011 | 8510.1312 | 48440.6 | 55639.6866 | 0.057913 | -429634.9117 | 429634.9117
C | Xist Rating 2064 | -82.47 | 342.509 | 150.28 | 35.7 | 2360.08 | 8586.68 | 25468.8 | 0.99 | 3.81 | 13.394 | 51.792 | 1 | 1 | 1530 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 808348.6407 | 57646.1919 | 2279.9064 | 8566.1189 | 49080.073 | 54695.3078 | 0.058294 | -422342.6684 | 422342.6684
C | Xist Rating 2065 | -82.32 | 344.732 | 150.28 | 35.7 | 2365.74 | 8676.12 | 25364.3 | 0.97 | 3.79 | 13.385 | 51.371 | 1 | 1 | 1540 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 815546.2817 | 58345.8458 | 2309.8065 | 8622.1066 | 49723.7392 | 54244.9493 | 0.058675 | -418865.1199 | 418865.1199
C | Xist Rating 2066 | -82.01 | 351.175 | 150.28 | 35.7 | 2364.14 | 8701.39 | 25021.8 | 0.95 | 3.72 | 13.38 | 49.864 | 1 | 1 | 1550 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 830226.8645 | 59049.693 | 2339.9013 | 8678.0943 | 50371.5987 | 52666.8227 | 0.059056 | -406679.2441 | 406679.2441
C | Xist Rating 2067 | -81.83 | 353.173 | 150.28 | 35.7 | 2376.52 | 8886.04 | 24921.2 | 0.94 | 3.7 | 13.396 | 49.445 | 1 | 1 | 1560 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 839322.698 | 59757.7334 | 2370.191 | 8734.082 | 51023.6514 | 52229.085 | 0.059437 | -403299.1501 | 403299.1501
C | Xist Rating 2068 | -81.24 | 368.07 | 150.28 | 35.7 | 2355.36 | 8705.72 | 24162.8 | 0.93 | 3.56 | 13.405 | 46.18 | 1 | 1 | 1570 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 866937.3552 | 60469.9671 | 2400.6755 | 8790.0697 | 51679.8974 | 48835.1937 | 0.059818 | -377092.4213 | 377092.4213
C | Xist Rating 2069 | -81.05 | 371.532 | 150.28 | 35.7 | 2358.62 | 8773.98 | 24008.1 | 0.92 | 3.53 | 13.398 | 45.571 | 1 | 1 | 1580 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 876302.8058 | 61186.3941 | 2431.3547 | 8846.0574 | 52340.3367 | 48198.3864 | 0.0602 | -372175.164 | 372175.164
C | Xist Rating 2070 | -80.86 | 375.029 | 150.28 | 35.7 | 2361.09 | 8832.06 | 23855.6 | 0.9 | 3.5 | 13.39 | 44.979 | 1 | 1 | 1590 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 885477.2216 | 61907.0144 | 2462.2288 | 8902.0451 | 53004.9693 | 47569.5095 | 0.060581 | -367319.1434 | 367319.1434
C | Xist Rating 2071 | -80.6 | 379.599 | 150.28 | 35.7 | 2365.62 | 8929.77 | 23645.7 | 0.89 | 3.46 | 13.394 | 44.137 | 1 | 1 | 1600 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 897986.9864 | 62631.8279 | 2493.2976 | 8958.0328 | 53673.7951 | 46691.1478 | 0.060962 | -360536.6667 | 360536.6667
C | Xist Rating 2072 | -80.49 | 382.018 | 150.28 | 35.7 | 2365.58 | 8943.85 | 23557 | 0.87 | 3.45 | 13.377 | 43.833 | 1 | 1 | 1610 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 903694.1404 | 63360.8346 | 2524.5612 | 9014.0205 | 54346.8141 | 46360.388 | 0.061343 | -357982.6274 | 357982.6274
C | Xist Rating 2073 | -79.77 | 398.577 | 150.28 | 35.7 | 2351.8 | 8875.01 | 22805.5 | 0.87 | 3.31 | 13.412 | 40.81 | 1 | 1 | 1620 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 937373.3886 | 64094.0347 | 2556.0196 | 9070.0082 | 55024.0265 | 43228.4351 | 0.061724 | -333798.5175 | 333798.5175
C | Xist Rating 2074 | -79.61 | 400.65 | 150.28 | 35.7 | 2359.86 | 9005.53 | 22723.7 | 0.86 | 3.29 | 13.419 | 40.518 | 1 | 1 | 1630 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 945477.909 | 64831.428 | 2587.6728 | 9125.9959 | 55705.4321 | 42921.0644 | 0.062105 | -331425.0823 | 331425.0823
C | Xist Rating 2075 | -79.44 | 404.295 | 150.28 | 35.7 | 2358.72 | 9013.46 | 22589.1 | 0.84 | 3.27 | 13.403 | 40.044 | 1 | 1 | 1640 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 953618.7024 | 65573.0146 | 2619.5208 | 9181.9836 | 56391.0309 | 42413.2718 | 0.062486 | -327504.0424 | 327504.0424
C | Xist Rating 2076 | -79.24 | 409.222 | 150.28 | 35.7 | 2355.18 | 8996 | 22403.5 | 0.83 | 3.24 | 13.387 | 39.377 | 1 | 1 | 1650 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 963791.47 | 66318.7944 | 2651.5635 | 9237.9713 | 57080.8231 | 41714.7448 | 0.062867 | -322110.202 | 322110.202
C | Xist Rating 2077 | -79 | 413.906 | 150.28 | 35.7 | 2357.01 | 9057.2 | 22221.1 | 0.82 | 3.2 | 13.386 | 38.712 | 1 | 1 | 1660 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 975580.5811 | 67068.7675 | 2683.8011 | 9293.959 | 57774.8085 | 41019.1018 | 0.063248 | -316738.631 | 316738.631
C | Xist Rating 2078 | -78.37 | 428.847 | 150.28 | 35.7 | 2344 | 8979.95 | 21633.5 | 0.82 | 3.1 | 13.407 | 36.536 | 1 | 1 | 1670 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1005217.368 | 67822.9339 | 2716.2334 | 9349.9467 | 58472.9871 | 38765.5384 | 0.063629 | -299337.2123 | 299337.2123
C | Xist Rating 2079 | -78.21 | 431.032 | 150.28 | 35.7 | 2350.47 | 9090.44 | 21560.8 | 0.8 | 3.08 | 13.415 | 36.302 | 1 | 1 | 1680 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1013127.785 | 68581.2935 | 2748.8606 | 9405.9344 | 59175.3591 | 38507.7473 | 0.06401 | -297346.6173 | 297346.6173
C | Xist Rating 2080 | -77.97 | 437.291 | 150.28 | 35.7 | 2343.77 | 9034.54 | 21346.6 | 0.79 | 3.04 | 13.39 | 35.572 | 1 | 1 | 1690 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1024909.5271 | 69343.8464 | 2781.6825 | 9461.9221 | 59881.9243 | 37742.7955 | 0.064391 | -291439.8626 | 291439.8626
C | Xist Rating 2081 | -77.75 | 441.404 | 150.28 | 35.6 | 2347.37 | 9117.86 | 21206.1 | 0.78 | 3.02 | 13.396 | 35.1 | 1 | 1 | 1700 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1036138.5075 | 70110.5926 | 2814.6992 | 9517.9098 | 60592.6827 | 37247.5191 | 0.064772 | -287615.469 | 287615.469
C | Xist Rating 2082 | -77.52 | 446.28 | 150.28 | 35.6 | 2346.11 | 9133.36 | 21045.4 | 0.77 | 2.99 | 13.381 | 34.566 | 1 | 1 | 1710 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1047021.9708 | 70881.532 | 2847.9107 | 9573.8976 | 61307.6344 | 36686.4912 | 0.065153 | -283283.3607 | 283283.3607
C | Xist Rating 2083 | -76.93 | 460.093 | 150.28 | 35.6 | 2336.64 | 9095.27 | 20567.5 | 0.76 | 2.9 | 13.413 | 32.923 | 1 | 1 | 1720 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1075071.7075 | 71656.6647 | 2881.317 | 9629.8853 | 62026.7794 | 34976.4153 | 0.065534 | -270078.6074 | 270078.6074
C | Xist Rating 2084 | -76.67 | 466.222 | 150.28 | 35.6 | 2334.15 | 9101.41 | 20374.1 | 0.75 | 2.87 | 13.401 | 32.299 | 1 | 1 | 1730 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1088232.0813 | 72435.9906 | 2914.9181 | 9685.873 | 62750.1177 | 34321.8624 | 0.065915 | -265024.3235 | 265024.3235
C | Xist Rating 2085 | -76.51 | 469.143 | 150.28 | 35.6 | 2336.41 | 9155.45 | 20290.3 | 0.74 | 2.85 | 13.398 | 32.047 | 1 | 1 | 1740 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1096110.3966 | 73219.5099 | 2948.714 | 9741.8607 | 63477.6492 | 34054.0407 | 0.066296 | -262956.2758 | 262956.2758
C | Xist Rating 2086 | -76.28 | 474.816 | 150.28 | 35.6 | 2332.05 | 9127.89 | 20123.6 | 0.73 | 2.82 | 13.385 | 31.529 | 1 | 1 | 1750 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1107294.6528 | 74007.2224 | 2982.7046 | 9797.8484 | 64209.374 | 33509.2885 | 0.066677 | -258749.8432 | 258749.8432
C | Xist Rating 2087 | -76.12 | 479.045 | 150.28 | 35.6 | 2328.37 | 9100.63 | 20000.7 | 0.72 | 2.8 | 13.379 | 31.153 | 1 | 1 | 1760 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1115394.0066 | 74799.1281 | 3016.8901 | 9853.8361 | 64945.292 | 33112.2925 | 0.067058 | -255684.3454 | 255684.3454
C | Xist Rating 2088 | -75.44 | 495.405 | 150.28 | 35.6 | 2317.34 | 9054.72 | 19497 | 0.72 | 2.71 | 13.415 | 29.534 | 1 | 1 | 1770 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1148021.8227 | 75595.2271 | 3051.2703 | 9909.8238 | 65685.4033 | 31437.3379 | 0.067439 | -242750.7904 | 242750.7904
C | Xist Rating 2089 | -75.35 | 499.744 | 150.28 | 35.6 | 2307.66 | 8936.01 | 19383.9 | 0.71 | 2.69 | 13.534 | 29.198 | 1 | 1 | 1780 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1153239.239 | 76395.5194 | 3085.8453 | 9965.8115 | 66429.7079 | 31088.7697 | 0.06782 | -240059.239 | 240059.239
C | Xist Rating 2090 | -75.23 | 502.188 | 150.28 | 35.6 | 2309.16 | 8972.72 | 19327 | 0.7 | 2.68 | 13.527 | 29.052 | 1 | 1 | 1790 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1159632.4421 | 77200.005 | 3120.6151 | 10021.7992 | 67178.2058 | 30930.2039 | 0.068201 | -238834.8358 | 238834.8358
C | Xist Rating 2091 | -74.92 | 509.688 | 150.28 | 35.6 | 2303.09 | 8932.11 | 19123.1 | 0.69 | 2.65 | 13.523 | 28.443 | 1 | 1 | 1800 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1173857.3359 | 78008.6838 | 3155.5797 | 10077.7869 | 67930.8969 | 30290.8659 | 0.068582 | -233898.0372 | 233898.0372
C | Xist Rating 2092 | -74.74 | 513.899 | 150.28 | 35.6 | 2304.68 | 8984.16 | 19012.6 | 0.68 | 2.63 | 13.513 | 28.127 | 1 | 1 | 1810 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1184372.7473 | 78821.5559 | 3190.7391 | 10133.7746 | 68687.7813 | 29955.3597 | 0.068963 | -231307.347 | 231307.347
C | Xist Rating 2093 | -74.07 | 530.518 | 150.28 | 35.6 | 2292.96 | 8923.88 | 18562.9 | 0.68 | 2.55 | 13.548 | 26.782 | 1 | 1 | 1820 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1216456.5533 | 79638.6212 | 3226.0933 | 10189.7623 | 69448.8589 | 28564.6398 | 0.069344 | -220568.5767 | 220568.5767
C | Xist Rating 2094 | -73.97 | 527.853 | 150.28 | 35.6 | 2313.37 | 9221.54 | 18632.1 | 0.67 | 2.56 | 13.579 | 26.997 | 1 | 1 | 1830 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1221119.2946 | 80459.8798 | 3261.6423 | 10245.75 | 70214.1298 | 28782.6369 | 0.069725 | -222251.8928 | 222251.8928
C | Xist Rating 2095 | -73.68 | 531.276 | 150.28 | 35.6 | 2324 | 9418.03 | 18546.2 | 0.66 | 2.55 | 13.599 | 26.758 | 1 | 1 | 1840 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1234685.424 | 81285.3317 | 3297.386 | 10301.7377 | 70983.594 | 28528.403 | 0.070106 | -220288.766 | 220288.766
C | Xist Rating 2096 | -73.44 | 537.065 | 150.28 | 35.6 | 2321.05 | 9410.2 | 18410.4 | 0.65 | 2.52 | 13.592 | 26.389 | 1 | 1 | 1850 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1246554.7183 | 82114.9768 | 3333.3246 | 10357.7254 | 71757.2514 | 28137.5659 | 0.070487 | -217270.8254 | 217270.8254
C | Xist Rating 2097 | -73.23 | 543.537 | 150.28 | 35.6 | 2312.87 | 9321.6 | 18259.9 | 0.64 | 2.5 | 13.568 | 25.98 | 1 | 1 | 1860 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1257130.4212 | 82948.8152 | 3369.4579 | 10413.7131 | 72535.1021 | 27704.1674 | 0.070868 | -213924.2372 | 213924.2372
C | Xist Rating 2098 | -72.53 | 558.757 | 150.28 | 35.6 | 2309.74 | 9387.35 | 17880.7 | 0.64 | 2.43 | 13.623 | 24.9 | 1 | 1 | 1870 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1290583.3932 | 83786.8469 | 3405.7861 | 10469.7008 | 73317.1461 | 26589.432 | 0.071249 | -205316.5459 | 205316.5459
C | Xist Rating 2099 | -72.3 | 565.214 | 150.28 | 35.6 | 2303.37 | 9327.17 | 17739.8 | 0.63 | 2.41 | 13.604 | 24.532 | 1 | 1 | 1880 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1301896.9712 | 84629.0718 | 3442.309 | 10525.6885 | 74103.3833 | 26198.6839 | 0.07163 | -202299.2923 | 202299.2923
C | Xist Rating 2100 | -72.06 | 569.473 | 150.28 | 35.6 | 2307.56 | 9426.38 | 17647.5 | 0.63 | 2.39 | 13.612 | 24.295 | 1 | 1 | 1890 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1314093.1159 | 85475.4901 | 3479.0267 | 10581.6762 | 74893.8138 | 25956.8284 | 0.072011 | -200431.7487 | 200431.7487
C | Xist Rating 2101 | -71.88 | 574.19 | 150.28 | 35.6 | 2304 | 9397.07 | 17556 | 0.61 | 2.38 | 13.602 | 24.076 | 1 | 1 | 1900 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1322933.76 | 86326.1015 | 3515.9392 | 10637.6639 | 75688.4376 | 25709.5359 | 0.072392 | -198522.2214 | 198522.2214
C | Xist Rating 2102 | -71.67 | 578.628 | 150.28 | 35.6 | 2303.92 | 9425.76 | 17465.9 | 0.6 | 2.36 | 13.61 | 23.852 | 1 | 1 | 1910 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1333112.6218 | 87180.9063 | 3553.0464 | 10693.6517 | 76487.2546 | 25469.397 | 0.072773 | -196667.9328 | 196667.9328
C | Xist Rating 2103 | -70.9 | 597.131 | 150.28 | 35.6 | 2294.54 | 9410.51 | 17051.2 | 0.6 | 2.29 | 13.65 | 22.738 | 1 | 1 | 1920 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1370140.9647 | 88039.9043 | 3590.3485 | 10749.6394 | 77290.2649 | 24318.2357 | 0.073154 | -187778.9701 | 187778.9701
C | Xist Rating 2104 | -70.62 | 603.665 | 150.28 | 35.6 | 2292.3 | 9417.44 | 16924.4 | 0.59 | 2.27 | 13.649 | 22.43 | 1 | 1 | 1930 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1383781.2795 | 88903.0955 | 3627.8454 | 10805.6271 | 78097.4685 | 23990.1895 | 0.073535 | -185245.8839 | 185245.8839
C | Xist Rating 2105 | -70.44 | 605.748 | 150.28 | 35.6 | 2299.7 | 9558.73 | 16883.1 | 0.59 | 2.26 | 13.682 | 22.334 | 1 | 1 | 1940 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1393038.6756 | 89770.48 | 3665.537 | 10861.6148 | 78908.8653 | 23895.7964 | 0.073916 | -184517.0058 | 184517.0058
C | Xist Rating 2106 | -70.24 | 612.108 | 150.28 | 35.6 | 2291.52 | 9458.83 | 16773 | 0.57 | 2.24 | 13.67 | 22.084 | 1 | 1 | 1950 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1402657.7242 | 90642.0578 | 3703.4235 | 10917.6025 | 79724.4554 | 23615.274 | 0.074297 | -182350.8861 | 182350.8861
C | Xist Rating 2107 | -69.94 | 619.204 | 150.28 | 35.6 | 2289.7 | 9477.77 | 16637.9 | 0.57 | 2.22 | 13.681 | 21.756 | 1 | 1 | 1960 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1417791.3988 | 91517.8289 | 3741.5047 | 10973.5902 | 80544.2387 | 23278.6901 | 0.074678 | -179751.8743 | 179751.8743
C | Xist Rating 2108 | -69.23 | 635.952 | 150.281 | 35.6 | 2282.47 | 9480.69 | 16304 | 0.57 | 2.16 | 13.728 | 20.917 | 1 | 1 | 1970 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1451541.3614 | 92397.7932 | 3779.7807 | 11029.5779 | 81368.2153 | 22413.2511 | 0.075059 | -173069.1838 | 173069.1838
C | Xist Rating 2109 | -69 | 641.053 | 150.281 | 35.6 | 2282.91 | 9523.33 | 16214.9 | 0.56 | 2.15 | 13.727 | 20.714 | 1 | 1 | 1980 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1463466.3042 | 93281.9508 | 3818.2515 | 11085.5656 | 82196.3852 | 22193.7097 | 0.07544 | -171373.9436 | 171373.9436
C | Xist Rating 2110 | -68.74 | 647.782 | 150.281 | 35.6 | 2278.71 | 9495.25 | 16102.1 | 0.55 | 2.13 | 13.722 | 20.461 | 1 | 1 | 1990 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1476107.3212 | 94170.3017 | 3856.9171 | 11141.5533 | 83028.7484 | 21921.9254 | 0.075821 | -169275.2972 | 169275.2972
C | Xist Rating 2111 | -68.5 | 653.008 | 150.281 | 35.6 | 2278.62 | 9528.64 | 16015.5 | 0.54 | 2.12 | 13.721 | 20.27 | 1 | 1 | 2000 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1487957.089 | 95062.8458 | 3895.7775 | 11197.541 | 83865.3048 | 21714.6051 | 0.076202 | -167674.4246 | 167674.4246
C | Xist Rating 2112 | -68.32 | 656.904 | 150.281 | 35.6 | 2278.63 | 9553.84 | 15954.5 | 0.53 | 2.11 | 13.721 | 20.141 | 1 | 1 | 2010 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1496841.1615 | 95959.5832 | 3934.8326 | 11253.5287 | 84706.0545 | 21571.5977 | 0.076583 | -166570.1596 | 166570.1596
C | Xist Rating 2113 | -67.58 | 675.855 | 150.281 | 35.6 | 2268.2 | 9512.74 | 15615.3 | 0.53 | 2.05 | 13.758 | 19.339 | 1 | 1 | 2020 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1532974.311 | 96860.5138 | 3974.0826 | 11309.5164 | 85550.9974 | 20743.7573 | 0.076964 | -160177.7953 | 160177.7953
C | Xist Rating 2114 | -67.28 | 682.895 | 150.281 | 35.6 | 2266.59 | 9533.78 | 15500.3 | 0.53 | 2.03 | 13.755 | 19.084 | 1 | 1 | 2030 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1547842.9781 | 97765.6377 | 4013.5273 | 11365.5041 | 86400.1336 | 20482.064 | 0.077345 | -158157.0692 | 158157.0692
C | Xist Rating 2115 | -67.11 | 687.811 | 150.28 | 35.6 | 2263.2 | 9503.75 | 15431.9 | 0.52 | 2.02 | 13.734 | 18.95 | 1 | 1 | 2040 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1556653.8552 | 98674.9549 | 4053.1669 | 11421.4918 | 87253.4631 | 20332.5966 | 0.077726 | -157002.9212 | 157002.9212
C | Xist Rating 2116 | -66.9 | 691.913 | 150.28 | 35.6 | 2264.75 | 9560.95 | 15364.5 | 0.52 | 2.01 | 13.738 | 18.803 | 1 | 1 | 2050 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1567009.9668 | 99588.4654 | 4093.0012 | 11477.4795 | 88110.9858 | 20183.3297 | 0.078107 | -155850.3218 | 155850.3218
C | Xist Rating 2117 | -66.67 | 699.036 | 150.28 | 35.6 | 2258.93 | 9502.11 | 15264.5 | 0.51 | 1.99 | 13.729 | 18.601 | 1 | 1 | 2060 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1579073.3915 | 100506.1691 | 4133.0303 | 11533.4672 | 88972.7019 | 19963.6458 | 0.078488 | -154153.9813 | 154153.9813
C | Xist Rating 2118 | -65.86 | 719.42 | 150.281 | 35.6 | 2248.73 | 9470.38 | 14936.4 | 0.51 | 1.94 | 13.767 | 17.868 | 1 | 1 | 2070 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1617781.3366 | 101428.0661 | 4173.2542 | 11589.4549 | 89838.6111 | 19207.3632 | 0.078869 | -148314.1675 | 148314.1675
C | Xist Rating 2119 | -65.69 | 724.138 | 150.281 | 35.6 | 2246.79 | 9465.2 | 14873.7 | 0.5 | 1.93 | 13.762 | 17.747 | 1 | 1 | 2080 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1626986.017 | 102354.1563 | 4213.6729 | 11645.4426 | 90708.7137 | 19071.7833 | 0.07925 | -147267.2556 | 147267.2556
C | Xist Rating 2120 | -65.45 | 730.128 | 150.281 | 35.6 | 2244.8 | 9468.59 | 14791 | 0.5 | 1.91 | 13.759 | 17.583 | 1 | 1 | 2090 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1638991.3344 | 103284.4398 | 4254.2864 | 11701.4303 | 91583.0095 | 18904.4135 | 0.079631 | -145974.8698 | 145974.8698
C | Xist Rating 2121 | -65.22 | 736.125 | 150.281 | 35.6 | 2242.19 | 9460.8 | 14709.4 | 0.49 | 1.9 | 13.758 | 17.421 | 1 | 1 | 2100 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1650532.1138 | 104218.9166 | 4295.0947 | 11757.418 | 92461.4985 | 18726.2627 | 0.080012 | -144599.2369 | 144599.2369
C | Xist Rating 2122 | -65.02 | 741.445 | 150.281 | 35.6 | 2240.13 | 9457.69 | 14638.8 | 0.48 | 1.89 | 13.755 | 17.284 | 1 | 1 | 2110 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1660933.1879 | 105157.5866 | 4336.0977 | 11813.4058 | 93344.1809 | 18573.8617 | 0.080393 | -143422.437 | 143422.437
C | Xist Rating 2123 | -64.26 | 760.836 | 150.281 | 35.6 | 2231.06 | 9432.21 | 14359.4 | 0.48 | 1.84 | 13.805 | 16.696 | 1 | 1 | 2120 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1697470.7662 | 106100.4499 | 4377.2956 | 11869.3935 | 94231.0565 | 17968.4649 | 0.080774 | -138747.7227 | 138747.7227
C | Xist Rating 2124 | -63.97 | 768.219 | 150.281 | 35.6 | 2227.99 | 9424.94 | 14264 | 0.47 | 1.83 | 13.798 | 16.512 | 1 | 1 | 2130 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1711584.2498 | 107047.5065 | 4418.6882 | 11925.3812 | 95122.1253 | 17766.8568 | 0.081155 | -137190.9584 | 137190.9584
C | Xist Rating 2125 | -63.74 | 775.628 | 150.281 | 35.6 | 2222.4 | 9372.51 | 14170.1 | 0.47 | 1.81 | 13.795 | 16.332 | 1 | 1 | 2140 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1723755.6672 | 107998.7563 | 4460.2756 | 11981.3689 | 96017.3875 | 17582.6987 | 0.081536 | -135768.9386 | 135768.9386
C | Xist Rating 2126 | -63.58 | 779.674 | 150.281 | 35.6 | 2221.31 | 9376.56 | 14123.7 | 0.46 | 1.8 | 13.791 | 16.251 | 1 | 1 | 2150 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1731897.6529 | 108954.1994 | 4502.0578 | 12037.3566 | 96916.8428 | 17488.0146 | 0.081917 | -135037.8133 | 135037.8133
C | Xist Rating 2127 | -63.4 | 784.939 | 150.281 | 35.6 | 2218.75 | 9363.81 | 14059.1 | 0.46 | 1.79 | 13.782 | 16.132 | 1 | 1 | 2160 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1741583.4062 | 109913.8358 | 4544.0348 | 12093.3443 | 97820.4915 | 17366.8761 | 0.082298 | -134102.4136 | 134102.4136
C | Xist Rating 2128 | -62.62 | 805.975 | 150.281 | 35.6 | 2207.7 | 9308.46 | 13786 | 0.46 | 1.75 | 13.818 | 15.59 | 1 | 1 | 2170 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1779351.0075 | 110877.6654 | 4586.2066 | 12149.332 | 98728.3334 | 16808.4625 | 0.082679 | -129790.4917 | 129790.4917
C | Xist Rating 2129 | -62.34 | 813.133 | 150.281 | 35.6 | 2205.88 | 9322.01 | 13699.1 | 0.45 | 1.74 | 13.815 | 15.428 | 1 | 1 | 2180 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1793673.822 | 111845.6883 | 4628.5732 | 12205.3197 | 99640.3686 | 16629.4403 | 0.08306 | -128408.1304 | 128408.1304
C | Xist Rating 2130 | -62.12 | 818.632 | 150.281 | 35.6 | 2204.91 | 9336.86 | 13638.9 | 0.45 | 1.73 | 13.813 | 15.324 | 1 | 1 | 2190 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1805009.8831 | 112817.9045 | 4671.1346 | 12261.3074 | 100556.5971 | 16524.1348 | 0.083441 | -127594.9889 | 127594.9889
C | Xist Rating 2131 | -61.92 | 824.538 | 150.281 | 35.6 | 2201.49 | 9307.77 | 13579.4 | 0.44 | 1.72 | 13.805 | 15.227 | 1 | 1 | 2200 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1815212.1616 | 113794.3139 | 4713.8907 | 12317.2951 | 101477.0188 | 16412.218 | 0.083822 | -126730.7968 | 126730.7968
C | Xist Rating 2132 | -61.64 | 831.954 | 150.281 | 35.6 | 2198.79 | 9305.01 | 13495.4 | 0.44 | 1.7 | 13.803 | 15.076 | 1 | 1 | 2210 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1829292.1357 | 114774.9166 | 4756.8417 | 12373.2828 | 102401.6338 | 16258.0403 | 0.084203 | -125540.2775 | 125540.2775
C | Xist Rating 2133 | -60.86 | 852.855 | 150.281 | 35.6 | 2189.35 | 9274.18 | 13246.1 | 0.44 | 1.66 | 13.841 | 14.604 | 1 | 1 | 2220 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1867198.0942 | 115759.7125 | 4799.9874 | 12429.2705 | 103330.442 | 15772.2552 | 0.084584 | -121789.1738 | 121789.1738
C | Xist Rating 2134 | -60.62 | 858.816 | 150.281 | 35.6 | 2188.64 | 9297.54 | 13182.5 | 0.43 | 1.65 | 13.838 | 14.495 | 1 | 1 | 2230 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1879639.0502 | 116748.7018 | 4843.3279 | 12485.2582 | 104263.4435 | 15647.8244 | 0.084965 | -120828.3525 | 120828.3525
C | Xist Rating 2135 | -60.37 | 865.908 | 150.281 | 35.6 | 2185.25 | 9277.1 | 13111.8 | 0.43 | 1.64 | 13.838 | 14.377 | 1 | 1 | 2240 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1892225.457 | 117741.8842 | 4886.8633 | 12541.2459 | 105200.6383 | 15527.9488 | 0.085346 | -119902.705 | 119902.705
C | Xist Rating 2136 | -60.1 | 873.632 | 150.281 | 35.6 | 2181.33 | 9251.34 | 13034.1 | 0.42 | 1.63 | 13.837 | 14.247 | 1 | 1 | 2250 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 11 | E | Rod | 1905679.6906 | 118739.26 | 4930.5934 | 12597.2336 | 106142.0264 | 15381.6125 | 0.085727 | -118772.7347 | 118772.7347
C | Xist Rating 2137 | -59.95 | 877.64 | 150.281 | 35.6 | 2180.86 | 9265.18 | 12995.7 | 0.42 | 1.62 | 13.829 | 14.187 | 1 | 1 | 2260 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 1914009.9704 | 119740.829 | 4974.5182 | 12653.2213 | 107087.6077 | 15321.5672 | 0.086108 | -118309.081 | 118309.081
C | Xist Rating 2138 | -59.13 | 900.282 | 150.281 | 35.6 | 2170.49 | 9222.67 | 12751.9 | 0.41 | 1.59 | 13.868 | 13.75 | 1 | 1 | 2270 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 1954053.0782 | 120746.5913 | 5018.6379 | 12709.209 | 108037.3823 | 14857.9027 | 0.086489 | -114728.786 | 114728.786
C | Xist Rating 2139 | -58.9 | 907.32 | 150.281 | 35.6 | 2166.67 | 9193.49 | 12686.2 | 0.41 | 1.58 | 13.86 | 13.646 | 1 | 1 | 2280 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 1965863.0244 | 121756.5468 | 5062.9524 | 12765.1967 | 108991.3501 | 14752.1123 | 0.08687 | -113911.9008 | 113911.9008
C | Xist Rating 2140 | -58.61 | 915.469 | 150.281 | 35.6 | 2163.65 | 9187.05 | 12607 | 0.41 | 1.56 | 13.856 | 13.515 | 1 | 1 | 2290 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 1980754.5019 | 122770.6957 | 5107.4617 | 12821.1844 | 109949.5112 | 14618.4479 | 0.087251 | -112879.7795 | 112879.7795
C | Xist Rating 2141 | -58.42 | 921.131 | 150.281 | 35.6 | 2161.23 | 9174.1 | 12557.1 | 0.4 | 1.56 | 13.852 | 13.439 | 1 | 1 | 2300 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 1990775.9511 | 123789.0377 | 5152.1657 | 12877.1721 | 110911.8656 | 14527.6184 | 0.087632 | -112178.4186 | 112178.4186
| Xist Rating 2142 | -58.23 | 927.06 | 150.281 | 35.6 | 2157.95 | 9145.44 | 12507.7 | 0.4 | 1.55 | 13.849 | 13.367 | 1 | 1 | 2310 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2000549.127 | 124811.5731 | 5197.0645 | 12933.1599 | 111878.4132 | 14455.2059 | 0.088013 | -111619.2685 | 111619.2685
| Xist Rating 2143 | -57.39 | 950.218 | 150.281 | 35.6 | 2148.7 | 9122.97 | 12277.2 | 0.4 | 1.51 | 13.887 | 12.971 | 1 | 1 | 2320 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2041733.4166 | 125838.3017 | 5242.1582 | 12989.1476 | 112849.1541 | 14048.0244 | 0.088394 | -108475.1203 | 108475.1203
| Xist Rating 2144 | -57.15 | 957.287 | 150.281 | 35.6 | 2145.61 | 9105.83 | 12216.9 | 0.39 | 1.5 | 13.882 | 12.88 | 1 | 1 | 2330 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2053964.5601 | 126869.2236 | 5287.4466 | 13045.1353 | 113824.0883 | 13941.3035 | 0.088775 | -107651.05 | 107651.05
| Xist Rating 2145 | -56.92 | 964.333 | 150.281 | 35.6 | 2142.67 | 9091.02 | 12157.3 | 0.39 | 1.49 | 13.877 | 12.79 | 1 | 1 | 2340 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2066247.3891 | 127904.3387 | 5332.9298 | 13101.123 | 114803.2157 | 13850.0609 | 0.089156 | -106946.4989 | 106946.4989
| Xist Rating 2146 | -56.71 | 970.793 | 150.281 | 35.6 | 2139.77 | 9072.68 | 12104.8 | 0.38 | 1.49 | 13.872 | 12.713 | 1 | 1 | 2350 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2077273.7376 | 128943.6471 | 5378.6078 | 13157.1107 | 115786.5364 | 13757.7045 | 0.089537 | -106233.3477 | 106233.3477
| Xist Rating 2147 | -56.43 | 978.567 | 150.281 | 35.6 | 2137.5 | 9074.1 | 12039.9 | 0.38 | 1.48 | 13.866 | 12.615 | 1 | 1 | 2360 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2091686.9625 | 129987.1488 | 5424.4805 | 13213.0984 | 116774.0504 | 13658.0534 | 0.089918 | -105463.8678 | 105463.8678
| Xist Rating 2148 | -55.69 | 999.897 | 150.281 | 35.6 | 2128.3 | 9035.85 | 11846.8 | 0.38 | 1.45 | 13.904 | 12.301 | 1 | 1 | 2370 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2128080.7851 | 131034.8437 | 5470.5481 | 13269.0861 | 117765.7576 | 13335.8607 | 0.090299 | -102975.9817 | 102975.9817
| Xist Rating 2149 | -55.43 | 1007.18 | 150.281 | 35.6 | 2125.9 | 9030.06 | 11791.2 | 0.37 | 1.44 | 13.896 | 12.222 | 1 | 1 | 2380 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2141163.962 | 132086.7319 | 5516.8105 | 13325.0738 | 118761.6581 | 13241.0387 | 0.09068 | -102243.7914 | 102243.7914
| Xist Rating 2150 | -55.18 | 1014.51 | 150.281 | 35.6 | 2123.89 | 9035.25 | 11730 | 0.37 | 1.43 | 13.89 | 12.13 | 1 | 1 | 2390 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2154707.6439 | 133142.8134 | 5563.2676 | 13381.0615 | 119761.7519 | 13147.5637 | 0.091061 | -101522.0021 | 101522.0021
C | Xist Rating 2151 | -50.79 | 1163.46 | 150.281 | 35.6 | 2034.62 | 8316.31 | 10538.2 | 0.4 | 1.25 | 13.888 | 10.314 | 1 | 1 | 2400 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2367198.9852 | 134203.0881 | 5609.9196 | 13437.0492 | 120766.0389 | 11308.6964 | 0.091442 | -87322.7563 | 87322.7563
C | Xist Rating 2152 | -50.32 | 1164.91 | 150.281 | 35.6 | 2051.88 | 8612.52 | 10538 | 0.39 | 1.25 | 13.884 | 10.324 | 1 | 1 | 2410 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2390255.5308 | 135267.5561 | 5656.7663 | 13493.0369 | 121774.5192 | 11306.4002 | 0.091823 | -87305.025 | 87305.025
C | Xist Rating 2153 | -50.34 | 1166.31 | 150.281 | 35.6 | 2050.07 | 8580.8 | 10538 | 0.39 | 1.25 | 13.924 | 10.334 | 1 | 1 | 2420 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2391017.1417 | 136336.2173 | 5703.8078 | 13549.0246 | 122787.1927 | 11320.9045 | 0.092204 | -87417.0238 | 87417.0238
C | Xist Rating 2154 | -49.88 | 1167.67 | 150.281 | 35.6 | 2066.55 | 8877.08 | 10537.9 | 0.39 | 1.25 | 13.919 | 10.343 | 1 | 1 | 2430 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2413048.4385 | 137409.0719 | 5751.0441 | 13605.0123 | 123804.0596 | 11332.4727 | 0.092585 | -87506.3505 | 87506.3505
C | Xist Rating 2155 | -49.86 | 1169.04 | 150.281 | 35.6 | 2065.96 | 8866.21 | 10537.9 | 0.38 | 1.25 | 13.913 | 10.354 | 1 | 1 | 2440 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2415189.8784 | 138486.1197 | 5798.4752 | 13661 | 124825.1197 | 11330.8566 | 0.092966 | -87493.8712 | 87493.8712
C | Xist Rating 2156 | -49.84 | 1170.37 | 150.281 | 35.6 | 2065.32 | 8854.4 | 10537.9 | 0.38 | 1.25 | 13.908 | 10.365 | 1 | 1 | 2450 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2417188.5684 | 139567.3607 | 5846.1011 | 13716.9877 | 125850.373 | 11344.4413 | 0.093347 | -87598.7685 | 87598.7685
C | Xist Rating 2157 | -49.82 | 1171.84 | 150.281 | 35.6 | 2064.33 | 8836.26 | 10537.9 | 0.37 | 1.25 | 13.904 | 10.376 | 1 | 1 | 2460 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2419064.4672 | 140652.795 | 5893.9217 | 13772.9754 | 126879.8196 | 11342.7344 | 0.093728 | -87585.5884 | 87585.5884
C | Xist Rating 2158 | -49.8 | 1173.19 | 150.281 | 35.6 | 2063.73 | 8825.26 | 10537.9 | 0.36 | 1.25 | 13.941 | 10.387 | 1 | 1 | 2470 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2421147.3987 | 141742.4226 | 5941.9372 | 13828.9631 | 127913.4595 | 11342.5446 | 0.094109 | -87584.1225 | 87584.1225
C | Xist Rating 2159 | -49.78 | 1174.54 | 150.281 | 35.6 | 2062.99 | 8811.84 | 10537.9 | 0.36 | 1.25 | 13.935 | 10.397 | 1 | 1 | 2480 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2423064.2746 | 142836.2435 | 5990.1474 | 13884.9508 | 128951.2926 | 11354.9391 | 0.09449 | -87679.8296 | 87679.8296
C | Xist Rating 2160 | -49.77 | 1175.94 | 150.281 | 35.6 | 2062.13 | 8796.15 | 10537.9 | 0.35 | 1.25 | 13.93 | 10.408 | 1 | 1 | 2490 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2424941.1522 | 143934.2576 | 6038.5525 | 13940.9385 | 129993.3191 | 11352.8626 | 0.094871 | -87663.7955 | 87663.7955
C | Xist Rating 2161 | -49.75 | 1176.92 | 150.281 | 35.6 | 2062.11 | 8795.87 | 10537.9 | 0.35 | 1.25 | 13.925 | 10.417 | 1 | 1 | 2500 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2426938.5012 | 145036.465 | 6087.1523 | 13996.9262 | 131039.5387 | 11364.1984 | 0.095252 | -87751.3275 | 87751.3275
C | Xist Rating 2162 | -49.71 | 1178.77 | 150.281 | 35.6 | 2061.51 | 8784.95 | 10537.8 | 0.34 | 1.25 | 13.92 | 10.429 | 1 | 1 | 2510 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2430046.1427 | 146142.8656 | 6135.9469 | 14052.914 | 132089.9517 | 11362.9867 | 0.095633 | -87741.9715 | 87741.9715
C | Xist Rating 2163 | -49.68 | 1180.22 | 150.281 | 35.6 | 2060.86 | 8773.19 | 10537.8 | 0.34 | 1.25 | 13.957 | 10.44 | 1 | 1 | 2520 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2432268.1892 | 147253.4595 | 6184.9363 | 14108.9017 | 133144.5579 | 11377.9527 | 0.096014 | -87857.5347 | 87857.5347
C | Xist Rating 2164 | -49.66 | 1181.56 | 150.281 | 35.6 | 2060.49 | 8766.52 | 10537.7 | 0.33 | 1.25 | 13.951 | 10.45 | 1 | 1 | 2530 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2434592.5644 | 148368.2467 | 6234.1205 | 14164.8894 | 134203.3574 | 11374.4121 | 0.096395 | -87830.1952 | 87830.1952
C | Xist Rating 2165 | -49.64 | 1182.71 | 150.281 | 35.6 | 2060.4 | 8764.85 | 10537.8 | 0.33 | 1.25 | 13.958 | 10.46 | 1 | 1 | 2540 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2436855.684 | 149487.2272 | 6283.4995 | 14220.8771 | 135266.3501 | 11387.1237 | 0.096776 | -87928.3511 | 87928.3511
C | Xist Rating 2166 | -49.62 | 1184.26 | 150.281 | 35.6 | 2059.33 | 8745.55 | 10537.7 | 0.32 | 1.25 | 13.953 | 10.471 | 1 | 1 | 2550 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2438782.1458 | 150610.4009 | 6333.0732 | 14276.8648 | 136333.5361 | 11384.4746 | 0.097157 | -87907.8954 | 87907.8954
C | Xist Rating 2167 | -49.6 | 1185.71 | 150.281 | 35.6 | 2058.65 | 8733.38 | 10537.7 | 0.32 | 1.25 | 13.95 | 10.482 | 1 | 1 | 2560 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2440961.8915 | 151737.7678 | 6382.8418 | 14332.8525 | 137404.9154 | 11397.7894 | 0.097538 | -88010.7082 | 88010.7082
C | Xist Rating 2168 | -49.58 | 1187.1 | 150.281 | 35.6 | 2057.97 | 8721.08 | 10537.7 | 0.31 | 1.25 | 13.947 | 10.492 | 1 | 1 | 2570 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2443016.187 | 152869.3281 | 6432.8051 | 14388.8402 | 138480.4879 | 11393.9979 | 0.097919 | -87981.4313 | 87981.4313
C | Xist Rating 2169 | -49.55 | 1188.46 | 150.281 | 35.6 | 2058.07 | 8722.85 | 10537.7 | 0.31 | 1.25 | 13.982 | 10.502 | 1 | 1 | 2580 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2445933.8722 | 154005.0816 | 6482.9633 | 14444.8279 | 139560.2537 | 11407.5757 | 0.0983 | -88086.2754 | 88086.2754
C | Xist Rating 2170 | -49.53 | 1189.82 | 150.281 | 35.6 | 2057.2 | 8707.24 | 10537.8 | 0.3 | 1.25 | 13.982 | 10.512 | 1 | 1 | 2590 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2447697.704 | 155145.0284 | 6533.3162 | 14500.8156 | 140644.2128 | 11403.671 | 0.098681 | -88056.1247 | 88056.1247
C | Xist Rating 2171 | -49.52 | 1191 | 150.281 | 35.6 | 2056.55 | 8695.57 | 10537.8 | 0.3 | 1.25 | 13.976 | 10.521 | 1 | 1 | 2600 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2449351.05 | 156289.1684 | 6583.8639 | 14556.8033 | 141732.3651 | 11414.6879 | 0.099062 | -88141.1945 | 88141.1945
C | Xist Rating 2172 | -49.5 | 1192.69 | 150.281 | 35.6 | 2055.08 | 8669.43 | 10537.8 | 0.3 | 1.25 | 13.973 | 10.533 | 1 | 1 | 2610 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2451073.3652 | 157437.5017 | 6634.6064 | 14612.791 | 142824.7107 | 11428.924 | 0.099443 | -88251.1218 | 88251.1218
C | Xist Rating 2173 | -49.48 | 1194.09 | 150.281 | 35.6 | 2054.55 | 8659.89 | 10537.8 | 0.29 | 1.25 | 13.97 | 10.543 | 1 | 1 | 2620 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2453317.6095 | 158590.0283 | 6685.5437 | 14668.7787 | 143921.2496 | 11424.6759 | 0.099824 | -88218.3187 | 88218.3187
C | Xist Rating 2174 | -49.46 | 1195.51 | 150.281 | 35.6 | 2053.85 | 8647.52 | 10537.8 | 0.29 | 1.25 | 14.006 | 10.553 | 1 | 1 | 2630 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2455398.2135 | 159746.7481 | 6736.6758 | 14724.7664 | 145021.9817 | 11438.1076 | 0.10021 | -88322.0349 | 88322.0349
C | Xist Rating 2175 | -49.43 | 1196.76 | 150.281 | 35.6 | 2053.99 | 8650.03 | 10537.7 | 0.28 | 1.25 | 14 | 10.563 | 1 | 1 | 2640 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2458133.0724 | 160907.6612 | 6788.0027 | 14780.7541 | 146126.9071 | 11433.5401 | 0.10059 | -88286.7662 | 88286.7662
C | Xist Rating 2176 | -49.4 | 1198.26 | 150.281 | 35.6 | 2053.47 | 8640.85 | 10537.7 | 0.28 | 1.25 | 13.998 | 10.573 | 1 | 1 | 2650 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2460590.9622 | 162072.7675 | 6839.5243 | 14836.7418 | 147236.0257 | 11445.6157 | 0.10097 | -88380.0108 | 88380.0108
C | Xist Rating 2177 | -49.38 | 1199.6 | 150.281 | 35.6 | 2053.04 | 8633.19 | 10537.7 | 0.28 | 1.25 | 13.995 | 10.583 | 1 | 1 | 2660 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2462826.784 | 163242.0672 | 6891.2408 | 14892.7295 | 148349.3376 | 11457.6574 | 0.10135 | -88472.9936 | 88472.9936
C | Xist Rating 2178 | -49.36 | 1200.99 | 150.281 | 35.6 | 2052.07 | 8616.24 | 10537.7 | 0.27 | 1.25 | 13.989 | 10.593 | 1 | 1 | 2670 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2464515.5493 | 164415.5601 | 6943.152 | 14948.7172 | 149466.8428 | 11452.8556 | 0.10173 | -88435.9148 | 88435.9148
C | Xist Rating 2179 | -49.32 | 1202.41 | 150.281 | 35.6 | 2052.09 | 8616.53 | 10537.7 | 0.27 | 1.25 | 14.028 | 10.603 | 1 | 1 | 2680 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2467453.5369 | 165593.2462 | 6995.258 | 15004.7049 | 150588.5413 | 11466.1986 | 0.10211 | -88538.9459 | 88538.9459
C | Xist Rating 2180 | -49.29 | 1203.78 | 150.281 | 35.6 | 2052.14 | 8617.44 | 10537.6 | 0.27 | 1.25 | 14.02 | 10.613 | 1 | 1 | 2690 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2470325.0892 | 166775.1256 | 7047.5588 | 15060.6926 | 151714.433 | 11478.0208 | 0.10249 | -88630.2345 | 88630.2345
C | Xist Rating 2181 | -49.25 | 1204.98 | 150.281 | 35.6 | 2052.52 | 8624.09 | 10537.7 | 0.26 | 1.25 | 14.017 | 10.622 | 1 | 1 | 2700 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2473245.5496 | 167961.1983 | 7100.0544 | 15116.6803 | 152844.518 | 11472.0018 | 0.10287 | -88583.757 | 88583.757
C | Xist Rating 2182 | -49.22 | 1206.64 | 150.281 | 35.6 | 2051.67 | 8609.08 | 10537.7 | 0.26 | 1.25 | 14.016 | 10.633 | 1 | 1 | 2710 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2475627.0888 | 169151.4643 | 7152.7448 | 15172.668 | 153978.7962 | 11485.0273 | 0.10325 | -88684.3365 | 88684.3365
C | Xist Rating 2183 | -49.21 | 1207.98 | 150.281 | 35.6 | 2050.77 | 8593.19 | 10537.7 | 0.26 | 1.25 | 14.011 | 10.643 | 1 | 1 | 2720 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2477289.1446 | 170345.9235 | 7205.63 | 15228.6558 | 155117.2677 | 11496.8873 | 0.10363 | -88775.916 | 88775.916
C | Xist Rating 2184 | -49.18 | 1209.31 | 150.281 | 35.6 | 2050.57 | 8589.8 | 10537.7 | 0.25 | 1.25 | 14.052 | 10.652 | 1 | 1 | 2730 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2479774.8067 | 171544.576 | 7258.71 | 15284.6435 | 156259.9325 | 11491.9755 | 0.10402 | -88737.9887 | 88737.9887
C | Xist Rating 2185 | -49.16 | 1210.59 | 150.281 | 35.6 | 2050.04 | 8580.41 | 10537.7 | 0.25 | 1.25 | 14.045 | 10.661 | 1 | 1 | 2740 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2481757.9236 | 172747.4217 | 7311.9847 | 15340.6312 | 157406.7906 | 11502.6818 | 0.1044 | -88820.6595 | 88820.6595
C | Xist Rating 2186 | -49.12 | 1212.14 | 150.281 | 35.6 | 2050.14 | 8582.19 | 10537.8 | 0.25 | 1.25 | 14.044 | 10.672 | 1 | 1 | 2750 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2485056.6996 | 173954.4607 | 7365.4543 | 15396.6189 | 158557.8419 | 11515.6483 | 0.10478 | -88920.7839 | 88920.7839
C | Xist Rating 2187 | -49.02 | 1213.56 | 150.281 | 35.6 | 2052.38 | 8621.52 | 10537.9 | 0.24 | 1.25 | 14.05 | 10.682 | 1 | 1 | 2760 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2490686.2728 | 175165.693 | 7419.1186 | 15452.6066 | 159713.0864 | 11510.4106 | 0.10516 | -88880.3394 | 88880.3394
C | Xist Rating 2188 | -48.93 | 1214.8 | 150.281 | 35.6 | 2054.74 | 8663.26 | 10537.9 | 0.24 | 1.25 | 14.054 | 10.691 | 1 | 1 | 2770 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2496098.152 | 176381.1186 | 7472.9777 | 15508.5943 | 160872.5243 | 11521.3877 | 0.10554 | -88965.1022 | 88965.1022
C | Xist Rating 2189 | -48.7 | 1216.34 | 150.282 | 35.6 | 2062.3 | 8799.03 | 10538.1 | 0.24 | 1.25 | 14.116 | 10.702 | 1 | 1 | 2780 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2508457.982 | 177600.7374 | 7527.0316 | 15564.582 | 162036.1554 | 11536.1774 | 0.10592 | -89079.3038 | 89079.3038
C | Xist Rating 2190 | -48.92 | 1217.75 | 150.281 | 35.6 | 2052.23 | 8618.89 | 10537.9 | 0.23 | 1.25 | 14.082 | 10.711 | 1 | 1 | 2790 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2499103.0825 | 178824.5494 | 7581.2803 | 15620.5697 | 163203.9798 | 11528.4109 | 0.1063 | -89019.3331 | 89019.3331
C | Xist Rating 2191 | -48.43 | 1218.73 | 150.281 | 35.6 | 2071.27 | 8964.71 | 10538.2 | 0.23 | 1.25 | 14.139 | 10.72 | 1 | 1 | 2800 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2524318.8871 | 180052.5548 | 7635.7238 | 15676.5574 | 164375.9974 | 11540.8546 | 0.10668 | -89115.4202 | 89115.4202
C | Xist Rating 2192 | -48.19 | 1220.47 | 150.281 | 35.6 | 2079.04 | 9111.91 | 10538.3 | 0.22 | 1.25 | 14.176 | 10.732 | 1 | 1 | 2810 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2537405.9488 | 181284.7534 | 7690.3621 | 15732.5451 | 165552.2083 | 11537.9905 | 0.10706 | -89093.3041 | 89093.3041
C | Xist Rating 2193 | -48.02 | 1221.95 | 150.281 | 35.6 | 2084.36 | 9215.14 | 10538.3 | 0.22 | 1.25 | 14.203 | 10.742 | 1 | 1 | 2820 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2546983.702 | 182521.1453 | 7745.1952 | 15788.5328 | 166732.6125 | 11550.5243 | 0.10744 | -89190.0867 | 89190.0867
C | Xist Rating 2194 | -47.88 | 1223.32 | 150.282 | 35.6 | 2088.56 | 9297.79 | 10538.3 | 0.22 | 1.25 | 14.263 | 10.752 | 1 | 1 | 2830 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2554977.2192 | 183761.7304 | 7800.223 | 15844.5205 | 167917.2099 | 11563.9843 | 0.10783 | -89294.0218 | 89294.0218
C | Xist Rating 2195 | -47.78 | 1224.64 | 150.282 | 35.6 | 2091.11 | 9348.51 | 10538.3 | 0.22 | 1.25 | 14.273 | 10.761 | 1 | 1 | 2840 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2560856.9504 | 185006.5088 | 7855.4457 | 15900.5082 | 169106.0006 | 11575.0174 | 0.10821 | -89379.2163 | 89379.2163
C | Xist Rating 2196 | -47.68 | 1226.08 | 150.282 | 35.6 | 2093.79 | 9402.22 | 10538.3 | 0.21 | 1.25 | 14.283 | 10.771 | 1 | 1 | 2850 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2567154.0432 | 186255.4805 | 7910.8631 | 15956.4959 | 170298.9845 | 11568.8444 | 0.10859 | -89331.55 | 89331.55
C | Xist Rating 2197 | -47.61 | 1227.48 | 150.282 | 35.6 | 2095.12 | 9429.15 | 10538.2 | 0.21 | 1.25 | 14.286 | 10.78 | 1 | 1 | 2860 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2571717.8976 | 187508.6454 | 7966.4753 | 16012.4836 | 171496.1618 | 11579.6161 | 0.10897 | -89414.7265 | 89414.7265
C | Xist Rating 2198 | -47.52 | 1228.68 | 150.282 | 35.6 | 2097.49 | 9477.28 | 10538.2 | 0.21 | 1.25 | 14.289 | 10.789 | 1 | 1 | 2870 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2577144.0132 | 188766.0036 | 8022.2824 | 16068.4713 | 172697.5323 | 11590.3884 | 0.10935 | -89497.9073 | 89497.9073
C | Xist Rating 2199 | -47.43 | 1230.18 | 150.282 | 35.6 | 2099.28 | 9514.06 | 10538.2 | 0.2 | 1.25 | 14.333 | 10.799 | 1 | 1 | 2880 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2582492.2704 | 190027.555 | 8078.2842 | 16124.459 | 173903.096 | 11584.8081 | 0.10973 | -89454.8176 | 89454.8176
C | Xist Rating 2200 | -47.37 | 1231.53 | 150.282 | 35.6 | 2100.41 | 9537.41 | 10538.2 | 0.2 | 1.25 | 14.331 | 10.808 | 1 | 1 | 2890 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2586717.9273 | 191293.2998 | 8134.4807 | 16180.4467 | 175112.853 | 11595.3877 | 0.11011 | -89536.5105 | 89536.5105
C | Xist Rating 2201 | -47.3 | 1232.91 | 150.282 | 35.5 | 2101.76 | 9565.29 | 10538.2 | 0.2 | 1.25 | 14.332 | 10.817 | 1 | 1 | 2900 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2591280.9216 | 192563.2378 | 8190.8721 | 16236.4344 | 176326.8033 | 11606.045 | 0.11049 | -89618.803 | 89618.803
C | Xist Rating 2202 | -47.22 | 1234.45 | 150.282 | 35.5 | 2103.07 | 9592.35 | 10538.2 | 0.2 | 1.25 | 14.334 | 10.827 | 1 | 1 | 2910 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2596134.7615 | 193837.369 | 8247.4583 | 16292.4221 | 177544.9469 | 11617.767 | 0.11087 | -89709.3173 | 89709.3173
C | Xist Rating 2203 | -47.12 | 1235.84 | 150.282 | 35.5 | 2105.55 | 9644.25 | 10538.1 | 0.2 | 1.25 | 14.336 | 10.837 | 1 | 1 | 2920 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2602122.912 | 195115.6935 | 8304.2393 | 16348.4099 | 178767.2837 | 11629.4894 | 0.11125 | -89799.8343 | 89799.8343
C | Xist Rating 2204 | -46.96 | 1237.23 | 150.282 | 35.5 | 2111.07 | 9761.31 | 10537.9 | 0.19 | 1.25 | 14.387 | 10.846 | 1 | 1 | 2930 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2611879.1361 | 196398.2113 | 8361.215 | 16404.3976 | 179993.8138 | 11622.5654 | 0.11164 | -89746.3689 | 89746.3689
C | Xist Rating 2205 | -46.93 | 1238.6 | 150.282 | 35.5 | 2110.6 | 9751.44 | 10537.9 | 0.19 | 1.25 | 14.38 | 10.855 | 1 | 1 | 2940 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2614189.16 | 197684.9224 | 8418.3855 | 16460.3853 | 181224.5371 | 11632.9619 | 0.11202 | -89826.648 | 89826.648
C | Xist Rating 2206 | -46.91 | 1240.01 | 150.282 | 35.5 | 2109.9 | 9736.51 | 10537.9 | 0.19 | 1.25 | 14.376 | 10.865 | 1 | 1 | 2950 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2616297.099 | 198975.8267 | 8475.7509 | 16516.373 | 182459.4537 | 11644.4711 | 0.1124 | -89915.5189 | 89915.5189
C | Xist Rating 2207 | -46.9 | 1241.38 | 150.282 | 35.5 | 2109.19 | 9721.42 | 10537.9 | 0.19 | 1.25 | 14.372 | 10.874 | 1 | 1 | 2960 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2618306.2822 | 200270.9243 | 8533.311 | 16572.3607 | 183698.5636 | 11654.9411 | 0.11278 | -89996.3655 | 89996.3655
C | Xist Rating 2208 | -46.88 | 1242.76 | 150.282 | 35.5 | 2108.5 | 9706.72 | 10537.9 | 0.18 | 1.25 | 14.37 | 10.883 | 1 | 1 | 2970 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2620359.46 | 201570.2151 | 8591.0659 | 16628.3484 | 184941.8668 | 11646.3303 | 0.11316 | -89929.8755 | 89929.8755
C | Xist Rating 2209 | -46.86 | 1243.98 | 150.282 | 35.5 | 2107.84 | 9692.68 | 10537.9 | 0.18 | 1.25 | 14.406 | 10.891 | 1 | 1 | 2980 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2622110.8032 | 202873.6992 | 8649.0156 | 16684.3361 | 186189.3632 | 11656.6633 | 0.11354 | -90009.6643 | 90009.6643
C | Xist Rating 2210 | -46.85 | 1245.54 | 150.282 | 35.5 | 2106.69 | 9668.54 | 10537.9 | 0.18 | 1.25 | 14.405 | 10.901 | 1 | 1 | 2990 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2623966.6626 | 204181.3766 | 8707.16 | 16740.3238 | 187441.0528 | 11668.1865 | 0.11392 | -90098.6433 | 90098.6433
C | Xist Rating 2211 | -46.84 | 1246.97 | 150.282 | 35.5 | 2105.98 | 9653.85 | 10537.5 | 0.18 | 1.25 | 14.402 | 10.91 | 1 | 1 | 3000 | 152.4 | 2 | 2 | 19.05 | 1.3333 | 10 | E | Rod | 2626093.8806 | 205493.2473 | 8765.4993 | 16796.3115 | 188696.9358 | 11678.6226 | 0.1143 | -90179.2284 | 90179.2284
C | Xist Rating 2212 | -93.76 | 115.439 | 150.284 | 35.8 | 2406.37 | 7468.66 | 58746.2 | 2.44 | 10.95 | 15.02 | 368.889 | 1 | 1 | 1000 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 277788.9464 | 27893.3515 | 973.9444 | 5878.709 | 22014.6425 | 384733.4129 | 0.038101 | -2970809.4327 | 2970809.4327
C | Xist Rating 2213 | -93.7 | 116.668 | 150.284 | 35.8 | 2403.51 | 7449.78 | 58284.5 | 2.42 | 10.85 | 15.037 | 362.007 | 1 | 1 | 1010 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 280412.7047 | 28394.6329 | 993.5206 | 5937.4961 | 22457.1368 | 377591.157 | 0.038482 | -2915658.8261 | 2915658.8261
C | Xist Rating 2214 | -93.23 | 125.813 | 150.284 | 35.8 | 2397.91 | 7461.97 | 54967.8 | 2.43 | 10.07 | 15.09 | 313.709 | 1 | 1 | 1020 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 301688.2508 | 28900.3173 | 1013.2917 | 5996.2832 | 22904.0341 | 327462.8354 | 0.038863 | -2528581.2139 | 2528581.2139
C | Xist Rating 2215 | -93.15 | 128.416 | 150.283 | 35.8 | 2378.21 | 7290.64 | 54179 | 2.35 | 9.89 | 14.823 | 303.325 | 1 | 1 | 1030 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 305400.2154 | 29410.4045 | 1033.2576 | 6055.0703 | 23355.3342 | 316610.7997 | 0.039244 | -2444784.6713 | 2444784.6713
C | Xist Rating 2216 | -93.07 | 129.719 | 150.283 | 35.8 | 2383.5 | 7348.76 | 53794.7 | 2.3 | 9.8 | 14.763 | 298.364 | 1 | 1 | 1040 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 309185.2365 | 29924.8947 | 1053.4182 | 6113.8574 | 23811.0373 | 311433.4394 | 0.039625 | -2404806.4674 | 2404806.4674
C | Xist Rating 2217 | -92.92 | 132.201 | 150.283 | 35.8 | 2392.49 | 7451.63 | 53044.1 | 2.24 | 9.63 | 14.729 | 288.548 | 1 | 1 | 1050 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 316289.5705 | 30443.7878 | 1073.7737 | 6172.6445 | 24271.1434 | 301209.4846 | 0.040006 | -2325859.7979 | 2325859.7979
C | Xist Rating 2218 | -92.81 | 133.485 | 150.283 | 35.8 | 2406.21 | 7595.08 | 52678.2 | 2.19 | 9.54 | 14.717 | 283.931 | 1 | 1 | 1060 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 321192.9419 | 30967.0839 | 1094.3239 | 6231.4316 | 24735.6523 | 296393.2859 | 0.040387 | -2288670.3884 | 2288670.3884
C | Xist Rating 2219 | -92.35 | 143.399 | 150.283 | 35.8 | 2385.45 | 7460.08 | 49858.5 | 2.18 | 8.9 | 14.643 | 248.491 | 1 | 1 | 1070 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 342071.1445 | 31494.7829 | 1115.0689 | 6290.2187 | 25204.5642 | 259588.5531 | 0.040768 | -2004473.9976 | 2004473.9976
C | Xist Rating 2220 | -92.23 | 145.328 | 150.283 | 35.8 | 2390.98 | 7527.09 | 49381.5 | 2.13 | 8.79 | 14.582 | 242.984 | 1 | 1 | 1080 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 347476.3414 | 32026.8848 | 1136.0087 | 6349.0057 | 25677.879 | 253842.1173 | 0.041149 | -1960101.5435 | 1960101.5435
C | Xist Rating 2221 | -92.1 | 147.889 | 150.282 | 35.8 | 2389.28 | 7526.93 | 48761.8 | 2.07 | 8.65 | 14.492 | 235.903 | 1 | 1 | 1090 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 353348.2299 | 32563.3896 | 1157.1433 | 6407.7928 | 26155.5968 | 246450.5824 | 0.04153 | -1903026.0701 | 1903026.0701
C | Xist Rating 2222 | -91.99 | 149.787 | 150.282 | 35.8 | 2395.18 | 7598.56 | 48308.7 | 2.04 | 8.55 | 14.478 | 230.779 | 1 | 1 | 1100 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 358766.8267 | 33104.2974 | 1178.4727 | 6466.5799 | 26637.7174 | 241119.9182 | 0.041911 | -1861864.0943 | 1861864.0943
C | Xist Rating 2223 | -91.94 | 151.258 | 150.282 | 35.8 | 2388.51 | 7540.26 | 48010.8 | 1.96 | 8.49 | 14.307 | 227.715 | 1 | 1 | 1110 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 361281.2456 | 33649.608 | 1199.9969 | 6525.367 | 27124.241 | 237876.8934 | 0.042292 | -1836822.3164 | 1836822.3164
C | Xist Rating 2224 | -91.37 | 162.226 | 150.282 | 35.8 | 2386.23 | 7594.69 | 45448 | 2 | 7.92 | 14.467 | 199.252 | 1 | 1 | 1120 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 387108.548 | 34199.3217 | 1221.7158 | 6584.1541 | 27615.1676 | 208375.4782 | 0.042673 | -1609020.2081 | 1609020.2081
C | Xist Rating 2225 | -91.31 | 163.651 | 150.282 | 35.8 | 2383.83 | 7578.8 | 45188.8 | 1.95 | 7.86 | 14.353 | 196.77 | 1 | 1 | 1130 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 390116.1633 | 34753.4382 | 1243.6296 | 6642.9412 | 28110.497 | 205762.9957 | 0.043054 | -1588847.3112 | 1588847.3112
C | Xist Rating 2226 | -91.18 | 166.283 | 150.282 | 35.8 | 2381.72 | 7574.02 | 44681.8 | 1.89 | 7.75 | 14.205 | 191.715 | 1 | 1 | 1140 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 396039.5468 | 35311.9577 | 1265.7381 | 6701.7283 | 28610.2294 | 200467.6318 | 0.043435 | -1547957.9146 | 1547957.9146
C | Xist Rating 2227 | -91.01 | 168.852 | 150.282 | 35.8 | 2390.16 | 7676.99 | 44186.9 | 1.84 | 7.64 | 14.172 | 186.803 | 1 | 1 | 1150 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 403583.2963 | 35874.8801 | 1288.0414 | 6760.5154 | 29114.3647 | 195338.8196 | 0.043816 | -1508354.5863 | 1508354.5863
C | Xist Rating 2228 | -90.88 | 171.5 | 150.281 | 35.8 | 2389.65 | 7688.7 | 43704.3 | 1.79 | 7.53 | 14.091 | 182.147 | 1 | 1 | 1160 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 409824.975 | 36442.2054 | 1310.5395 | 6819.3025 | 29622.903 | 190470.8759 | 0.044197 | -1470765.6153 | 1470765.6153
C | Xist Rating 2229 | -90.36 | 181.401 | 150.282 | 35.8 | 2389.46 | 7756.96 | 41833.5 | 1.81 | 7.13 | 14.19 | 163.876 | 1 | 1 | 1170 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 433450.4335 | 37013.9337 | 1333.2324 | 6878.0896 | 30135.8441 | 171531.9549 | 0.044578 | -1324524.2879 | 1324524.2879
C | Xist Rating 2230 | -90.29 | 182.206 | 150.281 | 35.8 | 2397.91 | 7851.01 | 41726.1 | 1.76 | 7.11 | 14.142 | 163.045 | 1 | 1 | 1180 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 436913.5895 | 37590.0649 | 1356.1201 | 6936.8766 | 30653.1882 | 170638.4794 | 0.044959 | -1317625.1068 | 1317625.1068
C | Xist Rating 2231 | -90.07 | 187.33 | 150.281 | 35.8 | 2386.31 | 7761.99 | 40887.3 | 1.71 | 6.93 | 14.051 | 155.483 | 1 | 1 | 1190 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 447027.4523 | 38170.599 | 1379.2026 | 6995.6637 | 31174.9353 | 162750.4931 | 0.04534 | -1256716.1672 | 1256716.1672
C | Xist Rating 2232 | -89.96 | 188.647 | 150.281 | 35.8 | 2397.24 | 7887.63 | 40683.1 | 1.68 | 6.88 | 14.059 | 153.727 | 1 | 1 | 1200 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 452232.1343 | 38755.536 | 1402.4799 | 7054.4508 | 31701.0852 | 160915.709 | 0.045721 | -1242548.4508 | 1242548.4508
C | Xist Rating 2233 | -89.85 | 191.364 | 150.281 | 35.8 | 2392.46 | 7853.38 | 40282.2 | 1.63 | 6.8 | 13.977 | 150.324 | 1 | 1 | 1210 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 457830.7154 | 39344.876 | 1425.9519 | 7113.2379 | 32231.6381 | 157346.9101 | 0.046102 | -1214991.1321 | 1214991.1321
C | Xist Rating 2234 | -89.31 | 202.686 | 150.281 | 35.8 | 2379.84 | 7796.8 | 38538.7 | 1.64 | 6.43 | 14.002 | 135.242 | 1 | 1 | 1220 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 482360.2502 | 39938.6189 | 1449.6188 | 7172.025 | 32766.5939 | 141704.3748 | 0.046483 | -1094203.6203 | 1094203.6203
C | Xist Rating 2235 | -89.15 | 205.253 | 150.281 | 35.8 | 2386.54 | 7886.37 | 38184.2 | 1.61 | 6.35 | 14.001 | 132.379 | 1 | 1 | 1230 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 489844.4946 | 40536.7647 | 1473.4804 | 7230.8121 | 33305.9526 | 138718.1985 | 0.046864 | -1071145.1589 | 1071145.1589
C | Xist Rating 2236 | -89.02 | 207.96 | 150.281 | 35.8 | 2383.76 | 7873.23 | 37836.6 | 1.57 | 6.28 | 13.942 | 129.677 | 1 | 1 | 1240 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 495726.7296 | 41139.3135 | 1497.5369 | 7289.5992 | 33849.7143 | 135886.0029 | 0.047245 | -1049275.6951 | 1049275.6951
C | Xist Rating 2237 | -88.95 | 209.422 | 150.281 | 35.8 | 2385.14 | 7896.88 | 37665.3 | 1.53 | 6.24 | 13.898 | 128.427 | 1 | 1 | 1250 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 499500.7891 | 41746.2652 | 1521.7881 | 7348.3863 | 34397.8789 | 134562.6723 | 0.047626 | -1039057.2867 | 1039057.2867
C | Xist Rating 2238 | -88.76 | 213.296 | 150.281 | 35.8 | 2382.67 | 7895.62 | 37162.2 | 1.5 | 6.14 | 13.869 | 124.491 | 1 | 1 | 1260 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 508213.9803 | 42357.6198 | 1546.2341 | 7407.1734 | 34950.4464 | 130458.6688 | 0.048007 | -1007367.2595 | 1007367.2595
C | Xist Rating 2239 | -88.24 | 224.029 | 150.281 | 35.8 | 2375.95 | 7896.17 | 35778.3 | 1.51 | 5.85 | 13.922 | 113.748 | 1 | 1 | 1270 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 532281.7025 | 42973.3774 | 1570.8749 | 7465.9605 | 35507.4169 | 119323.8565 | 0.048388 | -921387.1906 | 921387.1906
C | Xist Rating 2240 | -88.11 | 226.804 | 150.281 | 35.8 | 2373.67 | 7887.99 | 35478.1 | 1.47 | 5.79 | 13.872 | 111.644 | 1 | 1 | 1280 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 538357.8507 | 43593.5378 | 1595.7105 | 7524.7475 | 36068.7903 | 117112.1106 | 0.048769 | -904308.6747 | 904308.6747
C | Xist Rating 2241 | -87.95 | 229.528 | 150.281 | 35.8 | 2377.74 | 7950.22 | 35183.6 | 1.43 | 5.73 | 13.865 | 109.582 | 1 | 1 | 1290 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 545757.9067 | 44218.1012 | 1620.7408 | 7583.5346 | 36634.5666 | 114947.2033 | 0.04915 | -887591.8348 | 887591.8348
C | Xist Rating 2242 | -87.72 | 233.38 | 150.281 | 35.8 | 2384.62 | 8053.83 | 34752.9 | 1.41 | 5.64 | 13.874 | 106.504 | 1 | 1 | 1300 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 556522.6156 | 44847.0676 | 1645.966 | 7642.3217 | 37204.7458 | 111744.1732 | 0.049531 | -862858.8851 | 862858.8851
C | Xist Rating 2243 | -87.59 | 235.502 | 150.281 | 35.8 | 2389.94 | 8128.21 | 34541.7 | 1.37 | 5.59 | 13.845 | 105.099 | 1 | 1 | 1310 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 562835.6499 | 45480.4368 | 1671.3859 | 7701.1088 | 37779.328 | 110258.9313 | 0.049912 | -851390.2408 | 851390.2408
C | Xist Rating 2244 | -87.06 | 246.332 | 150.281 | 35.7 | 2383.63 | 8132.7 | 33364.3 | 1.38 | 5.35 | 13.891 | 96.848 | 1 | 1 | 1320 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 587164.3452 | 46118.209 | 1697.0007 | 7759.8959 | 38358.3131 | 101710.7309 | 0.050293 | -785383.3034 | 785383.3034
C | Xist Rating 2245 | -86.88 | 250.402 | 150.281 | 35.7 | 2378.42 | 8098.49 | 32981.2 | 1.34 | 5.28 | 13.811 | 94.375 | 1 | 1 | 1330 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 595561.1248 | 46760.3841 | 1722.8102 | 7818.683 | 38941.7011 | 99111.6006 | 0.050674 | -765313.5084 | 765313.5084
C | Xist Rating 2246 | -86.68 | 254.37 | 150.281 | 35.7 | 2379.35 | 8135.65 | 32607.6 | 1.31 | 5.2 | 13.787 | 91.97 | 1 | 1 | 1340 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 605235.2595 | 47406.9622 | 1748.8145 | 7877.4701 | 39529.4921 | 96595.5323 | 0.051055 | -745885.0958 | 745885.0958
C | Xist Rating 2247 | -86.55 | 256.508 | 150.281 | 35.7 | 2383.44 | 8197.03 | 32425.2 | 1.28 | 5.16 | 13.766 | 90.863 | 1 | 1 | 1350 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 611371.4275 | 48057.9432 | 1775.0136 | 7936.2572 | 40121.686 | 95427.3548 | 0.051436 | -736864.739 | 736864.739
C | Xist Rating 2248 | -86.39 | 257.772 | 150.281 | 35.7 | 2401.11 | 8419.26 | 32304.7 | 1.27 | 5.14 | 13.803 | 90.101 | 1 | 1 | 1360 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 618938.9269 | 48713.3271 | 1801.4075 | 7995.0443 | 40718.2828 | 94638.39 | 0.051817 | -730772.5615 | 730772.5615
C | Xist Rating 2249 | -85.75 | 273.307 | 150.281 | 35.7 | 2372.4 | 8183.23 | 30903.6 | 1.26 | 4.86 | 13.785 | 81.283 | 1 | 1 | 1370 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 648393.5268 | 49373.1139 | 1827.9962 | 8053.8314 | 41319.2825 | 85478.8994 | 0.052198 | -660045.4034 | 660045.4034
C | Xist Rating 2250 | -85.68 | 274.832 | 150.281 | 35.7 | 2372.27 | 8190.44 | 30795.1 | 1.24 | 4.84 | 13.761 | 80.705 | 1 | 1 | 1380 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 651975.7086 | 50037.3036 | 1854.7797 | 8112.6185 | 41924.6852 | 84867.5378 | 0.052579 | -655324.6312 | 655324.6312
C | Xist Rating 2251 | -85.51 | 278.257 | 150.28 | 35.7 | 2372.67 | 8217.18 | 30528 | 1.21 | 4.79 | 13.738 | 79.168 | 1 | 1 | 1390 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 660212.0362 | 50705.8963 | 1881.7579 | 8171.4055 | 42534.4908 | 83251.5586 | 0.05296 | -642846.468 | 642846.468
C | Xist Rating 2252 | -85.34 | 281.678 | 150.28 | 35.7 | 2373.37 | 8247.68 | 30266.4 | 1.19 | 4.73 | 13.719 | 77.678 | 1 | 1 | 1400 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 668526.1149 | 51378.8919 | 1908.931 | 8230.1926 | 43148.6993 | 81692.9858 | 0.053341 | -630811.5822 | 630811.5822
C | Xist Rating 2253 | -85.14 | 285.707 | 150.28 | 35.7 | 2374.07 | 8282.84 | 29958.3 | 1.17 | 4.67 | 13.701 | 75.926 | 1 | 1 | 1410 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 678288.4175 | 52056.2905 | 1936.2988 | 8288.9797 | 43767.3108 | 79862.1819 | 0.053722 | -616674.5994 | 616674.5994
C | Xist Rating 2254 | -84.57 | 297.272 | 150.28 | 35.7 | 2369.25 | 8306.28 | 29052.6 | 1.17 | 4.49 | 13.755 | 70.706 | 1 | 1 | 1420 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 704311.686 | 52738.092 | 1963.8614 | 8347.7668 | 44390.3252 | 74452.4271 | 0.054103 | -574901.9067 | 574901.9067
C | Xist Rating 2255 | -84.48 | 299.651 | 150.28 | 35.7 | 2365.59 | 8274.69 | 28911.4 | 1.14 | 4.47 | 13.708 | 70.024 | 1 | 1 | 1430 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 708851.4091 | 53424.2964 | 1991.6188 | 8406.5539 | 45017.7425 | 73721.5 | 0.054484 | -569257.8812 | 569257.8812
C | Xist Rating 2256 | -84.23 | 304.944 | 150.28 | 35.7 | 2363.24 | 8281.18 | 28542.8 | 1.12 | 4.39 | 13.695 | 68.037 | 1 | 1 | 1440 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 720655.8586 | 54114.9037 | 2019.571 | 8465.341 | 45649.5627 | 71646.3722 | 0.054865 | -553234.2951 | 553234.2951
C | Xist Rating 2257 | -84.07 | 308.403 | 150.28 | 35.7 | 2362.41 | 8292.95 | 28317.5 | 1.1 | 4.35 | 13.677 | 66.875 | 1 | 1 | 1450 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 728574.3312 | 54809.914 | 2047.718 | 8524.1281 | 46285.7859 | 70427.4232 | 0.055246 | -543821.8938 | 543821.8938
C | Xist Rating 2258 | -83.93 | 310.423 | 150.28 | 35.7 | 2368.82 | 8385.96 | 28184.4 | 1.09 | 4.33 | 13.685 | 66.192 | 1 | 1 | 1460 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 735336.2109 | 55509.3271 | 2076.0598 | 8582.9152 | 46926.412 | 69716.4924 | 0.055627 | -538332.2747 | 538332.2747
C | Xist Rating 2259 | -83.37 | 323.68 | 150.28 | 35.7 | 2353.08 | 8280.48 | 27311 | 1.08 | 4.16 | 13.693 | 61.626 | 1 | 1 | 1470 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 761644.9344 | 56213.1433 | 2104.5964 | 8641.7023 | 47571.441 | 64972.9469 | 0.056008 | -501703.8738 | 501703.8738
C | Xist Rating 2260 | -83.17 | 327.753 | 150.28 | 35.7 | 2352.85 | 8303.72 | 27066.7 | 1.07 | 4.11 | 13.682 | 60.426 | 1 | 1 | 1480 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 771153.646 | 56921.3623 | 2133.3277 | 8700.4894 | 48220.8729 | 63723.5129 | 0.056389 | -492056.0751 | 492056.0751
C | Xist Rating 2261 | -82.95 | 331.214 | 150.28 | 35.7 | 2359.06 | 8403.81 | 26867.3 | 1.05 | 4.07 | 13.682 | 59.47 | 1 | 1 | 1490 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 781353.6988 | 57633.9843 | 2162.2539 | 8759.2764 | 48874.7078 | 62718.9945 | 0.05677 | -484299.4508 | 484299.4508
C | Xist Rating 2262 | -82.76 | 334.767 | 150.28 | 35.7 | 2362.24 | 8466.89 | 26670.7 | 1.02 | 4.03 | 13.669 | 58.55 | 1 | 1 | 1500 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 790799.9981 | 58351.0092 | 2191.3748 | 8818.0635 | 49532.9456 | 61741.5259 | 0.057151 | -476751.697 | 476751.697
C | Xist Rating 2263 | -82.52 | 338.867 | 150.28 | 35.7 | 2366.58 | 8550.41 | 26439.3 | 1.01 | 3.99 | 13.668 | 57.451 | 1 | 1 | 1510 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 801955.8649 | 59072.437 | 2220.6906 | 8876.8506 | 50195.5864 | 60597.1455 | 0.057532 | -467915.0949 | 467915.0949
C | Xist Rating 2264 | -81.88 | 351.807 | 150.28 | 35.7 | 2364.95 | 8623.62 | 25681.5 | 1.01 | 3.85 | 13.73 | 53.771 | 1 | 1 | 1520 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 832005.9646 | 59798.2678 | 2250.2011 | 8935.6377 | 50862.63 | 56785.9257 | 0.057913 | -438485.8662 | 438485.8662
C | Xist Rating 2265 | -81.72 | 356.25 | 150.28 | 35.7 | 2357.29 | 8549.89 | 25468.8 | 0.99 | 3.8 | 13.689 | 52.855 | 1 | 1 | 1530 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 839784.5625 | 60528.5015 | 2279.9064 | 8994.4248 | 51534.0766 | 55819.2609 | 0.058294 | -431021.5364 | 431021.5364
C | Xist Rating 2266 | -81.56 | 358.545 | 150.28 | 35.7 | 2363.04 | 8639.86 | 25364.4 | 0.97 | 3.79 | 13.68 | 52.424 | 1 | 1 | 1540 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 847256.1768 | 61263.1381 | 2309.8065 | 9053.2119 | 52209.9262 | 55358.2411 | 0.058675 | -427461.6638 | 427461.6638
C | Xist Rating 2267 | -81.24 | 365.227 | 150.28 | 35.7 | 2361.4 | 8664.3 | 25021.8 | 0.95 | 3.72 | 13.675 | 50.883 | 1 | 1 | 1550 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 862447.0378 | 62002.1776 | 2339.9013 | 9111.999 | 52890.1786 | 53744.5238 | 0.059056 | -415000.9668 | 415000.9668
C | Xist Rating 2268 | -81.05 | 367.297 | 150.28 | 35.7 | 2373.49 | 8843.83 | 24921 | 0.94 | 3.7 | 13.691 | 50.454 | 1 | 1 | 1560 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 871775.7565 | 62745.6201 | 2370.191 | 9170.7861 | 53574.834 | 53296.3205 | 0.059437 | -411540.0598 | 411540.0598
C | Xist Rating 2269 | -80.44 | 382.756 | 150.28 | 35.7 | 2352.62 | 8668.44 | 24162.7 | 0.93 | 3.56 | 13.698 | 47.117 | 1 | 1 | 1570 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 900479.4207 | 63493.4655 | 2400.6755 | 9229.5732 | 54263.8923 | 49827.4432 | 0.059818 | -384754.3083 | 384754.3083
C | Xist Rating 2270 | -80.24 | 386.338 | 150.28 | 35.7 | 2355.78 | 8734.74 | 24008.1 | 0.92 | 3.53 | 13.691 | 46.494 | 1 | 1 | 1580 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 910127.3336 | 64245.7138 | 2431.3547 | 9288.3603 | 54957.3536 | 49176.0115 | 0.0602 | -379724.1257 | 379724.1257
C | Xist Rating 2271 | -80.05 | 389.955 | 150.28 | 35.7 | 2358.08 | 8790.15 | 23855.6 | 0.9 | 3.5 | 13.682 | 45.888 | 1 | 1 | 1590 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 919545.0864 | 65002.3651 | 2462.2288 | 9347.1473 | 55655.2177 | 48532.2347 | 0.060581 | -374753.0516 | 374753.0516
C | Xist Rating 2272 | -79.78 | 394.693 | 150.28 | 35.7 | 2362.75 | 8889.03 | 23645.7 | 0.89 | 3.46 | 13.686 | 45.026 | 1 | 1 | 1600 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 932560.8858 | 65763.4193 | 2493.2976 | 9405.9344 | 56357.4848 | 47633.0113 | 0.060962 | -367809.4873 | 367809.4873
C | Xist Rating 2273 | -79.66 | 397.183 | 150.28 | 35.7 | 2362.72 | 8903.13 | 23557 | 0.87 | 3.45 | 13.668 | 44.714 | 1 | 1 | 1610 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 938432.2178 | 66528.8764 | 2524.5612 | 9464.7215 | 57064.1548 | 47293.5758 | 0.061343 | -365188.4563 | 365188.4563
C | Xist Rating 2274 | -78.91 | 414.376 | 150.28 | 35.7 | 2349.04 | 8835.78 | 22805.5 | 0.87 | 3.31 | 13.703 | 41.625 | 1 | 1 | 1620 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 973385.799 | 67298.7364 | 2556.0196 | 9523.5086 | 57775.2278 | 44093.1955 | 0.061724 | -340475.968 | 340475.968
C | Xist Rating 2275 | -78.74 | 416.522 | 150.28 | 35.7 | 2356.91 | 8962.78 | 22723.7 | 0.86 | 3.29 | 13.71 | 41.327 | 1 | 1 | 1630 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 981704.867 | 68072.9994 | 2587.6728 | 9582.2957 | 58490.7037 | 43779.4947 | 0.062105 | -338053.6532 | 338053.6532
C | Xist Rating 2276 | -78.57 | 420.286 | 150.28 | 35.7 | 2355.96 | 8973.29 | 22589 | 0.85 | 3.27 | 13.694 | 40.841 | 1 | 1 | 1640 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 990177.0046 | 68851.6653 | 2619.5208 | 9641.0828 | 59210.5825 | 43268.9912 | 0.062486 | -334111.6808 | 334111.6808
C | Xist Rating 2277 | -78.36 | 425.381 | 150.28 | 35.7 | 2352.42 | 8955.92 | 22403.4 | 0.83 | 3.24 | 13.677 | 40.159 | 1 | 1 | 1650 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1000674.772 | 69634.7341 | 2651.5635 | 9699.8699 | 59934.8642 | 42544.6529 | 0.062867 | -328518.5324 | 328518.5324
C | Xist Rating 2278 | -78.11 | 430.232 | 150.28 | 35.7 | 2354.28 | 9017.07 | 22221.1 | 0.82 | 3.2 | 13.677 | 39.479 | 1 | 1 | 1660 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1012886.593 | 70422.2059 | 2683.8011 | 9758.657 | 60663.5489 | 41833.3855 | 0.063248 | -323026.3142 | 323026.3142
C | Xist Rating 2279 | -77.45 | 445.736 | 150.281 | 35.7 | 2341.74 | 8946.93 | 21633.3 | 0.82 | 3.1 | 13.696 | 37.254 | 1 | 1 | 1670 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1043797.8206 | 71214.0806 | 2716.2334 | 9817.4441 | 61396.6365 | 39528.92 | 0.063629 | -305231.842 | 305231.842
C | Xist Rating 2280 | -77.3 | 447.992 | 150.28 | 35.7 | 2347.18 | 9041.55 | 21560.7 | 0.81 | 3.08 | 13.704 | 37.014 | 1 | 1 | 1680 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1051517.8626 | 72010.3582 | 2748.8606 | 9876.2312 | 62134.127 | 39274.8886 | 0.06401 | -303270.2793 | 303270.2793
C | Xist Rating 2281 | -77.03 | 454.467 | 150.28 | 35.7 | 2341.69 | 9003.81 | 21346.4 | 0.79 | 3.04 | 13.678 | 36.268 | 1 | 1 | 1690 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1064220.8292 | 72811.0387 | 2781.6825 | 9935.0182 | 62876.0205 | 38482.8259 | 0.064391 | -297154.181 | 297154.181
C | Xist Rating 2282 | -76.82 | 458.723 | 150.28 | 35.7 | 2342.73 | 9048.14 | 21206.5 | 0.78 | 3.02 | 13.675 | 35.786 | 1 | 1 | 1700 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1074664.1338 | 73616.1222 | 2814.6992 | 9993.8053 | 63622.3168 | 37976.512 | 0.064772 | -293244.5595 | 293244.5595
C | Xist Rating 2283 | -76.57 | 463.767 | 150.28 | 35.6 | 2343.73 | 9097.4 | 21045.4 | 0.77 | 2.99 | 13.67 | 35.239 | 1 | 1 | 1710 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1086944.6309 | 74425.6086 | 2847.9107 | 10052.5924 | 64373.0162 | 37402.4576 | 0.065153 | -288811.8634 | 288811.8634
C | Xist Rating 2284 | -75.97 | 478.095 | 150.281 | 35.7 | 2332.09 | 9026.69 | 20567.8 | 0.77 | 2.9 | 13.697 | 33.561 | 1 | 1 | 1720 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1114960.5686 | 75239.4979 | 2881.317 | 10111.3795 | 65128.1184 | 35666.1783 | 0.065534 | -275404.7751 | 275404.7751
C | Xist Rating 2285 | -75.66 | 484.439 | 150.281 | 35.6 | 2332.85 | 9081.65 | 20374.8 | 0.75 | 2.87 | 13.692 | 32.923 | 1 | 1 | 1730 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1130123.5211 | 76057.7902 | 2914.9181 | 10170.1666 | 65887.6236 | 34986.8099 | 0.065915 | -270158.8724 | 270158.8724
C | Xist Rating 2286 | -75.5 | 487.456 | 150.281 | 35.6 | 2335.11 | 9135.44 | 20290.5 | 0.74 | 2.85 | 13.688 | 32.664 | 1 | 1 | 1740 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1138263.3802 | 76880.4854 | 2948.714 | 10228.9537 | 66651.5317 | 34711.532 | 0.066296 | -268033.2488 | 268033.2488
C | Xist Rating 2287 | -75.28 | 493.32 | 150.281 | 35.6 | 2330.45 | 9103.38 | 20123.6 | 0.73 | 2.82 | 13.673 | 32.134 | 1 | 1 | 1750 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1149657.594 | 77707.5835 | 2982.7046 | 10287.7408 | 67419.8427 | 34154.0719 | 0.066677 | -263728.6899 | 263728.6899
C | Xist Rating 2288 | -75.11 | 497.693 | 150.281 | 35.6 | 2326.99 | 9079.59 | 20000.7 | 0.72 | 2.8 | 13.668 | 31.749 | 1 | 1 | 1760 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1158126.6341 | 78539.0845 | 3016.8901 | 10346.5279 | 68192.5566 | 33747.6533 | 0.067058 | -260590.4329 | 260590.4329
C | Xist Rating 2289 | -74.39 | 514.664 | 150.281 | 35.6 | 2316.28 | 9038.42 | 19497.3 | 0.72 | 2.71 | 13.703 | 30.094 | 1 | 1 | 1770 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1192105.9299 | 79374.9885 | 3051.2703 | 10405.315 | 68969.6735 | 32035.3489 | 0.067439 | -247368.4726 | 247368.4726
C | Xist Rating 2290 | -74.18 | 519.146 | 150.281 | 35.6 | 2315.54 | 9055.54 | 19383.3 | 0.71 | 2.69 | 13.698 | 29.757 | 1 | 1 | 1780 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1202103.3288 | 80215.2954 | 3085.8453 | 10464.1021 | 69751.1933 | 31678.5808 | 0.06782 | -244613.6041 | 244613.6041
C | Xist Rating 2291 | -74.19 | 521.662 | 150.281 | 35.6 | 2306.8 | 8937.2 | 19327 | 0.7 | 2.68 | 13.819 | 29.6 | 1 | 1 | 1790 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1203369.9016 | 81060.0052 | 3120.6151 | 10522.8892 | 70537.1161 | 31515.7013 | 0.068201 | -243355.8915 | 243355.8915
C | Xist Rating 2292 | -73.87 | 529.425 | 150.281 | 35.6 | 2300.55 | 8893.97 | 19123.1 | 0.69 | 2.65 | 13.814 | 28.977 | 1 | 1 | 1800 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1217968.6838 | 81909.118 | 3155.5797 | 10581.6762 | 71327.4417 | 30861.6247 | 0.068582 | -238305.2852 | 238305.2852
C | Xist Rating 2293 | -73.68 | 533.78 | 150.281 | 35.6 | 2302.35 | 8948.82 | 19012.6 | 0.68 | 2.63 | 13.804 | 28.655 | 1 | 1 | 1810 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1228948.383 | 82762.6337 | 3190.7391 | 10640.4633 | 72122.1703 | 30519.7413 | 0.068963 | -235665.3528 | 235665.3528
C | Xist Rating 2294 | -72.97 | 551.01 | 150.281 | 35.6 | 2291.61 | 8903.5 | 18562.9 | 0.68 | 2.55 | 13.841 | 27.281 | 1 | 1 | 1820 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1262700.0261 | 83620.5523 | 3226.0933 | 10699.2504 | 72921.3018 | 29099.1047 | 0.069344 | -224695.5729 | 224695.5729
C | Xist Rating 2295 | -72.88 | 548.248 | 150.281 | 35.6 | 2310.68 | 9178.97 | 18632 | 0.67 | 2.56 | 13.871 | 27.5 | 1 | 1 | 1830 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1266825.6886 | 84482.8738 | 3261.6423 | 10758.0375 | 73724.8363 | 29321.0498 | 0.069725 | -226409.3743 | 226409.3743
C | Xist Rating 2296 | -72.58 | 551.791 | 150.281 | 35.6 | 2321.32 | 9374.21 | 18546.2 | 0.67 | 2.55 | 13.892 | 27.256 | 1 | 1 | 1840 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1280883.4841 | 85349.5983 | 3297.386 | 10816.8246 | 74532.7737 | 29072.9824 | 0.070106 | -224493.864 | 224493.864
C | Xist Rating 2297 | -72.33 | 557.772 | 150.281 | 35.6 | 2318.36 | 9366.09 | 18410.3 | 0.65 | 2.52 | 13.884 | 26.877 | 1 | 1 | 1850 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1293116.2939 | 86220.7257 | 3333.3246 | 10875.6117 | 75345.114 | 28660.0924 | 0.070487 | -221305.6365 | 221305.6365
C | Xist Rating 2298 | -72.12 | 564.459 | 150.281 | 35.6 | 2310.3 | 9280.11 | 18259.9 | 0.64 | 2.5 | 13.859 | 26.459 | 1 | 1 | 1860 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1304069.6277 | 87096.256 | 3369.4579 | 10934.3988 | 76161.8572 | 28217.1357 | 0.070868 | -217885.2423 | 217885.2423
C | Xist Rating 2299 | -71.43 | 580.242 | 150.281 | 35.6 | 2304.08 | 9294.62 | 17880.5 | 0.64 | 2.43 | 13.904 | 25.355 | 1 | 1 | 1870 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1336923.9874 | 87976.1893 | 3405.7861 | 10993.1859 | 76983.0034 | 27077.0234 | 0.071249 | -209081.597 | 209081.597
C | Xist Rating 2300 | -71.15 | 586.914 | 150.281 | 35.6 | 2300.81 | 9285.39 | 17739.8 | 0.63 | 2.41 | 13.896 | 24.98 | 1 | 1 | 1880 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1350377.6003 | 88860.5254 | 3442.309 | 11051.973 | 77808.5525 | 26679.4335 | 0.07163 | -206011.5138 | 206011.5138
C | Xist Rating 2301 | -70.89 | 591.317 | 150.281 | 35.6 | 2304.8 | 9380.41 | 17647.5 | 0.63 | 2.39 | 13.904 | 24.737 | 1 | 1 | 1890 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 12 | E | Rod | 1362867.4216 | 89749.2646 | 3479.0267 | 11110.7601 | 78638.5045 | 26431.4296 | 0.072011 | -204096.4929 | 204096.4929
C | Xist Rating 2302 | -70.71 | 596.178 | 150.281 | 35.6 | 2301.25 | 9351.55 | 17556 | 0.61 | 2.38 | 13.884 | 24.512 | 1 | 1 | 1900 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1371954.6225 | 90642.4066 | 3515.9392 | 11169.5471 | 79472.8595 | 26176.9716 | 0.072392 | -202131.636 | 202131.636
C | Xist Rating 2303 | -70.49 | 600.76 | 150.281 | 35.6 | 2301.35 | 9382.74 | 17466 | 0.6 | 2.36 | 13.892 | 24.283 | 1 | 1 | 1910 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1382559.026 | 91539.9516 | 3553.0464 | 11228.3342 | 80311.6173 | 25931.4759 | 0.072773 | -200235.9835 | 200235.9835
C | Xist Rating 2304 | -69.69 | 619.945 | 150.281 | 35.6 | 2291.69 | 9362.68 | 17051.1 | 0.61 | 2.29 | 13.932 | 23.145 | 1 | 1 | 1920 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1420721.7571 | 92441.8995 | 3590.3485 | 11287.1213 | 81154.7781 | 24767.4568 | 0.073154 | -191247.7364 | 191247.7364
C | Xist Rating 2305 | -69.42 | 626.694 | 150.281 | 35.6 | 2288.29 | 9349.95 | 16924.8 | 0.6 | 2.27 | 13.932 | 22.83 | 1 | 1 | 1930 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1434057.6133 | 93348.2503 | 3627.8454 | 11345.9084 | 82002.3419 | 24432.0865 | 0.073535 | -188658.0954 | 188658.0954
C | Xist Rating 2306 | -69.21 | 628.849 | 150.281 | 35.6 | 2296.78 | 9508.57 | 16883.1 | 0.59 | 2.26 | 13.965 | 22.731 | 1 | 1 | 1940 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1444327.8062 | 94259.004 | 3665.537 | 11404.6955 | 82854.3085 | 24322.6 | 0.073916 | -187812.6697 | 187812.6697
C | Xist Rating 2307 | -69.01 | 635.401 | 150.281 | 35.6 | 2288.86 | 9413.73 | 16773 | 0.58 | 2.24 | 13.953 | 22.475 | 1 | 1 | 1950 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1454343.9329 | 95174.1607 | 3703.4235 | 11463.4826 | 83710.6781 | 24047.6227 | 0.074297 | -185689.3684 | 185689.3684
C | Xist Rating 2308 | -68.69 | 642.736 | 150.281 | 35.6 | 2286.88 | 9429.63 | 16637.8 | 0.57 | 2.22 | 13.965 | 22.139 | 1 | 1 | 1960 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1469860.1037 | 96093.7203 | 3741.5047 | 11522.2697 | 84571.4507 | 23690.6571 | 0.074678 | -182932.9748 | 182932.9748
C | Xist Rating 2309 | -67.96 | 660.094 | 150.281 | 35.6 | 2279.69 | 9432.94 | 16304 | 0.57 | 2.16 | 14.014 | 21.282 | 1 | 1 | 1970 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1504809.6909 | 97017.6829 | 3779.7807 | 11581.0568 | 85436.6261 | 22806.6984 | 0.075059 | -176107.2798 | 176107.2798
C | Xist Rating 2310 | -67.71 | 665.363 | 150.281 | 35.6 | 2280.05 | 9473.75 | 16215 | 0.56 | 2.15 | 14.014 | 21.075 | 1 | 1 | 1980 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1517060.9082 | 97946.0484 | 3818.2515 | 11639.8439 | 86306.2045 | 22582.872 | 0.07544 | -174378.9516 | 174378.9516
C | Xist Rating 2311 | -67.45 | 672.307 | 150.281 | 35.6 | 2275.92 | 9447.03 | 16102.1 | 0.55 | 2.13 | 14.008 | 20.816 | 1 | 1 | 1990 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1530116.9474 | 98878.8167 | 3856.9171 | 11698.631 | 87180.1858 | 22304.6237 | 0.075821 | -172230.3918 | 172230.3918
C | Xist Rating 2312 | -67.2 | 677.701 | 150.281 | 35.6 | 2275.61 | 9476.12 | 16015.5 | 0.54 | 2.12 | 14.008 | 20.621 | 1 | 1 | 2000 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1542183.1726 | 99815.9881 | 3895.7775 | 11757.418 | 88058.57 | 22093.0119 | 0.076202 | -170596.3816 | 170596.3816
C | Xist Rating 2313 | -67.03 | 681.716 | 150.281 | 35.6 | 2275.1 | 9492.28 | 15954 | 0.54 | 2.11 | 13.994 | 20.489 | 1 | 1 | 2010 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1550972.0716 | 100757.5623 | 3934.8326 | 11816.2051 | 88941.3572 | 21958.6396 | 0.076583 | -169558.7947 | 169558.7947
C | Xist Rating 2314 | -66.25 | 701.349 | 150.281 | 35.6 | 2265 | 9456.85 | 15615 | 0.54 | 2.05 | 14.03 | 19.669 | 1 | 1 | 2020 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1588555.485 | 101703.5395 | 3974.0826 | 11874.9922 | 89828.5473 | 21112.2184 | 0.076964 | -163022.9546 | 163022.9546
C | Xist Rating 2315 | -65.93 | 708.629 | 150.281 | 35.6 | 2263.87 | 9486.05 | 15500 | 0.53 | 2.03 | 14.03 | 19.408 | 1 | 1 | 2030 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1604243.9342 | 102653.9196 | 4013.5273 | 11933.7793 | 90720.1403 | 20831.7999 | 0.077345 | -160857.6369 | 160857.6369
C | Xist Rating 2316 | -65.74 | 713.689 | 150.281 | 35.6 | 2261.15 | 9467.72 | 15432 | 0.52 | 2.02 | 14.022 | 19.271 | 1 | 1 | 2040 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1613757.8824 | 103608.7027 | 4053.1669 | 11992.5664 | 91616.1363 | 20679.649 | 0.077726 | -159682.7678 | 159682.7678
C | Xist Rating 2317 | -65.54 | 717.934 | 150.281 | 35.6 | 2262.48 | 9520.74 | 15364.4 | 0.52 | 2.01 | 14.026 | 19.121 | 1 | 1 | 2050 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1624311.3163 | 104567.8886 | 4093.0012 | 12051.3535 | 92516.5351 | 20527.3337 | 0.078107 | -158506.6297 | 158506.6297
C | Xist Rating 2318 | -65.3 | 725.273 | 150.281 | 35.6 | 2255.76 | 9446.43 | 15264.4 | 0.51 | 1.99 | 14.015 | 18.913 | 1 | 1 | 2060 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1636041.8225 | 105531.4775 | 4133.0303 | 12110.1406 | 93421.3369 | 20301.1259 | 0.078488 | -156759.9127 | 156759.9127
C | Xist Rating 2319 | -64.47 | 746.387 | 150.281 | 35.6 | 2245.75 | 9417.82 | 14936.3 | 0.51 | 1.94 | 14.053 | 18.164 | 1 | 1 | 2070 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1676198.6052 | 106499.4694 | 4173.2542 | 12168.9277 | 94330.5417 | 19528.2927 | 0.078869 | -150792.2997 | 150792.2997
C | Xist Rating 2320 | -64.27 | 751.249 | 150.281 | 35.6 | 2244.78 | 9429.51 | 14873.7 | 0.5 | 1.93 | 14.05 | 18.041 | 1 | 1 | 2080 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1686388.7302 | 107471.8641 | 4213.6729 | 12227.7148 | 95244.1493 | 19390.5278 | 0.07925 | -149728.5155 | 149728.5155
C | Xist Rating 2321 | -64.03 | 757.43 | 150.281 | 35.6 | 2242.61 | 9429.63 | 14791 | 0.5 | 1.91 | 14.049 | 17.873 | 1 | 1 | 2090 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1698620.0923 | 108448.6618 | 4254.2864 | 12286.5019 | 96162.1599 | 19219.1621 | 0.079631 | -148405.2754 | 148405.2754
C | Xist Rating 2322 | -63.76 | 763.619 | 150.281 | 35.6 | 2241.15 | 9442.13 | 14709.7 | 0.49 | 1.9 | 14.059 | 17.708 | 1 | 1 | 2100 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1711384.7219 | 109429.8624 | 4295.0947 | 12345.2889 | 97084.5735 | 19038.1953 | 0.080012 | -147007.8973 | 147007.8973
C | Xist Rating 2323 | -63.55 | 769.106 | 150.281 | 35.6 | 2239.13 | 9439.78 | 14639 | 0.48 | 1.89 | 14.056 | 17.567 | 1 | 1 | 2110 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1722128.3178 | 110415.4659 | 4336.0977 | 12404.076 | 98011.3899 | 18881.4217 | 0.080393 | -145797.3336 | 145797.3336
C | Xist Rating 2324 | -62.81 | 789.179 | 150.281 | 35.6 | 2228.15 | 9380.61 | 14359.2 | 0.48 | 1.84 | 14.081 | 16.967 | 1 | 1 | 2120 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1758409.1889 | 111405.4724 | 4377.2956 | 12462.8631 | 98942.6093 | 18262.4873 | 0.080774 | -141018.0858 | 141018.0858
C | Xist Rating 2325 | -62.52 | 796.801 | 150.281 | 35.6 | 2224.96 | 9371.05 | 14263.8 | 0.48 | 1.83 | 14.076 | 16.778 | 1 | 1 | 2130 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1772850.353 | 112399.8818 | 4418.6882 | 12521.6502 | 99878.2316 | 18069.0116 | 0.081155 | -139524.1177 | 139524.1177
C | Xist Rating 2326 | -62.27 | 804.45 | 150.281 | 35.6 | 2219.51 | 9321.41 | 14169.9 | 0.47 | 1.81 | 14.072 | 16.594 | 1 | 1 | 2140 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1785484.8195 | 113398.6941 | 4460.2756 | 12580.4373 | 100818.2568 | 17867.2737 | 0.081536 | -137966.3516 | 137966.3516
C | Xist Rating 2327 | -62.11 | 808.615 | 150.281 | 35.6 | 2218.39 | 9324.72 | 14123.5 | 0.46 | 1.8 | 14.072 | 16.511 | 1 | 1 | 2150 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1793823.4298 | 114401.9094 | 4502.0578 | 12639.2244 | 101762.685 | 17770.4814 | 0.081917 | -137218.9467 | 137218.9467
C | Xist Rating 2328 | -61.9 | 814.048 | 150.281 | 35.6 | 2217.03 | 9333.27 | 14059.1 | 0.46 | 1.79 | 14.07 | 16.39 | 1 | 1 | 2160 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1804768.8374 | 115409.5276 | 4544.0348 | 12698.0115 | 102711.5161 | 17647.6355 | 0.082298 | -136270.3638 | 136270.3638
C | Xist Rating 2329 | -61.08 | 835.815 | 150.281 | 35.6 | 2206.08 | 9279.65 | 13786 | 0.46 | 1.75 | 14.107 | 15.836 | 1 | 1 | 2170 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1843874.7552 | 116421.5487 | 4586.2066 | 12756.7986 | 103664.7501 | 17076.8641 | 0.082679 | -131863.0179 | 131863.0179
C | Xist Rating 2330 | -60.79 | 843.212 | 150.281 | 35.6 | 2204.3 | 9293.69 | 13699.1 | 0.45 | 1.74 | 14.104 | 15.67 | 1 | 1 | 2180 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1858692.2116 | 117437.9727 | 4628.5732 | 12815.5857 | 104622.3871 | 16893.4652 | 0.08306 | -130446.86 | 130446.86
C | Xist Rating 2331 | -60.56 | 848.879 | 150.281 | 35.6 | 2203.44 | 9310.53 | 13638.9 | 0.45 | 1.73 | 14.099 | 15.564 | 1 | 1 | 2190 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1870453.9438 | 118458.7997 | 4671.1346 | 12874.3728 | 105584.4269 | 16786.0084 | 0.083441 | -129617.1073 | 129617.1073
C | Xist Rating 2332 | -60.36 | 854.952 | 150.281 | 35.6 | 2199.68 | 9275.42 | 13579.4 | 0.44 | 1.72 | 14.094 | 15.464 | 1 | 1 | 2200 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1880620.8154 | 119484.0296 | 4713.8907 | 12933.1599 | 106550.8697 | 16670.8819 | 0.083822 | -128728.131 | 128728.131
C | Xist Rating 2333 | -60.07 | 862.607 | 150.281 | 35.6 | 2196.96 | 9272.36 | 13495.4 | 0.44 | 1.7 | 14.091 | 15.309 | 1 | 1 | 2210 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1895113.0747 | 120513.6624 | 4756.8417 | 12991.9469 | 107521.7155 | 16512.5636 | 0.084203 | -127505.6392 | 127505.6392
C | Xist Rating 2334 | -59.26 | 884.239 | 150.281 | 35.6 | 2187.82 | 9246.82 | 13246.2 | 0.44 | 1.66 | 14.129 | 14.827 | 1 | 1 | 2220 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1934555.769 | 121547.6982 | 4799.9874 | 13050.734 | 108496.9641 | 16016.4503 | 0.084584 | -123674.784 | 123674.784
C | Xist Rating 2335 | -59.02 | 890.391 | 150.281 | 35.6 | 2186.56 | 9260.14 | 13182.5 | 0.43 | 1.65 | 14.126 | 14.716 | 1 | 1 | 2230 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1946893.345 | 122586.1368 | 4843.3279 | 13109.5211 | 109476.6157 | 15889.7115 | 0.084965 | -122696.1404 | 122696.1404
C | Xist Rating 2336 | -58.77 | 897.699 | 150.281 | 35.6 | 2182.85 | 9233.96 | 13111.7 | 0.43 | 1.64 | 14.123 | 14.595 | 1 | 1 | 2240 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1959542.2621 | 123628.9785 | 4886.8633 | 13168.3082 | 110460.6702 | 15766.6464 | 0.085346 | -121745.8642 | 121745.8642
C | Xist Rating 2337 | -58.48 | 905.661 | 150.281 | 35.6 | 2179.39 | 9216.48 | 13034.1 | 0.42 | 1.63 | 14.126 | 14.462 | 1 | 1 | 2250 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1973788.5268 | 124676.223 | 4930.5934 | 13227.0953 | 111449.1277 | 15617.1315 | 0.085727 | -120591.35 | 120591.35
C | Xist Rating 2338 | -58.32 | 909.79 | 150.281 | 35.6 | 2178.79 | 9228.1 | 12995.6 | 0.42 | 1.62 | 14.122 | 14.401 | 1 | 1 | 2260 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 1982241.3541 | 125727.8705 | 4974.5182 | 13285.8824 | 112441.9881 | 15556.2723 | 0.086108 | -120121.4115 | 120121.4115
C | Xist Rating 2339 | -57.48 | 933.21 | 150.281 | 35.6 | 2168 | 9177.95 | 12751.9 | 0.42 | 1.59 | 14.158 | 13.955 | 1 | 1 | 2270 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2023199.28 | 126783.9209 | 5018.6379 | 13344.6695 | 113439.2514 | 15097.2992 | 0.086489 | -116577.3425 | 116577.3425
C | Xist Rating 2340 | -57.23 | 940.463 | 150.281 | 35.6 | 2165.02 | 9163.82 | 12686.2 | 0.41 | 1.58 | 14.155 | 13.847 | 1 | 1 | 2280 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2036121.2043 | 127844.3742 | 5062.9524 | 13403.4566 | 114440.9176 | 14973.2116 | 0.08687 | -115619.1709 | 115619.1709
C | Xist Rating 2341 | -56.92 | 948.875 | 150.281 | 35.6 | 2161.93 | 9156.27 | 12606.9 | 0.41 | 1.56 | 14.15 | 13.713 | 1 | 1 | 2290 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2051401.3287 | 128909.2304 | 5107.4617 | 13462.2437 | 115446.9868 | 14836.4438 | 0.087251 | -114563.0863 | 114563.0863
C | Xist Rating 2342 | -56.72 | 954.705 | 150.281 | 35.6 | 2159.73 | 9147.06 | 12557.1 | 0.4 | 1.56 | 14.146 | 13.636 | 1 | 1 | 2300 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2061905.0297 | 129978.4896 | 5152.1657 | 13521.0308 | 116457.4589 | 14744.3268 | 0.087632 | -113851.7831 | 113851.7831
| Xist Rating 2343 | -56.53 | 960.801 | 150.281 | 35.6 | 2156.49 | 9119.26 | 12507.7 | 0.4 | 1.55 | 14.143 | 13.562 | 1 | 1 | 2310 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2071957.7485 | 131052.1517 | 5197.0645 | 13579.8178 | 117472.3339 | 14669.89 | 0.088013 | -113277.002 | 113277.002
| Xist Rating 2344 | -55.66 | 984.761 | 150.281 | 35.6 | 2147.15 | 9095.14 | 12277.2 | 0.4 | 1.51 | 14.182 | 13.158 | 1 | 1 | 2320 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2114429.5811 | 132130.2168 | 5242.1582 | 13638.6049 | 118491.6118 | 14254.4948 | 0.088394 | -110069.43 | 110069.43
| Xist Rating 2345 | -55.41 | 992.046 | 150.281 | 35.6 | 2144.16 | 9079.62 | 12216.9 | 0.39 | 1.5 | 14.176 | 13.064 | 1 | 1 | 2330 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2127105.3514 | 133212.6847 | 5287.4466 | 13697.392 | 119515.2927 | 14144.3624 | 0.088775 | -109219.0175 | 109219.0175
| Xist Rating 2346 | -55.17 | 999.307 | 150.281 | 35.6 | 2141.24 | 9065.3 | 12157.2 | 0.39 | 1.49 | 14.171 | 12.972 | 1 | 1 | 2340 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2139756.1207 | 134299.5556 | 5332.9298 | 13756.1791 | 120543.3765 | 14051.0942 | 0.089156 | -108498.8252 | 108498.8252
| Xist Rating 2347 | -54.95 | 1005.96 | 150.281 | 35.6 | 2138.39 | 9048.06 | 12104.8 | 0.38 | 1.49 | 14.166 | 12.894 | 1 | 1 | 2350 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2151134.8044 | 135390.8295 | 5378.6078 | 13814.9662 | 121575.8632 | 13957.4411 | 0.089537 | -107775.6605 | 107775.6605
| Xist Rating 2348 | -54.68 | 1013.97 | 150.281 | 35.6 | 2135.09 | 9030.64 | 12039.9 | 0.38 | 1.48 | 14.162 | 12.793 | 1 | 1 | 2360 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2164917.2073 | 136486.5062 | 5424.4805 | 13873.7533 | 122612.7529 | 13854.8049 | 0.089918 | -106983.1311 | 106983.1311
| Xist Rating 2349 | -53.89 | 1036.03 | 150.282 | 35.6 | 2126.9 | 9010.63 | 11846.8 | 0.38 | 1.45 | 14.197 | 12.473 | 1 | 1 | 2370 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2203532.207 | 137586.5859 | 5470.5481 | 13932.5404 | 123654.0455 | 13526.3106 | 0.090299 | -104446.5851 | 104446.5851
| Xist Rating 2350 | -53.65 | 1043.53 | 150.281 | 35.6 | 2123.58 | 8988.32 | 11791.2 | 0.37 | 1.44 | 14.191 | 12.392 | 1 | 1 | 2380 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2216019.4374 | 138691.0685 | 5516.8105 | 13991.3275 | 124699.741 | 13429.2279 | 0.09068 | -103696.938 | 103696.938
| Xist Rating 2351 | -53.38 | 1051.1 | 150.281 | 35.6 | 2121.63 | 8994.41 | 11730 | 0.37 | 1.43 | 14.186 | 12.298 | 1 | 1 | 2390 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2230045.293 | 139799.954 | 5563.2676 | 14050.1146 | 125749.8395 | 13333.7644 | 0.091061 | -102959.7946 | 102959.7946
C | Xist Rating 2352 | -48.79 | 1205.36 | 150.282 | 35.6 | 2033.64 | 8299.87 | 10538.2 | 0.4 | 1.25 | 14.183 | 10.444 | 1 | 1 | 2400 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2451268.3104 | 140913.2425 | 5609.9196 | 14108.9017 | 126804.3408 | 11456.3956 | 0.091442 | -88463.2499 | 88463.2499
C | Xist Rating 2353 | -48.31 | 1206.8 | 150.282 | 35.6 | 2050.37 | 8586.01 | 10538.1 | 0.39 | 1.25 | 14.179 | 10.454 | 1 | 1 | 2410 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2474386.516 | 142030.9339 | 5656.7663 | 14167.6887 | 127863.2451 | 11453.8335 | 0.091823 | -88443.4662 | 88443.4662
C | Xist Rating 2354 | -48.33 | 1208.2 | 150.282 | 35.6 | 2048.58 | 8554.72 | 10538 | 0.39 | 1.25 | 14.218 | 10.465 | 1 | 1 | 2420 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2475094.356 | 143153.0282 | 5703.8078 | 14226.4758 | 128926.5524 | 11469.3856 | 0.092204 | -88563.5556 | 88563.5556
C | Xist Rating 2355 | -47.85 | 1209.56 | 150.282 | 35.6 | 2065.58 | 8859.19 | 10538 | 0.39 | 1.25 | 14.215 | 10.474 | 1 | 1 | 2430 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2498442.9448 | 144279.5255 | 5751.0441 | 14285.2629 | 129994.2625 | 11481.0902 | 0.092585 | -88653.9352 | 88653.9352
C | Xist Rating 2356 | -47.84 | 1210.93 | 150.282 | 35.6 | 2064.53 | 8839.98 | 10537.9 | 0.38 | 1.25 | 14.206 | 10.485 | 1 | 1 | 2440 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2500001.3129 | 145410.4256 | 5798.4752 | 14344.05 | 131066.3756 | 11479.0774 | 0.092966 | -88638.3928 | 88638.3928
C | Xist Rating 2357 | -47.82 | 1212.26 | 150.282 | 35.6 | 2063.9 | 8828.41 | 10537.9 | 0.38 | 1.25 | 14.202 | 10.495 | 1 | 1 | 2450 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2501983.414 | 146545.7288 | 5846.1011 | 14402.8371 | 132142.8917 | 11491.7152 | 0.093347 | -88735.9787 | 88735.9787
C | Xist Rating 2358 | -47.8 | 1213.73 | 150.282 | 35.6 | 2063 | 8811.92 | 10537.9 | 0.37 | 1.25 | 14.198 | 10.506 | 1 | 1 | 2460 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2503924.99 | 147685.4348 | 5893.9217 | 14461.6242 | 133223.8106 | 11489.7342 | 0.093728 | -88720.6821 | 88720.6821
C | Xist Rating 2359 | -47.78 | 1215.08 | 150.282 | 35.6 | 2062.41 | 8801.23 | 10537.9 | 0.36 | 1.25 | 14.234 | 10.517 | 1 | 1 | 2470 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2505993.1428 | 148829.5438 | 5941.9372 | 14520.4113 | 134309.1325 | 11489.2278 | 0.094109 | -88716.7713 | 88716.7713
C | Xist Rating 2360 | -47.76 | 1216.43 | 150.282 | 35.6 | 2061.68 | 8787.9 | 10537.9 | 0.36 | 1.25 | 14.228 | 10.528 | 1 | 1 | 2480 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2507889.4024 | 149978.0557 | 5990.1474 | 14579.1984 | 135398.8573 | 11502.7081 | 0.09449 | -88820.8626 | 88820.8626
C | Xist Rating 2361 | -47.75 | 1217.83 | 150.282 | 35.6 | 2060.85 | 8772.9 | 10537.9 | 0.35 | 1.25 | 14.223 | 10.538 | 1 | 1 | 2490 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2509764.9555 | 151130.9705 | 6038.5525 | 14637.9855 | 136492.985 | 11499.3133 | 0.094871 | -88794.6493 | 88794.6493
C | Xist Rating 2362 | -47.73 | 1218.81 | 150.282 | 35.6 | 2060.85 | 8772.89 | 10537.9 | 0.35 | 1.25 | 14.218 | 10.547 | 1 | 1 | 2500 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2511784.5885 | 152288.2882 | 6087.1523 | 14696.7726 | 137591.5157 | 11510.6951 | 0.095252 | -88882.5363 | 88882.5363
C | Xist Rating 2363 | -47.69 | 1220.66 | 150.282 | 35.6 | 2060.06 | 8758.71 | 10537.8 | 0.34 | 1.25 | 14.213 | 10.56 | 1 | 1 | 2510 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2514632.8396 | 153450.0089 | 6135.9469 | 14755.5596 | 138694.4493 | 11510.2383 | 0.095633 | -88879.0088 | 88879.0088
C | Xist Rating 2364 | -47.67 | 1222.12 | 150.282 | 35.6 | 2059.5 | 8748.55 | 10537.8 | 0.34 | 1.25 | 14.25 | 10.57 | 1 | 1 | 2520 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2516956.14 | 154616.1325 | 6184.9363 | 14814.3467 | 139801.7858 | 11524.2104 | 0.096014 | -88986.8977 | 88986.8977
C | Xist Rating 2365 | -47.65 | 1223.46 | 150.282 | 35.6 | 2058.99 | 8739.34 | 10537.8 | 0.33 | 1.25 | 14.244 | 10.581 | 1 | 1 | 2530 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2519091.9054 | 155786.6591 | 6234.1205 | 14873.1338 | 140913.5252 | 11521.4207 | 0.096395 | -88965.3563 | 88965.3563
C | Xist Rating 2366 | -47.62 | 1224.61 | 150.282 | 35.6 | 2059.08 | 8741.05 | 10537.8 | 0.33 | 1.25 | 14.251 | 10.59 | 1 | 1 | 2540 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2521569.9588 | 156961.5885 | 6283.4995 | 14931.9209 | 142029.6676 | 11533.1371 | 0.096776 | -89055.8279 | 89055.8279
C | Xist Rating 2367 | -47.6 | 1226.15 | 150.282 | 35.6 | 2058.16 | 8724.49 | 10537.7 | 0.32 | 1.25 | 14.247 | 10.601 | 1 | 1 | 2550 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2523612.884 | 158140.9209 | 6333.0732 | 14990.708 | 143150.2129 | 11530.233 | 0.097157 | -89033.4032 | 89033.4032
C | Xist Rating 2368 | -47.59 | 1227.6 | 150.282 | 35.6 | 2057.36 | 8710.19 | 10537.7 | 0.32 | 1.25 | 14.243 | 10.612 | 1 | 1 | 2560 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2525615.136 | 159324.6562 | 6382.8418 | 15049.4951 | 144275.1611 | 11543.5532 | 0.097538 | -89136.2581 | 89136.2581
C | Xist Rating 2369 | -47.57 | 1228.99 | 150.282 | 35.6 | 2056.69 | 8698.17 | 10537.7 | 0.31 | 1.25 | 14.24 | 10.622 | 1 | 1 | 2570 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2527651.4431 | 160512.7945 | 6432.8051 | 15108.2822 | 145404.5123 | 11539.4662 | 0.097919 | -89104.6994 | 89104.6994
C | Xist Rating 2370 | -47.54 | 1230.36 | 150.282 | 35.6 | 2056.36 | 8692.24 | 10537.7 | 0.31 | 1.25 | 14.276 | 10.632 | 1 | 1 | 2580 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2530063.0896 | 161705.3357 | 6482.9633 | 15167.0693 | 146538.2664 | 11553.1206 | 0.0983 | -89210.1346 | 89210.1346
C | Xist Rating 2371 | -47.52 | 1231.72 | 150.282 | 35.6 | 2055.78 | 8681.79 | 10537.8 | 0.3 | 1.25 | 14.271 | 10.642 | 1 | 1 | 2590 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2532145.3416 | 162902.2798 | 6533.3162 | 15225.8564 | 147676.4234 | 11548.7413 | 0.098681 | -89176.3192 | 89176.3192
C | Xist Rating 2372 | -47.49 | 1232.89 | 150.282 | 35.6 | 2055.75 | 8681.32 | 10537.8 | 0.3 | 1.25 | 14.269 | 10.652 | 1 | 1 | 2600 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2534513.6175 | 164103.6268 | 6583.8639 | 15284.6435 | 148818.9834 | 11560.9754 | 0.099062 | -89270.7879 | 89270.7879
C | Xist Rating 2373 | -47.48 | 1234.58 | 150.282 | 35.6 | 2054.4 | 8657.24 | 10537.8 | 0.3 | 1.25 | 14.267 | 10.663 | 1 | 1 | 2610 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2536321.152 | 165309.3768 | 6634.6064 | 15343.4305 | 149965.9462 | 11574.2475 | 0.099443 | -89373.2715 | 89373.2715
C | Xist Rating 2374 | -47.47 | 1235.98 | 150.282 | 35.6 | 2053.3 | 8637.76 | 10537.8 | 0.29 | 1.25 | 14.262 | 10.673 | 1 | 1 | 2620 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2537837.734 | 166519.5297 | 6685.5437 | 15402.2176 | 151117.312 | 11569.6255 | 0.099824 | -89337.5816 | 89337.5816
C | Xist Rating 2375 | -47.43 | 1237.4 | 150.282 | 35.6 | 2053.08 | 8633.9 | 10537.8 | 0.29 | 1.25 | 14.3 | 10.684 | 1 | 1 | 2630 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2540481.192 | 167734.0855 | 6736.6758 | 15461.0047 | 152273.0808 | 11584.2021 | 0.10021 | -89450.1379 | 89450.1379
C | Xist Rating 2376 | -47.4 | 1238.65 | 150.282 | 35.6 | 2053.26 | 8637.14 | 10537.7 | 0.28 | 1.25 | 14.295 | 10.693 | 1 | 1 | 2640 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2543270.499 | 168953.0442 | 6788.0027 | 15519.7918 | 153433.2524 | 11578.3196 | 0.10059 | -89404.7147 | 89404.7147
C | Xist Rating 2377 | -47.38 | 1240.15 | 150.282 | 35.6 | 2052.45 | 8622.87 | 10537.7 | 0.28 | 1.25 | 14.291 | 10.704 | 1 | 1 | 2650 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2545345.8675 | 170176.4059 | 6839.5243 | 15578.5789 | 154597.827 | 11591.4042 | 0.10097 | -89505.7504 | 89505.7504
C | Xist Rating 2378 | -47.36 | 1241.49 | 150.282 | 35.6 | 2052.15 | 8617.53 | 10537.7 | 0.28 | 1.25 | 14.289 | 10.713 | 1 | 1 | 2660 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2547723.7035 | 171404.1705 | 6891.2408 | 15637.366 | 155766.8045 | 11602.4775 | 0.10135 | -89591.256 | 89591.256
C | Xist Rating 2379 | -47.34 | 1242.88 | 150.282 | 35.6 | 2051.23 | 8601.27 | 10537.7 | 0.27 | 1.25 | 14.287 | 10.723 | 1 | 1 | 2670 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2549432.7424 | 172636.3381 | 6943.152 | 15696.1531 | 156940.185 | 11597.49 | 0.10173 | -89552.7433 | 89552.7433
C | Xist Rating 2380 | -47.31 | 1244.3 | 150.282 | 35.6 | 2051.14 | 8599.84 | 10537.6 | 0.27 | 1.25 | 14.322 | 10.733 | 1 | 1 | 2680 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2552233.502 | 173872.9085 | 6995.258 | 15754.9402 | 158117.9683 | 11610.7393 | 0.10211 | -89655.051 | 89655.051
C | Xist Rating 2381 | -47.24 | 1245.68 | 150.282 | 35.6 | 2052.23 | 8618.96 | 10537.6 | 0.27 | 1.25 | 14.317 | 10.743 | 1 | 1 | 2690 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2556421.8664 | 175113.8819 | 7047.5588 | 15813.7273 | 159300.1546 | 11622.6948 | 0.10249 | -89747.3685 | 89747.3685
C | Xist Rating 2382 | -47.23 | 1246.88 | 150.282 | 35.6 | 2051.6 | 8607.79 | 10537.6 | 0.26 | 1.25 | 14.309 | 10.752 | 1 | 1 | 2700 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2558099.008 | 176359.2582 | 7100.0544 | 15872.5144 | 160486.7439 | 11616.1949 | 0.10287 | -89697.1782 | 89697.1782
C | Xist Rating 2383 | -47.2 | 1248.53 | 150.282 | 35.6 | 2050.8 | 8593.89 | 10537.7 | 0.26 | 1.25 | 14.308 | 10.763 | 1 | 1 | 2710 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2560485.324 | 177609.0375 | 7152.7448 | 15931.3015 | 161677.736 | 11629.2545 | 0.10325 | -89798.0204 | 89798.0204
C | Xist Rating 2384 | -47.2 | 1249.88 | 150.282 | 35.6 | 2049.59 | 8572.7 | 10537.6 | 0.26 | 1.25 | 14.302 | 10.773 | 1 | 1 | 2720 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2561741.5492 | 178863.2197 | 7205.63 | 15990.0885 | 162873.1311 | 11641.1168 | 0.10363 | -89889.6179 | 89889.6179
C | Xist Rating 2385 | -47.16 | 1251.2 | 150.282 | 35.6 | 2049.81 | 8576.48 | 10537.7 | 0.25 | 1.25 | 14.341 | 10.782 | 1 | 1 | 2730 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2564722.272 | 180121.8048 | 7258.71 | 16048.8756 | 164072.9291 | 11635.8216 | 0.10402 | -89848.7304 | 89848.7304
C | Xist Rating 2386 | -47.18 | 1252.48 | 150.282 | 35.6 | 2048.21 | 8548.6 | 10537.6 | 0.25 | 1.25 | 14.335 | 10.791 | 1 | 1 | 2740 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2565342.0608 | 181384.7928 | 7311.9847 | 16107.6627 | 165277.1301 | 11646.591 | 0.1044 | -89931.8883 | 89931.8883
C | Xist Rating 2387 | -47.12 | 1254.03 | 150.282 | 35.6 | 2048.33 | 8550.48 | 10537.8 | 0.25 | 1.25 | 14.338 | 10.802 | 1 | 1 | 2750 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2568667.2699 | 182652.1838 | 7365.4543 | 16166.4498 | 166485.734 | 11659.7133 | 0.10478 | -90033.2155 | 90033.2155
C | Xist Rating 2388 | -47.06 | 1255.45 | 150.282 | 35.6 | 2049.18 | 8565.27 | 10537.8 | 0.24 | 1.25 | 14.34 | 10.812 | 1 | 1 | 2760 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2572643.031 | 183923.9777 | 7419.1186 | 16225.2369 | 167698.7408 | 11654.026 | 0.10516 | -89989.2997 | 89989.2997
C | Xist Rating 2389 | -47.02 | 1256.69 | 150.282 | 35.6 | 2049.69 | 8574.22 | 10537.9 | 0.24 | 1.25 | 14.339 | 10.821 | 1 | 1 | 2770 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2575824.9261 | 185200.1745 | 7472.9777 | 16284.024 | 168916.1505 | 11664.8854 | 0.10554 | -90073.1529 | 90073.1529
C | Xist Rating 2390 | -46.85 | 1258.24 | 150.282 | 35.6 | 2054.55 | 8659.66 | 10538.1 | 0.24 | 1.25 | 14.397 | 10.832 | 1 | 1 | 2780 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2585116.992 | 186480.7742 | 7527.0316 | 16342.8111 | 170137.9632 | 11679.586 | 0.10592 | -90186.6675 | 90186.6675
C | Xist Rating 2391 | -46.99 | 1259.65 | 150.282 | 35.6 | 2047.52 | 8536.27 | 10537.9 | 0.23 | 1.25 | 14.371 | 10.841 | 1 | 1 | 2790 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2579158.568 | 187765.7769 | 7581.2803 | 16401.5982 | 171364.1787 | 11671.7285 | 0.1063 | -90125.9935 | 90125.9935
C | Xist Rating 2392 | -46.54 | 1260.62 | 150.282 | 35.6 | 2064.83 | 8845.33 | 10538.2 | 0.23 | 1.25 | 14.421 | 10.85 | 1 | 1 | 2800 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2602965.9946 | 189055.1825 | 7635.7238 | 16460.3853 | 172594.7973 | 11683.9999 | 0.10668 | -90220.7504 | 90220.7504
C | Xist Rating 2393 | -46.34 | 1262.36 | 150.282 | 35.6 | 2070.65 | 8952.93 | 10538.2 | 0.23 | 1.25 | 14.449 | 10.861 | 1 | 1 | 2810 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2613905.734 | 190348.9911 | 7690.3621 | 16519.1724 | 173829.8187 | 11697.7213 | 0.10706 | -90326.7034 | 90326.7034
C | Xist Rating 2394 | -46.06 | 1263.84 | 150.282 | 35.6 | 2080.15 | 9133.31 | 10538.2 | 0.22 | 1.25 | 14.485 | 10.872 | 1 | 1 | 2820 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2628976.776 | 191647.2025 | 7745.1952 | 16577.9594 | 175069.2431 | 11693.3713 | 0.10744 | -90293.1133 | 90293.1133
C | Xist Rating 2395 | -45.89 | 1265.21 | 150.282 | 35.6 | 2085.36 | 9234.64 | 10538.2 | 0.22 | 1.25 | 14.551 | 10.882 | 1 | 1 | 2830 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2638418.3256 | 192949.8169 | 7800.223 | 16636.7465 | 176313.0704 | 11707.0266 | 0.10783 | -90398.5561 | 90398.5561
C | Xist Rating 2396 | -45.77 | 1266.53 | 150.282 | 35.6 | 2088.7 | 9300.52 | 10538.2 | 0.22 | 1.25 | 14.566 | 10.891 | 1 | 1 | 2840 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2645401.211 | 194256.8342 | 7855.4457 | 16695.5336 | 177561.3006 | 11718.2281 | 0.10821 | -90485.0513 | 90485.0513
C | Xist Rating 2397 | -45.66 | 1267.97 | 150.282 | 35.6 | 2091.55 | 9357.2 | 10538.2 | 0.21 | 1.25 | 14.579 | 10.901 | 1 | 1 | 2850 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2652022.6535 | 195568.2545 | 7910.8631 | 16754.3207 | 178813.9338 | 11711.7902 | 0.10859 | -90435.3392 | 90435.3392
C | Xist Rating 2398 | -45.57 | 1269.38 | 150.282 | 35.6 | 2093.45 | 9395.4 | 10538.2 | 0.21 | 1.25 | 14.582 | 10.91 | 1 | 1 | 2860 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2657383.561 | 196884.0777 | 7966.4753 | 16813.1078 | 180070.9699 | 11722.5898 | 0.10897 | -90518.7308 | 90518.7308
C | Xist Rating 2399 | -45.47 | 1270.57 | 150.282 | 35.6 | 2096.16 | 9450.41 | 10538.2 | 0.21 | 1.25 | 14.587 | 10.919 | 1 | 1 | 2870 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2663318.0112 | 198204.3038 | 8022.2824 | 16871.8949 | 181332.4089 | 11733.444 | 0.10935 | -90602.544 | 90602.544
C | Xist Rating 2400 | -45.4 | 1272.08 | 150.282 | 35.6 | 2097.28 | 9473.11 | 10538.2 | 0.2 | 1.25 | 14.63 | 10.929 | 1 | 1 | 2880 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2667907.9424 | 199528.9328 | 8078.2842 | 16930.682 | 182598.2508 | 11727.4812 | 0.10973 | -90556.501 | 90556.501
C | Xist Rating 2401 | -45.3 | 1273.42 | 150.282 | 35.5 | 2099.89 | 9526.68 | 10538.1 | 0.2 | 1.25 | 14.63 | 10.938 | 1 | 1 | 2890 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2674041.9238 | 200857.9648 | 8134.4807 | 16989.4691 | 183868.4957 | 11738.1392 | 0.11011 | -90638.7996 | 90638.7996
C | Xist Rating 2402 | -45.25 | 1274.81 | 150.282 | 35.5 | 2100.45 | 9538.26 | 10538.1 | 0.2 | 1.25 | 14.631 | 10.948 | 1 | 1 | 2900 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2677674.6645 | 202191.3997 | 8190.8721 | 17048.2562 | 185143.1435 | 11749.8618 | 0.11049 | -90729.3181 | 90729.3181
C | Xist Rating 2403 | -45.18 | 1276.35 | 150.282 | 35.5 | 2101.67 | 9563.51 | 10538.1 | 0.2 | 1.25 | 14.634 | 10.958 | 1 | 1 | 2910 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2682466.5045 | 203529.2375 | 8247.4583 | 17107.0433 | 186422.1942 | 11761.6367 | 0.11087 | -90820.2408 | 90820.2408
C | Xist Rating 2404 | -45.1 | 1277.74 | 150.282 | 35.5 | 2103.23 | 9595.95 | 10538 | 0.2 | 1.25 | 14.64 | 10.967 | 1 | 1 | 2920 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2687381.1002 | 204871.4782 | 8304.2393 | 17165.8303 | 187705.6479 | 11772.4522 | 0.11125 | -90903.755 | 90903.755
C | Xist Rating 2405 | -44.88 | 1279.12 | 150.282 | 35.5 | 2110.42 | 9747.54 | 10537.9 | 0.19 | 1.25 | 14.688 | 10.977 | 1 | 1 | 2930 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2699480.4304 | 206218.1219 | 8361.215 | 17224.6174 | 188993.5045 | 11766.1198 | 0.11164 | -90854.858 | 90854.858
C | Xist Rating 2406 | -44.87 | 1280.49 | 150.282 | 35.5 | 2109.28 | 9723.27 | 10537.9 | 0.19 | 1.25 | 14.686 | 10.986 | 1 | 1 | 2940 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2700911.9472 | 207569.1685 | 8418.3855 | 17283.4045 | 190285.764 | 11776.6671 | 0.11202 | -90936.3018 | 90936.3018
C | Xist Rating 2407 | -44.85 | 1281.9 | 150.282 | 35.5 | 2108.59 | 9708.58 | 10537.9 | 0.19 | 1.25 | 14.683 | 10.995 | 1 | 1 | 2950 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 11 | E | Rod | 2703001.521 | 208924.618 | 8475.7509 | 17342.1916 | 191582.4264 | 11787.189 | 0.1124 | -91017.5489 | 91017.5489
C | Xist Rating 2408 | -44.83 | 1283.27 | 150.282 | 35.5 | 2107.93 | 9694.52 | 10537.9 | 0.19 | 1.25 | 14.678 | 11.004 | 1 | 1 | 2960 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 10 | E | Rod | 2705043.3311 | 210284.4705 | 8533.311 | 17400.9787 | 192883.4918 | 11797.6599 | 0.11278 | -91098.4027 | 91098.4027
C | Xist Rating 2409 | -44.81 | 1284.65 | 150.282 | 35.5 | 2107.28 | 9680.8 | 10537.9 | 0.18 | 1.25 | 14.675 | 11.013 | 1 | 1 | 2970 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 10 | E | Rod | 2707117.252 | 211648.7259 | 8591.0659 | 17459.7658 | 194188.9601 | 11788.6439 | 0.11316 | -91028.7833 | 91028.7833
C | Xist Rating 2410 | -44.79 | 1285.88 | 150.282 | 35.5 | 2106.71 | 9668.77 | 10537.9 | 0.18 | 1.25 | 14.711 | 11.021 | 1 | 1 | 2980 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 10 | E | Rod | 2708976.2548 | 213017.3842 | 8649.0156 | 17518.5529 | 195498.8313 | 11799.0015 | 0.11354 | -91108.7621 | 91108.7621
C | Xist Rating 2411 | -44.77 | 1287.43 | 150.282 | 35.5 | 2106 | 9653.94 | 10537.9 | 0.18 | 1.25 | 14.707 | 11.031 | 1 | 1 | 2990 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 10 | E | Rod | 2711327.58 | 214390.4455 | 8707.16 | 17577.34 | 196813.1055 | 11810.4769 | 0.11392 | -91197.3723 | 91197.3723
C | Xist Rating 2412 | -44.75 | 1288.87 | 150.282 | 35.5 | 2105.36 | 9640.42 | 10537.9 | 0.18 | 1.25 | 14.702 | 11.04 | 1 | 1 | 3000 | 152.4 | 2 | 2.1 | 19.05 | 1.3333 | 10 | E | Rod | 2713535.3432 | 215767.9096 | 8765.4993 | 17636.1271 | 198131.7826 | 11820.889 | 0.1143 | -91277.7717 | 91277.7717
C | Xist Rating 2413 | -93.49 | 120.215 | 150.285 | 35.8 | 2405.32 | 7458.58 | 58746.1 | 2.44 | 10.95 | 15.418 | 376.957 | 1 | 1 | 1000 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 289155.5438 | 29221.6064 | 973.9444 | 6158.6475 | 23062.9588 | 393155.5482 | 0.038101 | -3035842.9295 | 3035842.9295
C | Xist Rating 2414 | -93.43 | 121.492 | 150.285 | 35.8 | 2402.46 | 7439.76 | 58284.3 | 2.42 | 10.85 | 15.438 | 369.922 | 1 | 1 | 1010 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 291879.6703 | 29746.7583 | 993.5206 | 6220.234 | 23526.5243 | 385854.8057 | 0.038482 | -2979468.5309 | 2979468.5309
C | Xist Rating 2415 | -92.94 | 131.008 | 150.285 | 35.8 | 2396.85 | 7451.71 | 54967.8 | 2.43 | 10.07 | 15.491 | 320.57 | 1 | 1 | 1020 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 314006.5248 | 30276.5229 | 1013.2917 | 6281.8205 | 23994.7024 | 334632.5251 | 0.038863 | -2583943.6574 | 2583943.6574
C | Xist Rating 2416 | -92.86 | 133.706 | 150.284 | 35.8 | 2376.55 | 7275.05 | 54178.4 | 2.35 | 9.89 | 15.205 | 309.942 | 1 | 1 | 1030 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 317758.9943 | 30810.9 | 1033.2576 | 6343.407 | 24467.493 | 323523.99 | 0.039244 | -2498166.4943 | 2498166.4943
C | Xist Rating 2417 | -92.78 | 135.058 | 150.284 | 35.8 | 2380.66 | 7321.8 | 53794.7 | 2.3 | 9.8 | 15.143 | 304.873 | 1 | 1 | 1040 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 321527.1783 | 31349.8897 | 1053.4182 | 6404.9934 | 24944.8963 | 318233.7695 | 0.039625 | -2457316.8132 | 2457316.8132
C | Xist Rating 2418 | -92.62 | 137.635 | 150.284 | 35.8 | 2388.78 | 7415.72 | 53044 | 2.25 | 9.63 | 15.107 | 294.834 | 1 | 1 | 1050 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 328779.7353 | 31893.492 | 1073.7737 | 6466.5799 | 25426.9121 | 307784.4475 | 0.040006 | -2376629.9188 | 2376629.9188
C | Xist Rating 2419 | -92.51 | 138.966 | 150.284 | 35.8 | 2402.65 | 7559.68 | 52678.1 | 2.2 | 9.54 | 15.096 | 290.115 | 1 | 1 | 1060 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 333886.6599 | 32441.7069 | 1094.3239 | 6528.1664 | 25913.5405 | 302861.97 | 0.040387 | -2338619.8528 | 2338619.8528
C | Xist Rating 2420 | -92.03 | 149.276 | 150.284 | 35.8 | 2381.35 | 7420.18 | 49857.9 | 2.18 | 8.9 | 15.011 | 253.89 | 1 | 1 | 1070 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 355478.4026 | 32994.5344 | 1115.0689 | 6589.7529 | 26404.7816 | 265233.8834 | 0.040768 | -2048065.7418 | 2048065.7418
C | Xist Rating 2421 | -91.9 | 151.277 | 150.283 | 35.8 | 2388.17 | 7499.22 | 49381.4 | 2.13 | 8.79 | 14.948 | 248.266 | 1 | 1 | 1080 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 361275.1931 | 33551.9745 | 1136.0087 | 6651.3394 | 26900.6352 | 259365.2059 | 0.041149 | -2002749.3697 | 2002749.3697
C | Xist Rating 2422 | -91.77 | 153.934 | 150.283 | 35.8 | 2386.93 | 7503.7 | 48761.3 | 2.08 | 8.65 | 14.852 | 241.022 | 1 | 1 | 1090 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 367429.6826 | 34114.0272 | 1157.1433 | 6712.9258 | 27401.1014 | 251810.3219 | 0.04153 | -1944412.5582 | 1944412.5582
C | Xist Rating 2423 | -91.65 | 155.903 | 150.283 | 35.8 | 2392.64 | 7573.04 | 48308.7 | 2.04 | 8.55 | 14.841 | 235.787 | 1 | 1 | 1100 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 373019.7539 | 34680.6925 | 1178.4727 | 6774.5123 | 27906.1802 | 246357.2312 | 0.041911 | -1902305.2369 | 1902305.2369
C | Xist Rating 2424 | -91.6 | 157.422 | 150.283 | 35.8 | 2385.96 | 7514.85 | 48010.8 | 1.97 | 8.49 | 14.658 | 232.647 | 1 | 1 | 1110 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 375602.5951 | 35251.9703 | 1199.9969 | 6836.0988 | 28415.8716 | 243040.2904 | 0.042292 | -1876692.6997 | 1876692.6997
C | Xist Rating 2425 | -91 | 168.833 | 150.283 | 35.8 | 2383.71 | 7569.22 | 45448 | 2.01 | 7.92 | 14.826 | 203.568 | 1 | 1 | 1120 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 402448.9104 | 35827.8608 | 1221.7158 | 6897.6853 | 28930.1755 | 212901.1267 | 0.042673 | -1643966.0666 | 1643966.0666
C | Xist Rating 2426 | -90.94 | 170.306 | 150.283 | 35.8 | 2381.57 | 7556.01 | 45188.9 | 1.95 | 7.86 | 14.707 | 201.027 | 1 | 1 | 1130 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 405595.6604 | 36408.3638 | 1243.6296 | 6959.2717 | 29449.0921 | 210218.8485 | 0.043054 | -1623254.225 | 1623254.225
C | Xist Rating 2427 | -90.81 | 173.034 | 150.283 | 35.8 | 2378.27 | 7539.28 | 44681.9 | 1.89 | 7.75 | 14.604 | 195.856 | 1 | 1 | 1140 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 411521.5712 | 36993.4795 | 1265.7381 | 7020.8582 | 29972.6213 | 204806.5888 | 0.043435 | -1581462.1908 | 1581462.1908
C | Xist Rating 2428 | -90.64 | 175.699 | 150.282 | 35.8 | 2386.73 | 7641.73 | 44187 | 1.85 | 7.64 | 14.511 | 190.833 | 1 | 1 | 1150 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 419346.0743 | 37583.2077 | 1288.0414 | 7082.4447 | 30500.763 | 199563.6022 | 0.043816 | -1540977.2378 | 1540977.2378
C | Xist Rating 2429 | -90.5 | 178.442 | 150.282 | 35.8 | 2385.94 | 7650.43 | 43704.3 | 1.79 | 7.53 | 14.424 | 186.071 | 1 | 1 | 1160 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 425751.9055 | 38177.5485 | 1310.5395 | 7144.0312 | 31033.5174 | 194576.9373 | 0.044197 | -1502471.5331 | 1502471.5331
C | Xist Rating 2430 | -89.96 | 188.738 | 150.282 | 35.8 | 2385.7 | 7717.38 | 41833.3 | 1.81 | 7.13 | 14.527 | 167.404 | 1 | 1 | 1170 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 450272.2466 | 38776.502 | 1333.2324 | 7205.6176 | 31570.8843 | 175227.7671 | 0.044578 | -1353062.3701 | 1353062.3701
C | Xist Rating 2431 | -89.89 | 189.567 | 150.282 | 35.8 | 2393.64 | 7805.42 | 41726.4 | 1.76 | 7.11 | 14.479 | 166.553 | 1 | 1 | 1180 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 453755.1539 | 39380.068 | 1356.1201 | 7267.2041 | 32112.8639 | 174312.9038 | 0.044959 | -1345998.038 | 1345998.038
C | Xist Rating 2432 | -89.66 | 194.882 | 150.282 | 35.8 | 2382.33 | 7720.07 | 40886.8 | 1.71 | 6.93 | 14.378 | 158.817 | 1 | 1 | 1190 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 464273.2351 | 39988.2466 | 1379.2026 | 7328.7906 | 32659.456 | 166242.6737 | 0.04534 | -1283681.8602 | 1283681.8602
C | Xist Rating 2433 | -89.54 | 196.248 | 150.282 | 35.8 | 2394.43 | 7857.22 | 40683.1 | 1.68 | 6.88 | 14.39 | 157.024 | 1 | 1 | 1200 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 469902.0986 | 40601.0378 | 1402.4799 | 7390.3771 | 33210.6607 | 164369.5496 | 0.045721 | -1269218.0923 | 1269218.0923
C | Xist Rating 2434 | -89.42 | 199.06 | 150.282 | 35.8 | 2389.55 | 7822.18 | 40282.1 | 1.63 | 6.8 | 14.302 | 153.542 | 1 | 1 | 1210 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 475663.823 | 41218.4415 | 1425.9519 | 7451.9635 | 33766.478 | 160717.5305 | 0.046102 | -1241018.1694 | 1241018.1694
C | Xist Rating 2435 | -88.85 | 210.825 | 150.282 | 35.8 | 2377.74 | 7774.25 | 38538.7 | 1.64 | 6.43 | 14.328 | 138.134 | 1 | 1 | 1220 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 501287.0355 | 41840.4579 | 1449.6188 | 7513.55 | 34326.9079 | 144736.9496 | 0.046483 | -1117620.359 | 1117620.359
C | Xist Rating 2436 | -88.69 | 213.488 | 150.282 | 35.8 | 2383.56 | 7853.89 | 38184.2 | 1.61 | 6.35 | 14.325 | 135.205 | 1 | 1 | 1230 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 508861.4573 | 42467.0869 | 1473.4804 | 7575.1365 | 34891.9504 | 141681.7553 | 0.046864 | -1094028.9589 | 1094028.9589
C | Xist Rating 2437 | -88.56 | 216.291 | 150.282 | 35.8 | 2381.44 | 7847.92 | 37836.5 | 1.57 | 6.28 | 14.264 | 132.442 | 1 | 1 | 1240 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 515084.039 | 43098.3284 | 1497.5369 | 7636.723 | 35461.6055 | 138785.5503 | 0.047245 | -1071665.2311 | 1071665.2311
C | Xist Rating 2438 | -88.48 | 217.8 | 150.282 | 35.8 | 2382.96 | 7872.99 | 37665.3 | 1.53 | 6.24 | 14.219 | 131.162 | 1 | 1 | 1250 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 519008.688 | 43734.1826 | 1521.7881 | 7698.3094 | 36035.8732 | 137430.4839 | 0.047626 | -1061201.7676 | 1061201.7676
C | Xist Rating 2439 | -88.29 | 221.818 | 150.282 | 35.8 | 2380.56 | 7872.45 | 37162.2 | 1.51 | 6.14 | 14.189 | 127.138 | 1 | 1 | 1260 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 528051.0581 | 44374.6493 | 1546.2341 | 7759.8959 | 36614.7534 | 133242.6978 | 0.048007 | -1028864.794 | 1028864.794
C | Xist Rating 2440 | -87.74 | 232.97 | 150.282 | 35.8 | 2373.29 | 7866.86 | 35778.3 | 1.51 | 5.85 | 14.241 | 116.162 | 1 | 1 | 1270 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 552905.3713 | 45019.7287 | 1570.8749 | 7821.4824 | 37198.2463 | 121858.213 | 0.048388 | -940956.8197 | 940956.8197
C | Xist Rating 2441 | -87.61 | 235.841 | 150.281 | 35.8 | 2370.64 | 7854.65 | 35478 | 1.47 | 5.79 | 14.186 | 114.01 | 1 | 1 | 1280 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 559094.1082 | 45669.4206 | 1595.7105 | 7883.0689 | 37786.3517 | 119595.6812 | 0.048769 | -923486.1491 | 923486.1491
C | Xist Rating 2442 | -87.45 | 238.66 | 150.281 | 35.8 | 2374.16 | 7910.32 | 35183.4 | 1.43 | 5.73 | 14.179 | 111.902 | 1 | 1 | 1290 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 566617.0256 | 46323.7251 | 1620.7408 | 7944.6553 | 38379.0698 | 117382.4837 | 0.04915 | -906396.4243 | 906396.4243
C | Xist Rating 2443 | -87.21 | 242.656 | 150.281 | 35.8 | 2381.08 | 8013.64 | 34752.4 | 1.41 | 5.64 | 14.188 | 108.754 | 1 | 1 | 1300 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 577783.3485 | 46982.6422 | 1645.966 | 8006.2418 | 38976.4004 | 114106.594 | 0.049531 | -881100.8723 | 881100.8723
C | Xist Rating 2444 | -87.08 | 244.85 | 150.281 | 35.7 | 2386.33 | 8086.59 | 34541 | 1.37 | 5.59 | 14.157 | 107.316 | 1 | 1 | 1310 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 584292.9005 | 47646.1719 | 1671.3859 | 8067.8283 | 39578.3436 | 112586.3817 | 0.049912 | -869362.1958 | 869362.1958
C | Xist Rating 2445 | -86.52 | 256.099 | 150.281 | 35.7 | 2380.8 | 8099.82 | 33363.9 | 1.38 | 5.35 | 14.203 | 98.885 | 1 | 1 | 1320 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 609720.4992 | 48314.3142 | 1697.0007 | 8129.4148 | 40184.8994 | 103851.6278 | 0.050293 | -801914.7417 | 801914.7417
C | Xist Rating 2446 | -86.34 | 260.312 | 150.281 | 35.7 | 2375.65 | 8066.49 | 32980.8 | 1.34 | 5.28 | 14.117 | 96.356 | 1 | 1 | 1330 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 618410.2028 | 48987.0691 | 1722.8102 | 8191.0012 | 40796.0679 | 101193.3112 | 0.050674 | -781387.9261 | 781387.9261
C | Xist Rating 2447 | -86.13 | 264.424 | 150.281 | 35.7 | 2376.24 | 8099.41 | 32608 | 1.32 | 5.2 | 14.097 | 93.901 | 1 | 1 | 1340 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 628334.8858 | 49664.4366 | 1748.8145 | 8252.5877 | 41411.8489 | 98633.7325 | 0.051055 | -761623.5377 | 761623.5377
C | Xist Rating 2448 | -85.99 | 266.634 | 150.281 | 35.7 | 2380.28 | 8159.8 | 32424.9 | 1.29 | 5.16 | 14.072 | 92.766 | 1 | 1 | 1350 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 634663.5775 | 50346.4166 | 1775.0136 | 8314.1742 | 42032.2424 | 97435.8346 | 0.051436 | -752373.6873 | 752373.6873
C | Xist Rating 2449 | -85.84 | 267.946 | 150.281 | 35.7 | 2397.38 | 8373.57 | 32304.2 | 1.27 | 5.14 | 14.109 | 91.985 | 1 | 1 | 1360 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 642368.3815 | 51033.0093 | 1801.4075 | 8375.7607 | 42657.2486 | 96618.6119 | 0.051817 | -746063.31 | 746063.31
C | Xist Rating 2450 | -85.16 | 284.068 | 150.281 | 35.7 | 2369.35 | 8147.06 | 30903.6 | 1.27 | 4.86 | 14.09 | 82.978 | 1 | 1 | 1370 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 673056.5158 | 51724.2145 | 1827.9962 | 8437.3471 | 43286.8674 | 87271.4067 | 0.052198 | -673886.6691 | 673886.6691
C | Xist Rating 2451 | -85.09 | 285.641 | 150.281 | 35.7 | 2369.17 | 8153.65 | 30795.1 | 1.24 | 4.84 | 14.064 | 82.385 | 1 | 1 | 1380 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 676732.088 | 52420.0324 | 1854.7797 | 8498.9336 | 43921.0988 | 86635.4565 | 0.052579 | -668976.0303 | 668976.0303
C | Xist Rating 2452 | -84.91 | 289.185 | 150.281 | 35.7 | 2369.68 | 8181.47 | 30527.9 | 1.21 | 4.79 | 14.04 | 80.814 | 1 | 1 | 1390 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 685275.9108 | 53120.4628 | 1881.7579 | 8560.5201 | 44559.9427 | 84983.695 | 0.05296 | -656221.5657 | 656221.5657
C | Xist Rating 2453 | -84.73 | 292.726 | 150.281 | 35.7 | 2371.19 | 8221.48 | 30265.9 | 1.19 | 4.73 | 14.018 | 79.288 | 1 | 1 | 1400 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 694108.9639 | 53825.5058 | 1908.931 | 8622.1066 | 45203.3993 | 83387.297 | 0.053341 | -643894.6037 | 643894.6037
C | Xist Rating 2454 | -84.52 | 296.899 | 150.281 | 35.7 | 2370.78 | 8243.05 | 29958.1 | 1.17 | 4.67 | 14.002 | 77.498 | 1 | 1 | 1410 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 703882.2112 | 54535.1615 | 1936.2988 | 8683.693 | 45851.4684 | 81516.9595 | 0.053722 | -629452.3536 | 629452.3536
C | Xist Rating 2455 | -83.94 | 308.906 | 150.281 | 35.7 | 2365.91 | 8265.44 | 29052.4 | 1.18 | 4.49 | 14.057 | 72.165 | 1 | 1 | 1420 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 730843.7945 | 55249.4297 | 1963.8614 | 8745.2795 | 46504.1502 | 75999.0341 | 0.054103 | -586844.3965 | 586844.3965
C | Xist Rating 2456 | -83.85 | 311.357 | 150.281 | 35.7 | 2361.44 | 8224.17 | 28911.3 | 1.14 | 4.47 | 14.006 | 71.466 | 1 | 1 | 1430 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 735250.8741 | 55968.3105 | 1991.6188 | 8806.866 | 47161.4445 | 75240.7905 | 0.054484 | -580989.4398 | 580989.4398
C | Xist Rating 2457 | -83.58 | 316.841 | 150.281 | 35.7 | 2360.72 | 8250.31 | 28542.6 | 1.13 | 4.39 | 13.994 | 69.436 | 1 | 1 | 1440 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 747972.8855 | 56691.8039 | 2019.571 | 8868.4525 | 47823.3514 | 73129.88 | 0.054865 | -564689.5485 | 564689.5485
C | Xist Rating 2458 | -83.41 | 320.42 | 150.281 | 35.7 | 2360.31 | 8267.07 | 28317.5 | 1.11 | 4.35 | 13.976 | 68.248 | 1 | 1 | 1450 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 756290.5302 | 57419.9099 | 2047.718 | 8930.0389 | 48489.8709 | 71883.7424 | 0.055246 | -555067.2049 | 555067.2049
C | Xist Rating 2459 | -83.27 | 322.512 | 150.281 | 35.7 | 2366.37 | 8355.31 | 28184.4 | 1.09 | 4.33 | 13.984 | 67.549 | 1 | 1 | 1460 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 763182.7214 | 58152.6284 | 2076.0598 | 8991.6254 | 49161.003 | 71147.0636 | 0.055627 | -549378.7663 | 549378.7663
C | Xist Rating 2460 | -82.68 | 336.26 | 150.281 | 35.7 | 2351.04 | 8255.26 | 27311 | 1.08 | 4.16 | 13.991 | 62.883 | 1 | 1 | 1470 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 790560.7104 | 58889.9596 | 2104.5964 | 9053.2119 | 49836.7477 | 66299.5462 | 0.056008 | -511947.5217 | 511947.5217
C | Xist Rating 2461 | -82.47 | 340.476 | 150.281 | 35.7 | 2351.21 | 8283.42 | 27066.7 | 1.07 | 4.11 | 13.98 | 61.657 | 1 | 1 | 1480 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 800530.576 | 59631.9034 | 2133.3277 | 9114.7984 | 50517.105 | 65023.0577 | 0.056389 | -502090.8162 | 502090.8162
C | Xist Rating 2462 | -82.25 | 344.057 | 150.281 | 35.7 | 2355.91 | 8363.97 | 26867.2 | 1.05 | 4.07 | 13.977 | 60.679 | 1 | 1 | 1490 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 810567.3269 | 60378.4597 | 2162.2539 | 9176.3848 | 51202.0749 | 63995.2269 | 0.05677 | -494154.179 | 494154.179
C | Xist Rating 2463 | -82.05 | 347.73 | 150.281 | 35.7 | 2359.49 | 8431.72 | 26670.8 | 1.03 | 4.03 | 13.965 | 59.738 | 1 | 1 | 1500 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 820465.4577 | 61129.6287 | 2191.3748 | 9237.9713 | 51891.6573 | 63004.9518 | 0.057151 | -486507.5373 | 486507.5373
C | Xist Rating 2464 | -81.81 | 351.973 | 150.281 | 35.7 | 2363.44 | 8509.59 | 26439.3 | 1.01 | 3.99 | 13.964 | 58.614 | 1 | 1 | 1510 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 831867.0671 | 61885.4102 | 2220.6906 | 9299.5578 | 52585.8524 | 61825.1543 | 0.057532 | -477397.4536 | 477397.4536
C | Xist Rating 2465 | -81.14 | 365.404 | 150.281 | 35.7 | 2361.72 | 8580.75 | 25681.5 | 1.02 | 3.85 | 14.026 | 54.856 | 1 | 1 | 1520 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 862981.9349 | 62645.8043 | 2250.2011 | 9361.1443 | 53284.6601 | 57942.6221 | 0.057913 | -447417.5689 | 447417.5689
C | Xist Rating 2466 | -80.97 | 369.991 | 150.281 | 35.7 | 2353.99 | 8506.64 | 25469 | 0.99 | 3.81 | 13.983 | 53.918 | 1 | 1 | 1530 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 13 | E | Rod | 870955.1141 | 63410.811 | 2279.9064 | 9422.7307 | 53988.0803 | 56943.1461 | 0.058294 | -439699.8801 | 439699.8801
C | Xist Rating 2467 | -80.82 | 372.357 | 150.281 | 35.7 | 2359.63 | 8594.54 | 25364.2 | 0.97 | 3.79 | 13.952 | 53.477 | 1 | 1 | 1540 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 878624.7479 | 64180.4304 | 2309.8065 | 9484.3172 | 54696.1131 | 56469.9928 | 0.058675 | -436046.3157 | 436046.3157
C | Xist Rating 2468 | -80.48 | 379.279 | 150.281 | 35.7 | 2358.04 | 8619.34 | 25021.7 | 0.95 | 3.72 | 13.947 | 51.902 | 1 | 1 | 1550 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 894355.0532 | 64954.6623 | 2339.9013 | 9545.9037 | 55408.7586 | 54820.7069 | 0.059056 | -423310.9671 | 423310.9671
C | Xist Rating 2469 | -80.28 | 381.421 | 150.281 | 35.7 | 2370.64 | 8804.43 | 24921 | 0.94 | 3.7 | 13.963 | 51.463 | 1 | 1 | 1560 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 904211.8794 | 65733.5068 | 2370.191 | 9607.4902 | 56126.0166 | 54362.0442 | 0.059437 | -419769.2957 | 419769.2957
C | Xist Rating 2470 | -79.64 | 397.443 | 150.281 | 35.7 | 2349.32 | 8623.86 | 24162.6 | 0.94 | 3.56 | 13.971 | 48.054 | 1 | 1 | 1570 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 933720.7888 | 66516.9638 | 2400.6755 | 9669.0767 | 56847.8872 | 50828.2157 | 0.059818 | -392482.0083 | 392482.0083
C | Xist Rating 2471 | -79.43 | 401.144 | 150.281 | 35.7 | 2353.07 | 8697.62 | 24008.1 | 0.92 | 3.53 | 13.963 | 47.416 | 1 | 1 | 1580 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 943919.9121 | 67305.0335 | 2431.3547 | 9730.6631 | 57574.3704 | 50151.2298 | 0.0602 | -387254.5027 | 387254.5027
C | Xist Rating 2472 | -79.23 | 404.881 | 150.281 | 35.7 | 2355.31 | 8751.73 | 23855.6 | 0.9 | 3.5 | 13.954 | 46.796 | 1 | 1 | 1590 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 953620.2681 | 68097.7158 | 2462.2288 | 9792.2496 | 58305.4662 | 49492.6384 | 0.060581 | -382169.0348 | 382169.0348
C | Xist Rating 2473 | -78.95 | 409.786 | 150.281 | 35.7 | 2360.3 | 8854.44 | 23645.7 | 0.89 | 3.46 | 13.96 | 45.916 | 1 | 1 | 1600 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 967217.8958 | 68895.0106 | 2493.2976 | 9853.8361 | 59041.1746 | 48574.7644 | 0.060962 | -375081.455 | 375081.455
C | Xist Rating 2474 | -78.83 | 412.348 | 150.281 | 35.7 | 2360.34 | 8869.44 | 23557 | 0.87 | 3.45 | 13.942 | 45.596 | 1 | 1 | 1610 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 973281.4783 | 69696.9181 | 2524.5612 | 9915.4226 | 59781.4956 | 48226.7347 | 0.061343 | -372394.0622 | 372394.0622
C | Xist Rating 2475 | -78.05 | 430.176 | 150.281 | 35.7 | 2346.44 | 8799.14 | 22805.4 | 0.87 | 3.31 | 13.975 | 42.441 | 1 | 1 | 1620 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1009382.1734 | 70503.4381 | 2556.0196 | 9977.009 | 60526.4291 | 44957.7941 | 0.061724 | -347152.1688 | 347152.1688
C | Xist Rating 2476 | -77.88 | 432.393 | 150.281 | 35.7 | 2354.23 | 8924.17 | 22723.7 | 0.86 | 3.29 | 13.983 | 42.135 | 1 | 1 | 1630 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1017952.5724 | 71314.5708 | 2587.6728 | 10038.5955 | 61275.9753 | 44635.7554 | 0.062105 | -344665.4716 | 344665.4716
C | Xist Rating 2477 | -77.7 | 436.277 | 150.281 | 35.7 | 2353.53 | 8938.24 | 22588.8 | 0.85 | 3.27 | 13.968 | 41.637 | 1 | 1 | 1640 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1026791.0078 | 72130.316 | 2619.5208 | 10100.182 | 62030.134 | 44112.757 | 0.062486 | -340627.0165 | 340627.0165
C | Xist Rating 2478 | -77.48 | 441.539 | 150.281 | 35.7 | 2349.72 | 8916.86 | 22403.4 | 0.83 | 3.24 | 13.949 | 40.94 | 1 | 1 | 1650 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1037493.0191 | 72950.6738 | 2651.5635 | 10161.7685 | 62788.9054 | 43372.4175 | 0.062867 | -334910.3114 | 334910.3114
C | Xist Rating 2479 | -77.22 | 446.558 | 150.281 | 35.7 | 2351.16 | 8971.35 | 22221.2 | 0.82 | 3.2 | 13.949 | 40.245 | 1 | 1 | 1660 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1049929.3073 | 73775.6442 | 2683.8011 | 10223.3549 | 63552.2893 | 42645.4715 | 0.063248 | -329297.0267 | 329297.0267
C | Xist Rating 2480 | -76.54 | 462.624 | 150.281 | 35.7 | 2338.68 | 8902.43 | 21633.4 | 0.82 | 3.1 | 13.968 | 37.973 | 1 | 1 | 1670 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1081929.4963 | 74605.2273 | 2716.2334 | 10284.9414 | 64320.2858 | 40292.2965 | 0.063629 | -311126.433 | 311126.433
C | Xist Rating 2481 | -76.37 | 464.953 | 150.281 | 35.7 | 2344.56 | 9002.72 | 21560.7 | 0.81 | 3.08 | 13.978 | 37.727 | 1 | 1 | 1680 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1090110.2057 | 75439.4228 | 2748.8606 | 10346.5279 | 65092.895 | 40032.0513 | 0.06401 | -309116.8887 | 309116.8887
C | Xist Rating 2482 | -76.1 | 471.643 | 150.282 | 35.7 | 2339.06 | 8965.02 | 21346.5 | 0.79 | 3.04 | 13.951 | 36.964 | 1 | 1 | 1690 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1103201.2756 | 76278.231 | 2781.6825 | 10408.1144 | 65870.1167 | 39221.9586 | 0.064391 | -302861.5677 | 302861.5677
C | Xist Rating 2483 | -75.87 | 476.043 | 150.281 | 35.7 | 2341.08 | 9023.67 | 21206.3 | 0.78 | 3.02 | 13.949 | 36.47 | 1 | 1 | 1700 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1114454.7464 | 77121.6518 | 2814.6992 | 10469.7008 | 66651.951 | 38703.1308 | 0.064772 | -298855.3172 | 298855.3172
C | Xist Rating 2484 | -75.69 | 481.254 | 150.281 | 35.7 | 2334.23 | 8955.64 | 21046.9 | 0.77 | 2.99 | 14.091 | 35.905 | 1 | 1 | 1710 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1123357.5244 | 77969.6852 | 2847.9107 | 10531.2873 | 67438.3979 | 38118.9452 | 0.065153 | -294344.3909 | 294344.3909
C | Xist Rating 2485 | -74.99 | 496.096 | 150.282 | 35.7 | 2330.4 | 9001.53 | 20567.8 | 0.77 | 2.9 | 13.972 | 34.197 | 1 | 1 | 1720 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1156102.1184 | 78822.3311 | 2881.317 | 10592.8738 | 68229.4574 | 36342.9889 | 0.065534 | -280630.927 | 280630.927
C | Xist Rating 2486 | -74.69 | 502.657 | 150.281 | 35.6 | 2329.34 | 9028.63 | 20374.7 | 0.76 | 2.87 | 13.965 | 33.545 | 1 | 1 | 1730 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1170859.0564 | 79679.5897 | 2914.9181 | 10654.4603 | 69025.1294 | 35659.463 | 0.065915 | -275352.9212 | 275352.9212
C | Xist Rating 2487 | -74.51 | 505.769 | 150.281 | 35.6 | 2332.76 | 9099.71 | 20290.3 | 0.75 | 2.85 | 13.962 | 33.28 | 1 | 1 | 1740 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1179837.6924 | 80541.4608 | 2948.714 | 10716.0467 | 69825.4141 | 35377.9509 | 0.066296 | -273179.1591 | 273179.1591
C | Xist Rating 2488 | -74.28 | 511.825 | 150.281 | 35.6 | 2327.83 | 9063.5 | 20123.4 | 0.73 | 2.82 | 13.946 | 32.738 | 1 | 1 | 1750 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1191441.5898 | 81407.9446 | 2982.7046 | 10777.6332 | 70630.3114 | 34796.9579 | 0.066677 | -268692.8851 | 268692.8851
C | Xist Rating 2489 | -74.08 | 516.341 | 150.281 | 35.6 | 2325.76 | 9060.84 | 20001 | 0.72 | 2.8 | 13.945 | 32.345 | 1 | 1 | 1760 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1200885.2442 | 82279.0409 | 3016.8901 | 10839.2197 | 71439.8212 | 34382.3324 | 0.067058 | -265491.2571 | 265491.2571
C | Xist Rating 2490 | -73.34 | 533.923 | 150.281 | 35.6 | 2314.91 | 9017.56 | 19497.5 | 0.72 | 2.71 | 13.98 | 30.655 | 1 | 1 | 1770 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1235983.6919 | 83154.7498 | 3051.2703 | 10900.8062 | 72253.9437 | 32633.77 | 0.067439 | -251989.3218 | 251989.3218
C | Xist Rating 2491 | -73.13 | 538.549 | 150.281 | 35.6 | 2313.74 | 9028.19 | 19383.3 | 0.71 | 2.69 | 13.973 | 30.31 | 1 | 1 | 1780 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1246062.3633 | 84035.0714 | 3085.8453 | 10962.3926 | 73072.6787 | 32268.449 | 0.06782 | -249168.4101 | 249168.4101
C | Xist Rating 2492 | -73.13 | 541.136 | 150.281 | 35.6 | 2304.78 | 8906.76 | 19327.5 | 0.7 | 2.68 | 14.104 | 30.15 | 1 | 1 | 1790 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1247199.4301 | 84920.0055 | 3120.6151 | 11023.9791 | 73896.0263 | 32102.8825 | 0.068201 | -247889.9494 | 247889.9494
C | Xist Rating 2493 | -72.81 | 549.162 | 150.281 | 35.6 | 2298.97 | 8870.32 | 19123.1 | 0.69 | 2.65 | 14.094 | 29.512 | 1 | 1 | 1800 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1262506.9631 | 85809.5522 | 3155.5797 | 11085.5656 | 74723.9866 | 31432.8095 | 0.068582 | -242715.8234 | 242715.8234
C | Xist Rating 2494 | -72.62 | 553.661 | 150.281 | 35.6 | 2300.07 | 8914.45 | 19012.6 | 0.68 | 2.63 | 14.083 | 29.182 | 1 | 1 | 1810 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1273459.0563 | 86703.7114 | 3190.7391 | 11147.1521 | 75556.5594 | 31082.4225 | 0.068963 | -240010.2275 | 240010.2275
C | Xist Rating 2495 | -71.88 | 571.501 | 150.282 | 35.6 | 2289.35 | 8869.39 | 18562.9 | 0.68 | 2.55 | 14.119 | 27.779 | 1 | 1 | 1820 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1308365.8143 | 87602.4833 | 3226.0933 | 11208.7385 | 76393.7448 | 29631.6989 | 0.069344 | -228808.1246 | 228808.1246
C | Xist Rating 2496 | -71.79 | 568.644 | 150.282 | 35.6 | 2308.14 | 9139.03 | 18632 | 0.67 | 2.56 | 14.151 | 28.002 | 1 | 1 | 1830 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1312509.9622 | 88505.8678 | 3261.6423 | 11270.325 | 77235.5428 | 29857.7647 | 0.069725 | -230553.7443 | 230553.7443
C | Xist Rating 2497 | -71.48 | 572.307 | 150.282 | 35.6 | 2318.56 | 9329.32 | 18546.2 | 0.67 | 2.55 | 14.171 | 27.753 | 1 | 1 | 1840 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1326928.1179 | 89413.8649 | 3297.386 | 11331.9115 | 78081.9534 | 29604.5337 | 0.070106 | -228598.3616 | 228598.3616
C | Xist Rating 2498 | -71.29 | 578.479 | 150.282 | 35.6 | 2311.6 | 9256.87 | 18409.8 | 0.66 | 2.52 | 14.148 | 27.365 | 1 | 1 | 1850 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1337212.0564 | 90326.4745 | 3333.3246 | 11393.498 | 78932.9766 | 29192.842 | 0.070487 | -225419.3876 | 225419.3876
C | Xist Rating 2499 | -71 | 585.381 | 150.282 | 35.6 | 2307.85 | 9240.62 | 18259.9 | 0.65 | 2.5 | 14.141 | 26.938 | 1 | 1 | 1860 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1350971.5408 | 91243.6968 | 3369.4579 | 11455.0844 | 79788.6123 | 28741.4136 | 0.070868 | -221933.5777 | 221933.5777
C | Xist Rating 2500 | -70.28 | 601.726 | 150.282 | 35.6 | 2301.65 | 9255.12 | 17880.4 | 0.65 | 2.43 | 14.185 | 25.811 | 1 | 1 | 1870 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1384962.6479 | 92165.5316 | 3405.7861 | 11516.6709 | 80648.8607 | 27577.5434 | 0.071249 | -212946.4799 | 212946.4799
C | Xist Rating 2501 | -69.99 | 608.615 | 150.282 | 35.6 | 2298.83 | 9253.27 | 17739.8 | 0.63 | 2.41 | 14.18 | 25.427 | 1 | 1 | 1880 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1399102.4205 | 93091.979 | 3442.309 | 11578.2574 | 81513.7216 | 27158.72 | 0.07163 | -209712.4366 | 209712.4366
C | Xist Rating 2502 | -69.73 | 613.161 | 150.282 | 35.6 | 2302.25 | 9338.43 | 17647.5 | 0.63 | 2.39 | 14.185 | 25.179 | 1 | 1 | 1890 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1411649.9122 | 94023.0391 | 3479.0267 | 11639.8439 | 82383.1952 | 26905.4436 | 0.072011 | -207756.7036 | 207756.7036
C | Xist Rating 2503 | -69.52 | 618.165 | 150.282 | 35.6 | 2299.76 | 9326.86 | 17556.3 | 0.61 | 2.38 | 14.188 | 24.948 | 1 | 1 | 1900 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1421631.1404 | 94958.7117 | 3515.9392 | 11701.4303 | 83257.2813 | 26645.5503 | 0.072392 | -205749.8761 | 205749.8761
C | Xist Rating 2504 | -69.32 | 622.891 | 150.282 | 35.6 | 2298.48 | 9335.31 | 17465.9 | 0.6 | 2.36 | 14.182 | 24.714 | 1 | 1 | 1910 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1431702.5057 | 95898.9969 | 3553.0464 | 11763.0168 | 84135.9801 | 26393.9658 | 0.072773 | -203807.2075 | 203807.2075
C | Xist Rating 2505 | -68.49 | 642.758 | 150.282 | 35.6 | 2289.03 | 9318.48 | 17051.1 | 0.61 | 2.29 | 14.224 | 23.552 | 1 | 1 | 1920 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1471292.3447 | 96843.8947 | 3590.3485 | 11824.6033 | 85019.2914 | 25205.4553 | 0.073154 | -194629.8444 | 194629.8444
C | Xist Rating 2506 | -68.19 | 649.723 | 150.282 | 35.6 | 2285.99 | 9311.72 | 16924.9 | 0.6 | 2.27 | 14.224 | 23.23 | 1 | 1 | 1930 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1485260.2808 | 97793.4051 | 3627.8454 | 11886.1898 | 85907.2153 | 24862.6427 | 0.073535 | -191982.7362 | 191982.7362
C | Xist Rating 2507 | -67.99 | 651.95 | 150.282 | 35.6 | 2294.01 | 9461.25 | 16883 | 0.59 | 2.26 | 14.257 | 23.128 | 1 | 1 | 1940 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1495579.8195 | 98747.528 | 3665.537 | 11947.7762 | 86799.7518 | 24749.8653 | 0.073916 | -191111.8992 | 191111.8992
C | Xist Rating 2508 | -67.79 | 658.693 | 150.282 | 35.6 | 2285.94 | 9364.64 | 16772.8 | 0.58 | 2.24 | 14.246 | 22.866 | 1 | 1 | 1950 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1505732.6764 | 99706.2636 | 3703.4235 | 12009.3627 | 87696.9009 | 24468.5297 | 0.074297 | -188939.5007 | 188939.5007
C | Xist Rating 2509 | -67.45 | 666.268 | 150.282 | 35.6 | 2284.16 | 9383.58 | 16637.8 | 0.57 | 2.22 | 14.258 | 22.523 | 1 | 1 | 1960 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1521862.7149 | 100669.6118 | 3741.5047 | 12070.9492 | 88598.6626 | 24104.1134 | 0.074678 | -186125.5746 | 186125.5746
C | Xist Rating 2510 | -66.69 | 684.236 | 150.282 | 35.6 | 2276.98 | 9386.59 | 16304 | 0.57 | 2.16 | 14.308 | 21.648 | 1 | 1 | 1970 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1557991.6873 | 101637.5725 | 3779.7807 | 12132.5357 | 89505.0369 | 23201.5869 | 0.075059 | -179156.5041 | 179156.5041
C | Xist Rating 2511 | -66.45 | 689.673 | 150.282 | 35.6 | 2276.34 | 9410 | 16214.7 | 0.56 | 2.15 | 14.29 | 21.436 | 1 | 1 | 1980 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1569930.2368 | 102610.1459 | 3818.2515 | 12194.1221 | 90416.0237 | 22971.4876 | 0.07544 | -177379.738 | 177379.738
C | Xist Rating 2512 | -66.18 | 696.832 | 150.282 | 35.6 | 2272.22 | 9383.61 | 16101.8 | 0.55 | 2.13 | 14.286 | 21.171 | 1 | 1 | 1990 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1583355.607 | 103587.3318 | 3856.9171 | 12255.7086 | 91331.6232 | 22686.9295 | 0.075821 | -175182.4557 | 175182.4557
C | Xist Rating 2513 | -65.93 | 702.393 | 150.282 | 35.6 | 2271.62 | 9407.45 | 16015.1 | 0.55 | 2.12 | 14.285 | 20.971 | 1 | 1 | 2000 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1595569.9867 | 104569.1304 | 3895.7775 | 12317.2951 | 92251.8353 | 22482.7025 | 0.076202 | -173605.4691 | 173605.4691
C | Xist Rating 2514 | -65.73 | 706.529 | 150.282 | 35.6 | 2272.97 | 9455.35 | 15953.9 | 0.54 | 2.11 | 14.286 | 20.836 | 1 | 1 | 2010 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1605919.2211 | 105555.5415 | 3934.8326 | 12378.8816 | 93176.6599 | 22333.2052 | 0.076583 | -172451.0905 | 172451.0905
C | Xist Rating 2515 | -64.91 | 726.844 | 150.282 | 35.6 | 2262.75 | 9417.65 | 15615 | 0.54 | 2.05 | 14.323 | 19.998 | 1 | 1 | 2020 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1644666.261 | 106546.5652 | 3974.0826 | 12440.468 | 94106.0972 | 21468.2106 | 0.076964 | -165771.8315 | 165771.8315
C | Xist Rating 2516 | -64.59 | 734.363 | 150.282 | 35.6 | 2261.43 | 9443.35 | 15500 | 0.53 | 2.03 | 14.324 | 19.732 | 1 | 1 | 2030 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1660710.5191 | 107542.2015 | 4013.5273 | 12502.0545 | 95040.147 | 21182.4521 | 0.077345 | -163565.28 | 163565.28
C | Xist Rating 2517 | -64.4 | 739.567 | 150.282 | 35.6 | 2258.53 | 9422.05 | 15431.9 | 0.52 | 2.02 | 14.317 | 19.592 | 1 | 1 | 2040 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1670334.2565 | 108542.4504 | 4053.1669 | 12563.641 | 95978.8094 | 21027.0342 | 0.077726 | -162365.1845 | 162365.1845
C | Xist Rating 2518 | -64.19 | 743.955 | 150.282 | 35.6 | 2259.6 | 9469.91 | 15364.3 | 0.52 | 2.01 | 14.32 | 19.438 | 1 | 1 | 2050 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1681040.718 | 109547.3119 | 4093.0012 | 12625.2275 | 96922.0844 | 20870.5859 | 0.078107 | -161157.1324 | 161157.1324
C | Xist Rating 2519 | -63.92 | 751.51 | 150.282 | 35.6 | 2254.06 | 9416.56 | 15264.4 | 0.51 | 1.99 | 14.31 | 19.226 | 1 | 1 | 2060 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1693948.6306 | 110556.786 | 4133.0303 | 12686.8139 | 97869.972 | 20640.0682 | 0.078488 | -159377.1359 | 159377.1359
C | Xist Rating 2520 | -63.06 | 773.354 | 150.282 | 35.6 | 2243.41 | 9376.78 | 14936.3 | 0.51 | 1.94 | 14.349 | 18.462 | 1 | 1 | 2070 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1734950.0971 | 111570.8727 | 4173.2542 | 12748.4004 | 98822.4722 | 19851.7723 | 0.078869 | -153290.1238 | 153290.1238
C | Xist Rating 2521 | -62.87 | 778.359 | 150.282 | 35.6 | 2241.91 | 9379.24 | 14873.5 | 0.5 | 1.93 | 14.343 | 18.335 | 1 | 1 | 2080 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1745010.8257 | 112589.5719 | 4213.6729 | 12809.9869 | 99779.585 | 19709.5053 | 0.07925 | -152191.5752 | 152191.5752
C | Xist Rating 2522 | -62.62 | 784.732 | 150.282 | 35.6 | 2239.31 | 9371.54 | 14791 | 0.5 | 1.91 | 14.342 | 18.163 | 1 | 1 | 2090 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1757258.2149 | 113612.8838 | 4254.2864 | 12871.5734 | 100741.3104 | 19534.0513 | 0.079631 | -150836.7662 | 150836.7662
C | Xist Rating 2523 | -62.36 | 791.112 | 150.282 | 35.6 | 2238.19 | 9390 | 14709.4 | 0.49 | 1.9 | 14.341 | 17.994 | 1 | 1 | 2100 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1770658.9673 | 114640.8082 | 4295.0947 | 12933.1599 | 101707.6484 | 19348.2129 | 0.080012 | -149401.7716 | 149401.7716
C | Xist Rating 2524 | -62.13 | 796.767 | 150.282 | 35.6 | 2236.32 | 9390.21 | 14638.8 | 0.48 | 1.89 | 14.339 | 17.85 | 1 | 1 | 2110 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1781825.9774 | 115673.3453 | 4336.0977 | 12994.7463 | 102678.599 | 19188.1645 | 0.080393 | -148165.9202 | 148165.9202
C | Xist Rating 2525 | -61.33 | 817.522 | 150.282 | 35.6 | 2226.45 | 9350.65 | 14359.1 | 0.48 | 1.84 | 14.376 | 17.237 | 1 | 1 | 2120 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1820171.8569 | 116710.4949 | 4377.2956 | 13056.3328 | 103654.1621 | 18556.3378 | 0.080774 | -143287.1221 | 143287.1221
C | Xist Rating 2526 | -61.04 | 825.384 | 150.282 | 35.6 | 2223.08 | 9337.84 | 14263.8 | 0.48 | 1.83 | 14.371 | 17.044 | 1 | 1 | 2130 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1834894.6627 | 117752.2571 | 4418.6882 | 13117.9193 | 104634.3379 | 18358.7716 | 0.081155 | -141761.5681 | 141761.5681
C | Xist Rating 2527 | -60.78 | 833.272 | 150.282 | 35.6 | 2217.75 | 9290.36 | 14169.9 | 0.47 | 1.81 | 14.366 | 16.856 | 1 | 1 | 2140 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1847988.978 | 118798.632 | 4460.2756 | 13179.5058 | 105619.1262 | 18152.6152 | 0.081536 | -140169.6827 | 140169.6827
C | Xist Rating 2528 | -60.61 | 837.557 | 150.282 | 35.6 | 2216.71 | 9295.09 | 14123.5 | 0.46 | 1.8 | 14.367 | 16.771 | 1 | 1 | 2150 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1856620.9775 | 119849.6194 | 4502.0578 | 13241.0922 | 106608.5271 | 18053.5688 | 0.081917 | -139404.8726 | 139404.8726
C | Xist Rating 2529 | -60.39 | 843.158 | 150.282 | 35.6 | 2215.42 | 9304.76 | 14059.1 | 0.46 | 1.79 | 14.365 | 16.647 | 1 | 1 | 2160 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1867949.0964 | 120905.2194 | 4544.0348 | 13302.6787 | 107602.5407 | 17927.6683 | 0.082298 | -138432.7023 | 138432.7023
C | Xist Rating 2530 | -59.55 | 865.654 | 150.282 | 35.6 | 2204.41 | 9250.2 | 13786 | 0.46 | 1.75 | 14.401 | 16.081 | 1 | 1 | 2170 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1908256.3341 | 121965.432 | 4586.2066 | 13364.2652 | 108601.1668 | 17344.4509 | 0.082679 | -133929.2525 | 133929.2525
C | Xist Rating 2531 | -59.22 | 873.29 | 150.282 | 35.6 | 2203.82 | 9285.24 | 13699 | 0.45 | 1.74 | 14.4 | 15.912 | 1 | 1 | 2180 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1924573.9678 | 123030.2571 | 4628.5732 | 13425.8517 | 109604.4055 | 17157.7978 | 0.08306 | -132487.9664 | 132487.9664
C | Xist Rating 2532 | -59 | 879.125 | 150.282 | 35.6 | 2201.93 | 9283.59 | 13638.9 | 0.45 | 1.73 | 14.393 | 15.803 | 1 | 1 | 2190 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1935771.7112 | 124099.6949 | 4671.1346 | 13487.4381 | 110612.2568 | 17047.1969 | 0.083441 | -131633.9355 | 131633.9355
C | Xist Rating 2533 | -58.8 | 885.366 | 150.282 | 35.6 | 2198.17 | 9248.57 | 13579.4 | 0.44 | 1.72 | 14.387 | 15.701 | 1 | 1 | 2200 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1946184.9802 | 125173.7453 | 4713.8907 | 13549.0246 | 111624.7207 | 16929.7194 | 0.083822 | -130726.8054 | 130726.8054
C | Xist Rating 2534 | -58.5 | 893.261 | 150.282 | 35.6 | 2195.44 | 9245.44 | 13495.4 | 0.44 | 1.7 | 14.385 | 15.543 | 1 | 1 | 2210 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 1961100.9298 | 126252.4082 | 4756.8417 | 13610.6111 | 112641.7972 | 16768.387 | 0.084203 | -129481.0393 | 129481.0393
C | Xist Rating 2535 | -57.66 | 915.622 | 150.282 | 35.6 | 2186.18 | 9217.58 | 13246.1 | 0.44 | 1.66 | 14.424 | 15.051 | 1 | 1 | 2220 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2001714.504 | 127335.6838 | 4799.9874 | 13672.1976 | 113663.4862 | 16261.9905 | 0.084584 | -125570.7799 | 125570.7799
C | Xist Rating 2536 | -57.41 | 921.966 | 150.282 | 35.6 | 2184.4 | 9221.56 | 13182.6 | 0.43 | 1.65 | 14.42 | 14.936 | 1 | 1 | 2230 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2013942.5304 | 128423.5719 | 4843.3279 | 13733.784 | 114689.7879 | 16130.818 | 0.084965 | -124557.9006 | 124557.9006
C | Xist Rating 2537 | -57.16 | 929.489 | 150.282 | 35.6 | 2180.71 | 9195.85 | 13111.7 | 0.43 | 1.64 | 14.416 | 14.813 | 1 | 1 | 2240 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2026945.9572 | 129516.0727 | 4886.8633 | 13795.3705 | 115720.7022 | 16005.6894 | 0.085346 | -123591.6906 | 123591.6906
C | Xist Rating 2538 | -56.87 | 937.691 | 150.282 | 35.6 | 2177.07 | 9175.3 | 13034 | 0.42 | 1.63 | 14.413 | 14.677 | 1 | 1 | 2250 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2041418.9454 | 130613.186 | 4930.5934 | 13856.957 | 116756.229 | 15852.5658 | 0.085727 | -122409.3111 | 122409.3111
C | Xist Rating 2539 | -56.69 | 941.939 | 150.282 | 35.6 | 2177.13 | 9198.31 | 12995.6 | 0.42 | 1.62 | 14.416 | 14.614 | 1 | 1 | 2260 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2050723.6551 | 131714.9119 | 4974.5182 | 13918.5435 | 117796.3685 | 15789.9815 | 0.086108 | -121926.0516 | 121926.0516
C | Xist Rating 2540 | -55.82 | 966.137 | 150.282 | 35.6 | 2166.4 | 9149.29 | 12751.9 | 0.42 | 1.59 | 14.453 | 14.159 | 1 | 1 | 2270 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2093039.1968 | 132821.2504 | 5018.6379 | 13980.1299 | 118841.1205 | 15321.7599 | 0.086489 | -118310.5689 | 118310.5689
C | Xist Rating 2541 | -55.54 | 973.605 | 150.282 | 35.6 | 2164.3 | 9150.89 | 12686.1 | 0.41 | 1.58 | 14.449 | 14.049 | 1 | 1 | 2280 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2107173.3015 | 133932.2015 | 5062.9524 | 14041.7164 | 119890.4851 | 15195.3075 | 0.08687 | -117334.1365 | 117334.1365
C | Xist Rating 2542 | -55.24 | 982.281 | 150.282 | 35.6 | 2160.66 | 9133.45 | 12606.9 | 0.41 | 1.56 | 14.445 | 13.912 | 1 | 1 | 2290 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2122375.2655 | 135047.7652 | 5107.4617 | 14103.3029 | 120944.4623 | 15055.5203 | 0.087251 | -116254.737 | 116254.737
C | Xist Rating 2543 | -55.03 | 988.279 | 150.282 | 35.6 | 2158.16 | 9119.05 | 12557.1 | 0.4 | 1.56 | 14.441 | 13.833 | 1 | 1 | 2300 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2132864.2066 | 136167.9415 | 5152.1657 | 14164.8894 | 122003.0521 | 14961.0764 | 0.087632 | -115525.466 | 115525.466
| Xist Rating 2544 | -54.83 | 994.543 | 150.282 | 35.6 | 2155.06 | 9093.72 | 12507.7 | 0.4 | 1.55 | 14.437 | 13.757 | 1 | 1 | 2310 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2143299.8376 | 137292.7304 | 5197.0645 | 14226.4758 | 123066.2545 | 14884.5741 | 0.088013 | -114934.7356 | 114934.7356
| Xist Rating 2545 | -53.93 | 1019.3 | 150.282 | 35.6 | 2145.82 | 9071.27 | 12277.2 | 0.4 | 1.51 | 14.476 | 13.344 | 1 | 1 | 2320 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2187234.326 | 138422.1318 | 5242.1582 | 14288.0623 | 124134.0695 | 14459.8851 | 0.088394 | -111655.3995 | 111655.3995
| Xist Rating 2546 | -53.67 | 1026.81 | 150.282 | 35.6 | 2142.78 | 9054.94 | 12216.9 | 0.39 | 1.5 | 14.47 | 13.249 | 1 | 1 | 2330 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2200227.9318 | 139556.1459 | 5287.4466 | 14349.6488 | 125206.4971 | 14348.4599 | 0.088775 | -110795.004 | 110795.004
| Xist Rating 2547 | -53.42 | 1034.28 | 150.282 | 35.6 | 2139.84 | 9040.26 | 12157.2 | 0.39 | 1.49 | 14.465 | 13.154 | 1 | 1 | 2340 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2213193.7152 | 140694.7726 | 5332.9298 | 14411.2353 | 126283.5373 | 14252.1276 | 0.089156 | -110051.1515 | 110051.1515
| Xist Rating 2548 | -53.19 | 1041.12 | 150.282 | 35.6 | 2137.01 | 9023.33 | 12104.8 | 0.38 | 1.49 | 14.46 | 13.074 | 1 | 1 | 2350 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2224883.8512 | 141838.0118 | 5378.6078 | 14472.8217 | 127365.1901 | 14156.1392 | 0.089537 | -109309.9543 | 109309.9543
| Xist Rating 2549 | -52.91 | 1049.38 | 150.282 | 35.6 | 2133.71 | 9006.05 | 12039.9 | 0.38 | 1.48 | 14.456 | 12.972 | 1 | 1 | 2360 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2239072.5998 | 142985.8636 | 5424.4805 | 14534.4082 | 128451.4554 | 14052.5146 | 0.089918 | -108509.7926 | 108509.7926
| Xist Rating 2550 | -52.09 | 1072.17 | 150.282 | 35.6 | 2125.54 | 8986.23 | 11846.8 | 0.38 | 1.45 | 14.491 | 12.644 | 1 | 1 | 2370 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2278940.2218 | 144138.3281 | 5470.5481 | 14595.9947 | 129542.3334 | 13715.7623 | 0.090299 | -105909.4812 | 105909.4812
| Xist Rating 2551 | -51.84 | 1079.88 | 150.282 | 35.6 | 2122.24 | 8964.21 | 11791.2 | 0.37 | 1.44 | 14.485 | 12.561 | 1 | 1 | 2380 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2291764.5312 | 145295.4051 | 5516.8105 | 14657.5812 | 130637.8239 | 13616.3391 | 0.09068 | -105141.7609 | 105141.7609
| Xist Rating 2552 | -51.56 | 1087.69 | 150.282 | 35.6 | 2120.3 | 8970.5 | 11730 | 0.37 | 1.43 | 14.479 | 12.465 | 1 | 1 | 2390 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2306229.107 | 146457.0947 | 5563.2676 | 14719.1676 | 131737.9271 | 13518.8077 | 0.091061 | -104388.6499 | 104388.6499
C | Xist Rating 2553 | -46.8 | 1247.25 | 150.282 | 35.6 | 2032.24 | 8276.65 | 10538.2 | 0.4 | 1.25 | 14.477 | 10.575 | 1 | 1 | 2400 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2534711.34 | 147623.3969 | 5609.9196 | 14780.7541 | 132842.6428 | 11605.0902 | 0.091442 | -89611.4302 | 89611.4302
C | Xist Rating 2554 | -46.32 | 1248.7 | 150.282 | 35.6 | 2048.73 | 8557.24 | 10538 | 0.39 | 1.25 | 14.474 | 10.584 | 1 | 1 | 2410 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2558249.151 | 148794.3117 | 5656.7663 | 14842.3406 | 133951.9711 | 11601.2669 | 0.091823 | -89581.9075 | 89581.9075
C | Xist Rating 2555 | -46.32 | 1250.1 | 150.282 | 35.6 | 2047.72 | 8539.69 | 10538 | 0.39 | 1.25 | 14.513 | 10.595 | 1 | 1 | 2420 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2559854.772 | 149969.8391 | 5703.8078 | 14903.9271 | 135065.912 | 11616.8705 | 0.092204 | -89702.395 | 89702.395
C | Xist Rating 2556 | -45.84 | 1251.45 | 150.282 | 35.6 | 2063.93 | 8828.85 | 10538 | 0.39 | 1.25 | 14.506 | 10.604 | 1 | 1 | 2430 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2582905.1985 | 151149.9791 | 5751.0441 | 14965.5135 | 136184.4655 | 11628.4568 | 0.092585 | -89791.8608 | 89791.8608
C | Xist Rating 2557 | -45.82 | 1252.82 | 150.282 | 35.6 | 2063.24 | 8816.24 | 10537.9 | 0.38 | 1.25 | 14.501 | 10.615 | 1 | 1 | 2440 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2584868.3368 | 152334.7316 | 5798.4752 | 15027.1 | 137307.6316 | 11626.3428 | 0.092966 | -89775.5373 | 89775.5373
C | Xist Rating 2558 | -45.8 | 1254.15 | 150.282 | 35.6 | 2062.64 | 8805.31 | 10537.9 | 0.38 | 1.25 | 14.495 | 10.625 | 1 | 1 | 2450 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2586859.956 | 153524.0968 | 5846.1011 | 15088.6865 | 138435.4103 | 11638.9474 | 0.093347 | -89872.8667 | 89872.8667
C | Xist Rating 2559 | -45.78 | 1255.62 | 150.282 | 35.6 | 2061.65 | 8787.33 | 10537.9 | 0.37 | 1.25 | 14.491 | 10.637 | 1 | 1 | 2460 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2588648.973 | 154718.0745 | 5893.9217 | 15150.273 | 139567.8016 | 11637.7317 | 0.093728 | -89863.4796 | 89863.4796
C | Xist Rating 2560 | -45.76 | 1256.98 | 150.282 | 35.6 | 2061.06 | 8776.64 | 10537.9 | 0.36 | 1.25 | 14.528 | 10.647 | 1 | 1 | 2470 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2590711.1988 | 155916.6649 | 5941.9372 | 15211.8594 | 140704.8054 | 11635.9508 | 0.094109 | -89849.728 | 89849.728
C | Xist Rating 2561 | -45.75 | 1258.32 | 150.282 | 35.6 | 2060.35 | 8763.87 | 10537.9 | 0.36 | 1.25 | 14.522 | 10.658 | 1 | 1 | 2480 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2592579.612 | 157119.8678 | 5990.1474 | 15273.4459 | 141846.4219 | 11649.4786 | 0.09449 | -89954.1855 | 89954.1855
C | Xist Rating 2562 | -45.73 | 1259.72 | 150.282 | 35.6 | 2059.62 | 8750.57 | 10537.9 | 0.35 | 1.25 | 14.517 | 10.668 | 1 | 1 | 2490 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2594544.5064 | 158327.6834 | 6038.5525 | 15335.0324 | 142992.651 | 11645.8031 | 0.094871 | -89925.8048 | 89925.8048
C | Xist Rating 2563 | -45.71 | 1260.71 | 150.282 | 35.6 | 2059.64 | 8751 | 10537.9 | 0.35 | 1.25 | 14.512 | 10.677 | 1 | 1 | 2500 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2596608.7444 | 159540.1115 | 6087.1523 | 15396.6189 | 144143.4926 | 11657.231 | 0.095252 | -90014.048 | 90014.048
C | Xist Rating 2564 | -45.7 | 1262.56 | 150.282 | 35.6 | 2057.79 | 8717.73 | 10537.9 | 0.34 | 1.25 | 14.511 | 10.69 | 1 | 1 | 2510 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2598083.3424 | 160757.1522 | 6135.9469 | 15458.2053 | 145298.9468 | 11656.6426 | 0.095633 | -90009.5039 | 90009.5039
C | Xist Rating 2565 | -45.65 | 1264.01 | 150.282 | 35.6 | 2058.18 | 8724.82 | 10537.8 | 0.34 | 1.25 | 14.543 | 10.701 | 1 | 1 | 2520 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2601560.1018 | 161978.8055 | 6184.9363 | 15519.7918 | 146459.0137 | 11671.5066 | 0.096014 | -90124.2798 | 90124.2798
C | Xist Rating 2566 | -45.63 | 1265.35 | 150.282 | 35.6 | 2057.56 | 8713.74 | 10537.8 | 0.33 | 1.25 | 14.54 | 10.711 | 1 | 1 | 2530 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2603533.546 | 163205.0714 | 6234.1205 | 15581.3783 | 147623.6931 | 11667.503 | 0.096395 | -90093.3653 | 90093.3653
C | Xist Rating 2567 | -45.6 | 1266.5 | 150.283 | 35.6 | 2057.89 | 8719.69 | 10537.7 | 0.33 | 1.25 | 14.545 | 10.72 | 1 | 1 | 2540 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2606317.685 | 164435.9499 | 6283.4995 | 15642.9648 | 148792.9851 | 11679.1881 | 0.096776 | -90183.5947 | 90183.5947
C | Xist Rating 2568 | -45.58 | 1268.05 | 150.283 | 35.6 | 2057.01 | 8703.78 | 10537.7 | 0.32 | 1.25 | 14.541 | 10.731 | 1 | 1 | 2550 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2608391.5305 | 165671.441 | 6333.0732 | 15704.5512 | 149966.8897 | 11675.9914 | 0.097157 | -90158.911 | 90158.911
C | Xist Rating 2569 | -45.57 | 1269.49 | 150.283 | 35.6 | 2056.28 | 8690.85 | 10537.7 | 0.32 | 1.25 | 14.538 | 10.742 | 1 | 1 | 2560 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2610426.8972 | 166911.5446 | 6382.8418 | 15766.1377 | 151145.4069 | 11689.3905 | 0.097538 | -90262.375 | 90262.375
C | Xist Rating 2570 | -45.55 | 1270.88 | 150.283 | 35.6 | 2055.67 | 8679.85 | 10537.7 | 0.31 | 1.25 | 14.534 | 10.752 | 1 | 1 | 2570 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2612509.8896 | 168156.2609 | 6432.8051 | 15827.7242 | 152328.5367 | 11684.9703 | 0.097919 | -90228.2432 | 90228.2432
C | Xist Rating 2571 | -45.52 | 1272.25 | 150.283 | 35.6 | 2055.25 | 8672.38 | 10537.7 | 0.31 | 1.25 | 14.57 | 10.762 | 1 | 1 | 2580 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 12 | E | Rod | 2614791.8125 | 169405.5897 | 6482.9633 | 15889.3107 | 153516.2791 | 11698.6655 | 0.0983 | -90333.9939 | 90333.9939
C | Xist Rating 2572 | -45.5 | 1273.61 | 150.283 | 35.6 | 2054.66 | 8661.94 | 10537.7 | 0.3 | 1.25 | 14.563 | 10.773 | 1 | 1 | 2590 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2616835.5226 | 170659.5312 | 6533.3162 | 15950.8971 | 154708.634 | 11694.9546 | 0.098681 | -90305.3394 | 90305.3394
C | Xist Rating 2573 | -45.47 | 1274.79 | 150.283 | 35.6 | 2054.65 | 8661.78 | 10537.8 | 0.3 | 1.25 | 14.562 | 10.782 | 1 | 1 | 2600 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2619247.2735 | 171918.0852 | 6583.8639 | 16012.4836 | 155905.6016 | 11706.2245 | 0.099062 | -90392.3623 | 90392.3623
C | Xist Rating 2574 | -45.45 | 1276.47 | 150.283 | 35.6 | 2053.55 | 8642.29 | 10537.8 | 0.3 | 1.25 | 14.559 | 10.793 | 1 | 1 | 2610 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2621294.9685 | 173181.2519 | 6634.6064 | 16074.0701 | 157107.1818 | 11719.5009 | 0.099443 | -90494.8792 | 90494.8792
C | Xist Rating 2575 | -45.44 | 1277.87 | 150.283 | 35.6 | 2052.59 | 8625.25 | 10537.8 | 0.29 | 1.25 | 14.555 | 10.804 | 1 | 1 | 2620 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2622943.1833 | 174449.0311 | 6685.5437 | 16135.6566 | 158313.3745 | 11715.6477 | 0.099824 | -90465.1264 | 90465.1264
C | Xist Rating 2576 | -45.43 | 1279.3 | 150.283 | 35.6 | 2051.64 | 8608.45 | 10537.8 | 0.29 | 1.25 | 14.591 | 10.814 | 1 | 1 | 2630 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2624663.052 | 175721.4229 | 6736.6758 | 16197.2431 | 159524.1798 | 11729.1555 | 0.10021 | -90569.4298 | 90569.4298
C | Xist Rating 2577 | -45.4 | 1280.54 | 150.283 | 35.6 | 2051.79 | 8611.19 | 10537.8 | 0.28 | 1.25 | 14.587 | 10.823 | 1 | 1 | 2640 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2627399.1666 | 176998.4273 | 6788.0027 | 16258.8295 | 160739.5978 | 11722.9996 | 0.10059 | -90521.8955 | 90521.8955
C | Xist Rating 2578 | -45.35 | 1282.05 | 150.283 | 35.6 | 2051.84 | 8612.1 | 10537.7 | 0.28 | 1.25 | 14.584 | 10.834 | 1 | 1 | 2650 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2630561.472 | 178280.0443 | 6839.5243 | 16320.416 | 161959.6283 | 11736.1541 | 0.10097 | -90623.4711 | 90623.4711
C | Xist Rating 2579 | -45.33 | 1283.39 | 150.283 | 35.6 | 2051.48 | 8605.73 | 10537.6 | 0.28 | 1.25 | 14.58 | 10.844 | 1 | 1 | 2660 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2632848.9172 | 179566.2739 | 6891.2408 | 16382.0025 | 163184.2714 | 11748.236 | 0.10135 | -90716.7641 | 90716.7641
C | Xist Rating 2580 | -45.31 | 1284.77 | 150.283 | 35.6 | 2050.95 | 8596.45 | 10537.6 | 0.27 | 1.25 | 14.577 | 10.853 | 1 | 1 | 2670 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2634999.0315 | 180857.1161 | 6943.152 | 16443.589 | 164413.5271 | 11741.8658 | 0.10173 | -90667.5755 | 90667.5755
C | Xist Rating 2581 | -45.3 | 1286.19 | 150.283 | 35.6 | 2050.14 | 8582.18 | 10537.6 | 0.27 | 1.25 | 14.611 | 10.863 | 1 | 1 | 2680 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2636869.5666 | 182152.5708 | 6995.258 | 16505.1754 | 165647.3954 | 11755.1178 | 0.10211 | -90769.9038 | 90769.9038
C | Xist Rating 2582 | -45.24 | 1287.57 | 150.283 | 35.6 | 2051.07 | 8598.64 | 10537.6 | 0.27 | 1.25 | 14.607 | 10.873 | 1 | 1 | 2690 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2640896.1999 | 183452.6382 | 7047.5588 | 16566.7619 | 166885.8763 | 11767.1409 | 0.10249 | -90862.7429 | 90862.7429
C | Xist Rating 2583 | -45.24 | 1288.77 | 150.283 | 35.6 | 2049.83 | 8576.8 | 10537.6 | 0.26 | 1.25 | 14.602 | 10.882 | 1 | 1 | 2700 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2641759.4091 | 184757.3182 | 7100.0544 | 16628.3484 | 168128.9698 | 11760.4195 | 0.10287 | -90810.8423 | 90810.8423
C | Xist Rating 2584 | -45.21 | 1290.42 | 150.283 | 35.6 | 2048.68 | 8556.61 | 10537.7 | 0.26 | 1.25 | 14.602 | 10.894 | 1 | 1 | 2710 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2643657.6456 | 186066.6107 | 7152.7448 | 16689.9349 | 169376.6759 | 11774.5833 | 0.10325 | -90920.2111 | 90920.2111
C | Xist Rating 2585 | -45.18 | 1291.77 | 150.283 | 35.6 | 2048.76 | 8557.99 | 10537.8 | 0.26 | 1.25 | 14.602 | 10.903 | 1 | 1 | 2720 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2646526.7052 | 187380.5158 | 7205.63 | 16751.5213 | 170628.9945 | 11785.6316 | 0.10363 | -91005.5228 | 91005.5228
C | Xist Rating 2586 | -45.17 | 1293.09 | 150.283 | 35.6 | 2047.84 | 8541.96 | 10537.7 | 0.25 | 1.25 | 14.635 | 10.913 | 1 | 1 | 2730 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2648041.4256 | 188699.0336 | 7258.71 | 16813.1078 | 171885.9258 | 11780.8592 | 0.10402 | -90968.6721 | 90968.6721
C | Xist Rating 2587 | -45.13 | 1294.37 | 150.283 | 35.6 | 2048.19 | 8548.03 | 10537.8 | 0.25 | 1.25 | 14.633 | 10.922 | 1 | 1 | 2740 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2651115.6903 | 190022.1639 | 7311.9847 | 16874.6943 | 173147.4696 | 11791.7843 | 0.1044 | -91053.0328 | 91053.0328
C | Xist Rating 2588 | -45.13 | 1295.92 | 150.283 | 35.6 | 2046.59 | 8520.27 | 10537.7 | 0.25 | 1.25 | 14.626 | 10.932 | 1 | 1 | 2750 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2652216.9128 | 191349.9068 | 7365.4543 | 16936.2808 | 174413.6261 | 11803.5934 | 0.10478 | -91144.2193 | 91144.2193
C | Xist Rating 2589 | -45.07 | 1297.35 | 150.283 | 35.6 | 2047.29 | 8532.48 | 10537.8 | 0.24 | 1.25 | 14.627 | 10.942 | 1 | 1 | 2760 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2656051.6815 | 192682.2623 | 7419.1186 | 16997.8672 | 175684.3951 | 11797.5524 | 0.10516 | -91097.5722 | 91097.5722
C | Xist Rating 2590 | -44.94 | 1298.58 | 150.283 | 35.6 | 2051.08 | 8598.57 | 10537.9 | 0.24 | 1.25 | 14.639 | 10.951 | 1 | 1 | 2770 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2663491.4664 | 194019.2304 | 7472.9777 | 17059.4537 | 176959.7767 | 11808.83 | 0.10554 | -91184.6551 | 91184.6551
C | Xist Rating 2591 | -44.93 | 1300.13 | 150.283 | 35.6 | 2049.67 | 8573.78 | 10537.9 | 0.24 | 1.25 | 14.673 | 10.962 | 1 | 1 | 2780 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2664837.4571 | 195360.8111 | 7527.0316 | 17121.0402 | 178239.7709 | 11822.8452 | 0.10592 | -91292.8765 | 91292.8765
C | Xist Rating 2592 | -44.69 | 1301.54 | 150.283 | 35.6 | 2057.56 | 8713.45 | 10538.1 | 0.23 | 1.25 | 14.697 | 10.972 | 1 | 1 | 2790 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2677996.6424 | 196707.0044 | 7581.2803 | 17182.6267 | 179524.3777 | 11817.1488 | 0.1063 | -91248.8909 | 91248.8909
C | Xist Rating 2593 | -44.73 | 1302.51 | 150.283 | 35.6 | 2055.29 | 8672.87 | 10538 | 0.23 | 1.25 | 14.681 | 10.979 | 1 | 1 | 2800 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2677035.7779 | 198057.8103 | 7635.7238 | 17244.2131 | 180813.5971 | 11825.4717 | 0.10668 | -91313.1576 | 91313.1576
C | Xist Rating 2594 | -44.53 | 1304.26 | 150.283 | 35.6 | 2061.11 | 8777.45 | 10538.1 | 0.23 | 1.25 | 14.709 | 10.991 | 1 | 1 | 2810 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2688223.3286 | 199413.2287 | 7690.3621 | 17305.7996 | 182107.4291 | 11840.2584 | 0.10706 | -91427.3366 | 91427.3366
C | Xist Rating 2595 | -44.16 | 1305.73 | 150.283 | 35.6 | 2073.56 | 9007.56 | 10538.3 | 0.22 | 1.25 | 14.77 | 11.002 | 1 | 1 | 2820 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2707509.4988 | 200773.2598 | 7745.1952 | 17367.3861 | 183405.8737 | 11836.3017 | 0.10744 | -91396.7841 | 91396.7841
C | Xist Rating 2596 | -43.92 | 1307.1 | 150.283 | 35.6 | 2081.06 | 9150.83 | 10538.3 | 0.22 | 1.25 | 14.849 | 11.012 | 1 | 1 | 2830 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2720153.526 | 202137.9034 | 7800.223 | 17428.9726 | 184708.9309 | 11850.3479 | 0.10783 | -91505.2454 | 91505.2454
C | Xist Rating 2597 | -43.77 | 1308.42 | 150.283 | 35.6 | 2085.46 | 9236.61 | 10538.3 | 0.22 | 1.25 | 14.87 | 11.021 | 1 | 1 | 2840 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2728657.5732 | 203507.1597 | 7855.4457 | 17490.559 | 186016.6006 | 11861.7469 | 0.10821 | -91593.265 | 91593.265
C | Xist Rating 2598 | -43.66 | 1309.87 | 150.283 | 35.6 | 2088.41 | 9294.78 | 10538.3 | 0.21 | 1.25 | 14.878 | 11.031 | 1 | 1 | 2850 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2735545.6067 | 204881.0285 | 7910.8631 | 17552.1455 | 187328.883 | 11854.8164 | 0.10859 | -91539.7498 | 91539.7498
C | Xist Rating 2599 | -43.56 | 1311.27 | 150.283 | 35.6 | 2090.61 | 9338.39 | 10538.3 | 0.21 | 1.25 | 14.882 | 11.041 | 1 | 1 | 2860 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2741354.1747 | 206259.5099 | 7966.4753 | 17613.732 | 188645.7779 | 11866.7096 | 0.10897 | -91631.5857 | 91631.5857
C | Xist Rating 2600 | -43.46 | 1312.46 | 150.283 | 35.6 | 2093.26 | 9391.63 | 10538.2 | 0.21 | 1.25 | 14.887 | 11.049 | 1 | 1 | 2870 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2747320.0196 | 207642.6039 | 8022.2824 | 17675.3185 | 189967.2855 | 11876.5535 | 0.10935 | -91707.5979 | 91707.5979
C | Xist Rating 2601 | -43.37 | 1313.97 | 150.283 | 35.6 | 2095.27 | 9432.18 | 10538.2 | 0.2 | 1.25 | 14.933 | 11.059 | 1 | 1 | 2880 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2753121.9219 | 209030.3106 | 8078.2842 | 17736.9049 | 191293.4056 | 11870.3091 | 0.10973 | -91659.3805 | 91659.3805
C | Xist Rating 2602 | -43.29 | 1315.31 | 150.283 | 35.6 | 2096.72 | 9461.75 | 10538.2 | 0.2 | 1.25 | 14.934 | 11.069 | 1 | 1 | 2890 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2757836.7832 | 210422.6298 | 8134.4807 | 17798.4914 | 192624.1383 | 11882.0587 | 0.11011 | -91750.108 | 91750.108
C | Xist Rating 2603 | -43.21 | 1316.7 | 150.283 | 35.6 | 2098.55 | 9499.03 | 10538.2 | 0.2 | 1.25 | 14.934 | 11.078 | 1 | 1 | 2900 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2763160.785 | 211819.5615 | 8190.8721 | 17860.0779 | 193959.4837 | 11892.7441 | 0.11049 | -91832.6172 | 91832.6172
C | Xist Rating 2604 | -43.13 | 1318.24 | 150.283 | 35.5 | 2099.78 | 9524.44 | 10538.2 | 0.2 | 1.25 | 14.937 | 11.088 | 1 | 1 | 2910 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2768013.9872 | 213221.1059 | 8247.4583 | 17921.6644 | 195299.4416 | 11904.5461 | 0.11087 | -91923.7496 | 91923.7496
C | Xist Rating 2605 | -43.04 | 1319.63 | 150.283 | 35.5 | 2101.81 | 9566.29 | 10538.1 | 0.2 | 1.25 | 14.941 | 11.097 | 1 | 1 | 2920 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2773611.5303 | 214627.2629 | 8304.2393 | 17983.2508 | 196644.0121 | 11915.3364 | 0.11125 | -92007.0694 | 92007.0694
C | Xist Rating 2606 | -42.82 | 1321.02 | 150.283 | 35.5 | 2109.08 | 9719.06 | 10537.9 | 0.19 | 1.25 | 14.993 | 11.107 | 1 | 1 | 2930 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2786136.8616 | 216038.0325 | 8361.215 | 18044.8373 | 197993.1952 | 11908.7355 | 0.11164 | -91956.0989 | 91956.0989
C | Xist Rating 2607 | -42.8 | 1322.38 | 150.283 | 35.5 | 2108.43 | 9705.21 | 10537.9 | 0.19 | 1.25 | 14.988 | 11.116 | 1 | 1 | 2940 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2788145.6634 | 217453.4146 | 8418.3855 | 18106.4238 | 199346.9908 | 11919.2337 | 0.11202 | -92037.1632 | 92037.1632
C | Xist Rating 2608 | -42.78 | 1323.79 | 150.283 | 35.5 | 2107.85 | 9692.87 | 10537.9 | 0.19 | 1.25 | 14.984 | 11.125 | 1 | 1 | 2950 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2790350.7515 | 218873.4094 | 8475.7509 | 18168.0103 | 200705.3991 | 11929.7562 | 0.1124 | -92118.4149 | 92118.4149
C | Xist Rating 2609 | -42.76 | 1325.16 | 150.283 | 35.5 | 2107.19 | 9678.97 | 10537.9 | 0.19 | 1.25 | 14.98 | 11.134 | 1 | 1 | 2960 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2792363.9004 | 220298.0167 | 8533.311 | 18229.5967 | 202068.42 | 11940.278 | 0.11278 | -92199.6614 | 92199.6614
C | Xist Rating 2610 | -42.74 | 1326.55 | 150.283 | 35.5 | 2106.56 | 9665.67 | 10537.9 | 0.18 | 1.25 | 14.976 | 11.143 | 1 | 1 | 2970 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2794457.168 | 221727.2366 | 8591.0659 | 18291.1832 | 203436.0534 | 11930.8616 | 0.11316 | -92126.951 | 92126.951
C | Xist Rating 2611 | -42.72 | 1327.77 | 150.283 | 35.5 | 2105.99 | 9653.69 | 10537.9 | 0.18 | 1.25 | 15.012 | 11.152 | 1 | 1 | 2980 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2796270.3423 | 223161.0692 | 8649.0156 | 18352.7697 | 204808.2995 | 11942.282 | 0.11354 | -92215.1363 | 92215.1363
C | Xist Rating 2612 | -42.7 | 1329.33 | 150.283 | 35.5 | 2105.3 | 9639.22 | 10537.9 | 0.18 | 1.25 | 15.008 | 11.161 | 1 | 1 | 2990 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2798638.449 | 224599.5143 | 8707.16 | 18414.3562 | 206185.1581 | 11952.7433 | 0.11392 | -92295.9151 | 92295.9151
C | Xist Rating 2613 | -42.68 | 1330.76 | 150.283 | 35.5 | 2104.67 | 9626.08 | 10537.9 | 0.18 | 1.25 | 15.004 | 11.171 | 1 | 1 | 3000 | 152.4 | 2 | 2.2 | 19.05 | 1.3333 | 11 | E | Rod | 2800810.6492 | 226042.572 | 8765.4993 | 18475.9426 | 207566.6294 | 11964.2423 | 0.1143 | -92384.7079 | 92384.7079
C | Xist Rating 2614 | -93.22 | 124.991 | 150.285 | 35.8 | 2404.23 | 7448.06 | 58746 | 2.44 | 10.95 | 15.816 | 385.028 | 1 | 1 | 1000 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 300507.1119 | 30549.8612 | 973.9444 | 6438.5861 | 24111.2751 | 401580.7991 | 0.038101 | -3100900.4833 | 3100900.4833
C | Xist Rating 2615 | -93.16 | 126.315 | 150.286 | 35.8 | 2401.39 | 7429.46 | 58284.3 | 2.43 | 10.85 | 15.84 | 377.839 | 1 | 1 | 1010 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 303331.5779 | 31098.8837 | 993.5206 | 6502.9719 | 24595.9118 | 394127.8122 | 0.038482 | -3043350.4942 | 3043350.4942
C | Xist Rating 2616 | -92.64 | 136.203 | 150.286 | 35.8 | 2395.63 | 7439.93 | 54967.8 | 2.44 | 10.07 | 15.893 | 327.431 | 1 | 1 | 1020 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 326291.9929 | 31652.7284 | 1013.2917 | 6567.3578 | 25085.3706 | 341809.5923 | 0.038863 | -2639363.0684 | 2639363.0684
C | Xist Rating 2617 | -92.56 | 138.997 | 150.285 | 35.8 | 2375.16 | 7262.07 | 54179.1 | 2.35 | 9.89 | 15.591 | 316.571 | 1 | 1 | 1030 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 330140.1145 | 32211.3954 | 1033.2576 | 6631.7437 | 25579.6518 | 330450.0763 | 0.039244 | -2551647.8966 | 2551647.8966
C | Xist Rating 2618 | -92.48 | 140.396 | 150.285 | 35.8 | 2377.39 | 7290.98 | 53794.7 | 2.3 | 9.8 | 15.522 | 311.38 | 1 | 1 | 1040 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 333776.0464 | 32774.8847 | 1053.4182 | 6696.1295 | 26078.7552 | 325031.9153 | 0.039625 | -2509810.2931 | 2509810.2931
C | Xist Rating 2619 | -92.32 | 143.069 | 150.285 | 35.8 | 2385.32 | 7382.57 | 53043.9 | 2.25 | 9.63 | 15.484 | 301.121 | 1 | 1 | 1050 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 341265.3471 | 33343.1962 | 1073.7737 | 6760.5154 | 26582.6808 | 314353.4107 | 0.040006 | -2427353.7114 | 2427353.7114
C | Xist Rating 2620 | -92.2 | 144.448 | 150.285 | 35.8 | 2399.71 | 7530.63 | 52677.6 | 2.2 | 9.54 | 15.473 | 296.294 | 1 | 1 | 1060 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 346633.3101 | 33916.33 | 1094.3239 | 6824.9012 | 27091.4287 | 309318.26 | 0.040387 | -2388473.6124 | 2388473.6124
C | Xist Rating 2621 | -91.7 | 155.153 | 150.284 | 35.8 | 2378.01 | 7387.8 | 49857.8 | 2.19 | 8.9 | 15.379 | 259.295 | 1 | 1 | 1070 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 368955.3855 | 34494.286 | 1115.0689 | 6889.2871 | 27604.9989 | 270892.8208 | 0.040768 | -2091762.5566 | 2091762.5566
C | Xist Rating 2622 | -91.57 | 157.225 | 150.284 | 35.8 | 2384.95 | 7467.57 | 49381.4 | 2.13 | 8.79 | 15.314 | 253.547 | 1 | 1 | 1080 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 374973.7637 | 35077.0643 | 1136.0087 | 6953.673 | 28123.3913 | 264887.256 | 0.041149 | -2045389.1768 | 2045389.1768
C | Xist Rating 2623 | -91.43 | 159.978 | 150.284 | 35.8 | 2384.32 | 7477.94 | 48761.3 | 2.08 | 8.65 | 15.214 | 246.144 | 1 | 1 | 1090 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 381438.745 | 35664.6648 | 1157.1433 | 7018.0588 | 28646.606 | 257166.2996 | 0.04153 | -1985769.9981 | 1985769.9981
C | Xist Rating 2624 | -91.31 | 162.019 | 150.284 | 35.8 | 2390.05 | 7547.2 | 48308.7 | 2.04 | 8.55 | 15.203 | 240.794 | 1 | 1 | 1100 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 387233.511 | 36257.0876 | 1178.4727 | 7082.4447 | 29174.6429 | 251593.4051 | 0.041911 | -1942737.5838 | 1942737.5838
C | Xist Rating 2625 | -91.25 | 163.586 | 150.284 | 35.8 | 2383.64 | 7491.9 | 48010.8 | 1.97 | 8.49 | 15.01 | 237.58 | 1 | 1 | 1110 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 389930.133 | 36854.3326 | 1199.9969 | 7146.8305 | 29707.5021 | 248197.7055 | 0.042292 | -1916516.8917 | 1916516.8917
C | Xist Rating 2626 | -90.63 | 175.44 | 150.284 | 35.8 | 2381.45 | 7546.54 | 45448.1 | 2.01 | 7.92 | 15.186 | 207.884 | 1 | 1 | 1120 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 417801.588 | 37456.3999 | 1221.7158 | 7211.2164 | 30245.1835 | 217419.6132 | 0.042673 | -1678856.6217 | 1678856.6217
C | Xist Rating 2627 | -90.57 | 176.961 | 150.284 | 35.8 | 2379.11 | 7531.24 | 45188.9 | 1.95 | 7.86 | 15.059 | 205.283 | 1 | 1 | 1130 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 421009.6847 | 38063.2895 | 1243.6296 | 7275.6023 | 30787.6872 | 214673.4652 | 0.043054 | -1657651.5944 | 1657651.5944
C | Xist Rating 2628 | -90.44 | 179.784 | 150.283 | 35.8 | 2374.85 | 7504.95 | 44681.8 | 1.89 | 7.75 | 14.949 | 199.996 | 1 | 1 | 1140 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 426960.0324 | 38675.0013 | 1265.7381 | 7339.9881 | 31335.0132 | 209139.2921 | 0.043435 | -1614918.177 | 1614918.177
C | Xist Rating 2629 | -90.26 | 182.545 | 150.283 | 35.8 | 2383.29 | 7606.62 | 44186.9 | 1.85 | 7.64 | 14.849 | 194.863 | 1 | 1 | 1150 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 435057.673 | 39291.5353 | 1288.0414 | 7404.374 | 31887.1614 | 203780.984 | 0.043816 | -1573542.7422 | 1573542.7422
C | Xist Rating 2630 | -90.12 | 185.384 | 150.283 | 35.8 | 2382.7 | 7617.18 | 43704.2 | 1.79 | 7.53 | 14.758 | 189.995 | 1 | 1 | 1160 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 14 | E | Rod | 441714.4568 | 39912.8917 | 1310.5395 | 7468.7598 | 32444.1318 | 198683.0918 | 0.044197 | -1534178.1695 | 1534178.1695
C | Xist Rating 2631 | -89.55 | 196.075 | 150.283 | 35.8 | 2382.28 | 7681.76 | 41833.2 | 1.81 | 7.13 | 14.791 | 170.933 | 1 | 1 | 1170 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 467105.551 | 40539.0702 | 1333.2324 | 7533.1457 | 33005.9245 | 178917.6883 | 0.044578 | -1381554.9632 | 1381554.9632
C | Xist Rating 2632 | -89.48 | 196.928 | 150.283 | 35.8 | 2390.82 | 7775.52 | 41726.3 | 1.76 | 7.11 | 14.743 | 170.059 | 1 | 1 | 1180 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 470819.401 | 41170.0711 | 1356.1201 | 7597.5316 | 33572.5395 | 177978.4555 | 0.044959 | -1374302.4566 | 1374302.4566
C | Xist Rating 2633 | -89.24 | 202.435 | 150.283 | 35.8 | 2379.43 | 7689.66 | 40886.5 | 1.72 | 6.93 | 14.641 | 162.154 | 1 | 1 | 1190 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 481679.912 | 41805.8941 | 1379.2026 | 7661.9174 | 34143.9767 | 169739.9418 | 0.04534 | -1310686.8376 | 1310686.8376
C | Xist Rating 2634 | -89.12 | 203.848 | 150.283 | 35.8 | 2392.15 | 7832.73 | 40683 | 1.69 | 6.88 | 14.656 | 160.321 | 1 | 1 | 1200 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 487634.9932 | 42446.5395 | 1402.4799 | 7726.3033 | 34720.2362 | 167825.3998 | 0.045721 | -1295903.2513 | 1295903.2513
C | Xist Rating 2635 | -88.99 | 206.756 | 150.282 | 35.8 | 2387.38 | 7798.96 | 40282.1 | 1.64 | 6.8 | 14.568 | 156.762 | 1 | 1 | 1210 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 493605.1393 | 43092.0071 | 1425.9519 | 7790.6891 | 35301.3179 | 164092.9133 | 0.046102 | -1267081.98 | 1267081.98
C | Xist Rating 2636 | -88.4 | 218.964 | 150.283 | 35.8 | 2374.76 | 7742.46 | 38539.2 | 1.64 | 6.43 | 14.597 | 141.027 | 1 | 1 | 1220 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 519986.9486 | 43742.2969 | 1449.6188 | 7855.075 | 35887.2219 | 147765.4508 | 0.046483 | -1141005.6428 | 1141005.6428
C | Xist Rating 2637 | -88.24 | 221.723 | 150.283 | 35.8 | 2381.23 | 7828.69 | 38184.2 | 1.61 | 6.35 | 14.592 | 138.033 | 1 | 1 | 1230 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 527973.4593 | 44397.409 | 1473.4804 | 7919.4609 | 36477.9481 | 144642.3294 | 0.046864 | -1116889.7275 | 1116889.7275
C | Xist Rating 2638 | -88.1 | 224.622 | 150.282 | 35.8 | 2378.83 | 7819.69 | 37836.5 | 1.57 | 6.28 | 14.529 | 135.207 | 1 | 1 | 1240 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 534337.5523 | 45057.3434 | 1497.5369 | 7983.8467 | 37073.4966 | 141680.1235 | 0.047245 | -1094016.3585 | 1094016.3585
C | Xist Rating 2639 | -88.02 | 226.179 | 150.282 | 35.8 | 2380.34 | 7844.53 | 37665.3 | 1.53 | 6.24 | 14.484 | 133.896 | 1 | 1 | 1250 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 538382.9209 | 45722.1 | 1521.7881 | 8048.2326 | 37673.8674 | 140292.4562 | 0.047626 | -1083301.1596 | 1083301.1596
C | Xist Rating 2640 | -87.82 | 230.34 | 150.282 | 35.8 | 2377.97 | 7844.22 | 37162.2 | 1.51 | 6.14 | 14.454 | 129.785 | 1 | 1 | 1260 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 547741.6098 | 46391.6788 | 1546.2341 | 8112.6185 | 38279.0604 | 136014.2033 | 0.048007 | -1050265.6242 | 1050265.6242
C | Xist Rating 2641 | -87.25 | 241.911 | 150.282 | 35.8 | 2370.73 | 7838.85 | 35778.3 | 1.51 | 5.85 | 14.508 | 118.576 | 1 | 1 | 1270 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 573505.665 | 47066.08 | 1570.8749 | 8177.0043 | 38889.0757 | 124388.0996 | 0.048388 | -960491.9331 | 960491.9331
C | Xist Rating 2642 | -87.12 | 244.878 | 150.282 | 35.8 | 2367.03 | 7815.12 | 35478 | 1.47 | 5.79 | 14.452 | 116.377 | 1 | 1 | 1280 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 579633.5723 | 47745.3033 | 1595.7105 | 8241.3902 | 39503.9132 | 122076.242 | 0.048769 | -942640.3816 | 942640.3816
C | Xist Rating 2643 | -86.95 | 247.793 | 150.282 | 35.8 | 2371.43 | 7880.14 | 35183.5 | 1.44 | 5.73 | 14.446 | 114.221 | 1 | 1 | 1290 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 587623.754 | 48429.349 | 1620.7408 | 8305.776 | 40123.5729 | 119821.1924 | 0.04915 | -925227.4869 | 925227.4869
C | Xist Rating 2644 | -86.7 | 251.932 | 150.282 | 35.8 | 2378.1 | 7979.95 | 34752.4 | 1.41 | 5.64 | 14.456 | 111.004 | 1 | 1 | 1300 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 599119.4892 | 49118.2169 | 1645.966 | 8370.1619 | 40748.055 | 116465.2353 | 0.049531 | -899313.6751 | 899313.6751
C | Xist Rating 2645 | -86.56 | 254.198 | 150.282 | 35.8 | 2383.28 | 8051.71 | 34541.4 | 1.38 | 5.59 | 14.427 | 109.535 | 1 | 1 | 1310 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 605825.0094 | 49811.907 | 1671.3859 | 8434.5478 | 41377.3592 | 114921.0019 | 0.049912 | -887389.5142 | 887389.5142
C | Xist Rating 2646 | -85.99 | 265.866 | 150.282 | 35.7 | 2377.78 | 8064.95 | 33363.9 | 1.38 | 5.35 | 14.471 | 100.924 | 1 | 1 | 1320 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 632170.8575 | 50510.4194 | 1697.0007 | 8498.9336 | 42011.4858 | 105991.009 | 0.050293 | -818434.476 | 818434.476
C | Xist Rating 2647 | -85.79 | 270.223 | 150.282 | 35.7 | 2372.72 | 8032.88 | 32980.8 | 1.34 | 5.28 | 14.385 | 98.339 | 1 | 1 | 1330 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 641163.5166 | 51213.754 | 1722.8102 | 8563.3195 | 42650.4346 | 103274.0632 | 0.050674 | -797454.941 | 797454.941
C | Xist Rating 2648 | -85.57 | 274.478 | 150.282 | 35.7 | 2373.35 | 8065.88 | 32608 | 1.32 | 5.2 | 14.365 | 95.83 | 1 | 1 | 1340 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 651432.3613 | 51921.911 | 1748.8145 | 8627.7053 | 43294.2056 | 100658.2446 | 0.051055 | -777256.2832 | 777256.2832
C | Xist Rating 2649 | -85.44 | 276.76 | 150.282 | 35.7 | 2377.39 | 8125.89 | 32424.9 | 1.29 | 5.16 | 14.341 | 94.669 | 1 | 1 | 1350 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 657966.4564 | 52634.8901 | 1775.0136 | 8692.0912 | 43942.7989 | 99433.0958 | 0.051436 | -767796.0089 | 767796.0089
C | Xist Rating 2650 | -85.27 | 278.12 | 150.282 | 35.7 | 2394.1 | 8333.74 | 32304.1 | 1.28 | 5.14 | 14.378 | 93.871 | 1 | 1 | 1360 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 665847.092 | 53352.6915 | 1801.4075 | 8756.4771 | 44596.2145 | 98606.8112 | 0.051817 | -761415.6584 | 761415.6584
C | Xist Rating 2651 | -84.57 | 294.828 | 150.282 | 35.7 | 2366.37 | 8111.91 | 30903.5 | 1.27 | 4.86 | 14.358 | 84.672 | 1 | 1 | 1370 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 697672.1344 | 54075.3152 | 1827.9962 | 8820.8629 | 45254.4523 | 89051.5244 | 0.052198 | -687632.2666 | 687632.2666
C | Xist Rating 2652 | -84.5 | 296.449 | 150.282 | 35.7 | 2366.1 | 8117.43 | 30795.1 | 1.24 | 4.84 | 14.333 | 84.065 | 1 | 1 | 1380 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 701427.9789 | 54802.7611 | 1854.7797 | 8885.2488 | 45917.5124 | 88400.7672 | 0.052579 | -682607.2917 | 682607.2917
C | Xist Rating 2653 | -84.32 | 300.113 | 150.282 | 35.7 | 2366.58 | 8144.67 | 30527.9 | 1.22 | 4.79 | 14.309 | 82.459 | 1 | 1 | 1390 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 710241.4235 | 55535.0293 | 1881.7579 | 8949.6346 | 46585.3947 | 86721.2203 | 0.05296 | -669638.2761 | 669638.2761
C | Xist Rating 2654 | -84.12 | 303.774 | 150.282 | 35.7 | 2368.19 | 8185.58 | 30265.9 | 1.19 | 4.73 | 14.289 | 80.9 | 1 | 1 | 1400 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 719394.5491 | 56272.1198 | 1908.931 | 9014.0205 | 47258.0992 | 85081.5941 | 0.053341 | -656977.5172 | 656977.5172
C | Xist Rating 2655 | -83.91 | 308.09 | 150.282 | 35.7 | 2367.81 | 8207.28 | 29958.1 | 1.17 | 4.67 | 14.271 | 79.07 | 1 | 1 | 1410 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 729498.5829 | 57014.0324 | 1936.2988 | 9078.4064 | 47935.6261 | 83169.3708 | 0.053722 | -642211.8358 | 642211.8358
C | Xist Rating 2656 | -83.3 | 320.54 | 150.282 | 35.7 | 2362.93 | 8229.18 | 29052.4 | 1.18 | 4.49 | 14.326 | 73.625 | 1 | 1 | 1420 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 757413.5822 | 57760.7674 | 1963.8614 | 9142.7922 | 48617.9752 | 77535.4459 | 0.054103 | -598708.1611 | 598708.1611
C | Xist Rating 2657 | -83.21 | 323.063 | 150.282 | 35.7 | 2359.15 | 8196.47 | 28911.2 | 1.14 | 4.47 | 14.275 | 72.908 | 1 | 1 | 1430 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 762154.0765 | 58512.3246 | 1991.6188 | 9207.1781 | 49305.1465 | 76757.9619 | 0.054484 | -592704.6352 | 592704.6352
C | Xist Rating 2658 | -82.94 | 328.739 | 150.282 | 35.7 | 2357.09 | 8206.07 | 28542.4 | 1.13 | 4.39 | 14.262 | 70.834 | 1 | 1 | 1440 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 774867.4095 | 59268.704 | 2019.571 | 9271.5639 | 49997.1401 | 74601.2483 | 0.054865 | -576051.0649 | 576051.0649
C | Xist Rating 2659 | -82.76 | 332.438 | 150.282 | 35.7 | 2356.67 | 8222.68 | 28317.5 | 1.11 | 4.35 | 14.247 | 69.62 | 1 | 1 | 1450 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 783446.6615 | 60029.9058 | 2047.718 | 9335.9498 | 50693.956 | 73328.1136 | 0.055246 | -566220.2564 | 566220.2564
C | Xist Rating 2660 | -82.6 | 334.601 | 150.282 | 35.7 | 2364.71 | 8334.63 | 28184.4 | 1.09 | 4.33 | 14.256 | 68.906 | 1 | 1 | 1460 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 791234.3307 | 60795.9297 | 2076.0598 | 9400.3357 | 51395.5941 | 72575.7088 | 0.055627 | -560410.3858 | 560410.3858
C | Xist Rating 2661 | -81.99 | 348.84 | 150.282 | 35.7 | 2348.67 | 8226.07 | 27311 | 1.08 | 4.16 | 14.261 | 64.141 | 1 | 1 | 1470 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 819310.0428 | 61566.7759 | 2104.5964 | 9464.7215 | 52102.0544 | 67625.1914 | 0.056008 | -522183.8025 | 522183.8025
C | Xist Rating 2662 | -81.77 | 353.199 | 150.282 | 35.7 | 2348.91 | 8254.92 | 27066.7 | 1.07 | 4.11 | 14.25 | 62.888 | 1 | 1 | 1480 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 829632.6631 | 62342.4444 | 2133.3277 | 9529.1074 | 52813.337 | 66320.6151 | 0.056389 | -512110.2099 | 512110.2099
C | Xist Rating 2663 | -81.55 | 356.9 | 150.282 | 35.7 | 2353.87 | 8338.32 | 26867.2 | 1.05 | 4.07 | 14.249 | 61.888 | 1 | 1 | 1490 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 840096.203 | 63122.9352 | 2162.2539 | 9593.4932 | 53529.4419 | 65269.8464 | 0.05677 | -503996.4526 | 503996.4526
C | Xist Rating 2664 | -81.34 | 360.693 | 150.282 | 35.7 | 2356.62 | 8395.15 | 26670.7 | 1.03 | 4.03 | 14.235 | 60.925 | 1 | 1 | 1500 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 850016.3377 | 63908.2481 | 2191.3748 | 9657.8791 | 54250.369 | 64256.3481 | 0.057151 | -496170.4873 | 496170.4873
C | Xist Rating 2665 | -81.09 | 365.079 | 150.282 | 35.7 | 2360.78 | 8475.17 | 26439.2 | 1.01 | 3.99 | 14.234 | 59.777 | 1 | 1 | 1510 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 861871.2016 | 64698.3834 | 2220.6906 | 9722.265 | 54976.1184 | 63051.3857 | 0.057532 | -486866.0876 | 486866.0876
C | Xist Rating 2666 | -80.4 | 379.001 | 150.282 | 35.7 | 2359.13 | 8546.82 | 25681.5 | 1.02 | 3.85 | 14.298 | 55.94 | 1 | 1 | 1520 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 894112.6291 | 65493.3409 | 2250.2011 | 9786.6508 | 55706.6901 | 59087.2573 | 0.057913 | -456256.1388 | 456256.1388
C | Xist Rating 2667 | -80.22 | 383.732 | 150.282 | 35.7 | 2351.87 | 8479.01 | 25468.8 | 0.99 | 3.8 | 14.255 | 54.981 | 1 | 1 | 1530 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 902487.7788 | 66293.1206 | 2279.9064 | 9851.0367 | 56442.0839 | 58065.5376 | 0.058294 | -448366.6898 | 448366.6898
C | Xist Rating 2668 | -80.06 | 386.17 | 150.282 | 35.7 | 2356.52 | 8553.31 | 25364.2 | 0.97 | 3.79 | 14.246 | 54.529 | 1 | 1 | 1540 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 910017.3284 | 67097.7226 | 2309.8065 | 9915.4226 | 57182.3001 | 57582.1791 | 0.058675 | -444634.3235 | 444634.3235
C | Xist Rating 2669 | -79.71 | 393.331 | 150.282 | 35.7 | 2355.85 | 8590.1 | 25021.5 | 0.96 | 3.72 | 14.242 | 52.92 | 1 | 1 | 1550 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 926628.8363 | 67907.1469 | 2339.9013 | 9979.8084 | 57927.3385 | 55907.2646 | 0.059056 | -431701.078 | 431701.078
C | Xist Rating 2670 | -79.51 | 395.544 | 150.282 | 35.7 | 2367.86 | 8766.27 | 24921.1 | 0.94 | 3.7 | 14.258 | 52.473 | 1 | 1 | 1560 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 936592.8158 | 68721.3934 | 2370.191 | 10044.1943 | 58677.1991 | 55430.3182 | 0.059437 | -428018.2244 | 428018.2244
C | Xist Rating 2671 | -78.85 | 412.129 | 150.282 | 35.7 | 2346.66 | 8588.01 | 24162.6 | 0.94 | 3.56 | 14.264 | 48.991 | 1 | 1 | 1570 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 967126.6391 | 69540.4622 | 2400.6755 | 10108.5801 | 59431.8821 | 51820.6713 | 0.059818 | -400145.4875 | 400145.4875
C | Xist Rating 2672 | -78.63 | 415.95 | 150.282 | 35.7 | 2349.8 | 8653.25 | 24008 | 0.92 | 3.53 | 14.257 | 48.339 | 1 | 1 | 1580 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 977399.31 | 70364.3532 | 2431.3547 | 10172.966 | 60191.3872 | 51128.92 | 0.0602 | -394803.9675 | 394803.9675
C | Xist Rating 2673 | -78.42 | 419.807 | 150.282 | 35.7 | 2352.75 | 8716.49 | 23855.6 | 0.9 | 3.5 | 14.247 | 47.704 | 1 | 1 | 1590 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 987700.9193 | 71193.0665 | 2462.2288 | 10237.3519 | 60955.7146 | 50454.3892 | 0.060581 | -389595.4194 | 389595.4194
C | Xist Rating 2674 | -78.12 | 424.879 | 150.282 | 35.7 | 2357.72 | 8818.32 | 23645.7 | 0.89 | 3.46 | 14.253 | 46.805 | 1 | 1 | 1600 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1001745.7159 | 72026.602 | 2493.2976 | 10301.7377 | 61724.8643 | 49516.6918 | 0.060962 | -382354.7685 | 382354.7685
C | Xist Rating 2675 | -78 | 427.513 | 150.282 | 35.7 | 2357.64 | 8831.49 | 23557 | 0.87 | 3.45 | 14.234 | 46.477 | 1 | 1 | 1610 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1007921.7493 | 72864.9598 | 2524.5612 | 10366.1236 | 62498.8363 | 49159.9853 | 0.061343 | -379600.3759 | 379600.3759
C | Xist Rating 2676 | -77.19 | 445.975 | 150.282 | 35.7 | 2343.87 | 8763.08 | 22805.4 | 0.87 | 3.31 | 14.266 | 43.256 | 1 | 1 | 1620 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1045307.4232 | 73708.1399 | 2556.0196 | 10430.5094 | 63277.6304 | 45822.5545 | 0.061724 | -353829.6193 | 353829.6193
C | Xist Rating 2677 | -77.01 | 448.264 | 150.282 | 35.7 | 2351.7 | 8887.86 | 22723.7 | 0.86 | 3.29 | 14.275 | 42.943 | 1 | 1 | 1630 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1054182.4488 | 74556.1422 | 2587.6728 | 10494.8953 | 64061.2469 | 45493.21 | 0.062105 | -351286.5087 | 351286.5087
C | Xist Rating 2678 | -76.83 | 452.268 | 150.282 | 35.7 | 2350.54 | 8895.15 | 22589 | 0.85 | 3.27 | 14.257 | 42.435 | 1 | 1 | 1640 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1063074.0247 | 75408.9667 | 2619.5208 | 10559.2812 | 64849.6856 | 44959.5371 | 0.062486 | -347165.6278 | 347165.6278
C | Xist Rating 2679 | -76.6 | 457.698 | 150.282 | 35.7 | 2347.07 | 8878.76 | 22403.4 | 0.83 | 3.24 | 14.239 | 41.722 | 1 | 1 | 1650 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1074249.2449 | 76266.6136 | 2651.5635 | 10623.667 | 65642.9465 | 44202.3256 | 0.062867 | -341318.6417 | 341318.6417
C | Xist Rating 2680 | -76.33 | 462.884 | 150.282 | 35.7 | 2348.94 | 8939.25 | 22221 | 0.82 | 3.2 | 14.24 | 41.011 | 1 | 1 | 1660 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1087286.743 | 77129.0826 | 2683.8011 | 10688.0529 | 66441.0297 | 43458.7167 | 0.063248 | -335576.6909 | 335576.6909
C | Xist Rating 2681 | -75.62 | 479.513 | 150.282 | 35.7 | 2336.19 | 8866.46 | 21633.4 | 0.82 | 3.1 | 14.256 | 38.691 | 1 | 1 | 1670 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1120233.4755 | 77996.3739 | 2716.2334 | 10752.4387 | 67243.9352 | 41055.6166 | 0.063629 | -317020.5888 | 317020.5888
C | Xist Rating 2682 | -75.46 | 481.913 | 150.282 | 35.6 | 2342.23 | 8968.56 | 21560.4 | 0.81 | 3.08 | 14.26 | 38.439 | 1 | 1 | 1680 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1128751.086 | 78868.4875 | 2748.8606 | 10816.8246 | 68051.6629 | 40788.6634 | 0.06401 | -314959.247 | 314959.247
C | Xist Rating 2683 | -75.17 | 488.819 | 150.282 | 35.7 | 2336.65 | 8929.69 | 21346.5 | 0.79 | 3.04 | 14.239 | 37.66 | 1 | 1 | 1690 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1142198.9164 | 79745.4234 | 2781.6825 | 10881.2105 | 68864.2129 | 39961.989 | 0.064391 | -308575.8861 | 308575.8861
C | Xist Rating 2684 | -74.93 | 493.362 | 150.282 | 35.7 | 2338.49 | 8985.28 | 21206.1 | 0.78 | 3.02 | 14.237 | 37.155 | 1 | 1 | 1700 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1153722.1034 | 80627.1814 | 2814.6992 | 10945.5963 | 69681.5851 | 39431.6202 | 0.064772 | -304480.5193 | 304480.5193
C | Xist Rating 2685 | -74.71 | 498.741 | 150.282 | 35.6 | 2337.17 | 8999.65 | 21044.2 | 0.77 | 2.99 | 14.227 | 36.581 | 1 | 1 | 1710 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1165642.503 | 81513.7618 | 2847.9107 | 11009.9822 | 70503.7796 | 38828.997 | 0.065153 | -299827.2222 | 299827.2222
C | Xist Rating 2686 | -74.02 | 514.098 | 150.282 | 35.7 | 2327.82 | 8963.16 | 20567.8 | 0.77 | 2.9 | 14.259 | 34.834 | 1 | 1 | 1720 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1196727.6064 | 82405.1644 | 2881.317 | 11074.368 | 71330.7963 | 37021.5504 | 0.065534 | -285870.5988 | 285870.5988
C | Xist Rating 2687 | -73.72 | 520.874 | 150.282 | 35.6 | 2326.02 | 8978.91 | 20374.9 | 0.76 | 2.87 | 14.251 | 34.168 | 1 | 1 | 1730 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1211563.3415 | 83301.3892 | 2914.9181 | 11138.7539 | 72162.6353 | 36323.3031 | 0.065915 | -280478.9181 | 280478.9181
C | Xist Rating 2688 | -73.53 | 524.082 | 150.282 | 35.6 | 2329.76 | 9054.13 | 20290.2 | 0.75 | 2.85 | 14.249 | 33.896 | 1 | 1 | 1740 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1220985.2803 | 84202.4363 | 2948.714 | 11203.1398 | 72999.2966 | 36034.4543 | 0.066296 | -278248.5045 | 278248.5045
C | Xist Rating 2689 | -73.3 | 530.329 | 150.282 | 35.6 | 2324.08 | 9006.96 | 20123.5 | 0.73 | 2.82 | 14.231 | 33.342 | 1 | 1 | 1750 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1232527.0223 | 85108.3057 | 2982.7046 | 11267.5256 | 73840.7801 | 35440.531 | 0.066677 | -273662.3862 | 273662.3862
C | Xist Rating 2690 | -73.07 | 534.989 | 150.282 | 35.6 | 2324.05 | 9034.91 | 20001.3 | 0.72 | 2.8 | 14.232 | 32.941 | 1 | 1 | 1760 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1243341.1855 | 86018.9973 | 3016.8901 | 11331.9115 | 74687.0858 | 35017.5796 | 0.067058 | -270396.4674 | 270396.4674
C | Xist Rating 2691 | -72.32 | 553.181 | 150.282 | 35.6 | 2311.44 | 8965.25 | 19497.4 | 0.72 | 2.71 | 14.265 | 31.215 | 1 | 1 | 1770 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1278644.6906 | 86934.5112 | 3051.2703 | 11396.2973 | 75538.2138 | 33231.6096 | 0.067439 | -256605.6808 | 256605.6808
C | Xist Rating 2692 | -72.09 | 557.951 | 150.282 | 35.6 | 2311.46 | 8993.48 | 19383.2 | 0.71 | 2.69 | 14.26 | 30.862 | 1 | 1 | 1780 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1289681.4185 | 87854.8473 | 3085.8453 | 11460.6832 | 76394.1641 | 32857.9585 | 0.06782 | -253720.4462 | 253720.4462
C | Xist Rating 2693 | -72.08 | 560.61 | 150.282 | 35.6 | 2302.76 | 8876.6 | 19327.5 | 0.7 | 2.68 | 14.396 | 30.699 | 1 | 1 | 1790 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1290950.2836 | 88780.0057 | 3120.6151 | 11525.0691 | 77254.9366 | 32689.4184 | 0.068201 | -252419.0241 | 252419.0241
C | Xist Rating 2694 | -71.75 | 568.9 | 150.282 | 35.6 | 2300.06 | 8886.92 | 19122.1 | 0.69 | 2.65 | 14.381 | 30.045 | 1 | 1 | 1800 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1308504.134 | 89709.9863 | 3155.5797 | 11589.4549 | 78120.5314 | 32002.3071 | 0.068582 | -247113.3327 | 247113.3327
C | Xist Rating 2695 | -71.55 | 573.542 | 150.282 | 35.6 | 2298.81 | 8895.53 | 19012.6 | 0.68 | 2.63 | 14.376 | 29.709 | 1 | 1 | 1810 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1318464.085 | 90644.7892 | 3190.7391 | 11653.8408 | 78990.9484 | 31645.876 | 0.068963 | -244361.0663 | 244361.0663
C | Xist Rating 2696 | -70.78 | 591.993 | 150.282 | 35.6 | 2288.18 | 8851.85 | 18562.9 | 0.68 | 2.55 | 14.413 | 28.277 | 1 | 1 | 1820 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1354586.5427 | 91584.4144 | 3226.0933 | 11718.2267 | 79866.1877 | 30165.1808 | 0.069344 | -232927.5301 | 232927.5301
C | Xist Rating 2697 | -70.7 | 589.039 | 150.282 | 35.6 | 2306.2 | 9108.68 | 18632 | 0.67 | 2.56 | 14.445 | 28.505 | 1 | 1 | 1830 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1358441.7418 | 92528.8618 | 3261.6423 | 11782.6125 | 80746.2493 | 30396.2875 | 0.069725 | -234712.0746 | 234712.0746
C | Xist Rating 2698 | -70.39 | 592.822 | 150.282 | 35.6 | 2316.1 | 9289.65 | 18546.1 | 0.67 | 2.55 | 14.463 | 28.25 | 1 | 1 | 1840 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1373035.0342 | 93478.1314 | 3297.386 | 11846.9984 | 81631.1331 | 30136.8032 | 0.070106 | -232708.4062 | 232708.4062
C | Xist Rating 2699 | -70.18 | 599.186 | 150.282 | 35.6 | 2309.29 | 9219.99 | 18409.9 | 0.66 | 2.52 | 14.441 | 27.854 | 1 | 1 | 1850 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1383694.2379 | 94432.2234 | 3333.3246 | 11911.3842 | 82520.8391 | 29716.7039 | 0.070487 | -229464.5101 | 229464.5101
C | Xist Rating 2700 | -69.88 | 606.304 | 150.282 | 35.6 | 2305.53 | 9203.6 | 18259.9 | 0.65 | 2.5 | 14.432 | 27.417 | 1 | 1 | 1860 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1397852.0611 | 95391.1375 | 3369.4579 | 11975.7701 | 83415.3674 | 29254.6246 | 0.070868 | -225896.4563 | 225896.4563
C | Xist Rating 2701 | -69.14 | 623.211 | 150.282 | 35.6 | 2299.27 | 9216.88 | 17880.4 | 0.65 | 2.43 | 14.477 | 26.266 | 1 | 1 | 1870 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1432930.356 | 96354.8739 | 3405.7861 | 12040.156 | 84314.718 | 28065.9696 | 0.071249 | -216717.9776 | 216717.9776
C | Xist Rating 2702 | -68.84 | 630.315 | 150.282 | 35.6 | 2296.23 | 9211.26 | 17739.8 | 0.64 | 2.41 | 14.47 | 25.874 | 1 | 1 | 1880 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1447348.2125 | 97323.4326 | 3442.309 | 12104.5418 | 85218.8908 | 27650.5189 | 0.07163 | -213509.9774 | 213509.9774
C | Xist Rating 2703 | -68.57 | 635.005 | 150.282 | 35.6 | 2299.79 | 9298.1 | 17647.4 | 0.63 | 2.39 | 14.478 | 25.62 | 1 | 1 | 1890 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1460378.149 | 98296.8136 | 3479.0267 | 12168.9277 | 86127.8859 | 27379.0596 | 0.072011 | -211413.8408 | 211413.8408
C | Xist Rating 2704 | -68.38 | 640.153 | 150.282 | 35.6 | 2296.25 | 9269.52 | 17556 | 0.61 | 2.38 | 14.467 | 25.384 | 1 | 1 | 1900 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1469951.3263 | 99275.0167 | 3515.9392 | 12233.3135 | 87041.7032 | 27112.8301 | 0.072392 | -209358.0873 | 209358.0873
C | Xist Rating 2705 | -68.15 | 645.022 | 150.282 | 35.6 | 2295.52 | 9286.8 | 17465.7 | 0.6 | 2.36 | 14.476 | 25.145 | 1 | 1 | 1910 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1480660.9014 | 100258.0422 | 3553.0464 | 12297.6994 | 87960.3428 | 26856.6611 | 0.072773 | -207380.0181 | 207380.0181
C | Xist Rating 2706 | -67.28 | 665.572 | 150.283 | 35.6 | 2286.59 | 9278.2 | 17051.2 | 0.61 | 2.29 | 14.517 | 23.958 | 1 | 1 | 1920 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1521890.2795 | 101245.8899 | 3590.3485 | 12362.0853 | 88883.8046 | 25642.4677 | 0.073154 | -198004.3388 | 198004.3388
C | Xist Rating 2707 | -66.98 | 672.752 | 150.283 | 35.6 | 2283.3 | 9267.34 | 16924.8 | 0.6 | 2.27 | 14.518 | 23.629 | 1 | 1 | 1930 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1536094.6416 | 102238.5598 | 3627.8454 | 12426.4711 | 89812.0887 | 25292.2642 | 0.073535 | -195300.1596 | 195300.1596
C | Xist Rating 2708 | -66.77 | 675.05 | 150.283 | 35.6 | 2291.34 | 9416.1 | 16883 | 0.59 | 2.26 | 14.55 | 23.526 | 1 | 1 | 1940 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1546769.067 | 103236.0521 | 3665.537 | 12490.857 | 90745.1951 | 25178.2204 | 0.073916 | -194419.5438 | 194419.5438
C | Xist Rating 2709 | -66.55 | 681.985 | 150.283 | 35.6 | 2283.98 | 9331.76 | 16773 | 0.58 | 2.24 | 14.539 | 23.257 | 1 | 1 | 1950 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1557640.1003 | 104238.3665 | 3703.4235 | 12555.2428 | 91683.1237 | 24889.4367 | 0.074297 | -192189.6331 | 192189.6331
C | Xist Rating 2710 | -66.22 | 689.799 | 150.282 | 35.6 | 2281.3 | 9335.54 | 16637.5 | 0.57 | 2.22 | 14.512 | 22.907 | 1 | 1 | 1960 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1573638.4587 | 105245.5032 | 3741.5047 | 12619.6287 | 92625.8745 | 24515.6167 | 0.074678 | -189303.0934 | 189303.0934
C | Xist Rating 2711 | -65.44 | 708.378 | 150.282 | 35.6 | 2273.73 | 9331.79 | 16303.6 | 0.57 | 2.16 | 14.565 | 22.014 | 1 | 1 | 1970 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1610660.3099 | 106257.4622 | 3779.7807 | 12684.0146 | 93573.4476 | 23594.6131 | 0.075059 | -182191.3479 | 182191.3479
C | Xist Rating 2712 | -65.18 | 713.982 | 150.282 | 35.6 | 2273.81 | 9367.02 | 16214.6 | 0.56 | 2.15 | 14.583 | 21.797 | 1 | 1 | 1980 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1623459.4114 | 107274.2434 | 3818.2515 | 12748.4004 | 94525.843 | 23360.9481 | 0.07544 | -180387.0486 | 180387.0486
C | Xist Rating 2713 | -64.89 | 721.357 | 150.282 | 35.6 | 2269.94 | 9344.98 | 16101.7 | 0.55 | 2.13 | 14.58 | 21.526 | 1 | 1 | 1990 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1637437.1086 | 108295.8469 | 3856.9171 | 12812.7863 | 95483.0606 | 23070.0202 | 0.075821 | -178140.5809 | 178140.5809
C | Xist Rating 2714 | -64.63 | 727.086 | 150.282 | 35.6 | 2269.32 | 9368.28 | 16015.1 | 0.55 | 2.12 | 14.579 | 21.321 | 1 | 1 | 2000 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1649990.8015 | 109322.2727 | 3895.7775 | 12877.1721 | 96445.1005 | 22860.6732 | 0.076202 | -176524.0589 | 176524.0589
C | Xist Rating 2715 | -64.42 | 731.341 | 150.283 | 35.6 | 2270.47 | 9412.22 | 15954 | 0.54 | 2.11 | 14.582 | 21.183 | 1 | 1 | 2010 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1660487.8003 | 110353.5206 | 3934.8326 | 12941.558 | 97411.9626 | 22707.9653 | 0.076583 | -175344.889 | 175344.889
C | Xist Rating 2716 | -63.58 | 752.339 | 150.283 | 35.6 | 2260.57 | 9380.04 | 15615.1 | 0.54 | 2.05 | 14.619 | 20.329 | 1 | 1 | 2020 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1700714.9732 | 111389.5909 | 3974.0826 | 13005.9439 | 98383.647 | 21826.4264 | 0.076964 | -168537.879 | 168537.879
C | Xist Rating 2717 | -63.24 | 760.097 | 150.283 | 35.6 | 2258.88 | 9399.02 | 15500 | 0.53 | 2.03 | 14.618 | 20.057 | 1 | 1 | 2030 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1716967.9114 | 112430.4834 | 4013.5273 | 13070.3297 | 99360.1537 | 21534.1427 | 0.077345 | -166280.9422 | 166280.9422
C | Xist Rating 2718 | -63.06 | 765.444 | 150.283 | 35.6 | 2255.52 | 9369.78 | 15431.8 | 0.52 | 2.02 | 14.611 | 19.913 | 1 | 1 | 2040 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1726474.2509 | 113476.1982 | 4053.1669 | 13134.7156 | 100341.4826 | 21374.3719 | 0.077726 | -165047.2341 | 165047.2341
C | Xist Rating 2719 | -62.82 | 769.977 | 150.283 | 35.6 | 2257.72 | 9436.97 | 15364.3 | 0.52 | 2.01 | 14.616 | 19.756 | 1 | 1 | 2050 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1738392.4724 | 114526.7352 | 4093.0012 | 13199.1014 | 101327.6337 | 21214.9722 | 0.078107 | -163816.392 | 163816.392
C | Xist Rating 2720 | -62.55 | 777.746 | 150.283 | 35.6 | 2252.04 | 9381.58 | 15264.4 | 0.51 | 1.99 | 14.604 | 19.539 | 1 | 1 | 2060 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1751515.1018 | 115582.0944 | 4133.0303 | 13263.4873 | 102318.6071 | 20978.9635 | 0.078488 | -161993.9954 | 161993.9954
C | Xist Rating 2721 | -61.67 | 800.32 | 150.283 | 35.6 | 2240.78 | 9331.2 | 14936.2 | 0.51 | 1.94 | 14.643 | 18.759 | 1 | 1 | 2070 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1793341.0496 | 116642.276 | 4173.2542 | 13327.8732 | 103314.4028 | 20174.1189 | 0.078869 | -155779.1982 | 155779.1982
C | Xist Rating 2722 | -61.44 | 805.47 | 150.283 | 35.6 | 2240.49 | 9354.25 | 14873.8 | 0.5 | 1.93 | 14.643 | 18.63 | 1 | 1 | 2080 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1804647.4803 | 117707.2797 | 4213.6729 | 13392.259 | 104315.0207 | 20029.8476 | 0.07925 | -154665.1738 | 154665.1738
C | Xist Rating 2723 | -61.19 | 812.033 | 150.283 | 35.6 | 2238.15 | 9351.24 | 14791.1 | 0.5 | 1.91 | 14.638 | 18.453 | 1 | 1 | 2090 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1817451.659 | 118777.1058 | 4254.2864 | 13456.6449 | 105320.4609 | 19849.081 | 0.079631 | -153269.342 | 153269.342
C | Xist Rating 2724 | -60.94 | 818.605 | 150.283 | 35.6 | 2235.6 | 9344.5 | 14709.5 | 0.49 | 1.9 | 14.635 | 18.28 | 1 | 1 | 2100 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1830073.338 | 119851.7541 | 4295.0947 | 13521.0308 | 106330.7233 | 19658.7841 | 0.080012 | -151799.9199 | 151799.9199
C | Xist Rating 2725 | -60.69 | 824.428 | 150.283 | 35.6 | 2234.56 | 9359.22 | 14638.8 | 0.48 | 1.89 | 14.633 | 18.134 | 1 | 1 | 2110 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1842233.8317 | 120931.2246 | 4336.0977 | 13585.4166 | 107345.808 | 19496.4452 | 0.080393 | -150546.3819 | 150546.3819
C | Xist Rating 2726 | -59.88 | 845.865 | 150.283 | 35.6 | 2223.89 | 9305.46 | 14359.2 | 0.48 | 1.84 | 14.669 | 17.507 | 1 | 1 | 2120 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1881110.7148 | 122015.5174 | 4377.2956 | 13649.8025 | 108365.7149 | 18850.0972 | 0.080774 | -145555.4539 | 145555.4539
C | Xist Rating 2727 | -59.56 | 853.966 | 150.283 | 35.6 | 2221.36 | 9307.55 | 14263.8 | 0.48 | 1.83 | 14.665 | 17.31 | 1 | 1 | 2130 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1896965.9138 | 123104.6325 | 4418.6882 | 13714.1883 | 109390.4441 | 18648.4858 | 0.081155 | -143998.6645 | 143998.6645
C | Xist Rating 2728 | -59.29 | 862.094 | 150.283 | 35.6 | 2215.76 | 9255.59 | 14170 | 0.47 | 1.81 | 14.664 | 17.118 | 1 | 1 | 2140 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1910193.4014 | 124198.5698 | 4460.2756 | 13778.5742 | 110419.9956 | 18438.137 | 0.081536 | -142374.4064 | 142374.4064
C | Xist Rating 2729 | -59.12 | 866.499 | 150.283 | 35.6 | 2214.92 | 9263.81 | 14123.5 | 0.47 | 1.8 | 14.661 | 17.032 | 1 | 1 | 2150 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1919225.9651 | 125297.3293 | 4502.0578 | 13842.9601 | 111454.3693 | 18351.7796 | 0.081917 | -141707.5775 | 141707.5775
C | Xist Rating 2730 | -58.87 | 872.267 | 150.283 | 35.6 | 2214.97 | 9296.82 | 14059.1 | 0.46 | 1.79 | 14.662 | 16.904 | 1 | 1 | 2160 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1932045.237 | 126400.9112 | 4544.0348 | 13907.3459 | 112493.5652 | 18207.7901 | 0.082298 | -140595.7287 | 140595.7287
C | Xist Rating 2731 | -58 | 895.493 | 150.283 | 35.6 | 2203.81 | 9239.66 | 13786 | 0.46 | 1.75 | 14.698 | 16.327 | 1 | 1 | 2170 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1973496.4283 | 127509.3152 | 4586.2066 | 13971.7318 | 113537.5834 | 17613.2105 | 0.082679 | -136004.5427 | 136004.5427
C | Xist Rating 2732 | -57.68 | 903.369 | 150.283 | 35.6 | 2202.19 | 9256.4 | 13699 | 0.46 | 1.74 | 14.693 | 16.154 | 1 | 1 | 2180 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 1989390.1781 | 128622.5416 | 4628.5732 | 14036.1176 | 114586.4239 | 17436.3561 | 0.08306 | -134638.9203 | 134638.9203
C | Xist Rating 2733 | -57.45 | 909.372 | 150.283 | 35.6 | 2200.29 | 9254.44 | 13638.9 | 0.45 | 1.73 | 14.688 | 16.042 | 1 | 1 | 2190 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 2000882.1179 | 129740.5901 | 4671.1346 | 14100.5035 | 115640.0866 | 17308.4295 | 0.083441 | -133651.1048 | 133651.1048
C | Xist Rating 2734 | -57.24 | 915.78 | 150.283 | 35.6 | 2196.56 | 9220.16 | 13579.4 | 0.44 | 1.72 | 14.682 | 15.938 | 1 | 1 | 2200 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 2011565.7168 | 130863.461 | 4713.8907 | 14164.8894 | 116698.5716 | 17188.6436 | 0.083822 | -132726.1498 | 132726.1498
C | Xist Rating 2735 | -56.94 | 923.914 | 150.283 | 35.6 | 2193.31 | 9207.63 | 13495.5 | 0.44 | 1.7 | 14.679 | 15.776 | 1 | 1 | 2210 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 2026429.8153 | 131991.1541 | 4756.8417 | 14229.2752 | 117761.8788 | 17023.1718 | 0.084203 | -131448.4204 | 131448.4204
C | Xist Rating 2736 | -56.06 | 947.006 | 150.283 | 35.6 | 2184.6 | 9189.66 | 13246.2 | 0.44 | 1.66 | 14.718 | 15.274 | 1 | 1 | 2220 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 13 | E | Rod | 2068829.3076 | 133123.6694 | 4799.9874 | 14293.6611 | 118830.0083 | 16506.4483 | 0.084584 | -127458.4186 | 127458.4186
C | Xist Rating 2737 | -55.81 | 953.541 | 150.283 | 35.6 | 2182.64 | 9190.34 | 13182.5 | 0.43 | 1.65 | 14.709 | 15.157 | 1 | 1 | 2230 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2081236.7282 | 134261.007 | 4843.3279 | 14358.0469 | 119902.9601 | 16372.748 | 0.084965 | -126426.0203 | 126426.0203
C | Xist Rating 2738 | -55.54 | 961.279 | 150.283 | 35.6 | 2179.09 | 9167.08 | 13111.7 | 0.43 | 1.64 | 14.705 | 15.031 | 1 | 1 | 2240 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2094713.4561 | 135403.1669 | 4886.8633 | 14422.4328 | 120980.7341 | 16244.5596 | 0.085346 | -125436.1834 | 125436.1834
C | Xist Rating 2739 | -55.25 | 969.721 | 150.283 | 35.6 | 2175.15 | 9141.3 | 13034.1 | 0.42 | 1.63 | 14.705 | 14.892 | 1 | 1 | 2250 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2109288.6332 | 136550.149 | 4930.5934 | 14486.8187 | 122063.3303 | 16088.2119 | 0.085727 | -124228.9076 | 124228.9076
C | Xist Rating 2740 | -55.06 | 974.088 | 150.283 | 35.6 | 2175.52 | 9169.57 | 12995.6 | 0.42 | 1.62 | 14.705 | 14.828 | 1 | 1 | 2260 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2119147.9258 | 137701.9534 | 4974.5182 | 14551.2045 | 123150.7488 | 16024.5164 | 0.086108 | -123737.068 | 123737.068
C | Xist Rating 2741 | -54.16 | 999.065 | 150.283 | 35.6 | 2164.34 | 9112.7 | 12751.9 | 0.42 | 1.59 | 14.741 | 14.363 | 1 | 1 | 2270 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2162316.3421 | 138858.58 | 5018.6379 | 14615.5904 | 124242.9896 | 15545.9215 | 0.086489 | -120041.4853 | 120041.4853
C | Xist Rating 2742 | -53.88 | 1006.75 | 150.283 | 35.6 | 2161.96 | 9109.2 | 12686.2 | 0.41 | 1.58 | 14.739 | 14.251 | 1 | 1 | 2280 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2176553.23 | 140020.0289 | 5062.9524 | 14679.9762 | 125340.0526 | 15417.2358 | 0.08687 | -119047.8079 | 119047.8079
C | Xist Rating 2743 | -53.54 | 1015.69 | 150.283 | 35.6 | 2159.76 | 9117.48 | 12606.9 | 0.41 | 1.56 | 14.736 | 14.111 | 1 | 1 | 2290 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2193646.6344 | 141186.3 | 5107.4617 | 14744.3621 | 126441.9379 | 15274.4285 | 0.087251 | -117945.0879 | 117945.0879
C | Xist Rating 2744 | -53.34 | 1021.85 | 150.283 | 35.6 | 2156.76 | 9094.14 | 12557.1 | 0.4 | 1.56 | 14.731 | 14.03 | 1 | 1 | 2300 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2203885.206 | 142357.3934 | 5152.1657 | 14808.748 | 127548.6454 | 15177.6198 | 0.087632 | -117197.5568 | 117197.5568
| Xist Rating 2745 | -53.14 | 1028.28 | 150.283 | 35.6 | 2153.52 | 9066.37 | 12507.7 | 0.4 | 1.55 | 14.727 | 13.952 | 1 | 1 | 2310 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2214421.5456 | 143533.309 | 5197.0645 | 14873.1338 | 128660.1752 | 15099.0925 | 0.088013 | -116591.1898 | 116591.1898
| Xist Rating 2746 | -52.19 | 1053.85 | 150.283 | 35.6 | 2144.4 | 9046.06 | 12277.2 | 0.4 | 1.51 | 14.765 | 13.531 | 1 | 1 | 2320 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2259875.94 | 144714.0469 | 5242.1582 | 14937.5197 | 129776.5272 | 14666.1059 | 0.088394 | -113247.782 | 113247.782
| Xist Rating 2747 | -51.93 | 1061.56 | 150.283 | 35.6 | 2141.39 | 9030.29 | 12216.9 | 0.39 | 1.5 | 14.759 | 13.433 | 1 | 1 | 2330 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2273213.9684 | 145899.6071 | 5287.4466 | 15001.9055 | 130897.7015 | 14551.3152 | 0.088775 | -112361.3989 | 112361.3989
| Xist Rating 2748 | -51.67 | 1069.26 | 150.283 | 35.6 | 2138.49 | 9016.35 | 12157.2 | 0.39 | 1.49 | 14.754 | 13.337 | 1 | 1 | 2340 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2286601.8174 | 147089.9895 | 5332.9298 | 15066.2914 | 132023.6981 | 14453.9949 | 0.089156 | -111609.9175 | 111609.9175
| Xist Rating 2749 | -51.44 | 1076.29 | 150.283 | 35.6 | 2135.67 | 8999.44 | 12104.8 | 0.38 | 1.49 | 14.75 | 13.255 | 1 | 1 | 2350 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2298600.2643 | 148285.1942 | 5378.6078 | 15130.6773 | 133154.5169 | 14355.7156 | 0.089537 | -110851.0308 | 110851.0308
| Xist Rating 2750 | -51.15 | 1084.78 | 150.283 | 35.6 | 2132.42 | 8983.08 | 12039.9 | 0.38 | 1.48 | 14.746 | 13.15 | 1 | 1 | 2360 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2313206.5676 | 149485.2211 | 5424.4805 | 15195.0631 | 134290.1579 | 14249.0249 | 0.089918 | -110027.1934 | 110027.1934
| Xist Rating 2751 | -50.3 | 1108.3 | 150.283 | 35.6 | 2124.24 | 8963.15 | 11846.8 | 0.38 | 1.45 | 14.78 | 12.816 | 1 | 1 | 2370 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2354295.192 | 150690.0703 | 5470.5481 | 15259.449 | 135430.6213 | 13906.0507 | 0.090299 | -107378.8377 | 107378.8377
| Xist Rating 2752 | -50.04 | 1116.23 | 150.283 | 35.6 | 2120.92 | 8940.77 | 11791.2 | 0.37 | 1.44 | 14.774 | 12.731 | 1 | 1 | 2380 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2367434.5316 | 151899.7417 | 5516.8105 | 15323.8349 | 136575.9068 | 13804.2914 | 0.09068 | -106593.0788 | 106593.0788
| Xist Rating 2753 | -49.75 | 1124.28 | 150.283 | 35.6 | 2119.03 | 8947.8 | 11730 | 0.37 | 1.43 | 14.769 | 12.633 | 1 | 1 | 2390 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2382383.0484 | 153114.2354 | 5563.2676 | 15388.2207 | 137726.0147 | 13704.7706 | 0.091061 | -105824.606 | 105824.606
C | Xist Rating 2754 | -44.82 | 1289.14 | 150.283 | 35.6 | 2030.85 | 8253.65 | 10538.1 | 0.4 | 1.25 | 14.766 | 10.705 | 1 | 1 | 2400 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2618049.969 | 154333.5513 | 5609.9196 | 15452.6066 | 138880.9447 | 11752.5311 | 0.091442 | -90749.9301 | 90749.9301
C | Xist Rating 2755 | -44.31 | 1290.59 | 150.283 | 35.6 | 2047.36 | 8533.41 | 10538 | 0.39 | 1.25 | 14.763 | 10.714 | 1 | 1 | 2410 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2642302.3424 | 155557.6895 | 5656.7663 | 15516.9924 | 140040.6971 | 11748.4474 | 0.091823 | -90718.3968 | 90718.3968
C | Xist Rating 2756 | -44.31 | 1291.99 | 150.283 | 35.6 | 2046.37 | 8516.28 | 10538 | 0.39 | 1.25 | 14.802 | 10.725 | 1 | 1 | 2420 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2643889.5763 | 156786.65 | 5703.8078 | 15581.3783 | 141205.2717 | 11764.1016 | 0.092204 | -90839.2744 | 90839.2744
C | Xist Rating 2757 | -43.82 | 1293.35 | 150.283 | 35.6 | 2062.63 | 8805.12 | 10538 | 0.39 | 1.25 | 14.796 | 10.734 | 1 | 1 | 2430 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2667702.5105 | 158020.4327 | 5751.0441 | 15645.7642 | 142374.6685 | 11775.7809 | 0.092585 | -90929.4584 | 90929.4584
C | Xist Rating 2758 | -43.8 | 1294.72 | 150.283 | 35.6 | 2061.97 | 8793.1 | 10537.9 | 0.38 | 1.25 | 14.79 | 10.745 | 1 | 1 | 2440 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2669673.7984 | 159259.0376 | 5798.4752 | 15710.15 | 143548.8876 | 11773.3588 | 0.092966 | -90910.7562 | 90910.7562
C | Xist Rating 2759 | -43.78 | 1296.04 | 150.283 | 35.6 | 2061.36 | 8782.03 | 10537.9 | 0.38 | 1.25 | 14.785 | 10.756 | 1 | 1 | 2450 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2671605.0144 | 160502.4648 | 5846.1011 | 15774.5359 | 144727.929 | 11787.0929 | 0.093347 | -91016.807 | 91016.807
C | Xist Rating 2760 | -43.77 | 1297.52 | 150.283 | 35.6 | 2060.43 | 8765.27 | 10537.9 | 0.37 | 1.25 | 14.78 | 10.767 | 1 | 1 | 2460 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2673449.1336 | 161750.7143 | 5893.9217 | 15838.9217 | 145911.7926 | 11784.5276 | 0.093728 | -90996.9981 | 90996.9981
C | Xist Rating 2761 | -43.74 | 1298.87 | 150.283 | 35.6 | 2059.86 | 8755.05 | 10537.9 | 0.36 | 1.25 | 14.817 | 10.777 | 1 | 1 | 2470 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2675490.3582 | 163003.786 | 5941.9372 | 15903.3076 | 147100.4784 | 11782.4746 | 0.094109 | -90981.1458 | 90981.1458
C | Xist Rating 2762 | -43.73 | 1300.22 | 150.283 | 35.6 | 2059.16 | 8742.27 | 10537.9 | 0.36 | 1.25 | 14.811 | 10.788 | 1 | 1 | 2480 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2677361.0152 | 164261.68 | 5990.1474 | 15967.6935 | 148293.9865 | 11796.049 | 0.09449 | -91085.9634 | 91085.9634
C | Xist Rating 2763 | -43.71 | 1301.61 | 150.283 | 35.6 | 2058.34 | 8727.61 | 10537.9 | 0.35 | 1.25 | 14.806 | 10.799 | 1 | 1 | 2490 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2679155.9274 | 165524.3962 | 6038.5525 | 16032.0793 | 149492.3169 | 11793.1361 | 0.094871 | -91063.4711 | 91063.4711
C | Xist Rating 2764 | -43.7 | 1302.6 | 150.283 | 35.6 | 2058.23 | 8725.64 | 10537.9 | 0.35 | 1.25 | 14.804 | 10.807 | 1 | 1 | 2500 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2681050.398 | 166791.9347 | 6087.1523 | 16096.4652 | 150695.4695 | 11803.6885 | 0.095252 | -91144.9539 | 91144.9539
C | Xist Rating 2765 | -43.69 | 1304.45 | 150.283 | 35.6 | 2056.52 | 8694.94 | 10537.9 | 0.34 | 1.25 | 14.801 | 10.82 | 1 | 1 | 2510 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2682627.514 | 168064.2955 | 6135.9469 | 16160.851 | 151903.4444 | 11802.7408 | 0.095633 | -91137.636 | 91137.636
C | Xist Rating 2766 | -43.64 | 1305.9 | 150.283 | 35.6 | 2056.87 | 8701.23 | 10537.8 | 0.34 | 1.25 | 14.833 | 10.831 | 1 | 1 | 2520 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2686066.533 | 169341.4785 | 6184.9363 | 16225.2369 | 153116.2416 | 11817.649 | 0.096014 | -91252.7532 | 91252.7532
C | Xist Rating 2767 | -43.62 | 1307.24 | 150.283 | 35.6 | 2056.28 | 8690.79 | 10537.8 | 0.33 | 1.25 | 14.83 | 10.841 | 1 | 1 | 2530 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2688051.4672 | 170623.4837 | 6234.1205 | 16289.6228 | 154333.861 | 11813.3608 | 0.096395 | -91219.6405 | 91219.6405
C | Xist Rating 2768 | -43.59 | 1308.39 | 150.283 | 35.6 | 2056.65 | 8697.34 | 10537.7 | 0.33 | 1.25 | 14.834 | 10.851 | 1 | 1 | 2540 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2690900.2935 | 171910.3112 | 6283.4995 | 16354.0086 | 155556.3026 | 11826.0897 | 0.096776 | -91317.93 | 91317.93
C | Xist Rating 2769 | -43.57 | 1309.94 | 150.283 | 35.6 | 2055.81 | 8682.34 | 10537.7 | 0.32 | 1.25 | 14.831 | 10.862 | 1 | 1 | 2550 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2692987.7514 | 173201.961 | 6333.0732 | 16418.3945 | 156783.5665 | 11822.642 | 0.097157 | -91291.308 | 91291.308
C | Xist Rating 2770 | -43.56 | 1311.39 | 150.283 | 35.6 | 2055.01 | 8668.15 | 10537.7 | 0.32 | 1.25 | 14.826 | 10.872 | 1 | 1 | 2560 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2694919.5639 | 174498.433 | 6382.8418 | 16482.7803 | 158015.6527 | 11834.9708 | 0.097538 | -91386.5072 | 91386.5072
C | Xist Rating 2771 | -43.53 | 1312.78 | 150.283 | 35.6 | 2054.5 | 8659.16 | 10537.7 | 0.31 | 1.25 | 14.825 | 10.883 | 1 | 1 | 2570 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2697106.51 | 175799.7273 | 6432.8051 | 16547.1662 | 159252.5611 | 11831.4057 | 0.097919 | -91358.9787 | 91358.9787
C | Xist Rating 2772 | -43.51 | 1314.14 | 150.283 | 35.6 | 2053.98 | 8649.88 | 10537.7 | 0.31 | 1.25 | 14.86 | 10.893 | 1 | 1 | 2580 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2699217.2772 | 177105.8438 | 6482.9633 | 16611.5521 | 160494.2918 | 11845.1055 | 0.0983 | -91464.7649 | 91464.7649
C | Xist Rating 2773 | -43.49 | 1315.5 | 150.283 | 35.6 | 2053.64 | 8643.8 | 10537.7 | 0.3 | 1.25 | 14.858 | 10.903 | 1 | 1 | 2590 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2701563.42 | 178416.7826 | 6533.3162 | 16675.9379 | 161740.8447 | 11840.2339 | 0.098681 | -91427.1475 | 91427.1475
C | Xist Rating 2774 | -43.46 | 1316.68 | 150.283 | 35.6 | 2053.5 | 8641.34 | 10537.8 | 0.3 | 1.25 | 14.856 | 10.912 | 1 | 1 | 2600 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2703802.38 | 179732.5436 | 6583.8639 | 16740.3238 | 162992.2199 | 11851.5084 | 0.099062 | -91514.2067 | 91514.2067
C | Xist Rating 2775 | -43.45 | 1318.37 | 150.283 | 35.6 | 2052.2 | 8618.32 | 10537.8 | 0.3 | 1.25 | 14.852 | 10.924 | 1 | 1 | 2610 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2705558.914 | 181053.1269 | 6634.6064 | 16804.7096 | 164248.4173 | 11865.8278 | 0.099443 | -91624.7769 | 91624.7769
C | Xist Rating 2776 | -43.44 | 1319.76 | 150.283 | 35.6 | 2051.28 | 8602.18 | 10537.7 | 0.29 | 1.25 | 14.849 | 10.934 | 1 | 1 | 2620 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2707197.2928 | 182378.5325 | 6685.5437 | 16869.0955 | 165509.437 | 11860.6655 | 0.099824 | -91584.9153 | 91584.9153
C | Xist Rating 2777 | -43.41 | 1321.19 | 150.283 | 35.6 | 2050.99 | 8597.11 | 10537.7 | 0.29 | 1.25 | 14.884 | 10.944 | 1 | 1 | 2630 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2709747.4781 | 183708.7603 | 6736.6758 | 16933.4814 | 166775.2789 | 11874.1773 | 0.10021 | -91689.2498 | 91689.2498
C | Xist Rating 2778 | -43.37 | 1322.43 | 150.283 | 35.6 | 2051.23 | 8601.34 | 10537.7 | 0.28 | 1.25 | 14.881 | 10.953 | 1 | 1 | 2640 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2712608.0889 | 185043.8104 | 6788.0027 | 16997.8672 | 168045.9431 | 11867.7459 | 0.10059 | -91639.5881 | 91639.5881
C | Xist Rating 2779 | -43.35 | 1323.94 | 150.283 | 35.6 | 2050.55 | 8589.39 | 10537.7 | 0.28 | 1.25 | 14.877 | 10.964 | 1 | 1 | 2650 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2714805.167 | 186383.6827 | 6839.5243 | 17062.2531 | 169321.4296 | 11880.9041 | 0.10097 | -91741.1918 | 91741.1918
C | Xist Rating 2780 | -43.35 | 1325.28 | 150.283 | 35.6 | 2049.86 | 8577.39 | 10537.6 | 0.28 | 1.25 | 14.875 | 10.974 | 1 | 1 | 2660 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2716638.4608 | 187728.3772 | 6891.2408 | 17126.639 | 170601.7383 | 11893.0895 | 0.10135 | -91835.2843 | 91835.2843
C | Xist Rating 2781 | -43.33 | 1326.67 | 150.283 | 35.6 | 2048.65 | 8556.16 | 10537.7 | 0.27 | 1.25 | 14.874 | 10.984 | 1 | 1 | 2670 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2717882.4955 | 189077.8941 | 6943.152 | 17191.0248 | 171886.8693 | 11887.5064 | 0.10173 | -91792.1735 | 91792.1735
C | Xist Rating 2782 | -43.28 | 1328.08 | 150.284 | 35.6 | 2049.07 | 8563.5 | 10537.7 | 0.27 | 1.25 | 14.912 | 10.994 | 1 | 1 | 2680 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2721328.8856 | 190432.2331 | 6995.258 | 17255.4107 | 173176.8225 | 11900.9241 | 0.10211 | -91895.7811 | 91895.7811
C | Xist Rating 2783 | -43.26 | 1329.46 | 150.284 | 35.6 | 2048.67 | 8556.55 | 10537.7 | 0.27 | 1.25 | 14.906 | 11.004 | 1 | 1 | 2690 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2723624.8182 | 191791.3945 | 7047.5588 | 17319.7965 | 174471.5979 | 11912.9185 | 0.10249 | -91988.3987 | 91988.3987
C | Xist Rating 2784 | -43.2 | 1330.66 | 150.283 | 35.6 | 2049.47 | 8570.55 | 10537.7 | 0.26 | 1.25 | 14.902 | 11.013 | 1 | 1 | 2700 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2727147.7502 | 193155.3781 | 7100.0544 | 17384.1824 | 175771.1957 | 11905.9029 | 0.10287 | -91934.2263 | 91934.2263
C | Xist Rating 2785 | -43.19 | 1332.32 | 150.283 | 35.6 | 2048.13 | 8546.98 | 10537.7 | 0.26 | 1.25 | 14.895 | 11.024 | 1 | 1 | 2710 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2728764.5616 | 194524.1839 | 7152.7448 | 17448.5683 | 177075.6157 | 11918.842 | 0.10325 | -92034.1389 | 92034.1389
C | Xist Rating 2786 | -43.17 | 1333.66 | 150.283 | 35.6 | 2047.79 | 8541.24 | 10537.7 | 0.26 | 1.25 | 14.892 | 11.033 | 1 | 1 | 2720 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2731055.6114 | 195897.812 | 7205.63 | 17512.9541 | 178384.8579 | 11929.8293 | 0.10363 | -92118.9799 | 92118.9799
C | Xist Rating 2787 | -43.16 | 1334.98 | 150.284 | 35.6 | 2046.86 | 8525.05 | 10537.7 | 0.25 | 1.25 | 14.925 | 11.043 | 1 | 1 | 2730 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2732517.1628 | 197276.2624 | 7258.71 | 17577.34 | 179698.9224 | 11924.7359 | 0.10402 | -92079.65 | 92079.65
C | Xist Rating 2788 | -43.12 | 1336.27 | 150.284 | 35.6 | 2047.12 | 8529.48 | 10537.7 | 0.25 | 1.25 | 14.923 | 11.052 | 1 | 1 | 2740 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2735505.0424 | 198659.535 | 7311.9847 | 17641.7258 | 181017.8091 | 11935.6935 | 0.1044 | -92164.2616 | 92164.2616
C | Xist Rating 2789 | -43.07 | 1337.81 | 150.284 | 35.6 | 2047.34 | 8533.32 | 10537.8 | 0.25 | 1.25 | 14.924 | 11.063 | 1 | 1 | 2750 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2738951.9254 | 200047.6299 | 7365.4543 | 17706.1117 | 182341.5182 | 11948.8201 | 0.10478 | -92265.6217 | 92265.6217
C | Xist Rating 2790 | -43.07 | 1339.24 | 150.284 | 35.6 | 2046.13 | 8512.34 | 10537.7 | 0.24 | 1.25 | 14.917 | 11.072 | 1 | 1 | 2760 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2740259.1412 | 201440.547 | 7419.1186 | 17770.4976 | 183670.0494 | 11941.1678 | 0.10516 | -92206.5324 | 92206.5324
C | Xist Rating 2791 | -42.99 | 1340.47 | 150.284 | 35.6 | 2048.07 | 8545.89 | 10537.8 | 0.24 | 1.25 | 14.922 | 11.081 | 1 | 1 | 2770 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2745376.3929 | 202838.2863 | 7472.9777 | 17834.8834 | 185003.4029 | 11952.268 | 0.10554 | -92292.2456 | 92292.2456
C | Xist Rating 2792 | -42.97 | 1342.02 | 150.284 | 35.6 | 2047.04 | 8528.14 | 10537.8 | 0.24 | 1.25 | 14.957 | 11.092 | 1 | 1 | 2780 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2747168.6208 | 204240.848 | 7527.0316 | 17899.2693 | 186341.5787 | 11966.3436 | 0.10592 | -92400.933 | 92400.933
C | Xist Rating 2793 | -42.81 | 1343.43 | 150.284 | 35.6 | 2051.68 | 8609.12 | 10538 | 0.23 | 1.25 | 14.972 | 11.102 | 1 | 1 | 2790 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2756288.4624 | 205648.2319 | 7581.2803 | 17963.6551 | 187684.5767 | 11960.0637 | 0.1063 | -92352.4418 | 92352.4418
C | Xist Rating 2794 | -42.84 | 1344.41 | 150.284 | 35.6 | 2049.89 | 8577.58 | 10537.9 | 0.23 | 1.25 | 14.958 | 11.109 | 1 | 1 | 2800 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2755892.6149 | 207060.438 | 7635.7238 | 18028.041 | 189032.397 | 11968.4726 | 0.10668 | -92417.3732 | 92417.3732
C | Xist Rating 2795 | -42.74 | 1346.15 | 150.284 | 35.6 | 2051.55 | 8606.84 | 10538 | 0.23 | 1.25 | 14.965 | 11.121 | 1 | 1 | 2810 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2761694.0325 | 208477.4664 | 7690.3621 | 18092.4269 | 190385.0395 | 11982.6795 | 0.10706 | -92527.0751 | 92527.0751
C | Xist Rating 2796 | -42.24 | 1347.63 | 150.284 | 35.6 | 2068.44 | 8911.84 | 10538.2 | 0.22 | 1.25 | 15.04 | 11.132 | 1 | 1 | 2820 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2787491.7972 | 209899.317 | 7745.1952 | 18156.8127 | 191742.5043 | 11978.815 | 0.10744 | -92497.2339 | 92497.2339
C | Xist Rating 2797 | -41.94 | 1349 | 150.284 | 35.6 | 2078.26 | 9097.08 | 10538.3 | 0.22 | 1.25 | 15.13 | 11.142 | 1 | 1 | 2830 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2803572.74 | 211325.99 | 7800.223 | 18221.1986 | 193104.7914 | 11993.1948 | 0.10783 | -92608.2713 | 92608.2713
C | Xist Rating 2798 | -41.76 | 1350.31 | 150.284 | 35.6 | 2083.49 | 9198.01 | 10538.3 | 0.22 | 1.25 | 15.157 | 11.151 | 1 | 1 | 2840 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2813357.3819 | 212757.4851 | 7855.4457 | 18285.5844 | 194471.9007 | 12004.7895 | 0.10821 | -92697.8024 | 92697.8024
C | Xist Rating 2799 | -41.63 | 1351.76 | 150.284 | 35.6 | 2086.68 | 9260.65 | 10538.2 | 0.21 | 1.25 | 15.17 | 11.161 | 1 | 1 | 2850 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2820690.5568 | 214193.8025 | 7910.8631 | 18349.9703 | 195843.8322 | 11997.6548 | 0.10859 | -92642.7104 | 92642.7104
C | Xist Rating 2800 | -41.56 | 1353.16 | 150.284 | 35.6 | 2088.23 | 9291.32 | 10538.1 | 0.21 | 1.25 | 15.176 | 11.171 | 1 | 1 | 2860 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2825709.3068 | 215634.9422 | 7966.4753 | 18414.3562 | 197220.586 | 12009.6293 | 0.10897 | -92735.1743 | 92735.1743
C | Xist Rating 2801 | -41.43 | 1354.35 | 150.284 | 35.6 | 2091.76 | 9361.41 | 10538.2 | 0.21 | 1.25 | 15.185 | 11.18 | 1 | 1 | 2870 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2832975.156 | 217080.9041 | 8022.2824 | 18478.742 | 198602.1621 | 12020.6475 | 0.10935 | -92820.2537 | 92820.2537
C | Xist Rating 2802 | -41.33 | 1355.86 | 150.284 | 35.6 | 2093.76 | 9401.62 | 10538.2 | 0.2 | 1.25 | 15.23 | 11.19 | 1 | 1 | 2880 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2838845.4336 | 218531.6883 | 8078.2842 | 18543.1279 | 199988.5604 | 12014.0207 | 0.10973 | -92769.0829 | 92769.0829
C | Xist Rating 2803 | -41.25 | 1357.2 | 150.284 | 35.6 | 2095.38 | 9434.43 | 10538.2 | 0.2 | 1.25 | 15.232 | 11.199 | 1 | 1 | 2890 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2843849.736 | 219987.2947 | 8134.4807 | 18607.5138 | 201379.781 | 12024.7843 | 0.11011 | -92852.1971 | 92852.1971
C | Xist Rating 2804 | -41.14 | 1358.59 | 150.284 | 35.6 | 2098.03 | 9488.53 | 10538.1 | 0.2 | 1.25 | 15.233 | 11.208 | 1 | 1 | 2900 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2850362.5777 | 221447.7234 | 8190.8721 | 18671.8996 | 202775.8238 | 12035.5223 | 0.11049 | -92935.1132 | 92935.1132
C | Xist Rating 2805 | -41.08 | 1360.13 | 150.284 | 35.5 | 2098.51 | 9498.27 | 10538.2 | 0.2 | 1.25 | 15.235 | 11.218 | 1 | 1 | 2910 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2854246.4063 | 222912.9744 | 8247.4583 | 18736.2855 | 204176.6889 | 12047.3251 | 0.11087 | -93026.2512 | 93026.2512
C | Xist Rating 2806 | -41 | 1361.52 | 150.284 | 35.5 | 2100.45 | 9538.3 | 10538.1 | 0.2 | 1.25 | 15.24 | 11.228 | 1 | 1 | 2920 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2859804.684 | 224383.0476 | 8304.2393 | 18800.6713 | 205582.3762 | 12059.2068 | 0.11125 | -93117.9984 | 93117.9984
C | Xist Rating 2807 | -40.84 | 1362.91 | 150.284 | 35.5 | 2104.74 | 9627.37 | 10538 | 0.19 | 1.25 | 15.286 | 11.237 | 1 | 1 | 2930 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2868571.1934 | 225857.943 | 8361.215 | 18865.0572 | 206992.8858 | 12051.0518 | 0.11164 | -93055.0275 | 93055.0275
C | Xist Rating 2808 | -40.72 | 1364.27 | 150.284 | 35.5 | 2107.88 | 9693.46 | 10537.9 | 0.19 | 1.25 | 15.289 | 11.246 | 1 | 1 | 2940 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2875717.4476 | 227337.6607 | 8418.3855 | 18929.4431 | 208408.2177 | 12061.7752 | 0.11202 | -93137.8312 | 93137.8312
C | Xist Rating 2809 | -40.7 | 1365.68 | 150.284 | 35.5 | 2107.21 | 9679.42 | 10537.9 | 0.19 | 1.25 | 15.284 | 11.255 | 1 | 1 | 2950 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2877774.5528 | 228822.2007 | 8475.7509 | 18993.8289 | 209828.3718 | 12072.2982 | 0.1124 | -93219.0869 | 93219.0869
C | Xist Rating 2810 | -40.68 | 1367.05 | 150.284 | 35.5 | 2106.59 | 9666.29 | 10537.9 | 0.19 | 1.25 | 15.28 | 11.264 | 1 | 1 | 2960 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2879813.8595 | 230311.5629 | 8533.311 | 19058.2148 | 211253.3482 | 12082.8456 | 0.11278 | -93300.5306 | 93300.5306
C | Xist Rating 2811 | -40.67 | 1368.44 | 150.284 | 35.5 | 2105.94 | 9652.8 | 10537.9 | 0.18 | 1.25 | 15.277 | 11.274 | 1 | 1 | 2970 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2881852.5336 | 231805.7474 | 8591.0659 | 19122.6006 | 212683.1468 | 12074.1179 | 0.11316 | -93233.1377 | 93233.1377
C | Xist Rating 2812 | -40.65 | 1369.66 | 150.284 | 35.5 | 2105.37 | 9640.75 | 10537.9 | 0.18 | 1.25 | 15.313 | 11.282 | 1 | 1 | 2980 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2883641.0742 | 233304.7541 | 8649.0156 | 19186.9865 | 214117.7676 | 12084.5241 | 0.11354 | -93313.4915 | 93313.4915
C | Xist Rating 2813 | -40.63 | 1371.22 | 150.284 | 35.5 | 2104.54 | 9623.25 | 10537.9 | 0.18 | 1.25 | 15.308 | 11.292 | 1 | 1 | 2990 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2885787.3388 | 234808.5831 | 8707.16 | 19251.3724 | 215557.2108 | 12096.0239 | 0.11392 | -93402.2905 | 93402.2905
C | Xist Rating 2814 | -40.61 | 1372.65 | 150.284 | 35.5 | 2103.91 | 9610.1 | 10537.9 | 0.18 | 1.25 | 15.304 | 11.301 | 1 | 1 | 3000 | 152.4 | 2 | 2.3 | 19.05 | 1.3333 | 12 | E | Rod | 2887932.0615 | 236317.2344 | 8765.4993 | 19315.7582 | 217001.4761 | 12106.5087 | 0.1143 | -93483.2512 | 93483.2512
C | Xist Rating 2815 | -92.95 | 129.767 | 150.286 | 35.8 | 2403.15 | 7437.73 | 58746 | 2.45 | 10.95 | 16.082 | 393.099 | 1 | 1 | 1000 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 311849.5661 | 31878.116 | 973.9444 | 6718.5246 | 25159.5914 | 409998.8215 | 0.038101 | -3165902.2211 | 3165902.2211
C | Xist Rating 2816 | -92.88 | 131.139 | 150.286 | 35.8 | 2400.39 | 7419.88 | 58284.4 | 2.43 | 10.85 | 16.107 | 385.756 | 1 | 1 | 1010 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 314784.7442 | 32451.0091 | 993.5206 | 6785.7098 | 25665.2992 | 402378.9777 | 0.038482 | -3107063.8069 | 3107063.8069
C | Xist Rating 2817 | -92.35 | 141.397 | 150.286 | 35.8 | 2393.87 | 7422.96 | 54967.7 | 2.44 | 10.07 | 16.161 | 334.291 | 1 | 1 | 1020 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 338486.0364 | 33028.934 | 1013.2917 | 6852.8951 | 26176.0389 | 348963.5895 | 0.038863 | -2694604.3378 | 2694604.3378
C | Xist Rating 2818 | -92.26 | 144.287 | 150.286 | 35.8 | 2373.33 | 7244.94 | 54179.1 | 2.35 | 9.89 | 15.856 | 323.193 | 1 | 1 | 1030 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 342440.6657 | 33611.8909 | 1033.2576 | 6920.0803 | 26691.8106 | 337355.7648 | 0.039244 | -2604971.7928 | 2604971.7928
C | Xist Rating 2819 | -92.19 | 145.734 | 150.285 | 35.8 | 2373.69 | 7256.3 | 53794.4 | 2.31 | 9.8 | 15.784 | 317.888 | 1 | 1 | 1040 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 345927.3385 | 34199.8797 | 1053.4182 | 6987.2656 | 27212.6141 | 331825.9129 | 0.039625 | -2562271.7419 | 2562271.7419
C | Xist Rating 2820 | -92.02 | 148.503 | 150.285 | 35.8 | 2382.45 | 7355.15 | 53043.8 | 2.25 | 9.63 | 15.747 | 307.409 | 1 | 1 | 1050 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 353800.9723 | 34792.9004 | 1073.7737 | 7054.4508 | 27738.4496 | 320911.34 | 0.040006 | -2477992.3031 | 2477992.3031
C | Xist Rating 2821 | -91.9 | 149.93 | 150.285 | 35.8 | 2395.02 | 7484.7 | 52677.4 | 2.2 | 9.54 | 15.735 | 302.472 | 1 | 1 | 1060 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 359085.3486 | 35390.953 | 1094.3239 | 7121.6361 | 28269.3169 | 315761.4904 | 0.040387 | -2438226.5295 | 2438226.5295
C | Xist Rating 2822 | -91.38 | 161.03 | 150.285 | 35.8 | 2375.42 | 7362.88 | 49857.7 | 2.19 | 8.9 | 15.643 | 264.702 | 1 | 1 | 1070 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 382513.8826 | 35994.0376 | 1115.0689 | 7188.8213 | 28805.2162 | 276535.7117 | 0.040768 | -2135335.4642 | 2135335.4642
C | Xist Rating 2823 | -91.25 | 163.174 | 150.285 | 35.8 | 2380.29 | 7422.12 | 49382.1 | 2.14 | 8.79 | 15.581 | 258.833 | 1 | 1 | 1080 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 388401.4405 | 36602.154 | 1136.0087 | 7256.0066 | 29346.1475 | 270411.8331 | 0.041149 | -2088048.4968 | 2088048.4968
C | Xist Rating 2824 | -91.1 | 166.023 | 150.285 | 35.8 | 2381.38 | 7449.05 | 48762.9 | 2.08 | 8.65 | 15.481 | 251.273 | 1 | 1 | 1090 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 395363.8517 | 37215.3024 | 1157.1433 | 7323.1918 | 29892.1106 | 262519.8922 | 0.04153 | -2027109.0215 | 2027109.0215
C | Xist Rating 2825 | -90.97 | 168.136 | 150.285 | 35.8 | 2387.8 | 7524.8 | 48308.3 | 2.04 | 8.55 | 15.466 | 245.798 | 1 | 1 | 1100 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 401475.1408 | 37833.4827 | 1178.4727 | 7390.3771 | 30443.1056 | 256816.5054 | 0.041911 | -1983068.9802 | 1983068.9802
C | Xist Rating 2826 | -90.91 | 169.75 | 150.284 | 35.8 | 2381.37 | 7469.52 | 48010.9 | 1.97 | 8.49 | 15.274 | 242.512 | 1 | 1 | 1110 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 404237.5575 | 38456.6949 | 1199.9969 | 7457.5623 | 30999.1326 | 253345.4564 | 0.042292 | -1956266.4602 | 1956266.4602
C | Xist Rating 2827 | -90.27 | 182.047 | 150.285 | 35.8 | 2378.83 | 7520.2 | 45448.6 | 2.01 | 7.92 | 15.453 | 212.203 | 1 | 1 | 1120 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 433058.865 | 39084.939 | 1221.7158 | 7524.7475 | 31560.1915 | 221931.8307 | 0.042673 | -1713698.7687 | 1713698.7687
C | Xist Rating 2828 | -90.2 | 183.616 | 150.284 | 35.8 | 2376.92 | 7509.41 | 45189 | 1.95 | 7.86 | 15.324 | 209.539 | 1 | 1 | 1130 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 436440.5427 | 39718.2151 | 1243.6296 | 7591.9328 | 32126.2823 | 219119.4888 | 0.043054 | -1691982.6102 | 1691982.6102
C | Xist Rating 2829 | -90.07 | 186.535 | 150.284 | 35.8 | 2371.78 | 7474.43 | 44681.8 | 1.9 | 7.75 | 15.212 | 204.137 | 1 | 1 | 1140 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 442419.9823 | 40356.5231 | 1265.7381 | 7659.118 | 32697.405 | 213472.8877 | 0.043435 | -1648381.0537 | 1648381.0537
C | Xist Rating 2830 | -89.89 | 189.391 | 150.284 | 35.8 | 2379.39 | 7567.01 | 44186.9 | 1.85 | 7.64 | 15.112 | 198.893 | 1 | 1 | 1150 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 450635.0515 | 40999.863 | 1288.0414 | 7726.3033 | 33273.5597 | 207991.2135 | 0.043816 | -1606053.0182 | 1606053.0182
C | Xist Rating 2831 | -89.74 | 192.327 | 150.284 | 35.8 | 2379.33 | 7582.86 | 43704.2 | 1.8 | 7.53 | 15.02 | 193.919 | 1 | 1 | 1160 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 457609.4009 | 41648.2348 | 1310.5395 | 7793.4885 | 33854.7462 | 202790.3548 | 0.044197 | -1565893.3661 | 1565893.3661
C | Xist Rating 2832 | -89.15 | 203.412 | 150.284 | 35.8 | 2378.83 | 7645.97 | 41833.2 | 1.82 | 7.13 | 15.127 | 174.461 | 1 | 1 | 1170 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 483882.568 | 42301.6385 | 1333.2324 | 7860.6738 | 34440.9647 | 182621.3389 | 0.044578 | -1410153.5715 | 1410153.5715
C | Xist Rating 2833 | -89.07 | 204.29 | 150.284 | 35.8 | 2387.38 | 7739.3 | 41725.5 | 1.76 | 7.11 | 15.075 | 173.562 | 1 | 1 | 1180 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 487717.8602 | 42960.0741 | 1356.1201 | 7927.859 | 35032.2151 | 181647.222 | 0.044959 | -1402631.6987 | 1402631.6987
C | Xist Rating 2834 | -88.83 | 209.988 | 150.283 | 35.8 | 2376.06 | 7654.61 | 40886.4 | 1.72 | 6.93 | 14.97 | 165.491 | 1 | 1 | 1190 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 498944.0873 | 43623.5417 | 1379.2026 | 7995.0443 | 35628.4974 | 173235.5958 | 0.04534 | -1337679.3513 | 1337679.3513
C | Xist Rating 2835 | -88.7 | 211.448 | 150.283 | 35.8 | 2388.98 | 7798.8 | 40683.5 | 1.69 | 6.88 | 14.991 | 163.621 | 1 | 1 | 1200 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 505145.043 | 44292.0412 | 1402.4799 | 8062.2295 | 36229.8117 | 171282.8975 | 0.045721 | -1322601.1325 | 1322601.1325
C | Xist Rating 2836 | -88.56 | 214.453 | 150.283 | 35.8 | 2384.94 | 7772.95 | 40282.1 | 1.64 | 6.8 | 14.894 | 159.981 | 1 | 1 | 1210 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 511457.5378 | 44965.5726 | 1425.9519 | 8129.4148 | 36836.1578 | 167464.8374 | 0.046102 | -1293119.0842 | 1293119.0842
C | Xist Rating 2837 | -87.96 | 227.104 | 150.283 | 35.8 | 2370.67 | 7699.2 | 38538.6 | 1.64 | 6.43 | 14.916 | 143.914 | 1 | 1 | 1220 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 538388.6397 | 45644.1359 | 1449.6188 | 8196.6 | 37447.5359 | 150792.2053 | 0.046483 | -1164377.4387 | 1164377.4387
C | Xist Rating 2838 | -87.78 | 229.958 | 150.283 | 35.8 | 2378.92 | 7803.74 | 38184.2 | 1.61 | 6.35 | 14.918 | 140.86 | 1 | 1 | 1230 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 547051.6854 | 46327.7311 | 1473.4804 | 8263.7853 | 38063.9459 | 147607.1023 | 0.046864 | -1139782.9174 | 1139782.9174
C | Xist Rating 2839 | -87.64 | 232.952 | 150.283 | 35.8 | 2377.07 | 7800.65 | 37836.5 | 1.57 | 6.28 | 14.853 | 137.972 | 1 | 1 | 1240 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 553743.2106 | 47016.3583 | 1497.5369 | 8330.9705 | 38685.3878 | 144579.8454 | 0.047245 | -1116407.2422 | 1116407.2422
C | Xist Rating 2840 | -87.56 | 234.557 | 150.283 | 35.8 | 2377.86 | 7817.66 | 37665.3 | 1.54 | 6.24 | 14.804 | 136.631 | 1 | 1 | 1250 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 557743.708 | 47710.0174 | 1521.7881 | 8398.1557 | 39311.8616 | 143168.4769 | 0.047626 | -1105509.0289 | 1105509.0289
C | Xist Rating 2841 | -87.35 | 238.862 | 150.283 | 35.8 | 2375.31 | 7815.29 | 37162.2 | 1.51 | 6.14 | 14.772 | 132.431 | 1 | 1 | 1260 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 567371.2972 | 48408.7084 | 1546.2341 | 8465.341 | 39943.3674 | 138789.1902 | 0.048007 | -1071693.3377 | 1071693.3377
C | Xist Rating 2842 | -86.76 | 250.852 | 150.283 | 35.8 | 2368.22 | 7811.43 | 35778.2 | 1.51 | 5.85 | 14.829 | 120.993 | 1 | 1 | 1270 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 594072.7234 | 49112.4313 | 1570.8749 | 8532.5262 | 40579.905 | 126925.7435 | 0.048388 | -980086.9468 | 980086.9468
C | Xist Rating 2843 | -86.63 | 253.914 | 150.283 | 35.8 | 2364.03 | 7782.56 | 35478 | 1.47 | 5.79 | 14.766 | 118.742 | 1 | 1 | 1280 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 600260.3134 | 49821.1861 | 1595.7105 | 8599.7115 | 41221.4746 | 124558.7741 | 0.048769 | -961809.837 | 961809.837
C | Xist Rating 2844 | -86.45 | 256.926 | 150.283 | 35.8 | 2368.13 | 7843.75 | 35183.4 | 1.44 | 5.73 | 14.758 | 116.539 | 1 | 1 | 1290 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 608434.1684 | 50534.9728 | 1620.7408 | 8666.8967 | 41868.0761 | 122254.4109 | 0.04915 | -944016.1545 | 944016.1545
C | Xist Rating 2845 | -86.2 | 261.209 | 150.283 | 35.8 | 2374.99 | 7945.11 | 34752.1 | 1.41 | 5.64 | 14.77 | 113.255 | 1 | 1 | 1300 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 620368.7629 | 51253.7915 | 1645.966 | 8734.082 | 42519.7095 | 118828.6946 | 0.049531 | -917563.6814 | 917563.6814
C | Xist Rating 2846 | -86.05 | 263.546 | 150.283 | 35.7 | 2380.61 | 8021.35 | 34541 | 1.38 | 5.59 | 14.738 | 111.751 | 1 | 1 | 1310 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 627400.2431 | 51977.6421 | 1671.3859 | 8801.2672 | 43176.3749 | 117247.5159 | 0.049912 | -905354.2392 | 905354.2392
C | Xist Rating 2847 | -85.45 | 275.633 | 150.283 | 35.7 | 2374.8 | 8030.84 | 33363.9 | 1.38 | 5.35 | 14.784 | 102.963 | 1 | 1 | 1320 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 654573.2484 | 52706.5246 | 1697.0007 | 8868.4525 | 43838.0721 | 108134.0645 | 0.050293 | -834982.5828 | 834982.5828
C | Xist Rating 2848 | -85.25 | 280.133 | 150.283 | 35.7 | 2369.84 | 7999.92 | 32980.8 | 1.35 | 5.28 | 14.693 | 100.322 | 1 | 1 | 1330 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 663870.3887 | 53440.439 | 1722.8102 | 8935.6377 | 44504.8013 | 105366.7701 | 0.050674 | -813614.269 | 813614.269
C | Xist Rating 2849 | -85.02 | 284.532 | 150.283 | 35.7 | 2370.46 | 8032.67 | 32608 | 1.32 | 5.2 | 14.672 | 97.759 | 1 | 1 | 1340 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 674471.7247 | 54179.3853 | 1748.8145 | 9002.823 | 45176.5624 | 102685.8488 | 0.051055 | -792912.9054 | 792912.9054
C | Xist Rating 2850 | -84.88 | 286.886 | 150.283 | 35.7 | 2374.44 | 8091.59 | 32424.9 | 1.29 | 5.16 | 14.646 | 96.572 | 1 | 1 | 1350 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 681193.5938 | 54923.3636 | 1775.0136 | 9070.0082 | 45853.3554 | 101433.1672 | 0.051436 | -783240.0304 | 783240.0304
C | Xist Rating 2851 | -84.71 | 288.294 | 150.283 | 35.7 | 2390.99 | 8296.19 | 32304.1 | 1.28 | 5.14 | 14.686 | 95.757 | 1 | 1 | 1360 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 689308.0711 | 55672.3738 | 1801.4075 | 9137.1935 | 46535.1803 | 100589.4527 | 0.051817 | -776725.0905 | 776725.0905
C | Xist Rating 2852 | -83.99 | 305.588 | 150.283 | 35.7 | 2363.83 | 8082.17 | 30903.2 | 1.27 | 4.86 | 14.661 | 86.365 | 1 | 1 | 1370 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 722358.082 | 56426.4159 | 1827.9962 | 9204.3787 | 47222.0372 | 90833.3333 | 0.052198 | -701390.9227 | 701390.9227
C | Xist Rating 2853 | -83.91 | 307.257 | 150.283 | 35.7 | 2363.1 | 8082.18 | 30795.1 | 1.24 | 4.84 | 14.636 | 85.745 | 1 | 1 | 1380 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 726079.0167 | 57185.4899 | 1854.7797 | 9271.5639 | 47913.9259 | 90168.6858 | 0.052579 | -696258.6907 | 696258.6907
C | Xist Rating 2854 | -83.72 | 311.041 | 150.283 | 35.7 | 2363.86 | 8112.55 | 30527.5 | 1.22 | 4.78 | 14.609 | 84.102 | 1 | 1 | 1390 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 735257.3783 | 57949.5958 | 1881.7579 | 9338.7492 | 48610.8466 | 88450.2773 | 0.05296 | -682989.5958 | 682989.5958
C | Xist Rating 2855 | -83.52 | 314.821 | 150.283 | 35.7 | 2365.42 | 8152.64 | 30265.6 | 1.19 | 4.73 | 14.589 | 82.51 | 1 | 1 | 1400 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 744683.8898 | 58718.7337 | 1908.931 | 9405.9344 | 49312.7992 | 86775.9799 | 0.053341 | -670061.1154 | 670061.1154
C | Xist Rating 2856 | -83.3 | 319.281 | 150.282 | 35.7 | 2365.2 | 8175.97 | 29958 | 1.17 | 4.67 | 14.572 | 80.642 | 1 | 1 | 1410 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 755163.4212 | 59492.9034 | 1936.2988 | 9473.1197 | 50019.7837 | 84824.1485 | 0.053722 | -654989.59 | 654989.59
C | Xist Rating 2857 | -82.67 | 332.174 | 150.283 | 35.7 | 2360.33 | 8197.72 | 29052.3 | 1.18 | 4.49 | 14.629 | 75.084 | 1 | 1 | 1420 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 784040.2574 | 60272.1051 | 1963.8614 | 9540.3049 | 50731.8002 | 79073.3729 | 0.054103 | -610583.6255 | 610583.6255
C | Xist Rating 2858 | -82.57 | 334.769 | 150.282 | 35.7 | 2356.74 | 8167.47 | 28911.1 | 1.14 | 4.47 | 14.575 | 74.351 | 1 | 1 | 1430 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 788963.4931 | 61056.3387 | 1991.6188 | 9607.4902 | 51448.8485 | 78278.437 | 0.054484 | -604445.3414 | 604445.3414
C | Xist Rating 2859 | -82.29 | 340.636 | 150.282 | 35.7 | 2354.29 | 8172.26 | 28542.4 | 1.13 | 4.39 | 14.56 | 72.233 | 1 | 1 | 1440 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 801955.9284 | 61845.6042 | 2019.571 | 9674.6754 | 52170.9288 | 76075.8433 | 0.054865 | -587437.4968 | 587437.4968
C | Xist Rating 2860 | -82.1 | 344.455 | 150.282 | 35.7 | 2354.53 | 8196.67 | 28317.2 | 1.11 | 4.35 | 14.544 | 70.992 | 1 | 1 | 1450 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 811029.6312 | 62639.9017 | 2047.718 | 9741.8607 | 52898.041 | 74774.3606 | 0.055246 | -577387.7922 | 577387.7922
C | Xist Rating 2861 | -81.94 | 346.69 | 150.282 | 35.7 | 2362.18 | 8303.33 | 28184.2 | 1.1 | 4.33 | 14.555 | 70.263 | 1 | 1 | 1460 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 818944.1842 | 63439.231 | 2076.0598 | 9809.0459 | 53630.1851 | 74015.8054 | 0.055627 | -571530.4298 | 571530.4298
C | Xist Rating 2862 | -81.31 | 361.419 | 150.282 | 35.7 | 2345.29 | 8184.79 | 27310.8 | 1.09 | 4.16 | 14.557 | 65.398 | 1 | 1 | 1470 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 847632.3665 | 64243.5923 | 2104.5964 | 9876.2312 | 54367.3611 | 68961.2403 | 0.056008 | -532500.4177 | 532500.4177
C | Xist Rating 2863 | -81.09 | 365.923 | 150.282 | 35.7 | 2345.01 | 8206.99 | 27066.6 | 1.07 | 4.11 | 14.545 | 64.118 | 1 | 1 | 1480 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 858093.0942 | 65052.9855 | 2133.3277 | 9943.4164 | 55109.5691 | 67618.9085 | 0.056389 | -522135.2876 | 522135.2876
C | Xist Rating 2864 | -80.85 | 369.743 | 150.282 | 35.7 | 2351.14 | 8304.18 | 26867.2 | 1.05 | 4.07 | 14.545 | 63.097 | 1 | 1 | 1490 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 869317.557 | 65867.4106 | 2162.2539 | 10010.6017 | 55856.8089 | 66546.1489 | 0.05677 | -513851.7223 | 513851.7223
C | Xist Rating 2865 | -80.63 | 373.655 | 150.282 | 35.7 | 2354.65 | 8370.14 | 26670.7 | 1.03 | 4.03 | 14.531 | 62.113 | 1 | 1 | 1500 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 879826.7458 | 66686.8676 | 2191.3748 | 10077.7869 | 56609.0807 | 65510.5834 | 0.057151 | -505855.36 | 505855.36
C | Xist Rating 2866 | -80.38 | 378.186 | 150.282 | 35.7 | 2357.91 | 8438.29 | 26439.2 | 1.01 | 3.99 | 14.529 | 60.94 | 1 | 1 | 1510 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 891728.5513 | 67511.3566 | 2220.6906 | 10144.9721 | 57366.3844 | 64279.3262 | 0.057532 | -496347.9185 | 496347.9185
C | Xist Rating 2867 | -79.66 | 392.598 | 150.283 | 35.7 | 2356.16 | 8507.95 | 25681.5 | 1.02 | 3.85 | 14.594 | 57.025 | 1 | 1 | 1520 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 925023.7037 | 68340.8774 | 2250.2011 | 10212.1574 | 58128.7201 | 60234.599 | 0.057913 | -465115.6068 | 465115.6068
C | Xist Rating 2868 | -79.48 | 397.472 | 150.282 | 35.7 | 2349.2 | 8444.48 | 25468.8 | 0.99 | 3.8 | 14.549 | 56.044 | 1 | 1 | 1530 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 933741.2224 | 69175.4302 | 2279.9064 | 10279.3426 | 58896.0876 | 59189.4228 | 0.058294 | -457045.0335 | 457045.0335
C | Xist Rating 2869 | -79.31 | 399.982 | 150.282 | 35.7 | 2354.42 | 8525.81 | 25363.9 | 0.97 | 3.79 | 14.54 | 55.581 | 1 | 1 | 1540 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 941725.6204 | 70015.0149 | 2309.8065 | 10346.5279 | 59668.4871 | 58694.3654 | 0.058675 | -453222.3313 | 453222.3313
C | Xist Rating 2870 | -78.95 | 407.383 | 150.282 | 35.7 | 2352.79 | 8549.54 | 25021.5 | 0.96 | 3.72 | 14.535 | 53.939 | 1 | 1 | 1550 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 958486.6486 | 70859.6316 | 2339.9013 | 10413.7131 | 60445.9184 | 56985.0373 | 0.059056 | -440023.3532 | 440023.3532
C | Xist Rating 2871 | -78.74 | 409.668 | 150.282 | 35.7 | 2364.59 | 8721.65 | 24921 | 0.95 | 3.7 | 14.554 | 53.482 | 1 | 1 | 1560 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 968696.8561 | 71709.2801 | 2370.191 | 10480.8984 | 61228.3817 | 56507.7966 | 0.059437 | -436338.2266 | 436338.2266
C | Xist Rating 2872 | -78.05 | 426.815 | 150.282 | 35.7 | 2343.77 | 8549.54 | 24162.6 | 0.94 | 3.56 | 14.556 | 49.927 | 1 | 1 | 1570 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1000356.1926 | 72563.9606 | 2400.6755 | 10548.0836 | 62015.8769 | 52812.0223 | 0.059818 | -407800.4369 | 407800.4369
C | Xist Rating 2873 | -77.83 | 430.756 | 150.282 | 35.7 | 2347.25 | 8618.68 | 24007.9 | 0.92 | 3.53 | 14.549 | 49.261 | 1 | 1 | 1580 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1011092.021 | 73423.6729 | 2431.3547 | 10615.2689 | 62808.4041 | 52105.4414 | 0.0602 | -402344.4071 | 402344.4071
C | Xist Rating 2874 | -77.61 | 434.732 | 150.282 | 35.7 | 2349.61 | 8673.62 | 23855.5 | 0.9 | 3.5 | 14.54 | 48.613 | 1 | 1 | 1590 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1021450.6545 | 74288.4172 | 2462.2288 | 10682.4541 | 63605.9631 | 51417.1785 | 0.060581 | -397029.823 | 397029.823
C | Xist Rating 2875 | -77.3 | 439.972 | 150.282 | 35.7 | 2355.22 | 8783.45 | 23645.7 | 0.89 | 3.46 | 14.545 | 47.695 | 1 | 1 | 1600 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1036230.8538 | 75158.1934 | 2493.2976 | 10749.6394 | 64408.5541 | 50459.5938 | 0.060962 | -389635.6082 | 389635.6082
C | Xist Rating 2876 | -77.17 | 442.678 | 150.282 | 35.7 | 2355.17 | 8796.81 | 23557 | 0.87 | 3.45 | 14.525 | 47.358 | 1 | 1 | 1610 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1042581.9453 | 76033.0016 | 2524.5612 | 10816.8246 | 65216.177 | 50093.1731 | 0.061343 | -386806.2047 | 386806.2047
C | Xist Rating 2877 | -76.34 | 461.775 | 150.283 | 35.7 | 2341.47 | 8729.68 | 22805.4 | 0.88 | 3.31 | 14.557 | 44.072 | 1 | 1 | 1620 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1081232.3092 | 76912.8416 | 2556.0196 | 10884.0098 | 66028.8318 | 46698.924 | 0.061724 | -360596.7129 | 360596.7129
C | Xist Rating 2878 | -76.15 | 464.135 | 150.283 | 35.7 | 2349.22 | 8852.5 | 22723.7 | 0.87 | 3.29 | 14.566 | 43.752 | 1 | 1 | 1630 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1090355.2247 | 77797.7136 | 2587.6728 | 10951.1951 | 66846.5185 | 46362.2828 | 0.062105 | -357997.2584 | 357997.2584
C | Xist Rating 2879 | -75.96 | 468.259 | 150.283 | 35.7 | 2348.16 | 8861.14 | 22589 | 0.85 | 3.27 | 14.548 | 43.232 | 1 | 1 | 1640 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1099547.0534 | 78687.6175 | 2619.5208 | 11018.3803 | 67669.2371 | 45805.4036 | 0.062486 | -353697.185 | 353697.185
C | Xist Rating 2880 | -75.72 | 473.856 | 150.282 | 35.7 | 2344.69 | 8844.9 | 22403.4 | 0.83 | 3.24 | 14.528 | 42.503 | 1 | 1 | 1650 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1111045.4246 | 79582.5533 | 2651.5635 | 11085.5656 | 68496.9877 | 45031.1338 | 0.062867 | -347718.4791 | 347718.4791
C | Xist Rating 2881 | -75.45 | 479.211 | 150.283 | 35.7 | 2346.13 | 8898.68 | 22221 | 0.82 | 3.2 | 14.528 | 41.777 | 1 | 1 | 1660 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1124291.3034 | 80482.521 | 2683.8011 | 11152.7508 | 69329.7702 | 44271.7789 | 0.063248 | -341854.9417 | 341854.9417
C | Xist Rating 2882 | -74.71 | 496.402 | 150.283 | 35.7 | 2333.74 | 8831.26 | 21633.4 | 0.82 | 3.1 | 14.544 | 39.41 | 1 | 1 | 1670 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1158473.2035 | 81387.5206 | 2716.2334 | 11219.9361 | 70167.5846 | 41819.9752 | 0.063629 | -322922.7635 | 322922.7635
C | Xist Rating 2883 | -74.54 | 498.874 | 150.283 | 35.7 | 2339.7 | 8931.56 | 21560.7 | 0.81 | 3.08 | 14.548 | 39.153 | 1 | 1 | 1680 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1167215.4978 | 82297.5522 | 2748.8606 | 11287.1213 | 71010.4309 | 41547.7185 | 0.06401 | -320820.4694 | 320820.4694
C | Xist Rating 2884 | -74.24 | 505.995 | 150.283 | 35.7 | 2334.63 | 8900.34 | 21346.3 | 0.79 | 3.04 | 14.529 | 38.355 | 1 | 1 | 1690 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1181311.1069 | 83212.6157 | 2781.6825 | 11354.3066 | 71858.3091 | 40701.1005 | 0.064391 | -314283.1096 | 314283.1096
C | Xist Rating 2885 | -74 | 510.682 | 150.283 | 35.7 | 2336.12 | 8950.49 | 21206 | 0.78 | 3.02 | 14.525 | 37.84 | 1 | 1 | 1700 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1193014.4338 | 84132.7111 | 2814.6992 | 11421.4918 | 72711.2193 | 40160.1097 | 0.064772 | -310105.7215 | 310105.7215
C | Xist Rating 2886 | -73.74 | 516.229 | 150.283 | 35.7 | 2335.15 | 8969.53 | 21045.2 | 0.77 | 2.99 | 14.516 | 37.256 | 1 | 1 | 1710 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1205472.1494 | 85057.8384 | 2847.9107 | 11488.6771 | 73569.1613 | 39547.0404 | 0.065153 | -305371.7629 | 305371.7629
C | Xist Rating 2887 | -73.06 | 532.1 | 150.283 | 35.6 | 2325.35 | 8926.61 | 20567.5 | 0.77 | 2.9 | 14.546 | 35.47 | 1 | 1 | 1720 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1237318.735 | 85987.9976 | 2881.317 | 11555.8623 | 74432.1353 | 37699.0734 | 0.065534 | -291102.2515 | 291102.2515
C | Xist Rating 2888 | -72.73 | 539.091 | 150.283 | 35.7 | 2323.72 | 8944.79 | 20374.9 | 0.76 | 2.87 | 14.539 | 34.791 | 1 | 1 | 1730 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1252696.5385 | 86923.1888 | 2914.9181 | 11623.0476 | 75300.1412 | 36987.261 | 0.065915 | -285605.8252 | 285605.8252
C | Xist Rating 2889 | -72.54 | 542.395 | 150.283 | 35.6 | 2327.43 | 9019.15 | 20290.2 | 0.75 | 2.85 | 14.537 | 34.512 | 1 | 1 | 1740 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1262386.3948 | 87863.4118 | 2948.714 | 11690.2328 | 76173.179 | 36691.0162 | 0.066296 | -283318.3016 | 283318.3016
C | Xist Rating 2890 | -72.3 | 548.834 | 150.283 | 35.6 | 2321.82 | 8973.07 | 20123.5 | 0.73 | 2.82 | 14.517 | 33.947 | 1 | 1 | 1750 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1274293.7579 | 88808.6668 | 2982.7046 | 11757.418 | 77051.2488 | 36085.1999 | 0.066677 | -278640.3486 | 278640.3486
C | Xist Rating 2891 | -72.07 | 553.637 | 150.283 | 35.6 | 2321.33 | 8994.05 | 20001.1 | 0.72 | 2.8 | 14.518 | 33.536 | 1 | 1 | 1760 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1285174.1772 | 89758.9537 | 3016.8901 | 11824.6033 | 77934.3504 | 35651.7315 | 0.067058 | -275293.2201 | 275293.2201
C | Xist Rating 2892 | -71.29 | 572.44 | 150.283 | 35.6 | 2309.18 | 8931.21 | 19497.4 | 0.73 | 2.71 | 14.552 | 31.775 | 1 | 1 | 1770 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1321866.9992 | 90714.2726 | 3051.2703 | 11891.7885 | 78822.484 | 33841.109 | 0.067439 | -261312.0733 | 261312.0733
C | Xist Rating 2893 | -71.2 | 577.353 | 150.283 | 35.6 | 2299.45 | 8814.3 | 19383.8 | 0.71 | 2.69 | 14.69 | 31.407 | 1 | 1 | 1780 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1327594.3558 | 91674.6233 | 3085.8453 | 11958.9738 | 79715.6495 | 33448.2994 | 0.06782 | -258278.902 | 258278.902
C | Xist Rating 2894 | -71.04 | 580.084 | 150.283 | 35.6 | 2300.64 | 8845.31 | 19327.5 | 0.7 | 2.68 | 14.687 | 31.247 | 1 | 1 | 1790 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1334564.4538 | 92640.006 | 3120.6151 | 12026.159 | 80613.8469 | 33274.8597 | 0.068201 | -256939.6461 | 256939.6461
C | Xist Rating 2895 | -70.7 | 588.637 | 150.283 | 35.6 | 2297.79 | 8853.17 | 19122 | 0.69 | 2.65 | 14.671 | 30.58 | 1 | 1 | 1800 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1352564.2122 | 93610.4205 | 3155.5797 | 12093.3443 | 81517.0763 | 32574.0487 | 0.068582 | -251528.1698 | 251528.1698
C | Xist Rating 2896 | -70.48 | 593.423 | 150.283 | 35.6 | 2297.26 | 8872.45 | 19012.6 | 0.68 | 2.63 | 14.668 | 30.237 | 1 | 1 | 1810 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1363246.921 | 94585.867 | 3190.7391 | 12160.5295 | 82425.3375 | 32210.3129 | 0.068963 | -248719.4981 | 248719.4981
C | Xist Rating 2897 | -69.69 | 612.484 | 150.283 | 35.6 | 2286.31 | 8823.9 | 18562.9 | 0.68 | 2.55 | 14.704 | 28.775 | 1 | 1 | 1820 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1400328.294 | 95566.3454 | 3226.0933 | 12227.7148 | 83338.6307 | 30698.4962 | 0.069344 | -237045.6505 | 237045.6505
C | Xist Rating 2898 | -69.62 | 609.435 | 150.283 | 35.6 | 2303.36 | 9064.56 | 18632 | 0.68 | 2.56 | 14.736 | 29.008 | 1 | 1 | 1830 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1403748.2016 | 96551.8558 | 3261.6423 | 12294.9 | 84256.9558 | 30946.7332 | 0.069725 | -238962.4706 | 238962.4706
C | Xist Rating 2899 | -69.35 | 613.337 | 150.283 | 35.6 | 2309.54 | 9185.11 | 18545.8 | 0.67 | 2.55 | 14.743 | 28.747 | 1 | 1 | 1840 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1416526.335 | 97542.398 | 3297.386 | 12362.0853 | 85180.3128 | 30668.4097 | 0.070106 | -236813.3304 | 236813.3304
C | Xist Rating 2900 | -69.07 | 619.893 | 150.283 | 35.6 | 2307.01 | 9183.71 | 18409.8 | 0.66 | 2.52 | 14.733 | 28.342 | 1 | 1 | 1850 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1430099.3499 | 98537.9722 | 3333.3246 | 12429.2705 | 86108.7017 | 30239.4725 | 0.070487 | -233501.1911 | 233501.1911
C | Xist Rating 2901 | -68.77 | 627.226 | 150.283 | 35.6 | 2303.26 | 9167.61 | 18259.8 | 0.65 | 2.5 | 14.724 | 27.896 | 1 | 1 | 1860 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 14 | E | Rod | 1444664.5568 | 99538.5783 | 3369.4579 | 12496.4558 | 87042.1225 | 29767.8897 | 0.070868 | -229859.7533 | 229859.7533
C | Xist Rating 2902 | -68 | 644.696 | 150.283 | 35.6 | 2297 | 9180.53 | 17880.4 | 0.65 | 2.43 | 14.759 | 26.722 | 1 | 1 | 1870 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1480866.712 | 100544.2163 | 3405.7861 | 12563.641 | 87980.5753 | 28554.8895 | 0.071249 | -220493.2873 | 220493.2873
C | Xist Rating 2903 | -67.69 | 652.015 | 150.283 | 35.6 | 2293.95 | 9174.75 | 17739.8 | 0.64 | 2.41 | 14.752 | 26.321 | 1 | 1 | 1880 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1495689.8092 | 101554.8862 | 3442.309 | 12630.8262 | 88924.06 | 28129.9368 | 0.07163 | -217211.9154 | 217211.9154
C | Xist Rating 2904 | -67.41 | 656.849 | 150.283 | 35.6 | 2297.37 | 9258.57 | 17647.4 | 0.63 | 2.39 | 14.759 | 26.062 | 1 | 1 | 1890 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1509025.1871 | 102570.5881 | 3479.0267 | 12698.0115 | 89872.5766 | 27853.0736 | 0.072011 | -215074.0516 | 215074.0516
C | Xist Rating 2905 | -67.21 | 662.14 | 150.283 | 35.6 | 2293.94 | 9231.99 | 17556 | 0.61 | 2.38 | 14.749 | 25.82 | 1 | 1 | 1900 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1518909.4316 | 103591.3218 | 3515.9392 | 12765.1967 | 90826.1251 | 27580.2658 | 0.072392 | -212967.502 | 212967.502
C | Xist Rating 2906 | -66.98 | 667.153 | 150.283 | 35.6 | 2293.1 | 9247.28 | 17465.7 | 0.6 | 2.36 | 14.758 | 25.575 | 1 | 1 | 1910 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1529848.5443 | 104617.0875 | 3553.0464 | 12832.382 | 91784.7055 | 27317.7015 | 0.072773 | -210940.0498 | 210940.0498
C | Xist Rating 2907 | -66.08 | 688.385 | 150.283 | 35.6 | 2283.96 | 9235.02 | 17051 | 0.61 | 2.29 | 14.802 | 24.366 | 1 | 1 | 1920 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1572243.8046 | 105647.8851 | 3590.3485 | 12899.5672 | 92748.3179 | 26081.1372 | 0.073154 | -201391.6281 | 201391.6281
C | Xist Rating 2908 | -65.77 | 695.781 | 150.283 | 35.6 | 2280.93 | 9228.29 | 16924.7 | 0.6 | 2.27 | 14.801 | 24.029 | 1 | 1 | 1930 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1587027.7563 | 106683.7146 | 3627.8454 | 12966.7525 | 93716.9621 | 25722.3532 | 0.073535 | -198621.1931 | 198621.1931
C | Xist Rating 2909 | -65.55 | 698.151 | 150.283 | 35.6 | 2288.72 | 9372.16 | 16882.5 | 0.59 | 2.26 | 14.796 | 23.923 | 1 | 1 | 1940 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1597872.1567 | 107724.5761 | 3665.537 | 13033.9377 | 94690.6383 | 25603.1256 | 0.073916 | -197700.5493 | 197700.5493
C | Xist Rating 2910 | -65.32 | 705.277 | 150.283 | 35.6 | 2281.43 | 9289.33 | 16772.7 | 0.58 | 2.24 | 14.788 | 23.648 | 1 | 1 | 1950 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1609040.1061 | 108770.4694 | 3703.4235 | 13101.123 | 95669.3464 | 25308.1131 | 0.074297 | -195422.5409 | 195422.5409
C | Xist Rating 2911 | -64.98 | 713.331 | 150.283 | 35.6 | 2278.81 | 9293.97 | 16637.5 | 0.57 | 2.22 | 14.794 | 23.291 | 1 | 1 | 1960 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1625545.8161 | 109821.3947 | 3741.5047 | 13168.3082 | 96653.0865 | 24928.5221 | 0.074678 | -192491.4396 | 192491.4396
C | Xist Rating 2912 | -64.17 | 732.521 | 150.283 | 35.6 | 2271.29 | 9290.81 | 16303.5 | 0.57 | 2.16 | 14.85 | 22.379 | 1 | 1 | 1970 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1663767.6221 | 110877.3519 | 3779.7807 | 13235.4935 | 97641.8584 | 23988.0101 | 0.075059 | -185229.0552 | 185229.0552
C | Xist Rating 2913 | -63.9 | 738.292 | 150.283 | 35.6 | 2271.79 | 9332.85 | 16214.4 | 0.57 | 2.15 | 14.862 | 22.158 | 1 | 1 | 1980 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1677244.3827 | 111938.341 | 3818.2515 | 13302.6787 | 98635.6623 | 23762.9032 | 0.07544 | -183490.8394 | 183490.8394
C | Xist Rating 2914 | -63.61 | 745.882 | 150.283 | 35.6 | 2267.54 | 9304.39 | 16101.7 | 0.56 | 2.13 | 14.865 | 21.881 | 1 | 1 | 1990 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1691317.2703 | 113004.362 | 3856.9171 | 13369.8639 | 99634.4981 | 23465.9292 | 0.075821 | -181197.6848 | 181197.6848
C | Xist Rating 2915 | -63.34 | 751.778 | 150.283 | 35.6 | 2266.95 | 9327.85 | 16015.1 | 0.55 | 2.12 | 14.864 | 21.672 | 1 | 1 | 2000 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1704243.1371 | 114075.4149 | 3895.7775 | 13437.0492 | 100638.3657 | 23239.2387 | 0.076202 | -179447.2411 | 179447.2411
C | Xist Rating 2916 | -63.11 | 756.153 | 150.283 | 35.6 | 2268.55 | 9379.25 | 15954 | 0.54 | 2.11 | 14.868 | 21.531 | 1 | 1 | 2010 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1715370.8882 | 115151.4998 | 3934.8326 | 13504.2344 | 101647.2654 | 23083.2774 | 0.076583 | -178242.9496 | 178242.9496
C | Xist Rating 2917 | -62.25 | 777.833 | 150.283 | 35.6 | 2257.94 | 9334.93 | 15615.1 | 0.54 | 2.05 | 14.905 | 20.659 | 1 | 1 | 2020 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1756300.244 | 116232.6166 | 3974.0826 | 13571.4197 | 102661.1969 | 22183.1148 | 0.076964 | -171292.1321 | 171292.1321
C | Xist Rating 2918 | -61.9 | 785.831 | 150.283 | 35.6 | 2256.74 | 9362.15 | 15500 | 0.53 | 2.03 | 14.905 | 20.381 | 1 | 1 | 2030 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1773416.2509 | 117318.7653 | 4013.5273 | 13638.6049 | 103680.1604 | 21884.4573 | 0.077345 | -168985.9787 | 168985.9787
C | Xist Rating 2919 | -61.71 | 791.322 | 150.283 | 35.6 | 2252.84 | 9323.87 | 15431.7 | 0.52 | 2.02 | 14.897 | 20.234 | 1 | 1 | 2040 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1782721.8545 | 118409.9459 | 4053.1669 | 13705.7902 | 104704.1557 | 21721.3292 | 0.077726 | -167726.3463 | 167726.3463
C | Xist Rating 2920 | -61.46 | 795.998 | 150.283 | 35.6 | 2255.56 | 9399.46 | 15364.3 | 0.52 | 2.01 | 14.904 | 20.074 | 1 | 1 | 2050 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1795421.2489 | 119506.1584 | 4093.0012 | 13772.9754 | 105733.183 | 21558.9762 | 0.078107 | -166472.6999 | 166472.6999
C | Xist Rating 2921 | -61.19 | 803.983 | 150.283 | 35.6 | 2249.54 | 9338.23 | 15264.4 | 0.51 | 1.99 | 14.891 | 19.852 | 1 | 1 | 2060 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1808591.9178 | 120607.4029 | 4133.0303 | 13840.1607 | 106767.2422 | 21317.5292 | 0.078488 | -164608.3095 | 164608.3095
C | Xist Rating 2922 | -60.26 | 827.287 | 150.283 | 35.6 | 2239.14 | 9302.71 | 14936.2 | 0.51 | 1.94 | 14.931 | 19.056 | 1 | 1 | 2070 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1852411.4132 | 121713.6793 | 4173.2542 | 13907.3459 | 107806.3333 | 20496.1814 | 0.078869 | -158266.0801 | 158266.0801
C | Xist Rating 2923 | -60.06 | 832.58 | 150.283 | 35.6 | 2237.17 | 9296.78 | 14873.6 | 0.5 | 1.93 | 14.931 | 18.924 | 1 | 1 | 2080 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1862622.9986 | 122824.9876 | 4213.6729 | 13974.5312 | 108850.4564 | 20348.592 | 0.07925 | -157126.4336 | 157126.4336
C | Xist Rating 2924 | -59.77 | 839.335 | 150.283 | 35.6 | 2236.17 | 9316.7 | 14791.2 | 0.5 | 1.91 | 14.927 | 18.743 | 1 | 1 | 2090 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1876895.747 | 123941.3278 | 4254.2864 | 14041.7164 | 109899.6114 | 20163.7828 | 0.079631 | -155699.386 | 155699.386
C | Xist Rating 2925 | -59.5 | 846.099 | 150.283 | 35.6 | 2234.09 | 9318.09 | 14709.4 | 0.49 | 1.9 | 14.923 | 18.566 | 1 | 1 | 2100 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1890261.3149 | 125062.6999 | 4295.0947 | 14108.9017 | 110953.7982 | 19969.0785 | 0.080012 | -154195.9312 | 154195.9312
C | Xist Rating 2926 | -59.27 | 852.089 | 150.283 | 35.6 | 2232.13 | 9316.81 | 14638.8 | 0.48 | 1.89 | 14.92 | 18.417 | 1 | 1 | 2110 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1901973.4196 | 126189.1039 | 4336.0977 | 14176.0869 | 112013.017 | 19803.3696 | 0.080393 | -152916.3707 | 152916.3707
C | Xist Rating 2927 | -58.41 | 874.209 | 150.283 | 35.6 | 2222.38 | 9279.11 | 14359.2 | 0.48 | 1.84 | 14.957 | 17.778 | 1 | 1 | 2120 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1942824.5974 | 127320.5399 | 4377.2956 | 14243.2721 | 113077.2678 | 19144.667 | 0.080774 | -147830.0436 | 147830.0436
C | Xist Rating 2928 | -58.09 | 882.549 | 150.283 | 35.6 | 2218.93 | 9264.96 | 14263.9 | 0.48 | 1.83 | 14.952 | 17.576 | 1 | 1 | 2130 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1958314.4526 | 128457.0078 | 4418.6882 | 14310.4574 | 114146.5504 | 18937.8793 | 0.081155 | -146233.2838 | 146233.2838
C | Xist Rating 2929 | -57.81 | 890.916 | 150.283 | 35.6 | 2214.15 | 9227.55 | 14170 | 0.47 | 1.81 | 14.952 | 17.38 | 1 | 1 | 2140 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1972621.6614 | 129598.5076 | 4460.2756 | 14377.6426 | 115220.8649 | 18723.208 | 0.081536 | -144575.6488 | 144575.6488
C | Xist Rating 2930 | -57.63 | 895.44 | 150.283 | 35.6 | 2213.15 | 9232.84 | 14123.6 | 0.47 | 1.8 | 14.95 | 17.292 | 1 | 1 | 2150 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1981743.036 | 130745.0393 | 4502.0578 | 14444.8279 | 116300.2114 | 18634.8795 | 0.081917 | -143893.6001 | 143893.6001
C | Xist Rating 2931 | -57.36 | 901.376 | 150.283 | 35.6 | 2213.81 | 9276.5 | 14059 | 0.46 | 1.79 | 14.948 | 17.161 | 1 | 1 | 2160 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 1995475.2026 | 131896.6029 | 4544.0348 | 14512.0131 | 117384.5898 | 18487.422 | 0.082298 | -142754.9721 | 142754.9721
C | Xist Rating 2932 | -56.46 | 925.333 | 150.283 | 35.6 | 2202.27 | 9212.61 | 13786 | 0.46 | 1.75 | 14.984 | 16.572 | 1 | 1 | 2170 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2037833.1059 | 133053.1985 | 4586.2066 | 14579.1984 | 118474.0001 | 17880.4394 | 0.082679 | -138068.0133 | 138068.0133
C | Xist Rating 2933 | -56.13 | 933.448 | 150.283 | 35.6 | 2200.65 | 9229.18 | 13699.1 | 0.46 | 1.74 | 14.982 | 16.396 | 1 | 1 | 2180 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2054192.3412 | 134214.826 | 4628.5732 | 14646.3836 | 119568.4423 | 17700.6634 | 0.08306 | -136679.8305 | 136679.8305
C | Xist Rating 2934 | -55.9 | 939.618 | 150.283 | 35.6 | 2198.72 | 9226.78 | 13638.9 | 0.45 | 1.73 | 14.977 | 16.282 | 1 | 1 | 2190 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2065956.889 | 135381.4854 | 4671.1346 | 14713.5689 | 120667.9165 | 17570.4356 | 0.083441 | -135674.2465 | 135674.2465
C | Xist Rating 2935 | -55.68 | 946.194 | 150.283 | 35.6 | 2194.94 | 9191.69 | 13579.4 | 0.44 | 1.72 | 14.971 | 16.175 | 1 | 1 | 2200 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2076839.0584 | 136553.1767 | 4713.8907 | 14780.7541 | 121772.4226 | 17447.3075 | 0.083822 | -134723.4839 | 134723.4839
C | Xist Rating 2936 | -55.37 | 954.567 | 150.283 | 35.6 | 2191.58 | 9177.34 | 13495.4 | 0.44 | 1.7 | 14.969 | 16.01 | 1 | 1 | 2210 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2092009.9459 | 137729.8999 | 4756.8417 | 14847.9394 | 122881.9605 | 17278.8208 | 0.084203 | -133422.4743 | 133422.4743
C | Xist Rating 2937 | -54.47 | 978.389 | 150.283 | 35.6 | 2182.42 | 9151.15 | 13246.2 | 0.44 | 1.66 | 15.007 | 15.498 | 1 | 1 | 2220 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2135255.7214 | 138911.655 | 4799.9874 | 14915.1246 | 123996.5304 | 16751.7258 | 0.084584 | -129352.3859 | 129352.3859
C | Xist Rating 2938 | -54.21 | 985.116 | 150.283 | 35.6 | 2181.01 | 9161.46 | 13182.5 | 0.43 | 1.65 | 15.004 | 15.378 | 1 | 1 | 2230 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2148547.8472 | 140098.4421 | 4843.3279 | 14982.3099 | 125116.1323 | 16614.936 | 0.084965 | -128296.1314 | 128296.1314
C | Xist Rating 2939 | -53.93 | 993.07 | 150.283 | 35.6 | 2177.41 | 9137.49 | 13111.7 | 0.43 | 1.64 | 14.999 | 15.25 | 1 | 1 | 2240 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2162320.5487 | 141290.2611 | 4886.8633 | 15049.4951 | 126240.766 | 16484.6843 | 0.085346 | -127290.3622 | 127290.3622
C | Xist Rating 2940 | -53.63 | 1001.75 | 150.283 | 35.6 | 2173.53 | 9112.73 | 13034.1 | 0.42 | 1.63 | 14.999 | 15.107 | 1 | 1 | 2250 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2177333.6775 | 142487.112 | 4930.5934 | 15116.6803 | 127370.4317 | 16323.9427 | 0.085727 | -126049.1583 | 126049.1583
C | Xist Rating 2941 | -53.44 | 1006.24 | 150.283 | 35.6 | 2173.51 | 9134.01 | 12995.6 | 0.42 | 1.62 | 14.998 | 15.041 | 1 | 1 | 2260 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2187072.7024 | 143688.9948 | 4974.5182 | 15183.8656 | 128505.1292 | 16258.183 | 0.086108 | -125541.3795 | 125541.3795
C | Xist Rating 2942 | -52.51 | 1031.99 | 150.284 | 35.6 | 2162.75 | 9084.54 | 12751.8 | 0.42 | 1.59 | 15.036 | 14.567 | 1 | 1 | 2270 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2231936.3725 | 144895.9096 | 5018.6379 | 15251.0508 | 129644.8587 | 15770.3823 | 0.086489 | -121774.7117 | 121774.7117
C | Xist Rating 2943 | -52.22 | 1039.89 | 150.284 | 35.6 | 2160.13 | 9076.91 | 12686.1 | 0.41 | 1.58 | 15.031 | 14.452 | 1 | 1 | 2280 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2246297.5857 | 146107.8562 | 5062.9524 | 15318.2361 | 130789.6201 | 15638.2094 | 0.08687 | -120754.1074 | 120754.1074
C | Xist Rating 2944 | -51.86 | 1049.09 | 150.284 | 35.6 | 2158.28 | 9091.06 | 12606.9 | 0.41 | 1.56 | 15.03 | 14.31 | 1 | 1 | 2290 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2264229.9652 | 147324.8348 | 5107.4617 | 15385.4213 | 131939.4135 | 15493.4629 | 0.087251 | -119636.4137 | 119636.4137
C | Xist Rating 2945 | -51.64 | 1055.43 | 150.283 | 35.6 | 2155.93 | 9079.39 | 12557 | 0.4 | 1.56 | 15.026 | 14.227 | 1 | 1 | 2300 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2275433.1999 | 148546.8453 | 5152.1657 | 15452.6066 | 133094.2387 | 15394.3694 | 0.087632 | -118871.2398 | 118871.2398
| Xist Rating 2946 | -51.43 | 1062.03 | 150.283 | 35.6 | 2152.69 | 9051.77 | 12507.6 | 0.4 | 1.55 | 15.022 | 14.147 | 1 | 1 | 2310 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2286221.3607 | 149773.8877 | 5197.0645 | 15519.7918 | 134254.0959 | 15313.818 | 0.088013 | -118249.2432 | 118249.2432
| Xist Rating 2947 | -50.45 | 1088.39 | 150.284 | 35.6 | 2143.49 | 9029.81 | 12277.1 | 0.4 | 1.51 | 15.061 | 13.718 | 1 | 1 | 2320 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2332953.0811 | 151005.962 | 5242.1582 | 15586.9771 | 135418.985 | 14872.6179 | 0.088394 | -114842.4129 | 114842.4129
| Xist Rating 2948 | -50.2 | 1096.32 | 150.284 | 35.6 | 2139.95 | 9004.71 | 12216.9 | 0.39 | 1.5 | 15.054 | 13.618 | 1 | 1 | 2330 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2346069.984 | 152243.0683 | 5287.4466 | 15654.1623 | 136588.906 | 14755.4534 | 0.088775 | -113937.6999 | 113937.6999
| Xist Rating 2949 | -49.92 | 1104.23 | 150.284 | 35.6 | 2137.12 | 8991.91 | 12157.3 | 0.39 | 1.49 | 15.049 | 13.519 | 1 | 1 | 2340 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2359872.0176 | 153485.2064 | 5332.9298 | 15721.3476 | 137763.8589 | 14655.0692 | 0.089156 | -113162.5597 | 113162.5597
| Xist Rating 2950 | -49.68 | 1111.46 | 150.284 | 35.6 | 2134.33 | 8975.61 | 12104.8 | 0.38 | 1.49 | 15.044 | 13.435 | 1 | 1 | 2350 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2372222.4218 | 154732.3765 | 5378.6078 | 15788.5328 | 138943.8437 | 14554.4137 | 0.089537 | -112385.3246 | 112385.3246
| Xist Rating 2951 | -49.38 | 1120.19 | 150.284 | 35.6 | 2131.09 | 8959.64 | 12039.9 | 0.38 | 1.48 | 15.039 | 13.328 | 1 | 1 | 2360 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2387225.7071 | 155984.5785 | 5424.4805 | 15855.7181 | 140128.8605 | 14445.6559 | 0.089918 | -111545.5255 | 111545.5255
| Xist Rating 2952 | -48.51 | 1144.44 | 150.284 | 35.6 | 2122.87 | 8938.82 | 11846.8 | 0.38 | 1.45 | 15.074 | 12.987 | 1 | 1 | 2370 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2429497.3428 | 157241.8124 | 5470.5481 | 15922.9033 | 141318.9091 | 14095.5025 | 0.090299 | -108841.7338 | 108841.7338
| Xist Rating 2953 | -48.24 | 1152.58 | 150.284 | 35.6 | 2119.54 | 8916.25 | 11791.2 | 0.37 | 1.44 | 15.068 | 12.901 | 1 | 1 | 2380 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2442939.4132 | 158504.0783 | 5516.8105 | 15990.0885 | 142513.9897 | 13992.441 | 0.09068 | -108045.9207 | 108045.9207
| Xist Rating 2954 | -47.94 | 1160.87 | 150.284 | 35.6 | 2117.67 | 8923.57 | 11730 | 0.37 | 1.43 | 15.061 | 12.801 | 1 | 1 | 2390 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2458339.5729 | 159771.376 | 5563.2676 | 16057.2738 | 143714.1022 | 13890.8128 | 0.091061 | -107261.1742 | 107261.1742
C | Xist Rating 2955 | -42.83 | 1331.04 | 150.284 | 35.6 | 2029.61 | 8233.22 | 10538.1 | 0.4 | 1.25 | 15.059 | 10.835 | 1 | 1 | 2400 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2701492.0944 | 161043.7057 | 5609.9196 | 16124.459 | 144919.2467 | 11900.1442 | 0.091442 | -91889.7591 | 91889.7591
C | Xist Rating 2956 | -42.32 | 1332.48 | 150.284 | 35.6 | 2045.55 | 8502.18 | 10538 | 0.39 | 1.25 | 15.057 | 10.845 | 1 | 1 | 2410 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2725654.464 | 162321.0673 | 5656.7663 | 16191.6443 | 146129.423 | 11896.8771 | 0.091823 | -91864.5317 | 91864.5317
C | Xist Rating 2957 | -42.31 | 1333.88 | 150.284 | 35.6 | 2045.07 | 8493.8 | 10538 | 0.39 | 1.25 | 15.096 | 10.856 | 1 | 1 | 2420 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2727877.9716 | 163603.4608 | 5703.8078 | 16258.8295 | 147344.6313 | 11912.5827 | 0.092204 | -91985.8062 | 91985.8062
C | Xist Rating 2958 | -41.78 | 1335.24 | 150.284 | 35.6 | 2061.85 | 8791.01 | 10537.9 | 0.39 | 1.25 | 15.091 | 10.864 | 1 | 1 | 2430 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2753064.594 | 164890.8862 | 5751.0441 | 16326.0148 | 148564.8715 | 11923.3173 | 0.092585 | -92068.696 | 92068.696
C | Xist Rating 2959 | -41.78 | 1336.61 | 150.284 | 35.6 | 2060.67 | 8769.57 | 10538 | 0.38 | 1.25 | 15.083 | 10.875 | 1 | 1 | 2440 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2754312.1287 | 166183.3436 | 5798.4752 | 16393.2 | 149790.1436 | 11920.5411 | 0.092966 | -92047.2589 | 92047.2589
C | Xist Rating 2960 | -41.76 | 1337.94 | 150.284 | 35.6 | 2060.12 | 8759.65 | 10537.9 | 0.38 | 1.25 | 15.079 | 10.886 | 1 | 1 | 2450 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2756316.9528 | 167480.8329 | 5846.1011 | 16460.3853 | 151020.4476 | 11934.3668 | 0.093347 | -92154.0172 | 92154.0172
C | Xist Rating 2961 | -41.75 | 1339.41 | 150.284 | 35.6 | 2059.22 | 8743.45 | 10537.9 | 0.37 | 1.25 | 15.074 | 10.897 | 1 | 1 | 2460 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2758139.8602 | 168783.3541 | 5893.9217 | 16527.5705 | 152255.7835 | 11931.5274 | 0.093728 | -92132.0917 | 92132.0917
C | Xist Rating 2962 | -41.73 | 1340.76 | 150.284 | 35.6 | 2058.64 | 8732.92 | 10537.9 | 0.36 | 1.25 | 15.111 | 10.908 | 1 | 1 | 2470 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2760142.1664 | 170090.9072 | 5941.9372 | 16594.7558 | 153496.1514 | 11930.2362 | 0.094109 | -92122.1214 | 92122.1214
C | Xist Rating 2963 | -41.71 | 1342.11 | 150.284 | 35.6 | 2057.98 | 8721.13 | 10537.9 | 0.36 | 1.25 | 15.105 | 10.918 | 1 | 1 | 2480 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2762035.5378 | 171403.4922 | 5990.1474 | 16661.941 | 154741.5512 | 11942.8195 | 0.09449 | -92219.2864 | 92219.2864
C | Xist Rating 2964 | -41.7 | 1343.51 | 150.284 | 35.6 | 2057.17 | 8706.68 | 10537.9 | 0.35 | 1.25 | 15.099 | 10.929 | 1 | 1 | 2490 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2763828.4667 | 172721.1091 | 6038.5525 | 16729.1262 | 155991.9829 | 11939.5869 | 0.094871 | -92194.3249 | 92194.3249
C | Xist Rating 2965 | -41.68 | 1344.49 | 150.284 | 35.6 | 2057.1 | 8705.27 | 10537.9 | 0.35 | 1.25 | 15.098 | 10.938 | 1 | 1 | 2500 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2765750.379 | 174043.758 | 6087.1523 | 16796.3115 | 157247.4465 | 11951.263 | 0.095252 | -92284.4846 | 92284.4846
C | Xist Rating 2966 | -41.67 | 1346.34 | 150.284 | 35.6 | 2055.39 | 8674.87 | 10537.9 | 0.34 | 1.25 | 15.095 | 10.95 | 1 | 1 | 2510 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2767253.7726 | 175371.4388 | 6135.9469 | 16863.4967 | 158507.942 | 11948.9921 | 0.095633 | -92266.9497 | 92266.9497
C | Xist Rating 2967 | -41.63 | 1347.8 | 150.284 | 35.6 | 2055.53 | 8677.27 | 10537.8 | 0.34 | 1.25 | 15.13 | 10.961 | 1 | 1 | 2520 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2770443.334 | 176704.1514 | 6184.9363 | 16930.682 | 159773.4695 | 11964.0603 | 0.096014 | -92383.3025 | 92383.3025
C | Xist Rating 2968 | -41.6 | 1349.13 | 150.284 | 35.6 | 2055.13 | 8670.15 | 10537.8 | 0.33 | 1.25 | 15.123 | 10.971 | 1 | 1 | 2530 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2772637.5369 | 178041.8961 | 6234.1205 | 16997.8672 | 161044.0288 | 11959.3308 | 0.096395 | -92346.7825 | 92346.7825
C | Xist Rating 2969 | -41.58 | 1350.28 | 150.284 | 35.6 | 2054.82 | 8664.66 | 10537.8 | 0.33 | 1.25 | 15.118 | 10.981 | 1 | 1 | 2540 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2774582.3496 | 179384.6726 | 6283.4995 | 17065.0525 | 162319.6201 | 11971.765 | 0.096776 | -92442.7957 | 92442.7957
C | Xist Rating 2970 | -41.56 | 1351.83 | 150.284 | 35.6 | 2054.44 | 8658 | 10537.8 | 0.32 | 1.25 | 15.125 | 10.992 | 1 | 1 | 2550 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2777253.6252 | 180732.481 | 6333.0732 | 17132.2377 | 163600.2433 | 11968.4005 | 0.097157 | -92416.8158 | 92416.8158
C | Xist Rating 2971 | -41.54 | 1353.28 | 150.284 | 35.6 | 2053.88 | 8648.14 | 10537.7 | 0.32 | 1.25 | 15.121 | 11.002 | 1 | 1 | 2560 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2779474.7264 | 182085.3214 | 6382.8418 | 17199.423 | 164885.8984 | 11980.8081 | 0.097538 | -92512.6241 | 92512.6241
C | Xist Rating 2972 | -41.52 | 1354.67 | 150.284 | 35.6 | 2053.29 | 8637.75 | 10537.7 | 0.31 | 1.25 | 15.118 | 11.013 | 1 | 1 | 2570 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2781530.3643 | 183443.1937 | 6432.8051 | 17266.6082 | 166176.5855 | 11976.8741 | 0.097919 | -92482.2468 | 92482.2468
C | Xist Rating 2973 | -41.5 | 1356.03 | 150.284 | 35.6 | 2052.94 | 8631.5 | 10537.7 | 0.31 | 1.25 | 15.152 | 11.023 | 1 | 1 | 2580 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2783848.2282 | 184806.0979 | 6482.9633 | 17333.7935 | 167472.3044 | 11990.5787 | 0.0983 | -92588.0705 | 92588.0705
C | Xist Rating 2974 | -41.49 | 1357.39 | 150.284 | 35.6 | 2052.19 | 8618.16 | 10537.7 | 0.3 | 1.25 | 15.149 | 11.033 | 1 | 1 | 2590 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2785622.1841 | 186174.034 | 6533.3162 | 17400.9787 | 168773.0553 | 11985.3738 | 0.098681 | -92547.8798 | 92547.8798
C | Xist Rating 2975 | -41.44 | 1358.57 | 150.284 | 35.6 | 2052.88 | 8630.39 | 10537.7 | 0.3 | 1.25 | 15.151 | 11.042 | 1 | 1 | 2600 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2788981.1816 | 187547.0021 | 6583.8639 | 17468.164 | 170078.8381 | 11996.8274 | 0.099062 | -92636.3211 | 92636.3211
C | Xist Rating 2976 | -41.42 | 1360.26 | 150.284 | 35.6 | 2051.26 | 8601.75 | 10537.8 | 0.29 | 1.25 | 15.149 | 11.054 | 1 | 1 | 2610 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2790246.9276 | 188925.002 | 6634.6064 | 17535.3492 | 171389.6528 | 11993.5334 | 0.099443 | -92610.886 | 92610.886
C | Xist Rating 2977 | -41.44 | 1361.66 | 150.284 | 35.6 | 2050.34 | 8585.73 | 10537.7 | 0.29 | 1.25 | 15.143 | 11.064 | 1 | 1 | 2620 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2791865.9644 | 190308.0339 | 6685.5437 | 17602.5344 | 172705.4995 | 12005.6833 | 0.099824 | -92704.7041 | 92704.7041
C | Xist Rating 2978 | -41.4 | 1363.08 | 150.284 | 35.6 | 2049.71 | 8574.58 | 10537.7 | 0.29 | 1.25 | 15.182 | 11.074 | 1 | 1 | 2630 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2793918.7068 | 191696.0977 | 6736.6758 | 17669.7197 | 174026.378 | 12019.3701 | 0.10021 | -92810.3897 | 92810.3897
C | Xist Rating 2979 | -41.39 | 1364.33 | 150.284 | 35.6 | 2049.05 | 8563.15 | 10537.8 | 0.28 | 1.25 | 15.178 | 11.084 | 1 | 1 | 2640 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2795580.3865 | 193089.1934 | 6788.0027 | 17736.9049 | 175352.2885 | 12013.6301 | 0.10059 | -92766.0673 | 92766.0673
C | Xist Rating 2980 | -41.35 | 1365.83 | 150.284 | 35.6 | 2048.9 | 8560.43 | 10537.7 | 0.28 | 1.25 | 15.174 | 11.094 | 1 | 1 | 2650 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2798449.087 | 194487.3211 | 6839.5243 | 17804.0902 | 176683.2309 | 12025.787 | 0.10097 | -92859.9398 | 92859.9398
C | Xist Rating 2981 | -41.31 | 1367.17 | 150.284 | 35.6 | 2049.01 | 8562.47 | 10537.7 | 0.28 | 1.25 | 15.172 | 11.104 | 1 | 1 | 2660 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2801345.0017 | 195890.4806 | 6891.2408 | 17871.2754 | 178019.2052 | 12038.0097 | 0.10135 | -92954.3202 | 92954.3202
C | Xist Rating 2982 | -41.3 | 1368.56 | 150.284 | 35.6 | 2048.38 | 8551.37 | 10537.7 | 0.27 | 1.25 | 15.167 | 11.114 | 1 | 1 | 2670 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2803330.9328 | 197298.6721 | 6943.152 | 17938.4607 | 179360.2114 | 12031.9792 | 0.10173 | -92907.7543 | 92907.7543
C | Xist Rating 2983 | -41.26 | 1369.97 | 150.284 | 35.6 | 2048.38 | 8551.45 | 10537.7 | 0.27 | 1.25 | 15.205 | 11.124 | 1 | 1 | 2680 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2806219.1486 | 198711.8955 | 6995.258 | 18005.6459 | 180706.2495 | 12045.4324 | 0.10211 | -93011.6358 | 93011.6358
C | Xist Rating 2984 | -41.24 | 1371.35 | 150.284 | 35.6 | 2047.78 | 8541.02 | 10537.6 | 0.27 | 1.25 | 15.197 | 11.134 | 1 | 1 | 2690 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2808223.103 | 200130.1508 | 7047.5588 | 18072.8312 | 182057.3196 | 12057.3971 | 0.10249 | -93104.0244 | 93104.0244
C | Xist Rating 2985 | -41.19 | 1372.55 | 150.284 | 35.6 | 2048.88 | 8560.21 | 10537.7 | 0.26 | 1.25 | 15.193 | 11.143 | 1 | 1 | 2700 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2812190.244 | 201553.438 | 7100.0544 | 18140.0164 | 183413.4216 | 12050.0646 | 0.10287 | -93047.4044 | 93047.4044
C | Xist Rating 2986 | -41.18 | 1374.21 | 150.284 | 35.6 | 2047.44 | 8535.06 | 10537.6 | 0.26 | 1.25 | 15.185 | 11.154 | 1 | 1 | 2710 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2813612.5224 | 202981.7571 | 7152.7448 | 18207.2017 | 184774.5555 | 12063.006 | 0.10325 | -93147.335 | 93147.335
C | Xist Rating 2987 | -41.15 | 1375.55 | 150.284 | 35.6 | 2047.14 | 8529.95 | 10537.7 | 0.26 | 1.25 | 15.183 | 11.164 | 1 | 1 | 2720 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2815943.427 | 204415.1082 | 7205.63 | 18274.3869 | 186140.7213 | 12075.0973 | 0.10363 | -93240.7009 | 93240.7009
C | Xist Rating 2988 | -41.15 | 1376.88 | 150.284 | 35.6 | 2046.13 | 8512.41 | 10537.6 | 0.25 | 1.25 | 15.216 | 11.173 | 1 | 1 | 2730 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2817275.4744 | 205853.4912 | 7258.71 | 18341.5722 | 187511.919 | 12068.6432 | 0.10402 | -93190.864 | 93190.864
C | Xist Rating 2989 | -41.11 | 1378.16 | 150.284 | 35.6 | 2046.42 | 8517.32 | 10537.7 | 0.25 | 1.25 | 15.214 | 11.182 | 1 | 1 | 2740 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2820294.1872 | 207296.9061 | 7311.9847 | 18408.7574 | 188888.1487 | 12079.6334 | 0.1044 | -93275.7275 | 93275.7275
C | Xist Rating 2990 | -41.08 | 1379.71 | 150.284 | 35.6 | 2046.07 | 8511.39 | 10537.7 | 0.25 | 1.25 | 15.212 | 11.193 | 1 | 1 | 2750 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2822983.2397 | 208745.3529 | 7365.4543 | 18475.9426 | 190269.4102 | 12092.7002 | 0.10478 | -93376.6255 | 93376.6255
C | Xist Rating 2991 | -41.08 | 1381.13 | 150.284 | 35.6 | 2044.88 | 8490.75 | 10537.7 | 0.24 | 1.25 | 15.205 | 11.202 | 1 | 1 | 2760 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2824245.1144 | 210198.8316 | 7419.1186 | 18543.1279 | 191655.7037 | 12084.7238 | 0.10516 | -93315.0342 | 93315.0342
C | Xist Rating 2992 | -41.01 | 1382.37 | 150.284 | 35.6 | 2046.19 | 8513.42 | 10537.7 | 0.24 | 1.25 | 15.208 | 11.211 | 1 | 1 | 2770 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2828591.6703 | 211657.3423 | 7472.9777 | 18610.3131 | 193047.0291 | 12095.7955 | 0.10554 | -93400.5263 | 93400.5263
C | Xist Rating 2993 | -41 | 1383.91 | 150.284 | 35.6 | 2044.99 | 8492.64 | 10537.7 | 0.24 | 1.25 | 15.242 | 11.222 | 1 | 1 | 2780 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2830082.1109 | 213120.8848 | 7527.0316 | 18677.4984 | 194443.3865 | 12109.8719 | 0.10592 | -93509.2205 | 93509.2205
C | Xist Rating 2994 | -40.89 | 1385.32 | 150.284 | 35.6 | 2047.6 | 8537.76 | 10537.8 | 0.23 | 1.25 | 15.251 | 11.232 | 1 | 1 | 2790 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2836581.232 | 214589.4593 | 7581.2803 | 18744.6836 | 195844.7757 | 12103.0937 | 0.1063 | -93456.8811 | 93456.8811
C | Xist Rating 2995 | -40.92 | 1386.3 | 150.284 | 35.6 | 2045.99 | 8509.95 | 10537.7 | 0.23 | 1.25 | 15.238 | 11.239 | 1 | 1 | 2800 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2836355.937 | 216063.0657 | 7635.7238 | 18811.8689 | 197251.1969 | 12111.5602 | 0.10668 | -93522.2575 | 93522.2575
C | Xist Rating 2996 | -40.85 | 1388.04 | 150.284 | 35.6 | 2046.76 | 8523.19 | 10537.8 | 0.23 | 1.25 | 15.242 | 11.25 | 1 | 1 | 2810 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2840984.7504 | 217541.7041 | 7690.3621 | 18879.0541 | 198662.6499 | 12124.6706 | 0.10706 | -93623.4922 | 93623.4922
C | Xist Rating 2997 | -40.6 | 1389.52 | 150.284 | 35.6 | 2054.09 | 8651.63 | 10538 | 0.23 | 1.25 | 15.267 | 11.261 | 1 | 1 | 2820 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2854199.1368 | 219025.3743 | 7745.1952 | 18946.2394 | 200079.1349 | 12138.3923 | 0.10744 | -93729.4476 | 93729.4476
C | Xist Rating 2998 | -40.15 | 1390.89 | 150.284 | 35.6 | 2068.79 | 8918.37 | 10538.1 | 0.22 | 1.25 | 15.379 | 11.271 | 1 | 1 | 2830 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2877459.3231 | 220514.0765 | 7800.223 | 19013.4246 | 201500.6519 | 12134.1102 | 0.10783 | -93696.3822 | 93696.3822
C | Xist Rating 2999 | -39.78 | 1392.21 | 150.284 | 35.6 | 2080.3 | 9136.17 | 10538.2 | 0.22 | 1.25 | 15.441 | 11.281 | 1 | 1 | 2840 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2896214.463 | 222007.8106 | 7855.4457 | 19080.6099 | 202927.2007 | 12147.7481 | 0.10821 | -93801.691 | 93801.691
C | Xist Rating 3000 | -39.63 | 1393.65 | 150.284 | 35.6 | 2084.09 | 9209.77 | 10538.2 | 0.21 | 1.25 | 15.462 | 11.291 | 1 | 1 | 2850 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2904492.0285 | 223506.5766 | 7910.8631 | 19147.7951 | 204358.7814 | 12140.4933 | 0.10859 | -93745.671 | 93745.671
C | Xist Rating 3001 | -39.5 | 1395.06 | 150.284 | 35.6 | 2087.44 | 9275.68 | 10538.2 | 0.21 | 1.25 | 15.472 | 11.301 | 1 | 1 | 2860 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2912104.0464 | 225010.3745 | 7966.4753 | 19214.9803 | 205795.3941 | 12152.6029 | 0.10897 | -93839.1786 | 93839.1786
C | Xist Rating 3002 | -39.39 | 1396.25 | 150.284 | 35.6 | 2090.41 | 9334.45 | 10538.2 | 0.21 | 1.25 | 15.478 | 11.31 | 1 | 1 | 2870 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2918734.9625 | 226519.2043 | 8022.2824 | 19282.1656 | 207237.0387 | 12163.5679 | 0.10935 | -93923.8473 | 93923.8473
C | Xist Rating 3003 | -39.29 | 1397.75 | 150.284 | 35.6 | 2092.41 | 9374.58 | 10538.2 | 0.21 | 1.25 | 15.524 | 11.32 | 1 | 1 | 2880 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2924666.0775 | 228033.0661 | 8078.2842 | 19349.3508 | 208683.7152 | 12176.6569 | 0.10973 | -94024.9172 | 94024.9172
C | Xist Rating 3004 | -39.19 | 1399.1 | 150.284 | 35.6 | 2094.76 | 9421.92 | 10538.2 | 0.2 | 1.25 | 15.528 | 11.329 | 1 | 1 | 2890 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2930778.716 | 229551.9597 | 8134.4807 | 19416.5361 | 210135.4236 | 12167.4581 | 0.11011 | -93953.886 | 93953.886
C | Xist Rating 3005 | -39.09 | 1400.48 | 150.284 | 35.6 | 2096.98 | 9467.04 | 10538.1 | 0.2 | 1.25 | 15.531 | 11.338 | 1 | 1 | 2900 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2936778.5504 | 231075.8853 | 8190.8721 | 19483.7213 | 211592.164 | 12178.2746 | 0.11049 | -94037.4085 | 94037.4085
C | Xist Rating 3006 | -39.01 | 1402.02 | 150.284 | 35.5 | 2098.17 | 9491.5 | 10538.1 | 0.2 | 1.25 | 15.533 | 11.348 | 1 | 1 | 2910 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 13 | E | Rod | 2941676.3034 | 232604.8428 | 8247.4583 | 19550.9066 | 213053.9362 | 12190.1041 | 0.11087 | -94128.7528 | 94128.7528
C | Xist Rating 3007 | -38.92 | 1403.41 | 150.284 | 35.5 | 2099.98 | 9528.48 | 10538.1 | 0.2 | 1.25 | 15.536 | 11.358 | 1 | 1 | 2920 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 12 | E | Rod | 2947132.9318 | 234138.8323 | 8304.2393 | 19618.0918 | 214520.7404 | 12201.9602 | 0.11125 | -94220.302 | 94220.302
C | Xist Rating 3008 | -38.77 | 1404.8 | 150.285 | 35.5 | 2103.88 | 9609.45 | 10538 | 0.19 | 1.25 | 15.583 | 11.367 | 1 | 1 | 2930 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 12 | E | Rod | 2955530.624 | 235677.8536 | 8361.215 | 19685.2771 | 215992.5765 | 12193.4679 | 0.11164 | -94154.7268 | 94154.7268
C | Xist Rating 3009 | -38.62 | 1406.17 | 150.284 | 35.5 | 2107.94 | 9694.73 | 10538 | 0.19 | 1.25 | 15.587 | 11.376 | 1 | 1 | 2940 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 12 | E | Rod | 2964121.9898 | 237221.9069 | 8418.3855 | 19752.4623 | 217469.4445 | 12204.2417 | 0.11202 | -94237.9193 | 94237.9193
C | Xist Rating 3010 | -38.63 | 1407.58 | 150.284 | 35.5 | 2106.53 | 9665.03 | 10537.9 | 0.19 | 1.25 | 15.583 | 11.386 | 1 | 1 | 2950 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 12 | E | Rod | 2965109.4974 | 238770.992 | 8475.7509 | 19819.6476 | 218951.3445 | 12215.8537 | 0.1124 | -94327.5839 | 94327.5839
C | Xist Rating 3011 | -38.62 | 1408.95 | 150.284 | 35.5 | 2105.89 | 9651.62 | 10537.9 | 0.19 | 1.25 | 15.579 | 11.395 | 1 | 1 | 2960 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 12 | E | Rod | 2967093.7155 | 240325.1091 | 8533.311 | 19886.8328 | 220438.2763 | 12226.4265 | 0.11278 | -94409.2243 | 94409.2243
C | Xist Rating 3012 | -38.6 | 1410.33 | 150.284 | 35.5 | 2105.24 | 9638.08 | 10537.9 | 0.18 | 1.25 | 15.576 | 11.404 | 1 | 1 | 2970 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 12 | E | Rod | 2969083.1292 | 241884.2582 | 8591.0659 | 19954.0181 | 221930.2401 | 12216.2877 | 0.11316 | -94330.9352 | 94330.9352
C | Xist Rating 3013 | -38.59 | 1411.55 | 150.285 | 35.5 | 2104.67 | 9626.17 | 10537.9 | 0.18 | 1.25 | 15.612 | 11.412 | 1 | 1 | 2980 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 12 | E | Rod | 2970846.9385 | 243448.4391 | 8649.0156 | 20021.2033 | 223427.2358 | 12226.718 | 0.11354 | -94411.4753 | 94411.4753
C | Xist Rating 3014 | -38.56 | 1413.11 | 150.285 | 35.5 | 2103.99 | 9611.87 | 10537.9 | 0.18 | 1.25 | 15.607 | 11.422 | 1 | 1 | 2990 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 12 | E | Rod | 2973169.3089 | 245017.652 | 8707.16 | 20088.3885 | 224929.2634 | 12238.242 | 0.11392 | -94500.4606 | 94500.4606
C | Xist Rating 3015 | -38.55 | 1414.54 | 150.285 | 35.5 | 2102.86 | 9588.38 | 10537.9 | 0.18 | 1.25 | 15.608 | 11.431 | 1 | 1 | 3000 | 152.4 | 2 | 2.4 | 19.05 | 1.3333 | 12 | E | Rod | 2974579.5844 | 246591.8967 | 8765.4993 | 20155.5738 | 226436.3229 | 12248.8719 | 0.1143 | -94582.5422 | 94582.5422
C | Xist Rating 3016 | -92.68 | 134.542 | 150.287 | 35.8 | 2401.48 | 7421.73 | 58745.7 | 2.45 | 10.95 | 16.48 | 401.168 | 1 | 1 | 1000 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 323099.9222 | 33206.3709 | 973.9444 | 6998.4631 | 26207.9077 | 418422.1738 | 0.038101 | -3230945.1145 | 3230945.1145
C | Xist Rating 3017 | -92.61 | 135.963 | 150.287 | 35.8 | 2398.53 | 7402.16 | 58284.1 | 2.43 | 10.85 | 16.508 | 393.671 | 1 | 1 | 1010 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 326111.3344 | 33803.1344 | 993.5206 | 7068.4478 | 26734.6867 | 410642.808 | 0.038482 | -3170874.9137 | 3170874.9137
C | Xist Rating 3018 | -92.06 | 146.592 | 150.287 | 35.8 | 2392.31 | 7408.04 | 54967.6 | 2.44 | 10.07 | 16.561 | 341.152 | 1 | 1 | 1020 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 350693.5075 | 34405.1396 | 1013.2917 | 7138.4324 | 27266.7072 | 356133.351 | 0.038863 | -2749967.3356 | 2749967.3356
C | Xist Rating 3019 | -91.97 | 149.578 | 150.286 | 35.8 | 2371.72 | 7229.93 | 54178.6 | 2.35 | 9.89 | 16.238 | 329.809 | 1 | 1 | 1030 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 354757.1342 | 35012.3863 | 1033.2576 | 7208.417 | 27803.9693 | 344267.9166 | 0.039244 | -2658345.5968 | 2658345.5968
C | Xist Rating 3020 | -91.9 | 151.073 | 150.286 | 35.8 | 2369.67 | 7218.87 | 53794.4 | 2.31 | 9.8 | 16.161 | 324.395 | 1 | 1 | 1040 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 357993.1559 | 35624.8747 | 1053.4182 | 7278.4016 | 28346.473 | 338624.02 | 0.039625 | -2614764.9231 | 2614764.9231
C | Xist Rating 3021 | -91.72 | 153.937 | 150.286 | 35.8 | 2379.16 | 7323.83 | 53043.7 | 2.26 | 9.63 | 16.124 | 313.698 | 1 | 1 | 1050 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 366240.7529 | 36242.6046 | 1073.7737 | 7348.3863 | 28894.2183 | 327489.9691 | 0.040006 | -2528790.7331 | 2528790.7331
C | Xist Rating 3022 | -91.6 | 155.412 | 150.286 | 35.8 | 2391.41 | 7449.58 | 52677.3 | 2.21 | 9.54 | 16.112 | 308.653 | 1 | 1 | 1060 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 371653.8109 | 36865.5761 | 1094.3239 | 7418.3709 | 29447.2051 | 322227.5128 | 0.040387 | -2488155.4407 | 2488155.4407
C | Xist Rating 3023 | -91.05 | 166.907 | 150.286 | 35.8 | 2372.71 | 7336.88 | 49857.7 | 2.19 | 8.9 | 16.013 | 270.11 | 1 | 1 | 1070 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 396021.908 | 37493.7891 | 1115.0689 | 7488.3555 | 30005.4336 | 282190.7751 | 0.040768 | -2179002.3645 | 2179002.3645
C | Xist Rating 3024 | -90.92 | 169.123 | 150.286 | 35.8 | 2378.01 | 7399.96 | 49381.6 | 2.14 | 8.79 | 15.945 | 264.11 | 1 | 1 | 1080 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 402176.1852 | 38127.2438 | 1136.0087 | 7558.3402 | 30568.9036 | 275929.6992 | 0.041149 | -2130655.9962 | 2130655.9962
C | Xist Rating 3025 | -90.76 | 172.067 | 150.286 | 35.8 | 2378.73 | 7423.22 | 48762.7 | 2.08 | 8.65 | 15.842 | 256.393 | 1 | 1 | 1090 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 409300.9349 | 38765.94 | 1157.1433 | 7628.3248 | 31137.6152 | 267873.6913 | 0.04153 | -2068449.6386 | 2068449.6386
C | Xist Rating 3026 | -90.63 | 174.252 | 150.285 | 35.8 | 2385.19 | 7498.91 | 48308.2 | 2.04 | 8.55 | 15.827 | 250.804 | 1 | 1 | 1100 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 415624.1279 | 39409.8778 | 1178.4727 | 7698.3094 | 31711.5684 | 262051.5402 | 0.041911 | -2023492.5314 | 2023492.5314
C | Xist Rating 3027 | -90.57 | 175.914 | 150.285 | 35.8 | 2378.67 | 7442.97 | 48011.5 | 1.97 | 8.49 | 15.627 | 247.45 | 1 | 1 | 1110 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 418441.3544 | 40059.0572 | 1199.9969 | 7768.2941 | 32290.7631 | 258508.162 | 0.042292 | -1996131.5041 | 1996131.5041
C | Xist Rating 3028 | -89.9 | 188.654 | 150.285 | 35.8 | 2376.59 | 7497.9 | 45448.1 | 2.01 | 7.92 | 15.81 | 216.515 | 1 | 1 | 1120 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 448353.2099 | 40713.4782 | 1221.7158 | 7838.2787 | 32875.1995 | 226445.8604 | 0.042673 | -1748554.9102 | 1748554.9102
C | Xist Rating 3029 | -89.83 | 190.271 | 150.285 | 35.8 | 2374.62 | 7486.51 | 45189 | 1.95 | 7.86 | 15.677 | 213.796 | 1 | 1 | 1130 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 451821.322 | 41373.1407 | 1243.6296 | 7908.2633 | 33464.8774 | 223575.2428 | 0.043054 | -1726388.7613 | 1726388.7613
C | Xist Rating 3030 | -89.69 | 193.286 | 150.285 | 35.8 | 2369.7 | 7453.86 | 44681.1 | 1.9 | 7.75 | 15.555 | 208.273 | 1 | 1 | 1140 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 458029.8342 | 42038.0449 | 1265.7381 | 7978.248 | 34059.7969 | 217801.4191 | 0.043435 | -1681804.8258 | 1681804.8258
C | Xist Rating 3031 | -89.51 | 196.238 | 150.285 | 35.8 | 2375.77 | 7530.46 | 44186.9 | 1.85 | 7.64 | 15.449 | 202.923 | 1 | 1 | 1150 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 466216.3533 | 42708.1906 | 1288.0414 | 8048.2326 | 34659.958 | 212208.4999 | 0.043816 | -1638617.7862 | 1638617.7862
C | Xist Rating 3032 | -89.36 | 199.269 | 150.284 | 35.8 | 2376.16 | 7550.74 | 43704.2 | 1.8 | 7.53 | 15.353 | 197.843 | 1 | 1 | 1160 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 473495.027 | 43383.5779 | 1310.5395 | 8118.2172 | 35265.3607 | 206896.5894 | 0.044197 | -1597600.6208 | 1597600.6208
C | Xist Rating 3033 | -88.75 | 210.749 | 150.285 | 35.8 | 2375.49 | 7611.63 | 41833.2 | 1.82 | 7.13 | 15.464 | 177.988 | 1 | 1 | 1170 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 500632.142 | 44064.2068 | 1333.2324 | 8188.2019 | 35876.0049 | 186316.2894 | 0.044578 | -1438684.9994 | 1438684.9994
C | Xist Rating 3034 | -88.67 | 211.651 | 150.285 | 35.8 | 2384.16 | 7705.58 | 41725.5 | 1.77 | 7.11 | 15.409 | 177.068 | 1 | 1 | 1180 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 504609.8482 | 44750.0772 | 1356.1201 | 8258.1865 | 36491.8907 | 185327.4404 | 0.044959 | -1431049.3698 | 1431049.3698
C | Xist Rating 3035 | -88.41 | 217.54 | 150.284 | 35.8 | 2373.06 | 7623.53 | 40886.4 | 1.72 | 6.93 | 15.299 | 168.828 | 1 | 1 | 1190 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 516235.4724 | 45441.1893 | 1379.2026 | 8328.1711 | 37113.0182 | 176731.2499 | 0.04534 | -1364671.8651 | 1364671.8651
C | Xist Rating 3036 | -88.28 | 219.049 | 150.284 | 35.8 | 2385.31 | 7759.89 | 40682.8 | 1.69 | 6.88 | 15.316 | 166.914 | 1 | 1 | 1200 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 522499.7702 | 46137.5429 | 1402.4799 | 8398.1557 | 37739.3872 | 174732.2167 | 0.045721 | -1349235.8612 | 1349235.8612
C | Xist Rating 3037 | -88.14 | 222.149 | 150.284 | 35.8 | 2380.43 | 7725.19 | 40282.4 | 1.64 | 6.8 | 15.222 | 163.2 | 1 | 1 | 1210 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 528810.1441 | 46839.1381 | 1425.9519 | 8468.1404 | 38370.9977 | 170836.9394 | 0.046102 | -1319157.5622 | 1319157.5622
C | Xist Rating 3038 | -87.52 | 235.243 | 150.284 | 35.8 | 2368.14 | 7672.57 | 38538.4 | 1.64 | 6.43 | 15.24 | 146.806 | 1 | 1 | 1220 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 557088.358 | 47545.9749 | 1449.6188 | 8538.125 | 39007.8499 | 153824.6007 | 0.046483 | -1187792.7924 | 1187792.7924
C | Xist Rating 3039 | -87.33 | 238.193 | 150.284 | 35.8 | 2374.47 | 7756.13 | 38183.8 | 1.62 | 6.35 | 15.242 | 143.686 | 1 | 1 | 1230 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 565582.1327 | 48258.0533 | 1473.4804 | 8608.1096 | 39649.9436 | 150579.0626 | 0.046864 | -1162731.6076 | 1162731.6076
C | Xist Rating 3040 | -87.18 | 241.283 | 150.284 | 35.8 | 2374.62 | 7774.33 | 37836.5 | 1.57 | 6.28 | 15.175 | 140.737 | 1 | 1 | 1240 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 572955.4375 | 48975.3732 | 1497.5369 | 8678.0943 | 40297.279 | 147479.3927 | 0.047245 | -1138796.7781 | 1138796.7781
C | Xist Rating 3041 | -87.09 | 242.936 | 150.284 | 35.8 | 2375.96 | 7797.11 | 37665.3 | 1.54 | 6.24 | 15.124 | 139.366 | 1 | 1 | 1250 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 577206.2186 | 49697.9348 | 1521.7881 | 8748.0789 | 40949.8559 | 146036.3821 | 0.047626 | -1127654.2323 | 1127654.2323
C | Xist Rating 3042 | -86.88 | 247.384 | 150.284 | 35.8 | 2372.77 | 7787.94 | 37162.1 | 1.51 | 6.14 | 15.092 | 135.081 | 1 | 1 | 1260 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 586985.3337 | 50425.7379 | 1546.2341 | 8818.0635 | 41607.6743 | 141568.5017 | 0.048007 | -1093154.4443 | 1093154.4443
C | Xist Rating 3043 | -86.26 | 259.793 | 150.284 | 35.8 | 2366.33 | 7790.93 | 35778.2 | 1.52 | 5.85 | 15.149 | 123.408 | 1 | 1 | 1270 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 614755.9697 | 51158.7826 | 1570.8749 | 8888.0482 | 42270.7344 | 129469.8483 | 0.048388 | -999731.8502 | 999731.8502
C | Xist Rating 3044 | -86.13 | 262.951 | 150.284 | 35.8 | 2362.24 | 7763.18 | 35478 | 1.48 | 5.79 | 15.083 | 121.108 | 1 | 1 | 1280 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 621153.3702 | 51897.0688 | 1595.7105 | 8958.0328 | 42939.0361 | 127051.2518 | 0.048769 | -981056.0887 | 981056.0887
C | Xist Rating 3045 | -85.96 | 266.058 | 150.284 | 35.8 | 2364.88 | 7808.28 | 35183.4 | 1.44 | 5.73 | 15.07 | 118.857 | 1 | 1 | 1290 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 629195.243 | 52640.5967 | 1620.7408 | 9028.0174 | 43612.5793 | 124687.6293 | 0.04915 | -962804.8221 | 962804.8221
C | Xist Rating 3046 | -85.69 | 270.485 | 150.284 | 35.8 | 2371.9 | 7910.65 | 34751.8 | 1.42 | 5.64 | 15.084 | 115.505 | 1 | 1 | 1300 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 641563.3715 | 53389.3662 | 1645.966 | 9098.0021 | 44291.3641 | 121199.9051 | 0.049531 | -935873.5408 | 935873.5408
C | Xist Rating 3047 | -85.53 | 272.894 | 150.283 | 35.8 | 2377.73 | 7988.76 | 34541 | 1.38 | 5.59 | 15.051 | 113.968 | 1 | 1 | 1310 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 648868.2506 | 54143.3772 | 1671.3859 | 9167.9867 | 44975.3905 | 119575.2306 | 0.049912 | -923328.2346 | 923328.2346
C | Xist Rating 3048 | -84.92 | 285.4 | 150.284 | 35.8 | 2371.56 | 7993.85 | 33363.9 | 1.38 | 5.35 | 15.097 | 105.002 | 1 | 1 | 1320 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 676843.224 | 54902.6298 | 1697.0007 | 9237.9713 | 45664.6585 | 110277.12 | 0.050293 | -851530.6895 | 851530.6895
C | Xist Rating 3049 | -84.71 | 290.044 | 150.283 | 35.7 | 2367.05 | 7968.18 | 32980.8 | 1.35 | 5.28 | 15.001 | 102.305 | 1 | 1 | 1330 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 686548.6502 | 55667.124 | 1722.8102 | 9307.956 | 46359.168 | 107450.9011 | 0.050674 | -829707.3763 | 829707.3763
C | Xist Rating 3050 | -84.47 | 294.586 | 150.283 | 35.7 | 2367.69 | 8000.9 | 32607.9 | 1.32 | 5.2 | 14.979 | 99.688 | 1 | 1 | 1340 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 697488.3263 | 56436.8597 | 1748.8145 | 9377.9406 | 47058.9192 | 104713.453 | 0.051055 | -808569.5276 | 808569.5276
C | Xist Rating 3051 | -84.33 | 297.012 | 150.283 | 35.7 | 2371.64 | 8059.14 | 32424.9 | 1.29 | 5.16 | 14.952 | 98.475 | 1 | 1 | 1350 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 704405.5397 | 57211.8371 | 1775.0136 | 9447.9252 | 47763.9119 | 103433.3167 | 0.051436 | -798684.6547 | 798684.6547
C | Xist Rating 3052 | -84.15 | 298.467 | 150.283 | 35.7 | 2387.91 | 8259.22 | 32304 | 1.28 | 5.14 | 14.994 | 97.643 | 1 | 1 | 1360 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 712712.334 | 57992.056 | 1801.4075 | 9517.9098 | 48474.1462 | 102572.0942 | 0.051817 | -792034.5225 | 792034.5225
C | Xist Rating 3053 | -83.4 | 316.349 | 150.283 | 35.7 | 2361.05 | 8049.8 | 30903.2 | 1.27 | 4.86 | 14.966 | 88.059 | 1 | 1 | 1370 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 746915.8065 | 58777.5165 | 1827.9962 | 9587.8945 | 49189.6221 | 92616.3367 | 0.052198 | -715158.8023 | 715158.8023
C | Xist Rating 3054 | -83.32 | 318.065 | 150.283 | 35.7 | 2360.58 | 8052.76 | 30794.7 | 1.24 | 4.84 | 14.937 | 87.424 | 1 | 1 | 1380 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 750817.8777 | 59568.2186 | 1854.7797 | 9657.8791 | 49910.3395 | 91935.4125 | 0.052579 | -709900.8863 | 709900.8863
C | Xist Rating 3055 | -83.13 | 321.969 | 150.283 | 35.7 | 2360.94 | 8078.27 | 30527.5 | 1.22 | 4.78 | 14.911 | 85.747 | 1 | 1 | 1390 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 760149.4909 | 60364.1623 | 1881.7579 | 9727.8637 | 50636.2986 | 90181.5633 | 0.05296 | -696358.1276 | 696358.1276
C | Xist Rating 3056 | -82.92 | 325.869 | 150.283 | 35.7 | 2362.12 | 8113.56 | 30265.5 | 1.19 | 4.73 | 14.889 | 84.121 | 1 | 1 | 1400 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 769741.6823 | 61165.3476 | 1908.931 | 9797.8484 | 51367.4992 | 88471.4043 | 0.053341 | -683152.7325 | 683152.7325
C | Xist Rating 3057 | -82.69 | 330.472 | 150.283 | 35.7 | 2362.42 | 8142.8 | 29958 | 1.17 | 4.67 | 14.872 | 82.214 | 1 | 1 | 1410 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 780713.6622 | 61971.7744 | 1936.2988 | 9867.833 | 52103.9414 | 86478.8521 | 0.053722 | -667766.7732 | 667766.7732
C | Xist Rating 3058 | -82.04 | 343.809 | 150.283 | 35.7 | 2357.54 | 8164.19 | 29052.3 | 1.18 | 4.49 | 14.93 | 76.544 | 1 | 1 | 1420 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 810543.4699 | 62783.4428 | 1963.8614 | 9937.8176 | 52845.6252 | 80612.1882 | 0.054103 | -622465.949 | 622465.949
C | Xist Rating 3059 | -81.93 | 346.475 | 150.283 | 35.7 | 2354 | 8134.63 | 28911 | 1.15 | 4.47 | 14.873 | 75.794 | 1 | 1 | 1430 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 815602.15 | 63600.3528 | 1991.6188 | 10007.8023 | 53592.5506 | 79808.2995 | 0.054484 | -616258.5341 | 616258.5341
C | Xist Rating 3060 | -81.64 | 352.534 | 150.283 | 35.7 | 2352.03 | 8145.19 | 28542.3 | 1.13 | 4.39 | 14.86 | 73.632 | 1 | 1 | 1440 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 829170.544 | 64422.5044 | 2019.571 | 10077.7869 | 54344.7175 | 77550.5842 | 0.054865 | -598825.055 | 598825.055
C | Xist Rating 3061 | -81.45 | 356.472 | 150.283 | 35.7 | 2351.78 | 8163.44 | 28317 | 1.11 | 4.35 | 14.841 | 72.364 | 1 | 1 | 1450 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 838343.7202 | 65249.8976 | 2047.718 | 10147.7715 | 55102.126 | 76220.6076 | 0.055246 | -588555.328 | 588555.328
C | Xist Rating 3062 | -81.29 | 358.779 | 150.283 | 35.7 | 2358.76 | 8261.25 | 28184 | 1.1 | 4.33 | 14.851 | 71.619 | 1 | 1 | 1460 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 846273.554 | 66082.5323 | 2076.0598 | 10217.7562 | 55864.7762 | 75445.3178 | 0.055627 | -582568.7458 | 582568.7458
C | Xist Rating 3063 | -80.63 | 373.999 | 150.283 | 35.7 | 2342.59 | 8152.06 | 27310.7 | 1.09 | 4.16 | 14.853 | 66.656 | 1 | 1 | 1470 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 876126.3174 | 66920.4086 | 2104.5964 | 10287.7408 | 56632.6679 | 70288.9307 | 0.056008 | -542752.4917 | 542752.4917
C | Xist Rating 3064 | -80.4 | 378.646 | 150.283 | 35.7 | 2343.17 | 8184.43 | 27066.5 | 1.07 | 4.11 | 14.842 | 65.349 | 1 | 1 | 1480 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 887231.9478 | 67763.5266 | 2133.3277 | 10357.7254 | 57405.8011 | 68918.3824 | 0.056389 | -532169.4806 | 532169.4806
C | Xist Rating 3065 | -80.16 | 382.586 | 150.283 | 35.7 | 2348.28 | 8268.69 | 26867.2 | 1.05 | 4.07 | 14.84 | 64.306 | 1 | 1 | 1490 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 15 | E | Rod | 898419.0521 | 68611.886 | 2162.2539 | 10427.7101 | 58184.176 | 67822.3813 | 0.05677 | -523706.4506 | 523706.4506
C | Xist Rating 3066 | -79.93 | 386.618 | 150.283 | 35.7 | 2351.95 | 8336.16 | 26670.7 | 1.03 | 4.03 | 14.801 | 63.301 | 1 | 1 | 1500 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 909306.2051 | 69465.4871 | 2191.3748 | 10497.6947 | 58967.7924 | 66763.0181 | 0.057151 | -515526.329 | 515526.329
C | Xist Rating 3067 | -79.66 | 391.292 | 150.283 | 35.7 | 2355.73 | 8410.52 | 26439.2 | 1.01 | 3.99 | 14.8 | 62.104 | 1 | 1 | 1510 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 921778.3032 | 70324.3298 | 2220.6906 | 10567.6793 | 59756.6505 | 65506.6645 | 0.057532 | -505825.0994 | 505825.0994
C | Xist Rating 3068 | -78.91 | 406.195 | 150.283 | 35.7 | 2353.92 | 8478.78 | 25681.4 | 1.02 | 3.85 | 14.865 | 58.109 | 1 | 1 | 1520 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 956150.5344 | 71188.414 | 2250.2011 | 10637.6639 | 60550.7501 | 61379.1647 | 0.057913 | -473953.64 | 473953.64
C | Xist Rating 3069 | -78.73 | 411.213 | 150.283 | 35.7 | 2347.04 | 8416.56 | 25468.7 | 0.99 | 3.8 | 14.82 | 57.107 | 1 | 1 | 1530 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 965133.3595 | 72057.7398 | 2279.9064 | 10707.6486 | 61350.0912 | 60311.7464 | 0.058294 | -465711.3189 | 465711.3189
C | Xist Rating 3070 | -78.56 | 413.795 | 150.283 | 35.7 | 2351.51 | 8487.73 | 25363.9 | 0.97 | 3.79 | 14.81 | 56.634 | 1 | 1 | 1540 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 973043.0805 | 72932.3072 | 2309.8065 | 10777.6332 | 62154.674 | 59805.9832 | 0.058675 | -461805.9492 | 461805.9492
C | Xist Rating 3071 | -78.19 | 421.434 | 150.283 | 35.7 | 2349.62 | 8507.89 | 25021.6 | 0.96 | 3.72 | 14.805 | 54.958 | 1 | 1 | 1550 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 990209.7551 | 73812.1162 | 2339.9013 | 10847.6178 | 62964.4984 | 58061.276 | 0.059056 | -448333.7827 | 448333.7827
C | Xist Rating 3072 | -77.97 | 423.792 | 150.283 | 35.7 | 2361.97 | 8685.99 | 24921 | 0.95 | 3.7 | 14.826 | 54.491 | 1 | 1 | 1560 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1000983.9902 | 74697.1668 | 2370.191 | 10917.6025 | 63779.5643 | 57573.7105 | 0.059437 | -444568.9312 | 444568.9312
C | Xist Rating 3073 | -77.26 | 441.502 | 150.283 | 35.7 | 2340.81 | 8510.24 | 24162.6 | 0.94 | 3.56 | 14.826 | 50.864 | 1 | 1 | 1570 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1033472.2966 | 75587.4589 | 2400.6755 | 10987.5871 | 64599.8718 | 53802.9564 | 0.059818 | -415452.1675 | 415452.1675
C | Xist Rating 3074 | -77.03 | 445.562 | 150.283 | 35.7 | 2344.32 | 8579.39 | 24007.9 | 0.92 | 3.53 | 14.819 | 50.184 | 1 | 1 | 1580 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1044539.9078 | 76482.9926 | 2431.3547 | 11057.5717 | 65425.4209 | 53081.5679 | 0.0602 | -409881.7968 | 409881.7968
C | Xist Rating 3075 | -76.81 | 449.658 | 150.283 | 35.7 | 2346.48 | 8631.03 | 23855.5 | 0.9 | 3.5 | 14.81 | 49.522 | 1 | 1 | 1590 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1055113.5038 | 77383.7679 | 2462.2288 | 11127.5564 | 66256.2116 | 52378.4924 | 0.060581 | -404452.8346 | 404452.8346
C | Xist Rating 3076 | -76.48 | 455.066 | 150.283 | 35.7 | 2352.8 | 8749.81 | 23645.7 | 0.89 | 3.46 | 14.818 | 48.584 | 1 | 1 | 1600 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1070679.2848 | 78289.7848 | 2493.2976 | 11197.541 | 67092.2438 | 51400.2446 | 0.060962 | -396899.064 | 396899.064
C | Xist Rating 3077 | -76.35 | 457.843 | 150.283 | 35.7 | 2352.76 | 8763.36 | 23557 | 0.87 | 3.45 | 14.798 | 48.24 | 1 | 1 | 1610 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1077194.6967 | 79201.0433 | 2524.5612 | 11267.5256 | 67933.5177 | 51026.2693 | 0.061343 | -394011.3259 | 394011.3259
C | Xist Rating 3078 | -75.48 | 477.574 | 150.283 | 35.7 | 2339.28 | 8699.28 | 22805.5 | 0.88 | 3.31 | 14.83 | 44.887 | 1 | 1 | 1620 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1117179.3067 | 80117.5433 | 2556.0196 | 11337.5103 | 68780.0331 | 47562.7455 | 0.061724 | -367266.9133 | 367266.9133
C | Xist Rating 3079 | -75.29 | 480.007 | 150.283 | 35.7 | 2346.85 | 8819 | 22723.7 | 0.87 | 3.29 | 14.839 | 44.56 | 1 | 1 | 1630 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1126504.4279 | 81039.285 | 2587.6728 | 11407.4949 | 69631.7901 | 47218.743 | 0.062105 | -364610.6171 | 364610.6171
C | Xist Rating 3080 | -75.09 | 484.25 | 150.283 | 35.7 | 2345.78 | 8827.37 | 22589 | 0.85 | 3.27 | 14.821 | 44.029 | 1 | 1 | 1640 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1135943.965 | 81966.2682 | 2619.5208 | 11477.4795 | 70488.7887 | 46650.1454 | 0.062486 | -360220.0572 | 360220.0572
C | Xist Rating 3081 | -74.85 | 490.015 | 150.283 | 35.7 | 2342.33 | 8811.35 | 22403.4 | 0.83 | 3.24 | 14.801 | 43.284 | 1 | 1 | 1650 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1147776.835 | 82898.493 | 2651.5635 | 11547.4642 | 71351.0288 | 45858.9599 | 0.062867 | -354110.7321 | 354110.7321
C | Xist Rating 3082 | -74.56 | 495.537 | 150.283 | 35.7 | 2343.67 | 8863.35 | 22221.2 | 0.82 | 3.2 | 14.801 | 42.544 | 1 | 1 | 1660 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1161375.2008 | 83835.9594 | 2683.8011 | 11617.4488 | 72218.5106 | 45084.9644 | 0.063248 | -348134.1443 | 348134.1443
C | Xist Rating 3083 | -73.8 | 513.29 | 150.283 | 35.7 | 2331.88 | 8804.72 | 21633.3 | 0.82 | 3.1 | 14.818 | 40.128 | 1 | 1 | 1670 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1196930.6852 | 84778.6673 | 2716.2334 | 11687.4334 | 73091.2339 | 42582.436 | 0.063629 | -328810.2835 | 328810.2835
C | Xist Rating 3084 | -73.62 | 515.834 | 150.283 | 35.7 | 2337.41 | 8898.22 | 21560.7 | 0.81 | 3.08 | 14.821 | 39.865 | 1 | 1 | 1680 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1205715.5499 | 85726.6169 | 2748.8606 | 11757.418 | 73969.1988 | 42303.7817 | 0.06401 | -326658.5887 | 326658.5887
C | Xist Rating 3085 | -73.31 | 523.171 | 150.283 | 35.7 | 2332.04 | 8862.8 | 21346.3 | 0.79 | 3.04 | 14.8 | 39.051 | 1 | 1 | 1690 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1220055.6988 | 86679.808 | 2781.6825 | 11827.4027 | 74852.4053 | 41440.1135 | 0.064391 | -319989.5721 | 319989.5721
C | Xist Rating 3086 | -73.06 | 528.001 | 150.283 | 35.7 | 2333.98 | 8919.16 | 21206.1 | 0.78 | 3.02 | 14.799 | 38.525 | 1 | 1 | 1700 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1232343.774 | 87638.2407 | 2814.6992 | 11897.3873 | 75740.8534 | 40887.7669 | 0.064772 | -315724.4982 | 315724.4982
C | Xist Rating 3087 | -72.79 | 533.716 | 150.283 | 35.7 | 2333.03 | 8938.28 | 21045.1 | 0.77 | 2.99 | 14.79 | 37.929 | 1 | 1 | 1710 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1245175.4395 | 88601.915 | 2847.9107 | 11967.3719 | 76634.543 | 40262.1215 | 0.065153 | -310893.4295 | 310893.4295
C | Xist Rating 3088 | -72.08 | 550.102 | 150.284 | 35.7 | 2323.13 | 8894 | 20567.7 | 0.77 | 2.9 | 14.821 | 36.107 | 1 | 1 | 1720 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1277958.4593 | 89570.8308 | 2881.317 | 12037.3566 | 77533.4743 | 38376.9224 | 0.065534 | -296336.4225 | 296336.4225
C | Xist Rating 3089 | -71.78 | 557.308 | 150.284 | 35.6 | 2320.84 | 8902.48 | 20374 | 0.76 | 2.87 | 14.811 | 35.412 | 1 | 1 | 1730 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1293422.6987 | 90544.9883 | 2914.9181 | 12107.3412 | 78437.6471 | 37648.199 | 0.065915 | -290709.4129 | 290709.4129
C | Xist Rating 3090 | -71.55 | 560.708 | 150.284 | 35.6 | 2325.48 | 8989.88 | 20290.3 | 0.75 | 2.85 | 14.812 | 35.129 | 1 | 1 | 1740 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1303915.2398 | 91524.3873 | 2948.714 | 12177.3258 | 79347.0615 | 37347.8562 | 0.066296 | -288390.2458 | 288390.2458
C | Xist Rating 3091 | -71.27 | 567.338 | 150.284 | 35.6 | 2321.86 | 8973.68 | 20124 | 0.73 | 2.82 | 14.799 | 34.552 | 1 | 1 | 1750 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1317279.4087 | 92509.0279 | 2982.7046 | 12247.3105 | 80261.7175 | 36729.6398 | 0.066677 | -283616.5423 | 283616.5423
C | Xist Rating 3092 | -71.07 | 572.286 | 150.284 | 35.6 | 2319.09 | 8960.54 | 20001.1 | 0.72 | 2.8 | 14.792 | 34.131 | 1 | 1 | 1760 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1327182.7397 | 93498.9101 | 3016.8901 | 12317.2951 | 81181.615 | 36285.2017 | 0.067058 | -280184.7095 | 280184.7095
C | Xist Rating 3093 | -70.36 | 591.698 | 150.284 | 35.6 | 2300.18 | 8797.9 | 19498.3 | 0.72 | 2.71 | 14.985 | 32.329 | 1 | 1 | 1770 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1361011.9056 | 94494.0339 | 3051.2703 | 12387.2797 | 82106.7542 | 34429.6265 | 0.067439 | -265856.4498 | 265856.4498
C | Xist Rating 3094 | -70.16 | 596.755 | 150.284 | 35.6 | 2297.31 | 8782.92 | 19383.8 | 0.71 | 2.69 | 14.969 | 31.959 | 1 | 1 | 1780 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1370931.229 | 95494.3993 | 3085.8453 | 12457.2644 | 83037.1349 | 34037.3557 | 0.06782 | -262827.4386 | 262827.4386
C | Xist Rating 3095 | -70.02 | 599.558 | 150.284 | 35.6 | 2297.77 | 8802.93 | 19327.5 | 0.7 | 2.68 | 14.965 | 31.796 | 1 | 1 | 1790 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1377646.3857 | 96500.0062 | 3120.6151 | 12527.249 | 83972.7572 | 33860.6092 | 0.068201 | -261462.6491 | 261462.6491
C | Xist Rating 3096 | -69.67 | 608.374 | 150.284 | 35.6 | 2292.98 | 8781.94 | 19122.7 | 0.69 | 2.65 | 14.952 | 31.116 | 1 | 1 | 1800 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1394989.4145 | 97510.8547 | 3155.5797 | 12597.2336 | 84913.6211 | 33146.3278 | 0.068582 | -255947.1569 | 255947.1569
C | Xist Rating 3097 | -69.42 | 613.304 | 150.284 | 35.6 | 2295.26 | 8842.72 | 19012.6 | 0.68 | 2.63 | 14.947 | 30.765 | 1 | 1 | 1810 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1407692.139 | 98526.9448 | 3190.7391 | 12667.2183 | 85859.7266 | 32774.0325 | 0.068963 | -253072.3917 | 253072.3917
C | Xist Rating 3098 | -68.63 | 632.975 | 150.284 | 35.6 | 2282.7 | 8770.47 | 18562.8 | 0.68 | 2.55 | 14.981 | 29.273 | 1 | 1 | 1820 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1444892.0325 | 99548.2765 | 3226.0933 | 12737.2029 | 86811.0736 | 31231.035 | 0.069344 | -241157.7738 | 241157.7738
C | Xist Rating 3099 | -68.59 | 629.831 | 150.284 | 35.6 | 2297.55 | 8975.26 | 18631.7 | 0.68 | 2.56 | 15.003 | 29.509 | 1 | 1 | 1830 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1447068.2141 | 100574.8498 | 3261.6423 | 12807.1875 | 87767.6623 | 31481.9141 | 0.069725 | -243094.9957 | 243094.9957
C | Xist Rating 3100 | -68.27 | 633.853 | 150.284 | 35.6 | 2306.62 | 9139.1 | 18545.8 | 0.67 | 2.55 | 15.023 | 29.244 | 1 | 1 | 1840 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1462058.0069 | 101606.6646 | 3297.386 | 12877.1721 | 88729.4925 | 31200.0162 | 0.070106 | -240918.2546 | 240918.2546
C | Xist Rating 3101 | -67.96 | 640.6 | 150.284 | 35.6 | 2305.26 | 9156.11 | 18409.8 | 0.66 | 2.52 | 15.016 | 28.83 | 1 | 1 | 1850 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1476749.556 | 102643.721 | 3333.3246 | 12947.1568 | 89696.5643 | 30761.7486 | 0.070487 | -237534.0685 | 237534.0685
C | Xist Rating 3102 | -67.64 | 648.148 | 150.284 | 35.6 | 2301.56 | 9140.68 | 18259.9 | 0.65 | 2.5 | 15.007 | 28.375 | 1 | 1 | 1860 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1491751.5109 | 103686.019 | 3369.4579 | 13017.1414 | 90668.8776 | 30280.667 | 0.070868 | -233819.2842 | 233819.2842
C | Xist Rating 3103 | -66.85 | 666.181 | 150.284 | 35.6 | 2295.32 | 9153.75 | 17880.4 | 0.65 | 2.43 | 15.053 | 27.178 | 1 | 1 | 1870 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1529098.5729 | 104733.5586 | 3405.7861 | 13087.126 | 91646.4326 | 29044.4631 | 0.071249 | -224273.6455 | 224273.6455
C | Xist Rating 3104 | -66.53 | 673.715 | 150.284 | 35.6 | 2291.76 | 9139.75 | 17739.8 | 0.64 | 2.41 | 15.043 | 26.768 | 1 | 1 | 1880 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1543993.0884 | 105786.3398 | 3442.309 | 13157.1107 | 92629.2291 | 28609.8401 | 0.07163 | -220917.6015 | 220917.6015
C | Xist Rating 3105 | -66.25 | 678.693 | 150.284 | 35.6 | 2295.12 | 9222.16 | 17647.3 | 0.63 | 2.39 | 15.051 | 26.503 | 1 | 1 | 1890 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1557681.8782 | 106844.3626 | 3479.0267 | 13227.0953 | 93617.2673 | 28326.6363 | 0.072011 | -218730.7767 | 218730.7767
C | Xist Rating 3106 | -66.04 | 684.128 | 150.284 | 35.6 | 2292.03 | 9201.11 | 17556 | 0.62 | 2.38 | 15.043 | 26.257 | 1 | 1 | 1900 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1568041.8998 | 107907.6269 | 3515.9392 | 13297.0799 | 94610.547 | 28062.1751 | 0.072392 | -216688.6777 | 216688.6777
C | Xist Rating 3107 | -65.81 | 689.284 | 150.284 | 35.6 | 2290.57 | 9206.31 | 17465.6 | 0.6 | 2.36 | 15.05 | 26.006 | 1 | 1 | 1910 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1578853.2519 | 108976.1328 | 3553.0464 | 13367.0646 | 95609.0683 | 27780.2941 | 0.072773 | -214512.0671 | 214512.0671
C | Xist Rating 3108 | -64.88 | 711.199 | 150.284 | 35.6 | 2281.58 | 9196.29 | 17050.8 | 0.61 | 2.29 | 15.083 | 24.772 | 1 | 1 | 1920 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1622657.4144 | 110049.8803 | 3590.3485 | 13437.0492 | 96612.8311 | 26517.5197 | 0.073154 | -204761.2579 | 204761.2579
C | Xist Rating 3109 | -64.56 | 718.81 | 150.284 | 35.6 | 2278.67 | 9191.53 | 16924.4 | 0.6 | 2.27 | 15.073 | 24.429 | 1 | 1 | 1930 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1637930.7827 | 111128.8694 | 3627.8454 | 13507.0338 | 97621.8356 | 26151.8713 | 0.073535 | -201937.8177 | 201937.8177
C | Xist Rating 3110 | -64.34 | 721.252 | 150.284 | 35.6 | 2286.17 | 9329.52 | 16882.3 | 0.59 | 2.26 | 15.088 | 24.32 | 1 | 1 | 1940 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1648904.6848 | 112213.1001 | 3665.537 | 13577.0185 | 98636.0816 | 26030.3909 | 0.073916 | -200999.7788 | 200999.7788
C | Xist Rating 3111 | -64.1 | 728.569 | 150.284 | 35.6 | 2279.11 | 9251.19 | 16772.6 | 0.58 | 2.24 | 15.079 | 24.039 | 1 | 1 | 1950 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1660488.8936 | 113302.5723 | 3703.4235 | 13647.0031 | 99655.5692 | 25728.9187 | 0.074297 | -198671.8904 | 198671.8904
C | Xist Rating 3112 | -63.74 | 736.863 | 150.284 | 35.6 | 2276.51 | 9255.87 | 16637.4 | 0.57 | 2.22 | 15.087 | 23.674 | 1 | 1 | 1960 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1677475.9881 | 114397.2861 | 3741.5047 | 13716.9877 | 100680.2984 | 25340.9398 | 0.074678 | -195676.0204 | 195676.0204
C | Xist Rating 3113 | -62.91 | 756.663 | 150.284 | 35.6 | 2268.94 | 9251.7 | 16303.5 | 0.57 | 2.16 | 15.142 | 22.745 | 1 | 1 | 1970 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1716822.9472 | 115497.2415 | 3779.7807 | 13786.9724 | 101710.2692 | 24382.7979 | 0.075059 | -188277.5022 | 188277.5022
C | Xist Rating 3114 | -62.62 | 762.601 | 150.284 | 35.6 | 2269.44 | 9293.35 | 16214.4 | 0.57 | 2.15 | 15.154 | 22.519 | 1 | 1 | 1980 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1730677.2134 | 116602.4385 | 3818.2515 | 13856.957 | 102745.4815 | 24152.5731 | 0.07544 | -186499.7675 | 186499.7675
C | Xist Rating 3115 | -62.32 | 770.407 | 150.284 | 35.6 | 2265.17 | 9264.54 | 16101.6 | 0.56 | 2.13 | 15.158 | 22.236 | 1 | 1 | 1990 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1745102.8242 | 117712.8771 | 3856.9171 | 13926.9416 | 103785.9355 | 23849.2322 | 0.075821 | -184157.4493 | 184157.4493
C | Xist Rating 3116 | -62.05 | 776.471 | 150.284 | 35.6 | 2264.5 | 9286.64 | 16015.1 | 0.55 | 2.12 | 15.156 | 22.022 | 1 | 1 | 2000 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1758318.5795 | 118828.5572 | 3895.7775 | 13996.9262 | 104831.631 | 23617.1108 | 0.076202 | -182365.0695 | 182365.0695
C | Xist Rating 3117 | -61.83 | 780.966 | 150.284 | 35.6 | 2265.4 | 9325.66 | 15954 | 0.54 | 2.11 | 15.16 | 21.878 | 1 | 1 | 2010 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1769200.3764 | 119949.479 | 3934.8326 | 14066.9109 | 105882.5681 | 23457.843 | 0.076583 | -181135.2454 | 181135.2454
C | Xist Rating 3118 | -60.93 | 803.328 | 150.284 | 35.6 | 2255.3 | 9289.85 | 15615.1 | 0.54 | 2.05 | 15.198 | 20.989 | 1 | 1 | 2020 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1811745.6384 | 121075.6423 | 3974.0826 | 14136.8955 | 106938.7468 | 22540.1454 | 0.076964 | -174049.028 | 174049.028
C | Xist Rating 3119 | -60.57 | 811.565 | 150.284 | 35.6 | 2253.9 | 9313.53 | 15499.9 | 0.53 | 2.03 | 15.199 | 20.705 | 1 | 1 | 2030 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1829186.3535 | 122207.0472 | 4013.5273 | 14206.8801 | 108000.167 | 22235.1095 | 0.077345 | -171693.6218 | 171693.6218
C | Xist Rating 3120 | -60.36 | 817.199 | 150.284 | 35.6 | 2250.8 | 9288.91 | 15431.7 | 0.52 | 2.02 | 15.191 | 20.555 | 1 | 1 | 2040 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1839351.5092 | 123343.6937 | 4053.1669 | 14276.8648 | 109066.8289 | 22068.6669 | 0.077726 | -170408.3959 | 170408.3959
C | Xist Rating 3121 | -60.09 | 822.019 | 150.284 | 35.6 | 2253.7 | 9367.21 | 15364.3 | 0.52 | 2.01 | 15.198 | 20.391 | 1 | 1 | 2050 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1852584.2203 | 124485.5817 | 4093.0012 | 14346.8494 | 110138.7323 | 21902.2285 | 0.078107 | -169123.2026 | 169123.2026
C | Xist Rating 3122 | -59.83 | 830.22 | 150.284 | 35.6 | 2247.18 | 9297.72 | 15264.4 | 0.51 | 1.99 | 15.19 | 20.165 | 1 | 1 | 2060 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1865653.7796 | 125632.7113 | 4133.0303 | 14416.834 | 111215.8773 | 21656.6599 | 0.078488 | -167226.9872 | 167226.9872
C | Xist Rating 3123 | -58.87 | 854.254 | 150.284 | 35.6 | 2236.78 | 9262.05 | 14936.2 | 0.51 | 1.94 | 15.225 | 19.353 | 1 | 1 | 2070 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1910778.2621 | 126785.0826 | 4173.2542 | 14486.8187 | 112298.2639 | 20818.528 | 0.078869 | -160755.1545 | 160755.1545
C | Xist Rating 3124 | -58.65 | 859.691 | 150.284 | 35.6 | 2235.47 | 9267.49 | 14873.6 | 0.5 | 1.93 | 15.224 | 19.218 | 1 | 1 | 2080 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1921813.4398 | 127942.6954 | 4213.6729 | 14556.8033 | 113385.8921 | 20667.5695 | 0.07925 | -159589.4934 | 159589.4934
C | Xist Rating 3125 | -58.36 | 866.637 | 150.284 | 35.6 | 2233.69 | 9273.97 | 14791 | 0.5 | 1.91 | 15.222 | 19.034 | 1 | 1 | 2090 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1935798.4005 | 129105.5498 | 4254.2864 | 14626.7879 | 114478.7618 | 20479.8042 | 0.079631 | -158139.6192 | 158139.6192
C | Xist Rating 3126 | -58.07 | 873.592 | 150.284 | 35.6 | 2232.28 | 9286.69 | 14709.5 | 0.49 | 1.9 | 15.218 | 18.853 | 1 | 1 | 2100 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1950101.9498 | 130273.6457 | 4295.0947 | 14696.7726 | 115576.8732 | 20280.7343 | 0.080012 | -156602.4546 | 156602.4546
C | Xist Rating 3127 | -57.83 | 879.75 | 150.284 | 35.6 | 2230.65 | 9290.96 | 14638.8 | 0.48 | 1.89 | 15.215 | 18.7 | 1 | 1 | 2110 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 1962414.3375 | 131446.9833 | 4336.0977 | 14766.7572 | 116680.2261 | 20110.6572 | 0.080393 | -155289.1639 | 155289.1639
C | Xist Rating 3128 | -56.94 | 902.552 | 150.284 | 35.6 | 2220.67 | 9249.36 | 14359.2 | 0.48 | 1.84 | 15.253 | 18.048 | 1 | 1 | 2120 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2004270.1498 | 132625.5624 | 4377.2956 | 14836.7418 | 117788.8206 | 19438.5632 | 0.080774 | -150099.4321 | 150099.4321
C | Xist Rating 3129 | -56.61 | 911.132 | 150.284 | 35.6 | 2217.47 | 9239.72 | 14263.9 | 0.48 | 1.83 | 15.247 | 17.843 | 1 | 1 | 2130 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2020407.876 | 133809.3831 | 4418.6882 | 14906.7265 | 118902.6567 | 19228.6778 | 0.081155 | -148478.7531 | 148478.7531
C | Xist Rating 3130 | -56.33 | 919.738 | 150.284 | 35.6 | 2211.84 | 9187.49 | 14170 | 0.47 | 1.81 | 15.245 | 17.642 | 1 | 1 | 2140 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2034313.2979 | 134998.4454 | 4460.2756 | 14976.7111 | 120021.7343 | 19008.5043 | 0.081536 | -146778.6319 | 146778.6319
C | Xist Rating 3131 | -56.11 | 924.382 | 150.284 | 35.6 | 2212.81 | 9226.93 | 14123.5 | 0.47 | 1.8 | 15.247 | 17.552 | 1 | 1 | 2150 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2045481.7334 | 136192.7493 | 4502.0578 | 15046.6957 | 121146.0536 | 18918.3418 | 0.081917 | -146082.4209 | 146082.4209
C | Xist Rating 3132 | -55.86 | 930.486 | 150.284 | 35.6 | 2211.88 | 9242.57 | 14059.1 | 0.46 | 1.79 | 15.243 | 17.419 | 1 | 1 | 2160 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2058123.3737 | 137392.2947 | 4544.0348 | 15116.6803 | 122275.6144 | 18768.4932 | 0.082298 | -144925.3297 | 144925.3297
C | Xist Rating 3133 | -54.93 | 955.172 | 150.284 | 35.6 | 2200.84 | 9187.71 | 13786 | 0.46 | 1.75 | 15.278 | 16.818 | 1 | 1 | 2170 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2102180.7445 | 138597.0818 | 4586.2066 | 15186.665 | 123410.4168 | 18149.0647 | 0.082679 | -140142.267 | 140142.267
C | Xist Rating 3134 | -54.59 | 963.527 | 150.284 | 35.6 | 2199.23 | 9204.36 | 13699.1 | 0.46 | 1.74 | 15.276 | 16.638 | 1 | 1 | 2180 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2119017.4842 | 139807.1104 | 4628.5732 | 15256.6496 | 124550.4608 | 17965.1953 | 0.08306 | -138722.4762 | 138722.4762
C | Xist Rating 3135 | -54.34 | 969.864 | 150.284 | 35.6 | 2197.68 | 9208.45 | 13639 | 0.45 | 1.73 | 15.272 | 16.522 | 1 | 1 | 2190 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2131450.7155 | 141022.3806 | 4671.1346 | 15326.6342 | 125695.7463 | 17832.7068 | 0.083441 | -137699.4348 | 137699.4348
C | Xist Rating 3136 | -54.13 | 976.608 | 150.284 | 35.6 | 2192.89 | 9155.78 | 13579.5 | 0.44 | 1.72 | 15.265 | 16.412 | 1 | 1 | 2200 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2141593.9171 | 142242.8924 | 4713.8907 | 15396.6189 | 126846.2735 | 17706.1884 | 0.083822 | -136722.4933 | 136722.4933
C | Xist Rating 3137 | -53.81 | 985.221 | 150.284 | 35.6 | 2189.99 | 9149.45 | 13495.4 | 0.44 | 1.7 | 15.263 | 16.243 | 1 | 1 | 2210 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2157624.1378 | 143468.6457 | 4756.8417 | 15466.6035 | 128002.0422 | 17533.6057 | 0.084203 | -135389.8554 | 135389.8554
C | Xist Rating 3138 | -52.88 | 1009.77 | 150.284 | 35.6 | 2180.78 | 9122.35 | 13246.2 | 0.44 | 1.66 | 15.301 | 15.721 | 1 | 1 | 2220 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2202086.2206 | 144699.6407 | 4799.9874 | 15536.5881 | 129163.0525 | 16996.1836 | 0.084584 | -131240.0247 | 131240.0247
C | Xist Rating 3139 | -52.61 | 1016.69 | 150.284 | 35.6 | 2179.3 | 9131.33 | 13182.5 | 0.43 | 1.65 | 15.301 | 15.599 | 1 | 1 | 2230 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2215672.517 | 145935.8772 | 4843.3279 | 15606.5728 | 130329.3044 | 16857.2099 | 0.084965 | -130166.9063 | 130166.9063
C | Xist Rating 3140 | -52.32 | 1024.86 | 150.284 | 35.6 | 2175.64 | 9106.42 | 13111.8 | 0.43 | 1.64 | 15.297 | 15.468 | 1 | 1 | 2240 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2229726.4104 | 147177.3553 | 4886.8633 | 15676.5574 | 131500.7979 | 16723.9431 | 0.085346 | -129137.8555 | 129137.8555
C | Xist Rating 3141 | -52.01 | 1033.78 | 150.284 | 35.6 | 2171.99 | 9085.71 | 13034.1 | 0.42 | 1.63 | 15.293 | 15.322 | 1 | 1 | 2250 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2245359.8222 | 148424.075 | 4930.5934 | 15746.542 | 132677.533 | 16559.6735 | 0.085727 | -127869.409 | 127869.409
C | Xist Rating 3142 | -51.82 | 1038.39 | 150.284 | 35.6 | 2171.93 | 9106.26 | 12995.6 | 0.42 | 1.62 | 15.293 | 15.255 | 1 | 1 | 2260 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2255310.3927 | 149676.0363 | 4974.5182 | 15816.5267 | 133859.5096 | 16492.9732 | 0.086108 | -127354.3671 | 127354.3671
C | Xist Rating 3143 | -50.84 | 1064.92 | 150.284 | 35.6 | 2161.32 | 9059.42 | 12751.8 | 0.42 | 1.59 | 15.33 | 14.771 | 1 | 1 | 2270 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2301632.8944 | 150933.2391 | 5018.6379 | 15886.5113 | 135046.7278 | 15994.8003 | 0.086489 | -123507.6081 | 123507.6081
C | Xist Rating 3144 | -50.55 | 1073.03 | 150.284 | 35.6 | 2158.6 | 9049.86 | 12686.1 | 0.41 | 1.58 | 15.325 | 14.654 | 1 | 1 | 2280 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2316242.558 | 152195.6836 | 5062.9524 | 15956.4959 | 136239.1876 | 15860.3053 | 0.08687 | -122469.073 | 122469.073
C | Xist Rating 3145 | -50.18 | 1082.5 | 150.284 | 35.6 | 2156.49 | 9059.37 | 12606.9 | 0.41 | 1.56 | 15.324 | 14.508 | 1 | 1 | 2290 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2334400.425 | 153463.3696 | 5107.4617 | 16026.4806 | 137436.889 | 15711.4588 | 0.087251 | -121319.7205 | 121319.7205
C | Xist Rating 3146 | -49.95 | 1089 | 150.284 | 35.6 | 2154.55 | 9054.88 | 12557 | 0.4 | 1.56 | 15.321 | 14.424 | 1 | 1 | 2300 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2346304.95 | 154736.2972 | 5152.1657 | 16096.4652 | 138639.832 | 15611.119 | 0.087632 | -120544.9227 | 120544.9227
| Xist Rating 3147 | -49.73 | 1095.77 | 150.284 | 35.6 | 2151.3 | 9027.17 | 12507.6 | 0.4 | 1.55 | 15.317 | 14.342 | 1 | 1 | 2310 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2357330.001 | 156014.4663 | 5197.0645 | 16166.4498 | 139848.0165 | 15528.5435 | 0.088013 | -119907.2965 | 119907.2965
| Xist Rating 3148 | -48.72 | 1122.93 | 150.284 | 35.6 | 2142.23 | 9007.49 | 12277.1 | 0.4 | 1.51 | 15.355 | 13.905 | 1 | 1 | 2320 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2405574.3339 | 157297.8771 | 5242.1582 | 16236.4344 | 141061.4427 | 15079.0467 | 0.088394 | -116436.4014 | 116436.4014
| Xist Rating 3149 | -48.45 | 1131.08 | 150.284 | 35.6 | 2139.19 | 8991.25 | 12216.8 | 0.39 | 1.5 | 15.349 | 13.802 | 1 | 1 | 2330 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2419595.0252 | 158586.5294 | 5287.4466 | 16306.4191 | 142280.1104 | 14958.5531 | 0.088775 | -115505.9819 | 115505.9819
| Xist Rating 3150 | -48.18 | 1139.2 | 150.284 | 35.6 | 2135.79 | 8968.46 | 12157.2 | 0.39 | 1.49 | 15.342 | 13.702 | 1 | 1 | 2340 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2433091.968 | 159880.4234 | 5332.9298 | 16376.4037 | 143504.0197 | 14857.1002 | 0.089156 | -114722.5892 | 114722.5892
| Xist Rating 3151 | -47.93 | 1146.62 | 150.284 | 35.6 | 2132.96 | 8951.62 | 12104.8 | 0.38 | 1.49 | 15.338 | 13.616 | 1 | 1 | 2350 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2445694.5952 | 161179.5589 | 5378.6078 | 16446.3883 | 144733.1705 | 14754.1503 | 0.089537 | -113927.6374 | 113927.6374
| Xist Rating 3152 | -47.62 | 1155.59 | 150.284 | 35.6 | 2129.74 | 8935.76 | 12039.9 | 0.38 | 1.48 | 15.334 | 13.507 | 1 | 1 | 2360 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2461106.2466 | 162483.936 | 5424.4805 | 16516.373 | 145967.563 | 14643.4057 | 0.089918 | -113072.4974 | 113072.4974
| Xist Rating 3153 | -46.71 | 1180.57 | 150.284 | 35.6 | 2121.62 | 8916.71 | 11846.8 | 0.38 | 1.45 | 15.368 | 13.159 | 1 | 1 | 2370 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2504720.9234 | 163793.5546 | 5470.5481 | 16586.3576 | 147207.197 | 14285.9927 | 0.090299 | -110312.6489 | 110312.6489
| Xist Rating 3154 | -46.44 | 1188.93 | 150.284 | 35.6 | 2118.35 | 8895.28 | 11791.2 | 0.37 | 1.44 | 15.362 | 13.071 | 1 | 1 | 2380 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2518569.8655 | 165108.4149 | 5516.8105 | 16656.3422 | 148452.0726 | 14180.5907 | 0.09068 | -109498.7626 | 109498.7626
| Xist Rating 3155 | -46.13 | 1197.46 | 150.284 | 35.6 | 2116.44 | 8901.88 | 11730 | 0.37 | 1.43 | 15.355 | 12.968 | 1 | 1 | 2390 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2534352.2424 | 166428.5167 | 5563.2676 | 16726.3269 | 149702.1898 | 14075.8957 | 0.091061 | -108690.3356 | 108690.3356
C | Xist Rating 3156 | -40.83 | 1372.93 | 150.284 | 35.6 | 2028.34 | 8212.15 | 10538.4 | 0.4 | 1.25 | 15.363 | 10.966 | 1 | 1 | 2400 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2784768.8362 | 167753.8601 | 5609.9196 | 16796.3115 | 150957.5486 | 12049.2691 | 0.091442 | -93041.2622 | 93041.2622
C | Xist Rating 3157 | -40.32 | 1374.37 | 150.284 | 35.6 | 2044.28 | 8480.15 | 10538 | 0.39 | 1.25 | 15.351 | 10.975 | 1 | 1 | 2410 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2809597.1036 | 169084.4451 | 5656.7663 | 16866.2961 | 152218.149 | 12044.2683 | 0.091823 | -93002.6476 | 93002.6476
C | Xist Rating 3158 | -40.31 | 1375.77 | 150.284 | 35.6 | 2043.8 | 8471.96 | 10538 | 0.39 | 1.25 | 15.39 | 10.986 | 1 | 1 | 2420 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2811798.726 | 170420.2717 | 5703.8078 | 16936.2808 | 153483.9909 | 12060.0253 | 0.092204 | -93124.319 | 93124.319
C | Xist Rating 3159 | -39.77 | 1377.13 | 150.284 | 35.6 | 2060.58 | 8768.03 | 10537.9 | 0.39 | 1.25 | 15.385 | 10.995 | 1 | 1 | 2430 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2837686.5354 | 171761.3398 | 5751.0441 | 17006.2654 | 154755.0745 | 12071.8499 | 0.092585 | -93215.6247 | 93215.6247
C | Xist Rating 3160 | -39.75 | 1378.5 | 150.284 | 35.6 | 2059.85 | 8754.82 | 10537.9 | 0.38 | 1.25 | 15.381 | 11.005 | 1 | 1 | 2440 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2839503.225 | 173107.6496 | 5798.4752 | 17076.25 | 156031.3996 | 12067.9312 | 0.092966 | -93185.3661 | 93185.3661
C | Xist Rating 3161 | -39.75 | 1379.83 | 150.284 | 35.6 | 2058.89 | 8737.49 | 10537.9 | 0.38 | 1.25 | 15.372 | 11.016 | 1 | 1 | 2450 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2840918.1887 | 174459.2009 | 5846.1011 | 17146.2347 | 157312.9663 | 12081.599 | 0.093347 | -93290.9052 | 93290.9052
C | Xist Rating 3162 | -39.73 | 1381.3 | 150.284 | 35.6 | 2058.03 | 8721.97 | 10537.9 | 0.37 | 1.25 | 15.367 | 11.027 | 1 | 1 | 2460 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2842756.839 | 175815.9938 | 5893.9217 | 17216.2193 | 158599.7745 | 12078.4864 | 0.093728 | -93266.8703 | 93266.8703
C | Xist Rating 3163 | -39.71 | 1382.65 | 150.284 | 35.6 | 2057.48 | 8712.16 | 10537.9 | 0.36 | 1.25 | 15.404 | 11.038 | 1 | 1 | 2470 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2844774.722 | 177178.0283 | 5941.9372 | 17286.2039 | 159891.8244 | 12076.9194 | 0.094109 | -93254.7703 | 93254.7703
C | Xist Rating 3164 | -39.7 | 1384 | 150.284 | 35.6 | 2056.82 | 8700.26 | 10537.9 | 0.36 | 1.25 | 15.398 | 11.048 | 1 | 1 | 2480 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2846638.88 | 178545.3044 | 5990.1474 | 17356.1885 | 161189.1158 | 12089.55 | 0.09449 | -93352.3004 | 93352.3004
C | Xist Rating 3165 | -39.68 | 1385.4 | 150.284 | 35.6 | 2055.92 | 8684.26 | 10537.9 | 0.35 | 1.25 | 15.396 | 11.059 | 1 | 1 | 2490 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2848271.568 | 179917.822 | 6038.5525 | 17426.1732 | 162491.6488 | 12086.1939 | 0.094871 | -93326.3853 | 93326.3853
C | Xist Rating 3166 | -39.67 | 1386.38 | 150.284 | 35.6 | 2055.97 | 8685.05 | 10537.9 | 0.35 | 1.25 | 15.391 | 11.068 | 1 | 1 | 2500 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2850355.6886 | 181295.5812 | 6087.1523 | 17496.1578 | 163799.4234 | 12097.7597 | 0.095252 | -93415.6934 | 93415.6934
C | Xist Rating 3167 | -39.66 | 1388.23 | 150.284 | 35.6 | 2054.28 | 8655.07 | 10537.9 | 0.34 | 1.25 | 15.388 | 11.081 | 1 | 1 | 2510 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2851813.1244 | 182678.582 | 6135.9469 | 17566.1424 | 165112.4396 | 12096.2436 | 0.095633 | -93403.9869 | 93403.9869
C | Xist Rating 3168 | -39.63 | 1389.69 | 150.284 | 35.6 | 2053.68 | 8644.39 | 10537.9 | 0.34 | 1.25 | 15.425 | 11.092 | 1 | 1 | 2520 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2853978.5592 | 184066.8244 | 6184.9363 | 17636.1271 | 166430.6974 | 12111.4333 | 0.096014 | -93521.2777 | 93521.2777
C | Xist Rating 3169 | -39.61 | 1391.03 | 150.284 | 35.6 | 2053.26 | 8636.95 | 10537.9 | 0.33 | 1.25 | 15.418 | 11.102 | 1 | 1 | 2530 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2856146.2578 | 185460.3084 | 6234.1205 | 17706.1117 | 167754.1967 | 12106.4142 | 0.096395 | -93482.5216 | 93482.5216
C | Xist Rating 3170 | -39.59 | 1392.18 | 150.284 | 35.6 | 2053.05 | 8633.41 | 10537.8 | 0.33 | 1.25 | 15.413 | 11.111 | 1 | 1 | 2540 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2858215.149 | 186859.034 | 6283.4995 | 17776.0963 | 169082.9376 | 12117.8535 | 0.096776 | -93570.8527 | 93570.8527
C | Xist Rating 3171 | -39.53 | 1393.72 | 150.285 | 35.6 | 2053.87 | 8647.85 | 10537.8 | 0.32 | 1.25 | 15.416 | 11.122 | 1 | 1 | 2550 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 14 | E | Rod | 2862519.6964 | 188263.0011 | 6333.0732 | 17846.081 | 170416.9201 | 12114.0491 | 0.097157 | -93541.4763 | 93541.4763
C | Xist Rating 3172 | -39.52 | 1395.17 | 150.285 | 35.6 | 2053.17 | 8635.49 | 10537.7 | 0.32 | 1.25 | 15.411 | 11.133 | 1 | 1 | 2560 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2864521.1889 | 189672.2098 | 6382.8418 | 17916.0656 | 171756.1442 | 12127.5003 | 0.097538 | -93645.3424 | 93645.3424
C | Xist Rating 3173 | -39.51 | 1396.56 | 150.285 | 35.6 | 2052.27 | 8619.65 | 10537.7 | 0.31 | 1.25 | 15.409 | 11.143 | 1 | 1 | 2570 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2866118.1912 | 191086.6601 | 6432.8051 | 17986.0502 | 173100.6099 | 12122.271 | 0.097919 | -93604.9633 | 93604.9633
C | Xist Rating 3174 | -39.5 | 1397.93 | 150.285 | 35.6 | 2051.48 | 8605.71 | 10537.7 | 0.31 | 1.25 | 15.445 | 11.153 | 1 | 1 | 2580 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2867825.4364 | 192506.352 | 6482.9633 | 18056.0349 | 174450.3171 | 12136.0878 | 0.0983 | -93711.6529 | 93711.6529
C | Xist Rating 3175 | -39.49 | 1399.29 | 150.285 | 35.6 | 2050.58 | 8589.91 | 10537.7 | 0.3 | 1.25 | 15.443 | 11.163 | 1 | 1 | 2590 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2869356.0882 | 193931.2854 | 6533.3162 | 18126.0195 | 175805.266 | 12130.6183 | 0.098681 | -93669.4189 | 93669.4189
C | Xist Rating 3176 | -39.47 | 1400.46 | 150.285 | 35.6 | 2050.32 | 8585.26 | 10537.7 | 0.3 | 1.25 | 15.439 | 11.173 | 1 | 1 | 2600 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2871391.1472 | 195361.4605 | 6583.8639 | 18196.0041 | 177165.4564 | 12142.9401 | 0.099062 | -93764.5647 | 93764.5647
C | Xist Rating 3177 | -39.42 | 1402.15 | 150.285 | 35.6 | 2050.23 | 8583.67 | 10537.8 | 0.29 | 1.25 | 15.441 | 11.184 | 1 | 1 | 2610 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2874729.9945 | 196796.8771 | 6634.6064 | 18265.9887 | 178530.8884 | 12138.4451 | 0.099443 | -93729.8558 | 93729.8558
C | Xist Rating 3178 | -39.41 | 1403.55 | 150.285 | 35.6 | 2049.11 | 8564.13 | 10537.8 | 0.29 | 1.25 | 15.437 | 11.194 | 1 | 1 | 2620 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2876028.3405 | 198237.5353 | 6685.5437 | 18335.9734 | 179901.5619 | 12150.7011 | 0.099824 | -93824.493 | 93824.493
C | Xist Rating 3179 | -39.38 | 1404.97 | 150.285 | 35.6 | 2048.85 | 8559.48 | 10537.8 | 0.29 | 1.25 | 15.473 | 11.205 | 1 | 1 | 2630 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2878572.7845 | 199683.4351 | 6736.6758 | 18405.958 | 181277.4771 | 12165.362 | 0.10021 | -93937.7007 | 93937.7007
C | Xist Rating 3180 | -39.36 | 1406.22 | 150.285 | 35.6 | 2048.64 | 8555.97 | 10537.8 | 0.28 | 1.25 | 15.467 | 11.214 | 1 | 1 | 2640 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2880838.5408 | 201134.5765 | 6788.0027 | 18475.9426 | 182658.6338 | 12158.2107 | 0.10059 | -93882.4806 | 93882.4806
C | Xist Rating 3181 | -39.34 | 1407.72 | 150.285 | 35.6 | 2047.87 | 8542.55 | 10537.8 | 0.28 | 1.25 | 15.465 | 11.225 | 1 | 1 | 2650 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2882827.5564 | 202590.9594 | 6839.5243 | 18545.9273 | 184045.0322 | 12171.509 | 0.10097 | -93985.1658 | 93985.1658
C | Xist Rating 3182 | -39.3 | 1409.06 | 150.285 | 35.6 | 2048.19 | 8548.03 | 10537.7 | 0.28 | 1.25 | 15.462 | 11.234 | 1 | 1 | 2660 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2886022.6014 | 204052.584 | 6891.2408 | 18615.9119 | 185436.6721 | 12182.6963 | 0.10135 | -94071.5514 | 94071.5514
C | Xist Rating 3183 | -39.27 | 1410.45 | 150.285 | 35.6 | 2048.21 | 8548.49 | 10537.7 | 0.27 | 1.25 | 15.459 | 11.244 | 1 | 1 | 2670 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2888897.7945 | 205519.4501 | 6943.152 | 18685.8965 | 186833.5535 | 12176.4197 | 0.10173 | -94023.0856 | 94023.0856
C | Xist Rating 3184 | -39.23 | 1411.87 | 150.285 | 35.6 | 2048.09 | 8546.43 | 10537.7 | 0.27 | 1.25 | 15.496 | 11.254 | 1 | 1 | 2680 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2891636.8283 | 206991.5578 | 6995.258 | 18755.8812 | 188235.6766 | 12189.8758 | 0.10211 | -94126.9896 | 94126.9896
C | Xist Rating 3185 | -39.2 | 1413.24 | 150.285 | 35.6 | 2048.25 | 8549.32 | 10537.6 | 0.27 | 1.25 | 15.491 | 11.264 | 1 | 1 | 2690 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2894668.83 | 208468.907 | 7047.5588 | 18825.8658 | 189643.0412 | 12201.9734 | 0.10249 | -94220.4043 | 94220.4043
C | Xist Rating 3186 | -39.16 | 1414.44 | 150.285 | 35.6 | 2048.44 | 8552.46 | 10537.6 | 0.26 | 1.25 | 15.484 | 11.273 | 1 | 1 | 2700 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2897395.4736 | 209951.4979 | 7100.0544 | 18895.8504 | 191055.6475 | 12194.2262 | 0.10287 | -94160.5826 | 94160.5826
C | Xist Rating 3187 | -39.14 | 1416.1 | 150.285 | 35.6 | 2047.4 | 8534.44 | 10537.6 | 0.26 | 1.25 | 15.479 | 11.284 | 1 | 1 | 2710 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2899323.14 | 211439.3303 | 7152.7448 | 18965.8351 | 192473.4953 | 12207.2964 | 0.10325 | -94261.5067 | 94261.5067
C | Xist Rating 3188 | -39.14 | 1417.45 | 150.285 | 35.6 | 2046.56 | 8519.89 | 10537.6 | 0.26 | 1.25 | 15.474 | 11.294 | 1 | 1 | 2720 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2900896.472 | 212932.4044 | 7205.63 | 19035.8197 | 193896.5847 | 12219.3268 | 0.10363 | -94354.4028 | 94354.4028
C | Xist Rating 3189 | -39.11 | 1418.77 | 150.285 | 35.6 | 2046.39 | 8516.99 | 10537.6 | 0.25 | 1.25 | 15.511 | 11.303 | 1 | 1 | 2730 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2903356.7403 | 214430.72 | 7258.71 | 19105.8043 | 195324.9156 | 12212.6729 | 0.10402 | -94303.023 | 94303.023
C | Xist Rating 3190 | -39.11 | 1420.05 | 150.285 | 35.6 | 2045.42 | 8500.1 | 10537.6 | 0.25 | 1.25 | 15.502 | 11.312 | 1 | 1 | 2740 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2904598.671 | 215934.2772 | 7311.9847 | 19175.789 | 196758.4882 | 12223.4812 | 0.1044 | -94386.4821 | 94386.4821
C | Xist Rating 3191 | -39.08 | 1421.6 | 150.285 | 35.6 | 2045.02 | 8493.23 | 10537.6 | 0.25 | 1.25 | 15.5 | 11.323 | 1 | 1 | 2750 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2907200.432 | 217443.0759 | 7365.4543 | 19245.7736 | 198197.3023 | 12236.5803 | 0.10478 | -94487.6293 | 94487.6293
C | Xist Rating 3192 | -39.07 | 1423.02 | 150.285 | 35.6 | 2044.18 | 8478.69 | 10537.6 | 0.24 | 1.25 | 15.494 | 11.333 | 1 | 1 | 2760 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2908909.0236 | 218957.1163 | 7419.1186 | 19315.7582 | 199641.3581 | 12229.3481 | 0.10516 | -94431.7842 | 94431.7842
C | Xist Rating 3193 | -39.01 | 1424.26 | 150.285 | 35.6 | 2044.99 | 8492.7 | 10537.6 | 0.24 | 1.25 | 15.496 | 11.342 | 1 | 1 | 2770 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2912597.4574 | 220476.3982 | 7472.9777 | 19385.7428 | 201090.6554 | 12240.421 | 0.10554 | -94517.2863 | 94517.2863
C | Xist Rating 3194 | -38.98 | 1425.81 | 150.285 | 35.6 | 2045.27 | 8497.6 | 10537.6 | 0.24 | 1.25 | 15.54 | 11.352 | 1 | 1 | 2780 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2916166.4187 | 222000.9217 | 7527.0316 | 19455.7275 | 202545.1942 | 12253.7889 | 0.10592 | -94620.51 | 94620.51
C | Xist Rating 3195 | -38.8 | 1427.21 | 150.285 | 35.6 | 2049.4 | 8569.1 | 10537.8 | 0.23 | 1.25 | 15.552 | 11.362 | 1 | 1 | 2790 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2924924.174 | 223530.6868 | 7581.2803 | 19525.7121 | 204004.9747 | 12246.7564 | 0.1063 | -94566.2068 | 94566.2068
C | Xist Rating 3196 | -38.61 | 1428.19 | 150.285 | 35.6 | 2055.36 | 8674.25 | 10538 | 0.23 | 1.25 | 15.568 | 11.37 | 1 | 1 | 2800 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2935444.5984 | 225065.6935 | 7635.7238 | 19595.6967 | 205469.9967 | 12257.1296 | 0.10668 | -94646.3061 | 94646.3061
C | Xist Rating 3197 | -38.88 | 1429.93 | 150.285 | 35.6 | 2043.96 | 8474.8 | 10537.8 | 0.23 | 1.25 | 15.538 | 11.381 | 1 | 1 | 2810 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2922719.7228 | 226605.9417 | 7690.3621 | 19665.6814 | 206940.2604 | 12269.289 | 0.10706 | -94740.1976 | 94740.1976
C | Xist Rating 3198 | -38.76 | 1431.41 | 150.285 | 35.6 | 2046.96 | 8526.67 | 10537.9 | 0.23 | 1.25 | 15.548 | 11.391 | 1 | 1 | 2820 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2930039.0136 | 228151.4316 | 7745.1952 | 19735.666 | 208415.7656 | 12281.5667 | 0.10744 | -94835.0023 | 94835.0023
C | Xist Rating 3199 | -38.3 | 1432.78 | 150.285 | 35.6 | 2062.08 | 8795.06 | 10538 | 0.22 | 1.25 | 15.652 | 11.401 | 1 | 1 | 2830 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2954506.9824 | 229702.163 | 7800.223 | 19805.6506 | 209896.5124 | 12276.7338 | 0.10783 | -94797.6841 | 94797.6841
C | Xist Rating 3200 | -37.85 | 1434.1 | 150.285 | 35.6 | 2076 | 9053.93 | 10538.2 | 0.22 | 1.25 | 15.718 | 11.411 | 1 | 1 | 2840 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2977191.6 | 231258.136 | 7855.4457 | 19875.6353 | 211382.5007 | 12290.5107 | 0.10821 | -94904.0658 | 94904.0658
C | Xist Rating 3201 | -37.66 | 1435.54 | 150.285 | 35.6 | 2080.95 | 9148.78 | 10538.2 | 0.21 | 1.25 | 15.748 | 11.421 | 1 | 1 | 2850 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2987286.963 | 232819.3506 | 7910.8631 | 19945.6199 | 212873.7307 | 12283.1707 | 0.10859 | -94847.3886 | 94847.3886
C | Xist Rating 3202 | -37.52 | 1436.95 | 150.285 | 35.6 | 2084.47 | 9217.42 | 10538.1 | 0.21 | 1.25 | 15.76 | 11.431 | 1 | 1 | 2860 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 2995279.1665 | 234385.8067 | 7966.4753 | 20015.6045 | 214370.2022 | 12295.3612 | 0.10897 | -94941.5199 | 94941.5199
C | Xist Rating 3203 | -37.38 | 1438.14 | 150.285 | 35.6 | 2088.32 | 9293.13 | 10538.1 | 0.21 | 1.25 | 15.771 | 11.44 | 1 | 1 | 2870 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3003296.5248 | 235957.5045 | 8022.2824 | 20085.5892 | 215871.9153 | 12306.4884 | 0.10935 | -95027.441 | 95027.441
C | Xist Rating 3204 | -37.25 | 1439.65 | 150.285 | 35.6 | 2091.14 | 9349.11 | 10538.2 | 0.21 | 1.25 | 15.82 | 11.45 | 1 | 1 | 2880 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3010509.701 | 237534.4438 | 8078.2842 | 20155.5738 | 217378.87 | 12319.6863 | 0.10973 | -95129.3519 | 95129.3519
C | Xist Rating 3205 | -37.15 | 1440.99 | 150.285 | 35.6 | 2093.37 | 9393.96 | 10538.1 | 0.2 | 1.25 | 15.823 | 11.459 | 1 | 1 | 2890 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3016525.2363 | 239116.6247 | 8134.4807 | 20225.5584 | 218891.0663 | 12310.1059 | 0.11011 | -95055.3748 | 95055.3748
C | Xist Rating 3206 | -37.06 | 1442.38 | 150.285 | 35.6 | 2095.07 | 9428.2 | 10538.1 | 0.2 | 1.25 | 15.827 | 11.468 | 1 | 1 | 2900 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3021887.0666 | 240704.0472 | 8190.8721 | 20295.5431 | 220408.5042 | 12320.9749 | 0.11049 | -95139.3024 | 95139.3024
C | Xist Rating 3207 | -36.97 | 1443.92 | 150.285 | 35.5 | 2096.89 | 9465.28 | 10538 | 0.2 | 1.25 | 15.83 | 11.478 | 1 | 1 | 2910 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3027741.4088 | 242296.7113 | 8247.4583 | 20365.5277 | 221931.1836 | 12332.857 | 0.11087 | -95231.053 | 95231.053
C | Xist Rating 3208 | -36.88 | 1445.31 | 150.285 | 35.5 | 2098.75 | 9503.34 | 10538.1 | 0.2 | 1.25 | 15.834 | 11.488 | 1 | 1 | 2920 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3033344.3625 | 243894.6169 | 8304.2393 | 20435.5123 | 223459.1046 | 12344.7659 | 0.11125 | -95323.0099 | 95323.0099
C | Xist Rating 3209 | -36.75 | 1446.69 | 150.285 | 35.5 | 2101.8 | 9566.3 | 10538 | 0.19 | 1.25 | 15.883 | 11.497 | 1 | 1 | 2930 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3040653.042 | 245497.7642 | 8361.215 | 20505.4969 | 224992.2672 | 12335.9588 | 0.11164 | -95255.0043 | 95255.0043
C | Xist Rating 3210 | -36.56 | 1448.06 | 150.285 | 35.5 | 2107.3 | 9681.33 | 10537.9 | 0.19 | 1.25 | 15.888 | 11.507 | 1 | 1 | 2940 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3051496.838 | 247106.153 | 8418.3855 | 20575.4816 | 226530.6714 | 12347.8217 | 0.11202 | -95346.6063 | 95346.6063
C | Xist Rating 3211 | -36.54 | 1449.47 | 150.285 | 35.5 | 2106.63 | 9667.28 | 10537.9 | 0.19 | 1.25 | 15.883 | 11.516 | 1 | 1 | 2950 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3053496.9861 | 248719.7834 | 8475.7509 | 20645.4662 | 228074.3172 | 12358.3957 | 0.1124 | -95428.2559 | 95428.2559
C | Xist Rating 3212 | -36.54 | 1450.84 | 150.285 | 35.5 | 2105.49 | 9643.23 | 10537.9 | 0.19 | 1.25 | 15.884 | 11.525 | 1 | 1 | 2960 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3054729.1116 | 250338.6554 | 8533.311 | 20715.4508 | 229623.2045 | 12369.1201 | 0.11278 | -95511.0669 | 95511.0669
C | Xist Rating 3213 | -36.52 | 1452.22 | 150.285 | 35.5 | 2104.8 | 9628.74 | 10537.9 | 0.18 | 1.25 | 15.882 | 11.534 | 1 | 1 | 2970 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3056632.656 | 251962.7689 | 8591.0659 | 20785.4355 | 231177.3334 | 12358.6252 | 0.11316 | -95430.0281 | 95430.0281
C | Xist Rating 3214 | -36.51 | 1453.45 | 150.285 | 35.5 | 2104.19 | 9616.05 | 10537.9 | 0.18 | 1.25 | 15.918 | 11.542 | 1 | 1 | 2980 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3058334.9555 | 253592.1241 | 8649.0156 | 20855.4201 | 232736.704 | 12369.0802 | 0.11354 | -95510.7588 | 95510.7588
C | Xist Rating 3215 | -36.48 | 1455.01 | 150.285 | 35.5 | 2103.43 | 9600.1 | 10537.9 | 0.18 | 1.25 | 15.915 | 11.552 | 1 | 1 | 2990 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3060511.6843 | 255226.7208 | 8707.16 | 20925.4047 | 234301.316 | 12380.6772 | 0.11392 | -95600.3073 | 95600.3073
C | Xist Rating 3216 | -36.45 | 1456.43 | 150.285 | 35.5 | 2102.89 | 9588.87 | 10538 | 0.18 | 1.25 | 15.91 | 11.561 | 1 | 1 | 3000 | 152.4 | 2 | 2.5 | 19.05 | 1.3333 | 13 | E | Rod | 3062712.0827 | 256866.5591 | 8765.4993 | 20995.3894 | 235871.1697 | 12391.1867 | 0.1143 | -95681.4593 | 95681.4593
C | Xist Rating 3217 | -92.41 | 139.318 | 150.288 | 35.8 | 2400.22 | 7409.78 | 58745.8 | 2.45 | 10.95 | 16.879 | 409.239 | 1 | 1 | 1000 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 334393.85 | 34534.6257 | 973.9444 | 7278.4016 | 27256.2241 | 426847.7129 | 0.038101 | -3296004.8938 | 3296004.8938
C | Xist Rating 3218 | -92.34 | 140.786 | 150.288 | 35.8 | 2397.01 | 7387.69 | 58284.1 | 2.43 | 10.85 | 16.91 | 401.588 | 1 | 1 | 1010 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 337465.4499 | 35155.2598 | 993.5206 | 7351.1857 | 27804.0742 | 418908.8252 | 0.038482 | -3234702.9079 | 3234702.9079
C | Xist Rating 3219 | -91.77 | 151.787 | 150.288 | 35.8 | 2390.29 | 7388.73 | 54967.6 | 2.44 | 10.07 | 16.962 | 348.012 | 1 | 1 | 1020 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 362814.9482 | 35781.3452 | 1013.2917 | 7423.9697 | 28357.3755 | 363302.1855 | 0.038863 | -2805323.1757 | 2805323.1757
C | Xist Rating 3220 | -91.68 | 154.868 | 150.287 | 35.8 | 2370.06 | 7214.61 | 54178.5 | 2.36 | 9.89 | 16.621 | 336.432 | 1 | 1 | 1030 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 367046.4521 | 36412.8818 | 1033.2576 | 7496.7537 | 28916.1281 | 351195.1202 | 0.039244 | -2711835.6268 | 2711835.6268
C | Xist Rating 3221 | -91.61 | 156.411 | 150.287 | 35.8 | 2366.24 | 7187.09 | 53793.8 | 2.31 | 9.8 | 16.538 | 330.895 | 1 | 1 | 1040 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 370105.9646 | 37049.8697 | 1053.4182 | 7569.5377 | 29480.3319 | 345414.8576 | 0.039625 | -2667201.9711 | 2667201.9711
C | Xist Rating 3222 | -91.42 | 159.371 | 150.287 | 35.8 | 2375.69 | 7291.09 | 53043.3 | 2.26 | 9.63 | 16.501 | 319.986 | 1 | 1 | 1050 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 378616.091 | 37692.3088 | 1073.7737 | 7642.3217 | 30049.987 | 334060.1482 | 0.040006 | -2579523.9148 | 2579523.9148
C | Xist Rating 3223 | -91.3 | 160.894 | 150.287 | 35.8 | 2388.59 | 7422.29 | 52677.3 | 2.21 | 9.54 | 16.49 | 314.836 | 1 | 1 | 1060 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 384309.7995 | 38340.1991 | 1094.3239 | 7715.1057 | 30625.0934 | 328688.2409 | 0.040387 | -2538043.4703 | 2538043.4703
C | Xist Rating 3224 | -90.73 | 172.784 | 150.287 | 35.8 | 2368.93 | 7300.92 | 49857.7 | 2.19 | 8.9 | 16.381 | 275.515 | 1 | 1 | 1070 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 409313.2011 | 38993.5407 | 1115.0689 | 7787.8898 | 31205.6509 | 287842.5129 | 0.040768 | -2222643.5856 | 2222643.5856
C | Xist Rating 3225 | -90.59 | 175.072 | 150.287 | 35.8 | 2375.65 | 7377.19 | 49381.2 | 2.14 | 8.79 | 16.31 | 269.389 | 1 | 1 | 1080 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 415909.7968 | 39652.3335 | 1136.0087 | 7860.6738 | 31791.6597 | 281449.7459 | 0.041149 | -2173280.3335 | 2173280.3335
C | Xist Rating 3226 | -90.43 | 178.112 | 150.286 | 35.8 | 2374.76 | 7384.68 | 48762.4 | 2.09 | 8.65 | 16.201 | 261.511 | 1 | 1 | 1090 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 422973.2531 | 40316.5776 | 1157.1433 | 7933.4578 | 32383.1198 | 273233.1257 | 0.04153 | -2109833.7706 | 2109833.7706
C | Xist Rating 3227 | -90.29 | 180.368 | 150.286 | 35.8 | 2382.15 | 7468.93 | 48308.7 | 2.05 | 8.55 | 16.191 | 255.814 | 1 | 1 | 1100 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 429663.6312 | 40986.2729 | 1178.4727 | 8006.2418 | 32980.0311 | 267299.0141 | 0.041911 | -2064012.1338 | 2064012.1338
C | Xist Rating 3228 | -90.23 | 182.079 | 150.286 | 35.8 | 2376.63 | 7423.08 | 48010.9 | 1.97 | 8.49 | 15.976 | 252.377 | 1 | 1 | 1110 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 432734.4138 | 41661.4195 | 1199.9969 | 8079.0258 | 33582.3937 | 263659.052 | 0.042292 | -2035905.3115 | 2035905.3115
C | Xist Rating 3229 | -89.54 | 195.261 | 150.286 | 35.8 | 2373.81 | 7470.26 | 45448.1 | 2.01 | 7.92 | 16.169 | 220.83 | 1 | 1 | 1120 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 463512.5144 | 42342.0173 | 1221.7158 | 8151.8098 | 34190.2075 | 230963.2075 | 0.042673 | -1783436.6671 | 1783436.6671
C | Xist Rating 3230 | -89.46 | 196.926 | 150.286 | 35.8 | 2372.41 | 7464.5 | 45189.1 | 1.95 | 7.86 | 16.03 | 218.052 | 1 | 1 | 1130 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 16 | E | Rod | 467189.2117 | 43028.0664 | 1243.6296 | 8224.5939 | 34803.4725 | 228029.9582 | 0.043054 | -1760786.8934 | 1760786.8934
C | Xist Rating 3231 | -89.32 | 200.036 | 150.285 | 35.8 | 2367.48 | 7431.87 | 44681.1 | 1.9 | 7.75 | 15.818 | 212.414 | 1 | 1 | 1140 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 473581.2293 | 43719.5667 | 1265.7381 | 8297.3779 | 35422.1888 | 222127.3758 | 0.043435 | -1715208.7165 | 1715208.7165
C | Xist Rating 3232 | -89.14 | 203.084 | 150.285 | 35.8 | 2372.4 | 7496.74 | 44186.9 | 1.86 | 7.64 | 15.711 | 206.952 | 1 | 1 | 1150 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 481796.4816 | 44416.5182 | 1288.0414 | 8370.1619 | 36046.3563 | 216425.6943 | 0.043816 | -1671181.8434 | 1671181.8434
C | Xist Rating 3233 | -88.98 | 206.211 | 150.285 | 35.8 | 2372.91 | 7518.03 | 43704.1 | 1.8 | 7.53 | 15.615 | 201.767 | 1 | 1 | 1160 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 489320.144 | 45118.921 | 1310.5395 | 8442.9459 | 36675.9751 | 210996.1788 | 0.044197 | -1629256.5634 | 1629256.5634
C | Xist Rating 3234 | -88.35 | 218.087 | 150.285 | 35.8 | 2372.24 | 7578.37 | 41833.2 | 1.82 | 7.13 | 15.727 | 181.516 | 1 | 1 | 1170 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 517354.7049 | 45826.775 | 1333.2324 | 8515.7299 | 37311.0451 | 190005.215 | 0.044578 | -1467169.9055 | 1467169.9055
C | Xist Rating 3235 | -88.27 | 219.012 | 150.285 | 35.8 | 2380.97 | 7672.35 | 41725.5 | 1.77 | 7.11 | 15.674 | 180.574 | 1 | 1 | 1180 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 521461.0016 | 46540.0803 | 1356.1201 | 8588.5139 | 37951.5664 | 188993.2254 | 0.044959 | -1459355.5896 | 1459355.5896
C | Xist Rating 3236 | -88 | 225.093 | 150.285 | 35.8 | 2369.91 | 7591.09 | 40886.4 | 1.72 | 6.93 | 15.562 | 172.165 | 1 | 1 | 1190 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 533450.1516 | 47258.8368 | 1379.2026 | 8661.298 | 38597.5389 | 180220.8486 | 0.04534 | -1391617.6213 | 1391617.6213
C | Xist Rating 3237 | -87.86 | 226.649 | 150.285 | 35.8 | 2382.06 | 7725.59 | 40682.7 | 1.69 | 6.88 | 15.58 | 170.211 | 1 | 1 | 1200 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 539891.5169 | 47983.0446 | 1402.4799 | 8734.082 | 39248.9626 | 178180.1448 | 0.045721 | -1375859.8476 | 1375859.8476
C | Xist Rating 3238 | -87.72 | 229.845 | 150.285 | 35.8 | 2378.17 | 7701.56 | 40281.8 | 1.64 | 6.8 | 15.483 | 166.417 | 1 | 1 | 1210 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 546610.4837 | 48712.7036 | 1425.9519 | 8806.866 | 39905.8376 | 174201.0048 | 0.046102 | -1345133.9833 | 1345133.9833
C | Xist Rating 3239 | -87.07 | 243.382 | 150.285 | 35.8 | 2365.19 | 7641.73 | 38538.3 | 1.64 | 6.43 | 15.504 | 149.697 | 1 | 1 | 1220 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 575644.6726 | 49447.8139 | 1449.6188 | 8879.65 | 40568.1639 | 156850.5765 | 0.046483 | -1211158.5755 | 1211158.5755
C | Xist Rating 3240 | -86.88 | 246.428 | 150.285 | 35.8 | 2371.8 | 7727.74 | 38183.7 | 1.62 | 6.35 | 15.506 | 146.512 | 1 | 1 | 1230 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 584477.9304 | 50188.3754 | 1473.4804 | 8952.434 | 41235.9414 | 153537.439 | 0.046864 | -1185575.4058 | 1185575.4058
C | Xist Rating 3241 | -86.73 | 249.614 | 150.285 | 35.8 | 2370.63 | 7731.78 | 37836.1 | 1.58 | 6.28 | 15.439 | 143.501 | 1 | 1 | 1240 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 591742.4368 | 50934.3882 | 1497.5369 | 9025.218 | 41909.1701 | 150381.4216 | 0.047245 | -1161205.4759 | 1161205.4759
C | Xist Rating 3242 | -86.63 | 251.314 | 150.284 | 35.8 | 2373.2 | 7767.56 | 37665.2 | 1.54 | 6.24 | 15.391 | 142.103 | 1 | 1 | 1250 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 596418.3848 | 51685.8521 | 1521.7881 | 9098.0021 | 42587.8501 | 148901.791 | 0.047626 | -1149780.1605 | 1149780.1605
C | Xist Rating 3243 | -86.41 | 255.907 | 150.284 | 35.8 | 2371.12 | 7770.17 | 37162.2 | 1.51 | 6.14 | 15.359 | 137.728 | 1 | 1 | 1260 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 606786.2058 | 52442.7674 | 1546.2341 | 9170.7861 | 43271.9813 | 144340.1777 | 0.048007 | -1114556.5915 | 1114556.5915
C | Xist Rating 3244 | -85.77 | 268.734 | 150.284 | 35.8 | 2364.23 | 7768.18 | 35778.3 | 1.52 | 5.85 | 15.416 | 125.823 | 1 | 1 | 1270 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 635348.9848 | 53205.1339 | 1570.8749 | 9243.5701 | 43961.5638 | 132000.9254 | 0.048388 | -1019276.1564 | 1019276.1564
C | Xist Rating 3245 | -85.63 | 271.988 | 150.284 | 35.8 | 2360.38 | 7743.12 | 35477.9 | 1.48 | 5.79 | 15.35 | 123.474 | 1 | 1 | 1280 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 641995.0354 | 53972.9516 | 1595.7105 | 9316.3541 | 44656.5975 | 129531.0116 | 0.048769 | -1000204.1364 | 1000204.1364
C | Xist Rating 3246 | -85.46 | 275.191 | 150.284 | 35.8 | 2362.34 | 7780.67 | 35183.4 | 1.44 | 5.73 | 15.335 | 121.176 | 1 | 1 | 1290 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 650094.7069 | 54746.2206 | 1620.7408 | 9389.1381 | 45357.0825 | 127117.9727 | 0.04915 | -981571.2896 | 981571.2896
C | Xist Rating 3247 | -85.18 | 279.761 | 150.284 | 35.8 | 2368.58 | 7873.82 | 34751.8 | 1.42 | 5.64 | 15.35 | 117.755 | 1 | 1 | 1300 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 662636.3094 | 55524.9408 | 1645.966 | 9461.9221 | 46063.0187 | 123558.5371 | 0.049531 | -954086.2716 | 954086.2716
C | Xist Rating 3248 | -85.03 | 282.242 | 150.284 | 35.8 | 2374.18 | 7948.84 | 34540.9 | 1.38 | 5.59 | 15.318 | 116.185 | 1 | 1 | 1310 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 670093.3116 | 56309.1123 | 1671.3859 | 9534.7062 | 46774.4061 | 121899.2176 | 0.049912 | -941273.4468 | 941273.4468
C | Xist Rating 3249 | -84.38 | 295.167 | 150.284 | 35.8 | 2368.75 | 7962.11 | 33363.8 | 1.38 | 5.35 | 15.364 | 107.041 | 1 | 1 | 1320 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 699176.8312 | 57098.735 | 1697.0007 | 9607.4902 | 47491.2448 | 112416.4195 | 0.050293 | -868049.7933 | 868049.7933
C | Xist Rating 3250 | -84.17 | 299.955 | 150.284 | 35.7 | 2364.28 | 7936.88 | 32980.8 | 1.35 | 5.28 | 15.269 | 104.287 | 1 | 1 | 1330 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 709177.6074 | 57893.8089 | 1722.8102 | 9680.2742 | 48213.5347 | 109530.7743 | 0.050674 | -845767.606 | 845767.606
C | Xist Rating 3251 | -83.93 | 304.641 | 150.284 | 35.7 | 2364.88 | 7968.96 | 32607.6 | 1.32 | 5.2 | 15.244 | 101.615 | 1 | 1 | 1340 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 720439.4081 | 58694.3341 | 1748.8145 | 9753.0582 | 48941.2759 | 106735.6502 | 0.051055 | -824184.3983 | 824184.3983
C | Xist Rating 3252 | -83.77 | 307.138 | 150.284 | 35.7 | 2368.91 | 8027.66 | 32424.9 | 1.29 | 5.16 | 15.22 | 100.378 | 1 | 1 | 1350 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 727582.2796 | 59500.3106 | 1775.0136 | 9825.8422 | 49674.4683 | 105430.4999 | 0.051436 | -814106.3735 | 814106.3735
C | Xist Rating 3253 | -83.59 | 308.641 | 150.284 | 35.7 | 2384.93 | 8223.64 | 32304.4 | 1.28 | 5.14 | 15.266 | 99.53 | 1 | 1 | 1360 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 736087.1801 | 60311.7383 | 1801.4075 | 9898.6262 | 50413.112 | 104552.9651 | 0.051817 | -807330.2824 | 807330.2824
C | Xist Rating 3254 | -82.81 | 327.109 | 150.284 | 35.7 | 2358.31 | 8018.03 | 30903.1 | 1.27 | 4.86 | 15.233 | 89.754 | 1 | 1 | 1370 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 771424.4258 | 61128.6172 | 1827.9962 | 9971.4103 | 51157.2069 | 94397.415 | 0.052198 | -728911.8165 | 728911.8165
C | Xist Rating 3255 | -82.74 | 328.874 | 150.284 | 35.7 | 2357.82 | 8020.7 | 30794.7 | 1.25 | 4.84 | 15.205 | 89.104 | 1 | 1 | 1380 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 775425.6947 | 61950.9474 | 1854.7797 | 10044.1943 | 51906.7531 | 93710.0521 | 0.052579 | -723604.1822 | 723604.1822
C | Xist Rating 3256 | -82.53 | 332.897 | 150.284 | 35.7 | 2358.24 | 8046.75 | 30527.5 | 1.22 | 4.78 | 15.179 | 87.392 | 1 | 1 | 1390 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 785051.0213 | 62778.7288 | 1881.7579 | 10116.9783 | 52661.7505 | 91910.2649 | 0.05296 | -709706.7027 | 709706.7027
C | Xist Rating 3257 | -82.32 | 336.917 | 150.284 | 35.7 | 2359.17 | 8078.82 | 30265.5 | 1.2 | 4.73 | 15.157 | 85.732 | 1 | 1 | 1400 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 794844.4789 | 63611.9615 | 1908.931 | 10189.7623 | 53422.1992 | 90173.9506 | 0.053341 | -696299.3439 | 696299.3439
C | Xist Rating 3258 | -82.08 | 341.664 | 150.284 | 35.7 | 2359.72 | 8110.93 | 29957.7 | 1.17 | 4.67 | 15.141 | 83.785 | 1 | 1 | 1410 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 806231.3741 | 64450.6454 | 1936.2988 | 10262.5463 | 54188.099 | 88130.225 | 0.053722 | -680518.2364 | 680518.2364
C | Xist Rating 3259 | -81.4 | 355.443 | 150.284 | 35.7 | 2354.83 | 8131.76 | 29052.2 | 1.18 | 4.49 | 15.198 | 78.004 | 1 | 1 | 1420 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 837007.8397 | 65294.7805 | 1963.8614 | 10335.3303 | 54959.4502 | 82148.5248 | 0.054103 | -634329.1337 | 634329.1337
C | Xist Rating 3260 | -81.3 | 358.181 | 150.284 | 35.7 | 2351.51 | 8105.02 | 28911 | 1.15 | 4.47 | 15.142 | 77.236 | 1 | 1 | 1430 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 842266.2033 | 66144.3669 | 1991.6188 | 10408.1144 | 55736.2526 | 81325.6433 | 0.054484 | -627975.0609 | 627975.0609
C | Xist Rating 3261 | -81 | 364.431 | 150.284 | 35.7 | 2349.39 | 8113.61 | 28542.2 | 1.13 | 4.39 | 15.128 | 75.03 | 1 | 1 | 1440 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 856190.5471 | 66999.4046 | 2019.571 | 10480.8984 | 56518.5062 | 79021.9526 | 0.054865 | -610186.5714 | 610186.5714
C | Xist Rating 3262 | -80.8 | 368.489 | 150.284 | 35.7 | 2349.24 | 8132.92 | 28317 | 1.11 | 4.35 | 15.109 | 73.736 | 1 | 1 | 1450 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 865669.0984 | 67859.8935 | 2047.718 | 10553.6824 | 57306.2111 | 77664.7624 | 0.055246 | -599706.7083 | 599706.7083
C | Xist Rating 3263 | -80.63 | 370.868 | 150.284 | 35.7 | 2356.33 | 8231.53 | 28183.8 | 1.1 | 4.33 | 15.122 | 72.976 | 1 | 1 | 1460 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 873887.3944 | 68725.8336 | 2076.0598 | 10626.4664 | 58099.3672 | 76874.069 | 0.055627 | -593601.1839 | 593601.1839
C | Xist Rating 3264 | -79.95 | 386.579 | 150.284 | 35.7 | 2340.79 | 8130.28 | 27310.7 | 1.09 | 4.16 | 15.123 | 67.913 | 1 | 1 | 1470 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 904900.2574 | 69597.225 | 2104.5964 | 10699.2504 | 58897.9746 | 71613.7153 | 0.056008 | -552982.1272 | 552982.1272
C | Xist Rating 3265 | -79.71 | 391.369 | 150.284 | 35.7 | 2340.91 | 8156.96 | 27066.5 | 1.07 | 4.11 | 15.111 | 66.579 | 1 | 1 | 1480 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 916159.6058 | 70474.0676 | 2133.3277 | 10772.0344 | 59702.0332 | 70214.8302 | 0.056389 | -542180.3071 | 542180.3071
C | Xist Rating 3266 | -79.47 | 395.429 | 150.284 | 35.7 | 2344.45 | 8221.33 | 26867 | 1.05 | 4.07 | 15.108 | 65.514 | 1 | 1 | 1490 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 927063.519 | 71356.3615 | 2162.2539 | 10844.8185 | 60511.543 | 69095.6817 | 0.05677 | -533538.5391 | 533538.5391
C | Xist Rating 3267 | -79.24 | 399.581 | 150.284 | 35.7 | 2347.63 | 8282.18 | 26670.7 | 1.03 | 4.03 | 15.095 | 64.489 | 1 | 1 | 1500 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 938068.343 | 72244.1066 | 2191.3748 | 10917.6025 | 61326.5041 | 68017.1149 | 0.057151 | -525210.1322 | 525210.1322
C | Xist Rating 3268 | -78.95 | 404.399 | 150.284 | 35.7 | 2353.4 | 8380.89 | 26439.2 | 1.01 | 3.99 | 15.096 | 63.267 | 1 | 1 | 1510 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 951712.6066 | 73137.303 | 2220.6906 | 10990.3865 | 62146.9165 | 66734.6733 | 0.057532 | -515307.4581 | 515307.4581
C | Xist Rating 3269 | -78.18 | 419.792 | 150.284 | 35.7 | 2351.21 | 8443.79 | 25681.4 | 1.02 | 3.85 | 15.161 | 59.194 | 1 | 1 | 1520 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 987019.1483 | 74035.9506 | 2250.2011 | 11063.1705 | 62972.7801 | 62526.5063 | 0.057913 | -482813.1081 | 482813.1081
C | Xist Rating 3270 | -77.98 | 424.954 | 150.284 | 35.7 | 2344.39 | 8382.55 | 25468.7 | 0.99 | 3.8 | 15.114 | 58.17 | 1 | 1 | 1530 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 996257.9081 | 74940.0494 | 2279.9064 | 11135.9545 | 63804.0949 | 61435.6316 | 0.058294 | -474389.6626 | 474389.6626
C | Xist Rating 3271 | -77.81 | 427.608 | 150.284 | 35.7 | 2349.34 | 8459.56 | 25363.9 | 0.97 | 3.79 | 15.104 | 57.686 | 1 | 1 | 1540 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1004596.5787 | 75849.5995 | 2309.8065 | 11208.7385 | 64640.861 | 60918.1695 | 0.058675 | -470393.957 | 470393.957
C | Xist Rating 3272 | -77.43 | 435.486 | 150.284 | 35.7 | 2347.46 | 8479.66 | 25021.6 | 0.96 | 3.72 | 15.099 | 55.977 | 1 | 1 | 1550 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1022285.9656 | 76764.6009 | 2339.9013 | 11281.5226 | 65483.0783 | 59139.1154 | 0.059056 | -456656.573 | 456656.573
C | Xist Rating 3273 | -77.2 | 437.916 | 150.284 | 35.7 | 2359.5 | 8652.72 | 24920.8 | 0.95 | 3.7 | 15.121 | 55.499 | 1 | 1 | 1560 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1033262.802 | 77685.0534 | 2370.191 | 11354.3066 | 66330.7469 | 58640.1138 | 0.059437 | -452803.4147 | 452803.4147
C | Xist Rating 3274 | -76.47 | 456.188 | 150.284 | 35.7 | 2338.64 | 8481.68 | 24162.5 | 0.94 | 3.56 | 15.118 | 51.801 | 1 | 1 | 1570 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1066859.5043 | 78610.9573 | 2400.6755 | 11427.0906 | 67183.8667 | 54795.3458 | 0.059818 | -423115.1359 | 423115.1359
C | Xist Rating 3275 | -76.23 | 460.368 | 150.284 | 35.7 | 2341.88 | 8546.74 | 24007.6 | 0.92 | 3.53 | 15.112 | 51.105 | 1 | 1 | 1580 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1078126.6118 | 79542.3123 | 2431.3547 | 11499.8746 | 68042.4377 | 54057.116 | 0.0602 | -417414.7205 | 417414.7205
C | Xist Rating 3276 | -76 | 464.584 | 150.284 | 35.7 | 2344.53 | 8604.76 | 23855.3 | 0.91 | 3.5 | 15.103 | 50.429 | 1 | 1 | 1590 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1089231.1255 | 80479.1187 | 2462.2288 | 11572.6586 | 68906.46 | 53349.9688 | 0.060581 | -411954.3176 | 411954.3176
C | Xist Rating 3277 | -75.67 | 470.159 | 150.284 | 35.7 | 2348.79 | 8694.71 | 23645.7 | 0.89 | 3.46 | 15.11 | 49.474 | 1 | 1 | 1600 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1104304.7576 | 81421.3762 | 2493.2976 | 11645.4426 | 69775.9336 | 52343.1466 | 0.060962 | -404179.9037 | 404179.9037
C | Xist Rating 3278 | -75.52 | 473.008 | 150.284 | 35.7 | 2350.44 | 8731.21 | 23557 | 0.87 | 3.45 | 15.089 | 49.121 | 1 | 1 | 1610 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1111776.9235 | 82369.085 | 2524.5612 | 11718.2267 | 70650.8584 | 51959.4571 | 0.061343 | -401217.1547 | 401217.1547
C | Xist Rating 3279 | -74.64 | 493.373 | 150.284 | 35.7 | 2335.98 | 8653.91 | 22805.3 | 0.88 | 3.31 | 15.109 | 45.703 | 1 | 1 | 1620 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1152509.4605 | 83322.2451 | 2556.0196 | 11791.0107 | 71531.2344 | 48427.9889 | 0.061724 | -373948.0933 | 373948.0933
C | Xist Rating 3280 | -74.43 | 495.878 | 150.284 | 35.7 | 2344.5 | 8785.92 | 22723.7 | 0.87 | 3.29 | 15.13 | 45.369 | 1 | 1 | 1630 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1162585.971 | 84280.8564 | 2587.6728 | 11863.7947 | 72417.0617 | 48077.3859 | 0.062105 | -371240.8298 | 371240.8298
C | Xist Rating 3281 | -74.23 | 500.241 | 150.284 | 35.7 | 2343.45 | 8794.49 | 22589 | 0.85 | 3.27 | 15.111 | 44.826 | 1 | 1 | 1640 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1172289.7714 | 85244.9189 | 2619.5208 | 11936.5787 | 73308.3402 | 47495.9495 | 0.062486 | -366751.1319 | 366751.1319
C | Xist Rating 3282 | -73.97 | 506.174 | 150.284 | 35.7 | 2340.04 | 8779.07 | 22403.4 | 0.83 | 3.24 | 15.09 | 44.066 | 1 | 1 | 1650 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1184467.407 | 86214.4327 | 2651.5635 | 12009.3627 | 74205.07 | 46688.8066 | 0.062867 | -360518.5884 | 360518.5884
C | Xist Rating 3283 | -73.68 | 511.863 | 150.284 | 35.7 | 2341.37 | 8830.45 | 22221.2 | 0.82 | 3.2 | 15.09 | 43.31 | 1 | 1 | 1660 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1198460.6723 | 87189.3977 | 2683.8011 | 12082.1467 | 75107.251 | 45898.0876 | 0.063248 | -354412.8662 | 354412.8662
C | Xist Rating 3284 | -72.89 | 530.179 | 150.284 | 35.7 | 2329.16 | 8766.06 | 21633.4 | 0.82 | 3.1 | 15.104 | 40.847 | 1 | 1 | 1670 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1234871.7196 | 88169.814 | 2716.2334 | 12154.9308 | 76014.8833 | 43346.6719 | 0.063629 | -334711.5103 | 334711.5103
C | Xist Rating 3285 | -72.7 | 532.795 | 150.284 | 35.7 | 2334.97 | 8862.99 | 21560.7 | 0.81 | 3.08 | 15.109 | 40.578 | 1 | 1 | 1680 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1244060.3411 | 89155.6815 | 2748.8606 | 12227.7148 | 76927.9668 | 43061.7983 | 0.06401 | -332511.7922 | 332511.7922
C | Xist Rating 3286 | -72.4 | 540.347 | 150.284 | 35.6 | 2329.83 | 8831.2 | 21345.4 | 0.79 | 3.04 | 15.088 | 39.745 | 1 | 1 | 1690 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1258916.651 | 90147.0003 | 2781.6825 | 12300.4988 | 77846.5015 | 42178.0669 | 0.064391 | -325687.8525 | 325687.8525
C | Xist Rating 3287 | -72.13 | 545.321 | 150.284 | 35.7 | 2331.36 | 8880.95 | 21206 | 0.78 | 3.02 | 15.085 | 39.21 | 1 | 1 | 1700 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1271339.5666 | 91143.7703 | 2814.6992 | 12373.2828 | 78770.4875 | 41616.1375 | 0.064772 | -321348.7824 | 321348.7824
C | Xist Rating 3288 | -71.85 | 551.203 | 150.284 | 35.7 | 2330.55 | 8901.99 | 21045.1 | 0.77 | 2.99 | 15.077 | 38.602 | 1 | 1 | 1710 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1284606.1517 | 92145.9916 | 2847.9107 | 12446.0668 | 79699.9248 | 40977.9698 | 0.065153 | -316421.0208 | 316421.0208
C | Xist Rating 3289 | -71.12 | 568.104 | 150.284 | 35.7 | 2320.88 | 8861.12 | 20567.5 | 0.77 | 2.9 | 15.108 | 36.744 | 1 | 1 | 1720 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1318501.2115 | 93153.6641 | 2881.317 | 12518.8508 | 80634.8132 | 39055.4839 | 0.065534 | -301576.0942 | 301576.0942
C | Xist Rating 3290 | -70.78 | 575.526 | 150.284 | 35.6 | 2319.11 | 8876.98 | 20374.5 | 0.76 | 2.87 | 15.1 | 36.035 | 1 | 1 | 1730 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1334708.1019 | 94166.7878 | 2914.9181 | 12591.6349 | 81575.153 | 38312.2158 | 0.065915 | -295836.7751 | 295836.7751
C | Xist Rating 3291 | -70.57 | 579.021 | 150.284 | 35.6 | 2323.14 | 8955.03 | 20290.1 | 0.75 | 2.85 | 15.099 | 35.745 | 1 | 1 | 1740 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1345146.8459 | 95185.3628 | 2948.714 | 12664.4189 | 82520.944 | 38004.3596 | 0.066296 | -293459.5912 | 293459.5912
C | Xist Rating 3292 | -70.28 | 585.843 | 150.284 | 35.6 | 2319.74 | 8942.11 | 20123.9 | 0.73 | 2.82 | 15.086 | 35.156 | 1 | 1 | 1750 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1359003.4408 | 96209.3891 | 2982.7046 | 12737.2029 | 83472.1862 | 37373.3274 | 0.066677 | -288586.9278 | 288586.9278
C | Xist Rating 3293 | -70.07 | 590.934 | 150.284 | 35.6 | 2316.98 | 8929.08 | 20001.1 | 0.73 | 2.8 | 15.079 | 34.727 | 1 | 1 | 1760 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1369182.2593 | 97238.8665 | 3016.8901 | 12809.9869 | 84428.8796 | 36932.3449 | 0.067058 | -285181.7777 | 285181.7777
C | Xist Rating 3294 | -69.21 | 610.957 | 150.284 | 35.6 | 2305.7 | 8879.29 | 19497.8 | 0.73 | 2.71 | 15.115 | 32.897 | 1 | 1 | 1770 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1408683.5549 | 98273.7953 | 3051.2703 | 12882.7709 | 85391.0243 | 35038.912 | 0.067439 | -270561.1907 | 270561.1907
C | Xist Rating 3295 | -69.13 | 616.157 | 150.284 | 35.6 | 2295.34 | 8754.11 | 19383.8 | 0.71 | 2.69 | 15.261 | 32.512 | 1 | 1 | 1780 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1414289.8084 | 99314.1752 | 3085.8453 | 12955.5549 | 86358.6203 | 34628.187 | 0.06782 | -267389.6809 | 267389.6809
C | Xist Rating 3296 | -68.99 | 619.033 | 150.284 | 35.6 | 2295.95 | 8776.35 | 19327.2 | 0.7 | 2.68 | 15.253 | 32.343 | 1 | 1 | 1790 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1421268.8163 | 100360.0064 | 3120.6151 | 13028.3389 | 87331.6675 | 34444.8435 | 0.068201 | -265973.951 | 265973.951
C | Xist Rating 3297 | -68.61 | 628.112 | 150.284 | 35.6 | 2293.24 | 8785.94 | 19121.9 | 0.69 | 2.65 | 15.241 | 31.649 | 1 | 1 | 1800 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1440411.5629 | 101411.2889 | 3155.5797 | 13101.123 | 88310.1659 | 33715.9367 | 0.068582 | -260345.526 | 260345.526
C | Xist Rating 3298 | -68.38 | 633.185 | 150.284 | 35.6 | 2292.16 | 8796.76 | 19012.5 | 0.68 | 2.63 | 15.238 | 31.292 | 1 | 1 | 1810 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1451361.3296 | 102468.0226 | 3190.7391 | 13173.907 | 89294.1156 | 33337.3757 | 0.068963 | -257422.3785 | 257422.3785
C | Xist Rating 3299 | -67.54 | 653.467 | 150.284 | 35.6 | 2281.43 | 8751.67 | 18562.8 | 0.68 | 2.55 | 15.272 | 29.771 | 1 | 1 | 1820 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1490839.2178 | 103530.2076 | 3226.0933 | 13246.691 | 90283.5166 | 31764.3504 | 0.069344 | -245275.8942 | 245275.8942
C | Xist Rating 3300 | -67.5 | 650.227 | 150.284 | 35.6 | 2295.76 | 8948.09 | 18631.7 | 0.68 | 2.56 | 15.296 | 30.012 | 1 | 1 | 1830 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1492765.1375 | 104597.8438 | 3261.6423 | 13319.475 | 91278.3687 | 32020.6223 | 0.069725 | -247254.7576 | 247254.7576
C | Xist Rating 3301 | -67.18 | 654.368 | 150.284 | 35.6 | 2304.32 | 9103.15 | 18545.7 | 0.67 | 2.55 | 15.315 | 29.741 | 1 | 1 | 1840 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1507873.2698 | 105670.9312 | 3297.386 | 13392.259 | 92278.6722 | 31732.2858 | 0.070106 | -245028.2993 | 245028.2993
C | Xist Rating 3302 | -66.88 | 661.307 | 150.284 | 35.6 | 2301.61 | 9098.8 | 18409.7 | 0.66 | 2.52 | 15.306 | 29.318 | 1 | 1 | 1850 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1522070.8043 | 106749.4699 | 3333.3246 | 13465.043 | 93284.4268 | 31284.4078 | 0.070487 | -241569.9042 | 241569.9042
C | Xist Rating 3303 | -66.56 | 669.071 | 150.284 | 35.6 | 2297.52 | 9077.3 | 18259.8 | 0.65 | 2.5 | 15.295 | 28.854 | 1 | 1 | 1860 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1537204.0039 | 107833.4598 | 3369.4579 | 13537.8271 | 94295.6327 | 30793.7153 | 0.070868 | -237780.9074 | 237780.9074
C | Xist Rating 3304 | -65.71 | 687.666 | 150.285 | 35.6 | 2292.83 | 9114.2 | 17880.4 | 0.65 | 2.43 | 15.344 | 27.633 | 1 | 1 | 1870 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1576701.2348 | 108922.901 | 3405.7861 | 13610.6111 | 95312.2899 | 29532.8349 | 0.071249 | -228044.7225 | 228044.7225
C | Xist Rating 3305 | -65.38 | 695.416 | 150.285 | 35.6 | 2290.13 | 9113.8 | 17739.7 | 0.64 | 2.41 | 15.337 | 27.215 | 1 | 1 | 1880 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1592593.0441 | 110017.7934 | 3442.309 | 13683.3951 | 96334.3983 | 29089.9052 | 0.07163 | -224624.5369 | 224624.5369
C | Xist Rating 3306 | -65.09 | 700.537 | 150.285 | 35.6 | 2292.96 | 9187.42 | 17647.4 | 0.63 | 2.39 | 15.343 | 26.945 | 1 | 1 | 1890 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1606303.3195 | 111118.1371 | 3479.0267 | 13756.1791 | 97361.958 | 28801.2374 | 0.072011 | -222395.5208 | 222395.5208
C | Xist Rating 3307 | -64.87 | 706.116 | 150.285 | 35.6 | 2289.8 | 9165.33 | 17556 | 0.62 | 2.38 | 15.334 | 26.693 | 1 | 1 | 1900 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1616864.4168 | 112223.932 | 3515.9392 | 13828.9631 | 98394.9688 | 28530.3262 | 0.072392 | -220303.6164 | 220303.6164
C | Xist Rating 3308 | -64.64 | 711.416 | 150.284 | 35.6 | 2288.55 | 9173.74 | 17465.5 | 0.61 | 2.36 | 15.331 | 26.437 | 1 | 1 | 1910 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1628111.0868 | 113335.1781 | 3553.0464 | 13901.7471 | 99433.431 | 28255.4472 | 0.072773 | -218181.0739 | 218181.0739
C | Xist Rating 3309 | -63.67 | 734.012 | 150.284 | 35.6 | 2279.48 | 9162.44 | 17050.6 | 0.61 | 2.29 | 15.372 | 25.179 | 1 | 1 | 1920 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1673165.6738 | 114451.8755 | 3590.3485 | 13974.5312 | 100477.3444 | 26955.3606 | 0.073154 | -208142.1497 | 208142.1497
C | Xist Rating 3310 | -63.34 | 741.839 | 150.284 | 35.6 | 2276.55 | 9157.31 | 16924.4 | 0.6 | 2.27 | 15.364 | 24.828 | 1 | 1 | 1930 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1688833.5755 | 115574.0242 | 3627.8454 | 14047.3152 | 101526.709 | 26581.337 | 0.073535 | -205254.0387 | 205254.0387
C | Xist Rating 3311 | -63.11 | 744.352 | 150.284 | 35.6 | 2284.57 | 9302.94 | 16882.4 | 0.59 | 2.26 | 15.381 | 24.717 | 1 | 1 | 1940 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1700524.2486 | 116701.6241 | 3665.537 | 14120.0992 | 102581.5249 | 26457.7075 | 0.073916 | -204299.4044 | 204299.4044
C | Xist Rating 3312 | -62.87 | 751.862 | 150.284 | 35.6 | 2277.05 | 9217.3 | 16772.4 | 0.58 | 2.24 | 15.364 | 24.43 | 1 | 1 | 1950 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1712027.3671 | 117834.6752 | 3703.4235 | 14192.8832 | 103641.792 | 26149.4202 | 0.074297 | -201918.891 | 201918.891
C | Xist Rating 3313 | -62.51 | 760.394 | 150.284 | 35.6 | 2274.22 | 9218.23 | 16637.3 | 0.57 | 2.22 | 15.378 | 24.058 | 1 | 1 | 1960 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1729303.2427 | 118973.1776 | 3741.5047 | 14265.6672 | 104707.5103 | 25754.296 | 0.074678 | -198867.8468 | 198867.8468
C | Xist Rating 3314 | -61.64 | 780.805 | 150.285 | 35.6 | 2266.74 | 9215.32 | 16303.4 | 0.57 | 2.16 | 15.434 | 23.11 | 1 | 1 | 1970 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1769881.9257 | 120117.1312 | 3779.7807 | 14338.4512 | 105778.6799 | 24776.5472 | 0.075059 | -191317.9302 | 191317.9302
C | Xist Rating 3315 | -61.35 | 786.911 | 150.285 | 35.6 | 2267.17 | 9255.49 | 16214.4 | 0.57 | 2.15 | 15.447 | 22.88 | 1 | 1 | 1980 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1784061.0119 | 121266.5361 | 3818.2515 | 14411.2353 | 106855.3008 | 24542.2937 | 0.07544 | -189509.0861 | 189509.0861
C | Xist Rating 3316 | -61.04 | 794.932 | 150.285 | 35.6 | 2263.02 | 9228.7 | 16101.7 | 0.56 | 2.13 | 15.451 | 22.591 | 1 | 1 | 1990 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1798947.0146 | 122421.3922 | 3856.9171 | 14484.0193 | 107937.3729 | 24232.5352 | 0.075821 | -187117.2139 | 187117.2139
C | Xist Rating 3317 | -60.76 | 801.164 | 150.285 | 35.6 | 2262.36 | 9250.65 | 16015.1 | 0.55 | 2.12 | 15.45 | 22.373 | 1 | 1 | 2000 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1812521.387 | 123581.6995 | 3895.7775 | 14556.8033 | 109024.8962 | 23996.1201 | 0.076202 | -185291.6784 | 185291.6784
C | Xist Rating 3318 | -60.53 | 805.778 | 150.285 | 35.6 | 2263.14 | 9287.52 | 15954 | 0.54 | 2.11 | 15.454 | 22.225 | 1 | 1 | 2010 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1823588.4229 | 124747.4581 | 3934.8326 | 14629.5873 | 110117.8708 | 23832.5058 | 0.076583 | -184028.2925 | 184028.2925
C | Xist Rating 3319 | -59.6 | 828.822 | 150.285 | 35.6 | 2252.78 | 9247.38 | 15615 | 0.54 | 2.05 | 15.491 | 21.319 | 1 | 1 | 2020 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1867153.6252 | 125918.668 | 3974.0826 | 14702.3713 | 111216.2966 | 22897.176 | 0.076964 | -176805.9239 | 176805.9239
C | Xist Rating 3320 | -59.23 | 837.299 | 150.285 | 35.6 | 2251.76 | 9276.97 | 15499.9 | 0.53 | 2.03 | 15.493 | 21.03 | 1 | 1 | 2030 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1885396.3962 | 127095.3291 | 4013.5273 | 14775.1553 | 112320.1737 | 22586.8002 | 0.077345 | -174409.284 | 174409.284
C | Xist Rating 3321 | -59.02 | 843.077 | 150.285 | 35.6 | 2248.58 | 9251.27 | 15431.8 | 0.52 | 2.02 | 15.485 | 20.876 | 1 | 1 | 2040 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1895726.0807 | 128277.4414 | 4053.1669 | 14847.9394 | 113429.502 | 22416.0046 | 0.077726 | -173090.4455 | 173090.4455
C | Xist Rating 3322 | -58.74 | 848.04 | 150.285 | 35.6 | 2251.37 | 9327.11 | 15364.3 | 0.52 | 2.01 | 15.492 | 20.709 | 1 | 1 | 2050 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1909251.8148 | 129465.005 | 4093.0012 | 14920.7234 | 114544.2816 | 22246.5192 | 0.078107 | -171781.7242 | 171781.7242
C | Xist Rating 3323 | -58.47 | 856.456 | 150.285 | 35.6 | 2244.93 | 9259.29 | 15264.4 | 0.51 | 1.99 | 15.484 | 20.477 | 1 | 1 | 2060 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1922683.7681 | 130658.0198 | 4133.0303 | 14993.5074 | 115664.5124 | 21994.5167 | 0.078488 | -169835.8278 | 169835.8278
C | Xist Rating 3324 | -57.48 | 881.221 | 150.285 | 35.6 | 2234.49 | 9223 | 14936.3 | 0.51 | 1.94 | 15.522 | 19.65 | 1 | 1 | 2070 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1969079.5123 | 131856.4859 | 4173.2542 | 15066.2914 | 116790.1945 | 21141.0164 | 0.078869 | -163245.3251 | 163245.3251
C | Xist Rating 3325 | -57.25 | 886.801 | 150.285 | 35.6 | 2233.4 | 9232.03 | 14873.5 | 0.5 | 1.93 | 15.518 | 19.512 | 1 | 1 | 2080 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1980581.3534 | 133060.4032 | 4213.6729 | 15139.0754 | 117921.3278 | 20986.5936 | 0.07925 | -162052.913 | 162052.913
C | Xist Rating 3326 | -56.95 | 893.939 | 150.285 | 35.6 | 2231.62 | 9238.47 | 14790.9 | 0.5 | 1.91 | 15.515 | 19.324 | 1 | 1 | 2090 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 1994932.1512 | 134269.7717 | 4254.2864 | 15211.8594 | 119057.9123 | 20794.6933 | 0.079631 | -160571.1099 | 160571.1099
C | Xist Rating 3327 | -56.66 | 901.086 | 150.285 | 35.6 | 2229.68 | 9241.84 | 14709.4 | 0.49 | 1.9 | 15.513 | 19.139 | 1 | 1 | 2100 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 2009133.4325 | 135484.5916 | 4295.0947 | 15284.6435 | 120199.9481 | 20591.3516 | 0.080012 | -159000.959 | 159000.959
C | Xist Rating 3328 | -56.38 | 907.411 | 150.285 | 35.6 | 2229.37 | 9268.83 | 14638.8 | 0.48 | 1.89 | 15.511 | 18.983 | 1 | 1 | 2110 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 2022954.8611 | 136704.8626 | 4336.0977 | 15357.4275 | 121347.4351 | 20417.9902 | 0.080393 | -157662.3078 | 157662.3078
C | Xist Rating 3329 | -55.49 | 930.895 | 150.285 | 35.6 | 2218.22 | 9207.03 | 14359.1 | 0.48 | 1.84 | 15.548 | 18.319 | 1 | 1 | 2120 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 2064929.9069 | 137930.5849 | 4377.2956 | 15430.2115 | 122500.3734 | 19733.4522 | 0.080774 | -152376.4873 | 152376.4873
C | Xist Rating 3330 | -55.14 | 939.714 | 150.285 | 35.6 | 2215.84 | 9211.37 | 14263.9 | 0.48 | 1.83 | 15.542 | 18.109 | 1 | 1 | 2130 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 2082255.8698 | 139161.7584 | 4418.6882 | 15502.9955 | 123658.7629 | 19518.4379 | 0.081155 | -150716.2035 | 150716.2035
C | Xist Rating 3331 | -54.85 | 948.56 | 150.285 | 35.6 | 2210.33 | 9161.49 | 14170 | 0.47 | 1.81 | 15.54 | 17.904 | 1 | 1 | 2140 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 2096630.6248 | 140398.3832 | 4460.2756 | 15575.7795 | 124822.6037 | 19293.8909 | 0.081536 | -148982.3112 | 148982.3112
C | Xist Rating 3332 | -54.64 | 953.324 | 150.285 | 35.6 | 2210.58 | 9188.42 | 14123.5 | 0.47 | 1.8 | 15.537 | 17.812 | 1 | 1 | 2150 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 2107398.9679 | 141640.4592 | 4502.0578 | 15648.5635 | 125991.8957 | 19201.4871 | 0.081917 | -148268.7933 | 148268.7933
C | Xist Rating 3333 | -54.36 | 959.595 | 150.285 | 35.6 | 2210.35 | 9215.88 | 14059.1 | 0.46 | 1.79 | 15.537 | 17.676 | 1 | 1 | 2160 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 2121040.8082 | 142887.9865 | 4544.0348 | 15721.3476 | 127166.639 | 19048.4814 | 0.082298 | -147087.3243 | 147087.3243
C | Xist Rating 3334 | -53.42 | 985.012 | 150.285 | 35.6 | 2198.59 | 9148.48 | 13786.1 | 0.46 | 1.75 | 15.571 | 17.064 | 1 | 1 | 2170 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 2165637.5331 | 144140.965 | 4586.2066 | 15794.1316 | 128346.8335 | 18417.6453 | 0.082679 | -142216.1751 | 142216.1751
C | Xist Rating 3335 | -53.05 | 993.606 | 150.285 | 35.6 | 2197.6 | 9175.88 | 13699.1 | 0.46 | 1.74 | 15.569 | 16.88 | 1 | 1 | 2180 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 2183548.5456 | 145399.3948 | 4628.5732 | 15866.9156 | 129532.4792 | 18229.6823 | 0.08306 | -140764.7749 | 140764.7749
C | Xist Rating 3336 | -52.8 | 1000.11 | 150.285 | 35.6 | 2195.73 | 9174.35 | 13639 | 0.45 | 1.73 | 15.566 | 16.761 | 1 | 1 | 2190 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 15 | E | Rod | 2195971.5303 | 146663.2758 | 4671.1346 | 15939.6996 | 130723.5762 | 18093.8953 | 0.083441 | -139716.2631 | 139716.2631
C | Xist Rating 3337 | -52.58 | 1007.02 | 150.285 | 35.6 | 2191.27 | 9127.6 | 13579.4 | 0.44 | 1.72 | 15.554 | 16.649 | 1 | 1 | 2200 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2206652.7154 | 147932.6081 | 4713.8907 | 16012.4836 | 131920.1244 | 17964.8523 | 0.083822 | -138719.8275 | 138719.8275
C | Xist Rating 3338 | -52.25 | 1015.87 | 150.285 | 35.6 | 2188.45 | 9122.73 | 13495.4 | 0.44 | 1.7 | 15.552 | 16.477 | 1 | 1 | 2210 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2223180.7015 | 149207.3916 | 4756.8417 | 16085.2676 | 133122.1239 | 17789.2111 | 0.084203 | -137363.5726 | 137363.5726
C | Xist Rating 3339 | -51.28 | 1041.16 | 150.285 | 35.6 | 2179.13 | 9093.6 | 13246.2 | 0.44 | 1.66 | 15.591 | 15.944 | 1 | 1 | 2220 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2268822.9908 | 150487.6263 | 4799.9874 | 16158.0517 | 134329.5746 | 17240.4663 | 0.084584 | -133126.3111 | 133126.3111
C | Xist Rating 3340 | -51 | 1048.27 | 150.285 | 35.6 | 2178 | 9108.51 | 13182.5 | 0.43 | 1.65 | 15.587 | 15.82 | 1 | 1 | 2230 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2283132.06 | 151773.3123 | 4843.3279 | 16230.8357 | 135542.4766 | 17099.011 | 0.084965 | -132034.0304 | 132034.0304
C | Xist Rating 3341 | -50.71 | 1056.65 | 150.285 | 35.6 | 2174.13 | 9079.93 | 13111.7 | 0.43 | 1.64 | 15.586 | 15.686 | 1 | 1 | 2240 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2297294.4645 | 153064.4495 | 4886.8633 | 16303.6197 | 136760.8298 | 16962.8134 | 0.085346 | -130982.3484 | 130982.3484
C | Xist Rating 3342 | -50.39 | 1065.81 | 150.285 | 35.6 | 2170.6 | 9061.38 | 13034 | 0.42 | 1.63 | 15.583 | 15.537 | 1 | 1 | 2250 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2313447.186 | 154361.038 | 4930.5934 | 16376.4037 | 137984.6343 | 16795.2348 | 0.085727 | -129688.3513 | 129688.3513
C | Xist Rating 3343 | -50.19 | 1070.54 | 150.285 | 35.6 | 2170.46 | 9080.39 | 12995.6 | 0.42 | 1.62 | 15.582 | 15.468 | 1 | 1 | 2260 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2323564.2484 | 155663.0777 | 4974.5182 | 16449.1877 | 139213.89 | 16726.4696 | 0.086108 | -129157.3645 | 129157.3645
C | Xist Rating 3344 | -49.19 | 1097.85 | 150.285 | 35.6 | 2159.88 | 9034.05 | 12751.8 | 0.42 | 1.59 | 15.619 | 14.976 | 1 | 1 | 2270 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2371224.258 | 156970.5687 | 5018.6379 | 16521.9717 | 140448.5969 | 16220.0431 | 0.086489 | -125246.8735 | 125246.8735
C | Xist Rating 3345 | -48.88 | 1106.18 | 150.285 | 35.6 | 2157.13 | 9024.17 | 12686.1 | 0.41 | 1.58 | 15.615 | 14.856 | 1 | 1 | 2280 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2386174.0634 | 158283.5109 | 5062.9524 | 16594.7558 | 141688.7551 | 16082.2335 | 0.08687 | -124182.7444 | 124182.7444
C | Xist Rating 3346 | -48.5 | 1115.91 | 150.285 | 35.6 | 2155.19 | 9036.5 | 12606.9 | 0.41 | 1.56 | 15.614 | 14.707 | 1 | 1 | 2290 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2404998.0729 | 159601.9043 | 5107.4617 | 16667.5398 | 142934.3646 | 15930.3249 | 0.087251 | -123009.7464 | 123009.7464
C | Xist Rating 3347 | -48.27 | 1122.57 | 150.285 | 35.6 | 2152.8 | 9024.09 | 12557 | 0.4 | 1.56 | 15.61 | 14.62 | 1 | 1 | 2300 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2416668.696 | 160925.7491 | 5152.1657 | 16740.3238 | 144185.4253 | 15826.5826 | 0.087632 | -122208.676 | 122208.676
| Xist Rating 3348 | -48.04 | 1129.51 | 150.285 | 35.6 | 2150.07 | 9005.51 | 12507.6 | 0.4 | 1.55 | 15.607 | 14.537 | 1 | 1 | 2310 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2428525.5657 | 162255.045 | 5197.0645 | 16813.1078 | 145441.9372 | 15743.0619 | 0.088013 | -121563.7508 | 121563.7508
| Xist Rating 3349 | -47 | 1157.48 | 150.285 | 35.6 | 2140.98 | 8985.45 | 12277.1 | 0.4 | 1.51 | 15.645 | 14.091 | 1 | 1 | 2320 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2478141.5304 | 163589.7922 | 5242.1582 | 16885.8918 | 146703.9004 | 15284.2706 | 0.088394 | -118021.0861 | 118021.0861
| Xist Rating 3350 | -46.71 | 1165.84 | 150.285 | 35.6 | 2137.96 | 8969.6 | 12216.8 | 0.39 | 1.5 | 15.639 | 13.987 | 1 | 1 | 2330 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2492519.2864 | 164929.9906 | 5287.4466 | 16958.6758 | 147971.3148 | 15162.4876 | 0.088775 | -117080.7103 | 117080.7103
| Xist Rating 3351 | -46.42 | 1174.18 | 150.285 | 35.6 | 2135.09 | 8956.12 | 12157.2 | 0.39 | 1.49 | 15.633 | 13.884 | 1 | 1 | 2340 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2506979.9762 | 166275.6403 | 5332.9298 | 17031.4599 | 149244.1804 | 15058.0108 | 0.089156 | -116273.9679 | 116273.9679
| Xist Rating 3352 | -46.18 | 1181.79 | 150.285 | 35.6 | 2131.76 | 8930.47 | 12104.8 | 0.38 | 1.49 | 15.628 | 13.796 | 1 | 1 | 2350 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2519292.6504 | 167626.7412 | 5378.6078 | 17104.2439 | 150522.4974 | 14952.6882 | 0.089537 | -115460.6949 | 115460.6949
| Xist Rating 3353 | -45.86 | 1191 | 150.285 | 35.6 | 2128.51 | 8914.19 | 12039.9 | 0.38 | 1.48 | 15.623 | 13.685 | 1 | 1 | 2360 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2535055.41 | 168983.2934 | 5424.4805 | 17177.0279 | 151806.2655 | 14839.8759 | 0.089918 | -114589.5879 | 114589.5879
| Xist Rating 3354 | -44.92 | 1216.71 | 150.285 | 35.6 | 2120.44 | 8895.79 | 11846.8 | 0.38 | 1.45 | 15.658 | 13.331 | 1 | 1 | 2370 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2579960.5524 | 170345.2968 | 5470.5481 | 17249.8119 | 153095.4849 | 14476.3215 | 0.090299 | -111782.3172 | 111782.3172
| Xist Rating 3355 | -44.64 | 1225.29 | 150.285 | 35.6 | 2117.15 | 8874.15 | 11791.2 | 0.37 | 1.44 | 15.651 | 13.24 | 1 | 1 | 2380 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2594122.7235 | 171712.7515 | 5516.8105 | 17322.5959 | 154390.1555 | 14367.5045 | 0.09068 | -110942.0615 | 110942.0615
| Xist Rating 3356 | -44.32 | 1234.05 | 150.285 | 35.6 | 2115.3 | 8881.77 | 11730 | 0.37 | 1.43 | 15.645 | 13.136 | 1 | 1 | 2390 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2610385.965 | 173085.6574 | 5563.2676 | 17395.3799 | 155690.2774 | 14261.8586 | 0.091061 | -110126.2917 | 110126.2917
C | Xist Rating 3357 | -39.86 | 1414.82 | 150.285 | 35.6 | 1995.29 | 7696.08 | 10538.5 | 0.4 | 1.25 | 15.619 | 11.1 | 1 | 1 | 2400 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2822976.1978 | 174464.0145 | 5609.9196 | 17468.164 | 156995.8506 | 12199.444 | 0.091442 | -94200.8729 | 94200.8729
C | Xist Rating 3358 | -38.33 | 1416.27 | 150.285 | 35.6 | 2042.88 | 8456.07 | 10538 | 0.39 | 1.25 | 15.642 | 11.105 | 1 | 1 | 2410 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2893269.6576 | 175847.8229 | 5656.7663 | 17540.948 | 158306.8749 | 12191.5332 | 0.091823 | -94139.7875 | 94139.7875
C | Xist Rating 3359 | -38.31 | 1417.67 | 150.285 | 35.6 | 2042.83 | 8455.34 | 10538 | 0.39 | 1.25 | 15.682 | 11.116 | 1 | 1 | 2420 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2896058.8061 | 177237.0826 | 5703.8078 | 17613.732 | 159623.3506 | 12207.3833 | 0.092204 | -94262.1784 | 94262.1784
C | Xist Rating 3360 | -37.75 | 1419.02 | 150.285 | 35.6 | 2059.31 | 8744.94 | 10538 | 0.39 | 1.25 | 15.675 | 11.125 | 1 | 1 | 2430 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2922202.0762 | 178631.7934 | 5751.0441 | 17686.516 | 160945.2774 | 12219.1739 | 0.092585 | -94353.2222 | 94353.2222
C | Xist Rating 3361 | -37.73 | 1420.39 | 150.285 | 35.6 | 2058.8 | 8735.9 | 10537.9 | 0.38 | 1.25 | 15.668 | 11.136 | 1 | 1 | 2440 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2924298.932 | 180031.9556 | 5798.4752 | 17759.3 | 162272.6555 | 12215.9027 | 0.092966 | -94327.9622 | 94327.9622
C | Xist Rating 3362 | -37.73 | 1421.72 | 150.285 | 35.6 | 2057.74 | 8716.9 | 10537.9 | 0.38 | 1.25 | 15.662 | 11.146 | 1 | 1 | 2450 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2925530.1128 | 181437.5689 | 5846.1011 | 17832.084 | 163605.4849 | 12228.706 | 0.093347 | -94426.8265 | 94426.8265
C | Xist Rating 3363 | -37.72 | 1423.19 | 150.285 | 35.6 | 2056.86 | 8701.04 | 10537.9 | 0.37 | 1.25 | 15.657 | 11.157 | 1 | 1 | 2460 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2927302.5834 | 182848.6336 | 5893.9217 | 17904.8681 | 164943.7655 | 12225.323 | 0.093728 | -94400.7037 | 94400.7037
C | Xist Rating 3364 | -37.7 | 1424.55 | 150.285 | 35.6 | 2056.34 | 8691.71 | 10537.9 | 0.36 | 1.25 | 15.693 | 11.168 | 1 | 1 | 2470 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2929359.147 | 184265.1494 | 5941.9372 | 17977.6521 | 166287.4973 | 12223.4432 | 0.094109 | -94386.1881 | 94386.1881
C | Xist Rating 3365 | -37.68 | 1425.89 | 150.285 | 35.6 | 2055.69 | 8680.22 | 10537.9 | 0.36 | 1.25 | 15.687 | 11.179 | 1 | 1 | 2480 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2931187.8141 | 185687.1165 | 5990.1474 | 18050.4361 | 167636.6804 | 12237.1589 | 0.09449 | -94492.0973 | 94492.0973
C | Xist Rating 3366 | -37.67 | 1427.29 | 150.285 | 35.6 | 2054.8 | 8664.27 | 10537.9 | 0.35 | 1.25 | 15.686 | 11.189 | 1 | 1 | 2490 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2932795.492 | 187114.5349 | 6038.5525 | 18123.2201 | 168991.3148 | 12232.5274 | 0.094871 | -94456.3342 | 94456.3342
C | Xist Rating 3367 | -37.65 | 1428.28 | 150.285 | 35.6 | 2054.88 | 8665.73 | 10537.9 | 0.35 | 1.25 | 15.681 | 11.198 | 1 | 1 | 2500 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2934944.0064 | 188547.4045 | 6087.1523 | 18196.0041 | 170351.4004 | 12244.1387 | 0.095252 | -94545.9936 | 94545.9936
C | Xist Rating 3368 | -37.61 | 1430.13 | 150.285 | 35.6 | 2053.76 | 8645.77 | 10538 | 0.34 | 1.25 | 15.677 | 11.211 | 1 | 1 | 2510 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2937143.7888 | 189985.7253 | 6135.9469 | 18268.7881 | 171716.9372 | 12242.3036 | 0.095633 | -94531.8236 | 94531.8236
C | Xist Rating 3369 | -37.57 | 1431.58 | 150.285 | 35.6 | 2054.16 | 8652.99 | 10537.9 | 0.34 | 1.25 | 15.711 | 11.222 | 1 | 1 | 2520 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2940694.3728 | 191429.4974 | 6184.9363 | 18341.5722 | 173087.9253 | 12257.4222 | 0.096014 | -94648.5648 | 94648.5648
C | Xist Rating 3370 | -37.56 | 1432.92 | 150.285 | 35.6 | 2053.65 | 8643.89 | 10537.8 | 0.33 | 1.25 | 15.703 | 11.232 | 1 | 1 | 2530 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2942716.158 | 192878.7207 | 6234.1205 | 18414.3562 | 174464.3646 | 12252.0849 | 0.096395 | -94607.3518 | 94607.3518
C | Xist Rating 3371 | -37.55 | 1434.07 | 150.285 | 35.6 | 2053.28 | 8637.34 | 10537.8 | 0.33 | 1.25 | 15.698 | 11.241 | 1 | 1 | 2540 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2944547.2496 | 194333.3953 | 6283.4995 | 18487.1402 | 175846.2551 | 12263.5663 | 0.096776 | -94696.0084 | 94696.0084
C | Xist Rating 3372 | -37.54 | 1435.62 | 150.285 | 35.6 | 2052.45 | 8622.78 | 10537.8 | 0.32 | 1.25 | 15.706 | 11.252 | 1 | 1 | 2550 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2946538.269 | 195793.5211 | 6333.0732 | 18559.9242 | 177233.5969 | 12259.6612 | 0.097157 | -94665.8543 | 94665.8543
C | Xist Rating 3373 | -37.54 | 1437.06 | 150.285 | 35.6 | 2051 | 8597.25 | 10537.8 | 0.32 | 1.25 | 15.706 | 11.263 | 1 | 1 | 2560 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2947410.06 | 197259.0982 | 6382.8418 | 18632.7082 | 178626.39 | 12273.3376 | 0.097538 | -94771.4593 | 94771.4593
C | Xist Rating 3374 | -37.51 | 1438.45 | 150.285 | 35.6 | 2050.67 | 8591.49 | 10537.7 | 0.31 | 1.25 | 15.706 | 11.273 | 1 | 1 | 2570 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2949786.2615 | 198730.1265 | 6432.8051 | 18705.4922 | 180024.6343 | 12267.8822 | 0.097919 | -94729.3344 | 94729.3344
C | Xist Rating 3375 | -37.49 | 1439.82 | 150.285 | 35.6 | 2050.21 | 8583.4 | 10537.7 | 0.31 | 1.25 | 15.741 | 11.284 | 1 | 1 | 2580 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2951933.3622 | 200206.6061 | 6482.9633 | 18778.2763 | 181428.3298 | 12282.7429 | 0.0983 | -94844.0848 | 94844.0848
C | Xist Rating 3376 | -37.47 | 1441.18 | 150.285 | 35.6 | 2049.78 | 8575.95 | 10537.7 | 0.3 | 1.25 | 15.737 | 11.294 | 1 | 1 | 2590 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2954101.9404 | 201688.5369 | 6533.3162 | 18851.0603 | 182837.4766 | 12276.9012 | 0.098681 | -94798.9771 | 94798.9771
C | Xist Rating 3377 | -37.45 | 1442.36 | 150.285 | 35.6 | 2049.53 | 8571.53 | 10537.7 | 0.3 | 1.25 | 15.733 | 11.303 | 1 | 1 | 2600 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2956160.0908 | 203175.9189 | 6583.8639 | 18923.8443 | 184252.0746 | 12288.2241 | 0.099062 | -94886.4091 | 94886.4091
C | Xist Rating 3378 | -37.41 | 1444.04 | 150.285 | 35.6 | 2048.9 | 8560.49 | 10537.7 | 0.29 | 1.25 | 15.735 | 11.314 | 1 | 1 | 2610 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2958693.556 | 204668.7522 | 6634.6064 | 18996.6283 | 185672.1239 | 12283.4247 | 0.099443 | -94849.3495 | 94849.3495
C | Xist Rating 3379 | -37.38 | 1445.44 | 150.285 | 35.6 | 2048.87 | 8559.91 | 10537.7 | 0.29 | 1.25 | 15.729 | 11.325 | 1 | 1 | 2620 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2961518.6528 | 206167.0367 | 6685.5437 | 19069.4123 | 187097.6244 | 12296.6892 | 0.099824 | -94951.7749 | 94951.7749
C | Xist Rating 3380 | -37.36 | 1446.87 | 150.285 | 35.6 | 2048.12 | 8546.91 | 10537.8 | 0.29 | 1.25 | 15.767 | 11.335 | 1 | 1 | 2630 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2963363.3844 | 207670.7725 | 6736.6758 | 19142.1963 | 188528.5762 | 12310.418 | 0.10021 | -95057.7847 | 95057.7847
C | Xist Rating 3381 | -37.34 | 1448.11 | 150.285 | 35.6 | 2048.19 | 8548.12 | 10537.7 | 0.28 | 1.25 | 15.762 | 11.344 | 1 | 1 | 2640 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2966004.4209 | 209179.9595 | 6788.0027 | 19214.9803 | 189964.9792 | 12302.9902 | 0.10059 | -95000.429 | 95000.429
C | Xist Rating 3382 | -37.32 | 1449.62 | 150.285 | 35.6 | 2047.46 | 8535.32 | 10537.7 | 0.28 | 1.25 | 15.758 | 11.355 | 1 | 1 | 2650 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2968038.9652 | 210694.5978 | 6839.5243 | 19287.7644 | 191406.8334 | 12316.2589 | 0.10097 | -95102.8865 | 95102.8865
C | Xist Rating 3383 | -37.28 | 1450.96 | 150.285 | 35.6 | 2047.57 | 8537.27 | 10537.7 | 0.28 | 1.25 | 15.754 | 11.365 | 1 | 1 | 2660 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2970942.1672 | 212214.6873 | 6891.2408 | 19360.5484 | 192854.1389 | 12328.4881 | 0.10135 | -95197.3173 | 95197.3173
C | Xist Rating 3384 | -37.27 | 1452.34 | 150.285 | 35.6 | 2047.02 | 8527.85 | 10537.6 | 0.27 | 1.25 | 15.75 | 11.375 | 1 | 1 | 2670 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2972969.0268 | 213740.2281 | 6943.152 | 19433.3324 | 194306.8957 | 12321.8664 | 0.10173 | -95146.1865 | 95146.1865
C | Xist Rating 3385 | -37.23 | 1453.76 | 150.286 | 35.6 | 2047.19 | 8530.87 | 10537.6 | 0.27 | 1.25 | 15.787 | 11.385 | 1 | 1 | 2680 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2976122.9344 | 215271.2201 | 6995.258 | 19506.1164 | 195765.1037 | 12335.3577 | 0.10211 | -95250.3623 | 95250.3623
C | Xist Rating 3386 | -37.19 | 1455.14 | 150.286 | 35.6 | 2047.39 | 8534.38 | 10537.6 | 0.27 | 1.25 | 15.783 | 11.394 | 1 | 1 | 2690 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2979239.0846 | 216807.6633 | 7047.5588 | 19578.9004 | 197228.7629 | 12346.4846 | 0.10249 | -95336.2813 | 95336.2813
C | Xist Rating 3387 | -37.15 | 1456.34 | 150.286 | 35.6 | 2047.61 | 8538.08 | 10537.5 | 0.26 | 1.25 | 15.775 | 11.403 | 1 | 1 | 2700 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2982016.3474 | 218349.5578 | 7100.0544 | 19651.6844 | 198697.8734 | 12338.3879 | 0.10287 | -95273.7607 | 95273.7607
C | Xist Rating 3388 | -37.13 | 1457.99 | 150.286 | 35.6 | 2046.61 | 8520.7 | 10537.6 | 0.26 | 1.25 | 15.771 | 11.414 | 1 | 1 | 2710 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2983936.9139 | 219896.9036 | 7152.7448 | 19724.4685 | 200172.4351 | 12351.5235 | 0.10325 | -95375.1906 | 95375.1906
C | Xist Rating 3389 | -37.13 | 1459.34 | 150.286 | 35.6 | 2045.69 | 8504.92 | 10537.6 | 0.26 | 1.25 | 15.765 | 11.424 | 1 | 1 | 2720 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2985357.2446 | 221449.7005 | 7205.63 | 19797.2525 | 201652.4481 | 12363.5563 | 0.10363 | -95468.1047 | 95468.1047
C | Xist Rating 3390 | -37.1 | 1460.66 | 150.286 | 35.6 | 2045.43 | 8500.4 | 10537.5 | 0.25 | 1.25 | 15.801 | 11.433 | 1 | 1 | 2730 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2987677.7838 | 223007.9488 | 7258.71 | 19870.0365 | 203137.9123 | 12356.5496 | 0.10402 | -95414.0009 | 95414.0009
C | Xist Rating 3391 | -37.13 | 1461.94 | 150.286 | 35.6 | 2043.81 | 8472.46 | 10537.5 | 0.25 | 1.25 | 15.795 | 11.443 | 1 | 1 | 2740 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2987927.5914 | 224571.6482 | 7311.9847 | 19942.8205 | 204628.8277 | 12368.5211 | 0.1044 | -95506.4412 | 95506.4412
C | Xist Rating 3392 | -37.1 | 1463.49 | 150.286 | 35.6 | 2043.13 | 8460.65 | 10537.6 | 0.25 | 1.25 | 15.796 | 11.453 | 1 | 1 | 2750 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2990100.3237 | 226140.799 | 7365.4543 | 20015.6045 | 206125.1944 | 12380.7069 | 0.10478 | -95600.5368 | 95600.5368
C | Xist Rating 3393 | -37.06 | 1464.92 | 150.286 | 35.6 | 2042.92 | 8457.06 | 10537.7 | 0.24 | 1.25 | 15.796 | 11.463 | 1 | 1 | 2760 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2992714.3664 | 227715.4009 | 7419.1186 | 20088.3885 | 207627.0124 | 12373.3198 | 0.10516 | -95543.4958 | 95543.4958
C | Xist Rating 3394 | -37.06 | 1466.15 | 150.286 | 35.6 | 2042.23 | 8445.33 | 10537.7 | 0.24 | 1.25 | 15.793 | 11.472 | 1 | 1 | 2770 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2994215.5145 | 229295.4541 | 7472.9777 | 20161.1726 | 209134.2816 | 12384.2762 | 0.10554 | -95628.0982 | 95628.0982
C | Xist Rating 3395 | -36.98 | 1467.7 | 150.286 | 35.6 | 2043.01 | 8458.5 | 10537.8 | 0.24 | 1.25 | 15.837 | 11.482 | 1 | 1 | 2780 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 2998525.777 | 230880.9586 | 7527.0316 | 20233.9566 | 210647.002 | 12397.6761 | 0.10592 | -95731.5686 | 95731.5686
C | Xist Rating 3396 | -36.88 | 1469.11 | 150.286 | 35.6 | 2045.15 | 8495.28 | 10537.9 | 0.23 | 1.25 | 15.844 | 11.492 | 1 | 1 | 2790 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3004550.3165 | 232471.9143 | 7581.2803 | 20306.7406 | 212165.1737 | 12390.1603 | 0.1063 | -95673.5335 | 95673.5335
C | Xist Rating 3397 | -36.76 | 1470.08 | 150.286 | 35.6 | 2048.6 | 8555 | 10538 | 0.23 | 1.25 | 15.852 | 11.5 | 1 | 1 | 2800 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3011605.888 | 234068.3212 | 7635.7238 | 20379.5246 | 213688.7966 | 12400.3327 | 0.10668 | -95752.082 | 95752.082
C | Xist Rating 3398 | -36.57 | 1471.83 | 150.286 | 35.6 | 2052.91 | 8630.65 | 10538.1 | 0.23 | 1.25 | 15.875 | 11.512 | 1 | 1 | 2810 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3021534.5253 | 235670.1794 | 7690.3621 | 20452.3086 | 215217.8708 | 12415.0953 | 0.10706 | -95866.0748 | 95866.0748
C | Xist Rating 3399 | -36.85 | 1473.3 | 150.286 | 35.6 | 2042.97 | 8457.87 | 10537.8 | 0.23 | 1.25 | 15.829 | 11.521 | 1 | 1 | 2820 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3009907.701 | 237277.4888 | 7745.1952 | 20525.0926 | 216752.3962 | 12424.741 | 0.10744 | -95940.5569 | 95940.5569
C | Xist Rating 3400 | -36.49 | 1474.67 | 150.286 | 35.6 | 2053.67 | 8644.1 | 10538 | 0.22 | 1.25 | 15.917 | 11.531 | 1 | 1 | 2830 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3028485.5389 | 238890.2495 | 7800.223 | 20597.8767 | 218292.3728 | 12419.1342 | 0.10783 | -95897.262 | 95897.262
C | Xist Rating 3401 | -36.09 | 1475.99 | 150.286 | 35.6 | 2065.65 | 8860.35 | 10538.2 | 0.22 | 1.25 | 15.985 | 11.541 | 1 | 1 | 2840 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3048878.7435 | 240508.4614 | 7855.4457 | 20670.6607 | 219837.8008 | 12432.9932 | 0.10821 | -96004.278 | 96004.278
C | Xist Rating 3402 | -35.69 | 1477.43 | 150.286 | 35.6 | 2077.62 | 9084.79 | 10538.2 | 0.21 | 1.25 | 16.048 | 11.552 | 1 | 1 | 2850 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3069538.1166 | 242132.1246 | 7910.8631 | 20743.4447 | 221388.6799 | 12427.2623 | 0.10859 | -95960.0254 | 95960.0254
C | Xist Rating 3403 | -35.54 | 1478.84 | 150.286 | 35.6 | 2081.17 | 9153.06 | 10538.2 | 0.21 | 1.25 | 16.059 | 11.561 | 1 | 1 | 2860 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3077717.4428 | 243761.239 | 7966.4753 | 20816.2287 | 222945.0103 | 12438.4156 | 0.10897 | -96046.1479 | 96046.1479
C | Xist Rating 3404 | -35.37 | 1480.03 | 150.286 | 35.6 | 2086.05 | 9248.22 | 10538.2 | 0.21 | 1.25 | 16.074 | 11.57 | 1 | 1 | 2870 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3087416.5815 | 245395.8047 | 8022.2824 | 20889.0127 | 224506.7919 | 12449.6789 | 0.10935 | -96133.1207 | 96133.1207
C | Xist Rating 3405 | -35.26 | 1481.54 | 150.286 | 35.6 | 2088.29 | 9292.5 | 10538.2 | 0.21 | 1.25 | 16.122 | 11.58 | 1 | 1 | 2880 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3093885.1666 | 247035.8216 | 8078.2842 | 20961.7967 | 226074.0248 | 12462.8783 | 0.10973 | -96235.0425 | 96235.0425
C | Xist Rating 3406 | -35.15 | 1482.88 | 150.286 | 35.6 | 2090.72 | 9340.82 | 10538.2 | 0.2 | 1.25 | 16.127 | 11.589 | 1 | 1 | 2890 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3100286.8736 | 248681.2897 | 8134.4807 | 21034.5808 | 227646.7089 | 12452.9869 | 0.11011 | -96158.6642 | 96158.6642
C | Xist Rating 3407 | -35.04 | 1484.27 | 150.286 | 35.6 | 2093.06 | 9387.67 | 10538.2 | 0.2 | 1.25 | 16.132 | 11.599 | 1 | 1 | 2900 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3106666.1662 | 250332.2091 | 8190.8721 | 21107.3648 | 229224.8443 | 12464.9477 | 0.11049 | -96251.022 | 96251.022
C | Xist Rating 3408 | -34.94 | 1485.81 | 150.286 | 35.6 | 2095.1 | 9428.78 | 10538.1 | 0.2 | 1.25 | 16.136 | 11.609 | 1 | 1 | 2910 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3112920.531 | 251988.5797 | 8247.4583 | 21180.1488 | 230808.4309 | 12476.8832 | 0.11087 | -96343.1852 | 96343.1852
C | Xist Rating 3409 | -34.84 | 1487.2 | 150.286 | 35.5 | 2096.91 | 9465.66 | 10538.1 | 0.2 | 1.25 | 16.14 | 11.618 | 1 | 1 | 2920 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3118524.552 | 253650.4016 | 8304.2393 | 21252.9328 | 232397.4688 | 12487.781 | 0.11125 | -96427.3349 | 96427.3349
C | Xist Rating 3410 | -34.72 | 1488.59 | 150.286 | 35.5 | 2099.8 | 9524.87 | 10538.1 | 0.19 | 1.25 | 16.188 | 11.628 | 1 | 1 | 2930 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3125741.282 | 255317.6747 | 8361.215 | 21325.7168 | 233991.9579 | 12479.6131 | 0.11164 | -96364.2641 | 96364.2641
C | Xist Rating 3411 | -34.5 | 1489.95 | 150.286 | 35.5 | 2106.06 | 9655.11 | 10537.9 | 0.19 | 1.25 | 16.196 | 11.637 | 1 | 1 | 2940 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3137924.097 | 256990.3991 | 8418.3855 | 21398.5008 | 235591.8983 | 12490.5385 | 0.11202 | -96448.6278 | 96448.6278
C | Xist Rating 3412 | -34.48 | 1491.36 | 150.286 | 35.5 | 2105.36 | 9640.51 | 10537.9 | 0.19 | 1.25 | 16.192 | 11.646 | 1 | 1 | 2950 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3139849.6896 | 258668.5747 | 8475.7509 | 21471.2849 | 237197.2899 | 12501.1639 | 0.1124 | -96530.6739 | 96530.6739
C | Xist Rating 3413 | -34.46 | 1492.73 | 150.286 | 35.5 | 2104.82 | 9629.2 | 10537.9 | 0.19 | 1.25 | 16.187 | 11.655 | 1 | 1 | 2960 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3141927.9586 | 260352.2016 | 8533.311 | 21544.0689 | 238808.1327 | 12511.7634 | 0.11278 | -96612.5201 | 96612.5201
C | Xist Rating 3414 | -34.45 | 1494.12 | 150.286 | 35.5 | 2104.17 | 9615.59 | 10537.9 | 0.18 | 1.25 | 16.184 | 11.664 | 1 | 1 | 2970 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3143882.4804 | 262041.2797 | 8591.0659 | 21616.8529 | 240424.4268 | 12500.8669 | 0.11316 | -96528.3808 | 96528.3808
C | Xist Rating 3415 | -34.44 | 1495.34 | 150.286 | 35.5 | 2103.56 | 9602.78 | 10537.9 | 0.18 | 1.25 | 16.22 | 11.673 | 1 | 1 | 2980 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3145537.4104 | 263735.809 | 8649.0156 | 21689.6369 | 242046.1721 | 12512.3848 | 0.11354 | -96617.3187 | 96617.3187
C | Xist Rating 3416 | -34.42 | 1496.9 | 150.286 | 35.5 | 2102.84 | 9587.83 | 10537.9 | 0.18 | 1.25 | 16.215 | 11.682 | 1 | 1 | 2990 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3147741.196 | 265435.7896 | 8707.16 | 21762.4209 | 243673.3687 | 12522.9194 | 0.11392 | -96698.6638 | 96698.6638
C | Xist Rating 3417 | -34.4 | 1498.33 | 150.286 | 35.5 | 2102.21 | 9574.78 | 10537.9 | 0.18 | 1.25 | 16.211 | 11.692 | 1 | 1 | 3000 | 152.4 | 2 | 2.6 | 19.05 | 1.3333 | 14 | E | Rod | 3149804.3093 | 267141.2215 | 8765.4993 | 21835.2049 | 245306.0165 | 12534.5158 | 0.1143 | -96788.2086 | 96788.2086
C | Xist Rating 3418 | -92.14 | 144.094 | 150.289 | 35.8 | 2398.15 | 7390.02 | 58745.8 | 2.45 | 10.95 | 17.144 | 417.309 | 1 | 1 | 1000 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 345559.0261 | 35862.8805 | 973.9444 | 7558.3402 | 28304.5404 | 435257.4975 | 0.038101 | -3360943.0217 | 3360943.0217
C | Xist Rating 3419 | -92.07 | 145.61 | 150.289 | 35.8 | 2395.22 | 7370.74 | 58284.2 | 2.43 | 10.85 | 17.176 | 409.504 | 1 | 1 | 1010 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 348767.9842 | 36507.3852 | 993.5206 | 7633.9236 | 28873.4616 | 427158.8422 | 0.038482 | -3298407.3522 | 3298407.3522
C | Xist Rating 3420 | -91.48 | 156.981 | 150.289 | 35.8 | 2388.32 | 7369.92 | 54967.6 | 2.44 | 10.07 | 17.228 | 354.872 | 1 | 1 | 1020 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 374920.8619 | 37157.5508 | 1013.2917 | 7709.507 | 29448.0438 | 370455.9595 | 0.038863 | -2860562.7223 | 2860562.7223
C | Xist Rating 3421 | -91.38 | 160.159 | 150.288 | 35.8 | 2368.2 | 7197.34 | 54179.2 | 2.36 | 9.89 | 16.888 | 343.06 | 1 | 1 | 1030 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 379288.5438 | 37813.3773 | 1033.2576 | 7785.0904 | 30028.2869 | 358107.38 | 0.039244 | -2765210.2646 | 2765210.2646
C | Xist Rating 3422 | -91.32 | 161.749 | 150.288 | 35.8 | 2363.33 | 7160.33 | 53793.7 | 2.31 | 9.8 | 16.8 | 337.402 | 1 | 1 | 1040 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 382266.2642 | 38474.8646 | 1053.4182 | 7860.6738 | 30614.1909 | 352200.5808 | 0.039625 | -2719599.5265 | 2719599.5265
C | Xist Rating 3423 | -91.13 | 164.805 | 150.288 | 35.8 | 2371.71 | 7253.67 | 53043.5 | 2.26 | 9.63 | 16.763 | 326.274 | 1 | 1 | 1050 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 390869.6666 | 39142.0129 | 1073.7737 | 7936.2572 | 31205.7558 | 340618.0949 | 0.040006 | -2630162.641 | 2630162.641
C | Xist Rating 3424 | -90.99 | 166.376 | 150.288 | 35.8 | 2385.79 | 7395.27 | 52677.2 | 2.21 | 9.54 | 16.754 | 321.019 | 1 | 1 | 1060 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 396938.197 | 39814.8221 | 1094.3239 | 8011.8406 | 31802.9816 | 335136.9982 | 0.040387 | -2587839.0653 | 2587839.0653
C | Xist Rating 3425 | -90.42 | 178.66 | 150.287 | 35.8 | 2365.72 | 7270.48 | 49857.4 | 2.2 | 8.9 | 16.644 | 280.923 | 1 | 1 | 1070 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 422659.5352 | 40493.2923 | 1115.0689 | 8087.424 | 32405.8683 | 293494.32 | 0.040768 | -2266285.3426 | 2266285.3426
C | Xist Rating 3426 | -90.26 | 181.02 | 150.287 | 35.8 | 2372.67 | 7348.51 | 49381.3 | 2.14 | 8.79 | 16.574 | 274.672 | 1 | 1 | 1080 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 429500.7234 | 41177.4233 | 1136.0087 | 8163.0074 | 33014.4159 | 286963.4831 | 0.041149 | -2215855.9508 | 2215855.9508
C | Xist Rating 3427 | -90.1 | 184.156 | 150.287 | 35.8 | 2373.52 | 7372.71 | 48762.6 | 2.09 | 8.65 | 16.466 | 266.637 | 1 | 1 | 1090 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 437097.9491 | 41867.2152 | 1157.1433 | 8238.5908 | 33628.6244 | 278583.5291 | 0.04153 | -2151148.1673 | 2151148.1673
C | Xist Rating 3428 | -89.95 | 186.484 | 150.287 | 35.8 | 2379.13 | 7439.37 | 48308.7 | 2.05 | 8.55 | 16.454 | 260.82 | 1 | 1 | 1100 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 443669.6789 | 42562.668 | 1178.4727 | 8314.1742 | 34248.4938 | 272524.3211 | 0.041911 | -2104360.5695 | 2104360.5695
C | Xist Rating 3429 | -89.89 | 188.243 | 150.286 | 35.8 | 2373.83 | 7395.9 | 48010.8 | 1.97 | 8.49 | 16.238 | 257.308 | 1 | 1 | 1110 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 446856.8807 | 43263.7818 | 1199.9969 | 8389.7576 | 34874.0242 | 268805.5685 | 0.042292 | -2075645.3472 | 2075645.3472
C | Xist Rating 3430 | -89.17 | 201.868 | 150.287 | 35.8 | 2371.07 | 7443.2 | 45448.2 | 2.01 | 7.92 | 16.433 | 225.145 | 1 | 1 | 1120 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 478643.1588 | 43970.5564 | 1221.7158 | 8465.341 | 35505.2154 | 235470.9683 | 0.042673 | -1818244.4005 | 1818244.4005
C | Xist Rating 3431 | -89.1 | 203.58 | 150.286 | 35.8 | 2369.67 | 7437.43 | 45189 | 1.95 | 7.86 | 16.293 | 222.307 | 1 | 1 | 1130 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 482417.4186 | 44682.992 | 1243.6296 | 8540.9244 | 36142.0676 | 232474.7458 | 0.043054 | -1795108.3649 | 1795108.3649
C | Xist Rating 3432 | -88.95 | 206.787 | 150.286 | 35.8 | 2364.89 | 7406.47 | 44681.2 | 1.9 | 7.75 | 16.164 | 216.554 | 1 | 1 | 1140 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 489028.5084 | 45401.0885 | 1265.7381 | 8616.5078 | 36784.5807 | 226460.3525 | 0.043435 | -1748666.8138 | 1748666.8138
C | Xist Rating 3433 | -88.77 | 209.931 | 150.286 | 35.8 | 2369.12 | 7464.1 | 44186.9 | 1.86 | 7.64 | 16.049 | 210.982 | 1 | 1 | 1150 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 497351.7307 | 46124.8458 | 1288.0414 | 8692.0912 | 37432.7546 | 220643.2504 | 0.043816 | -1703748.6932 | 1703748.6932
C | Xist Rating 3434 | -88.6 | 213.153 | 150.286 | 35.8 | 2369.94 | 7488.28 | 43704.1 | 1.8 | 7.53 | 15.948 | 205.69 | 1 | 1 | 1160 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 505159.8208 | 46854.2641 | 1310.5395 | 8767.6746 | 38086.5895 | 215101.3748 | 0.044197 | -1660955.7992 | 1660955.7992
C | Xist Rating 3435 | -87.95 | 225.424 | 150.286 | 35.8 | 2369.07 | 7546.1 | 41833.1 | 1.82 | 7.13 | 16.063 | 185.044 | 1 | 1 | 1170 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 534045.2357 | 47589.3433 | 1333.2324 | 8843.258 | 38746.0853 | 193701.1085 | 0.044578 | -1495708.6154 | 1495708.6154
C | Xist Rating 3436 | -87.86 | 226.373 | 150.286 | 35.8 | 2377.7 | 7638.47 | 41725.4 | 1.77 | 7.11 | 16.007 | 184.08 | 1 | 1 | 1180 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 538247.0821 | 48330.0834 | 1356.1201 | 8918.8414 | 39411.242 | 192665.3765 | 0.044959 | -1487710.9675 | 1487710.9675
C | Xist Rating 3437 | -87.59 | 232.645 | 150.286 | 35.8 | 2366.83 | 7559.68 | 40886.4 | 1.72 | 6.93 | 15.89 | 175.502 | 1 | 1 | 1190 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 550631.1654 | 49076.4844 | 1379.2026 | 8994.4248 | 40082.0596 | 183716.4108 | 0.04534 | -1418609.4266 | 1418609.4266
C | Xist Rating 3438 | -87.45 | 234.25 | 150.286 | 35.8 | 2378.99 | 7693.44 | 40682.7 | 1.69 | 6.88 | 15.91 | 173.508 | 1 | 1 | 1200 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 557278.4075 | 49828.5463 | 1402.4799 | 9070.0082 | 40758.5381 | 181634.0725 | 0.045721 | -1402530.1621 | 1402530.1621
C | Xist Rating 3439 | -87.3 | 237.541 | 150.285 | 35.8 | 2375.08 | 7669.21 | 40281.7 | 1.64 | 6.8 | 15.807 | 169.636 | 1 | 1 | 1210 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 564178.8783 | 50586.2692 | 1425.9519 | 9145.5916 | 41440.6776 | 177572.751 | 0.046102 | -1371169.7139 | 1371169.7139
C | Xist Rating 3440 | -86.63 | 251.521 | 150.285 | 35.8 | 2362.21 | 7610.72 | 38538.4 | 1.65 | 6.43 | 15.827 | 152.588 | 1 | 1 | 1220 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 594145.4214 | 51349.6529 | 1449.6188 | 9221.175 | 42128.4779 | 159890.4989 | 0.046483 | -1234632.0505 | 1234632.0505
C | Xist Rating 3441 | -86.43 | 254.662 | 150.285 | 35.8 | 2368.71 | 7695.01 | 38183.5 | 1.62 | 6.35 | 15.83 | 149.339 | 1 | 1 | 1230 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 603220.426 | 52118.6975 | 1473.4804 | 9296.7584 | 42821.9391 | 156502.213 | 0.046864 | -1208468.6042 | 1208468.6042
C | Xist Rating 3442 | -86.27 | 257.944 | 150.285 | 35.8 | 2367.64 | 7700.05 | 37835.8 | 1.58 | 6.28 | 15.761 | 146.268 | 1 | 1 | 1240 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 610718.5322 | 52893.4031 | 1497.5369 | 9372.3418 | 43521.0613 | 153283.2249 | 0.047245 | -1183612.4319 | 1183612.4319
C | Xist Rating 3443 | -86.17 | 259.693 | 150.285 | 35.8 | 2370.76 | 7741.43 | 37665.2 | 1.54 | 6.24 | 15.712 | 144.838 | 1 | 1 | 1250 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 615669.7767 | 53673.7695 | 1521.7881 | 9447.9252 | 44225.8443 | 151769.7824 | 0.047626 | -1171926.0302 | 1171926.0302
C | Xist Rating 3444 | -85.94 | 264.429 | 150.285 | 35.8 | 2368.75 | 7744.78 | 37162.2 | 1.51 | 6.14 | 15.678 | 140.376 | 1 | 1 | 1260 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 626366.1937 | 54459.7969 | 1546.2341 | 9523.5086 | 44936.2883 | 147117.3269 | 0.048007 | -1136001.0016 | 1136001.0016
C | Xist Rating 3445 | -85.29 | 277.675 | 150.285 | 35.8 | 2360.4 | 7727.06 | 35778.2 | 1.52 | 5.85 | 15.734 | 128.236 | 1 | 1 | 1270 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 655424.07 | 55251.4852 | 1570.8749 | 9599.092 | 45652.3932 | 134534.3385 | 0.048388 | -1038838.5005 | 1038838.5005
C | Xist Rating 3446 | -85.14 | 281.025 | 150.285 | 35.8 | 2357.82 | 7715.57 | 35477.9 | 1.48 | 5.79 | 15.665 | 125.84 | 1 | 1 | 1280 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 662606.3655 | 56048.8344 | 1595.7105 | 9674.6754 | 46374.1589 | 132014.8473 | 0.048769 | -1019383.6576 | 1019383.6576
C | Xist Rating 3447 | -84.96 | 284.323 | 150.285 | 35.8 | 2359.89 | 7754.14 | 35183.3 | 1.44 | 5.73 | 15.649 | 123.495 | 1 | 1 | 1290 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 670971.0045 | 56851.8444 | 1620.7408 | 9750.2588 | 47101.5856 | 129552.3961 | 0.04915 | -1000369.2621 | 1000369.2621
C | Xist Rating 3448 | -84.68 | 289.037 | 150.285 | 35.8 | 2366.13 | 7846.77 | 34751.8 | 1.42 | 5.64 | 15.666 | 120.005 | 1 | 1 | 1300 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 683899.1168 | 57660.5154 | 1645.966 | 9825.8422 | 47834.6732 | 125921.3064 | 0.049531 | -972330.9496 | 972330.9496
C | Xist Rating 3449 | -84.52 | 291.59 | 150.285 | 35.8 | 2370.58 | 7908.62 | 34540.6 | 1.38 | 5.59 | 15.629 | 118.402 | 1 | 1 | 1310 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 691237.4222 | 58474.8473 | 1671.3859 | 9901.4256 | 48573.4217 | 124226.7702 | 0.049912 | -959246.1907 | 959246.1907
C | Xist Rating 3450 | -83.85 | 304.934 | 150.285 | 35.8 | 2365.93 | 7930.22 | 33363.8 | 1.39 | 5.35 | 15.678 | 109.079 | 1 | 1 | 1320 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 721452.4986 | 59294.8402 | 1697.0007 | 9977.009 | 49317.8311 | 114567.7947 | 0.050293 | -884662.1418 | 884662.1418
C | Xist Rating 3451 | -83.63 | 309.865 | 150.285 | 35.7 | 2361.16 | 7901.82 | 32980.7 | 1.35 | 5.28 | 15.576 | 106.269 | 1 | 1 | 1330 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 731640.8434 | 60120.4939 | 1722.8102 | 10052.5924 | 50067.9015 | 111613.7864 | 0.050674 | -861852.0728 | 861852.0728
C | Xist Rating 3452 | -83.37 | 314.695 | 150.285 | 35.8 | 2362.09 | 7937.37 | 32607.9 | 1.32 | 5.2 | 15.553 | 103.546 | 1 | 1 | 1340 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 743337.9126 | 60951.8085 | 1748.8145 | 10128.1758 | 50823.6327 | 108765.49 | 0.051055 | -839858.283 | 839858.283
C | Xist Rating 3453 | -83.22 | 317.264 | 150.285 | 35.7 | 2366.13 | 7995.91 | 32424.5 | 1.29 | 5.16 | 15.523 | 102.28 | 1 | 1 | 1350 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 750687.8683 | 61788.7841 | 1775.0136 | 10203.7592 | 51585.0248 | 107429.3767 | 0.051436 | -829541.1705 | 829541.1705
C | Xist Rating 3454 | -83.03 | 318.815 | 150.285 | 35.7 | 2382.09 | 8189.96 | 32304.4 | 1.28 | 5.14 | 15.574 | 101.416 | 1 | 1 | 1360 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 759446.0234 | 62631.4205 | 1801.4075 | 10279.3426 | 52352.0779 | 106535.6066 | 0.051817 | -822639.7144 | 822639.7144
C | Xist Rating 3455 | -82.23 | 337.869 | 150.285 | 35.7 | 2355.31 | 7983.45 | 30903.1 | 1.27 | 4.86 | 15.537 | 91.448 | 1 | 1 | 1370 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 795786.2344 | 63479.7179 | 1827.9962 | 10354.926 | 53124.7918 | 96180.3404 | 0.052198 | -742679.0939 | 742679.0939
C | Xist Rating 3456 | -82.15 | 339.682 | 150.285 | 35.7 | 2355.09 | 7989.2 | 30794.6 | 1.25 | 4.84 | 15.508 | 90.784 | 1 | 1 | 1380 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 799981.6814 | 64333.6761 | 1854.7797 | 10430.5094 | 53903.1667 | 95478.1581 | 0.052579 | -737257.0285 | 737257.0285
C | Xist Rating 3457 | -81.94 | 343.825 | 150.285 | 35.7 | 2355.53 | 8015.23 | 30527.4 | 1.22 | 4.78 | 15.48 | 89.037 | 1 | 1 | 1390 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 809890.1022 | 65193.2953 | 1881.7579 | 10506.0928 | 54687.2024 | 93641.4749 | 0.05296 | -723074.6475 | 723074.6475
C | Xist Rating 3458 | -81.72 | 347.964 | 150.285 | 35.7 | 2356.45 | 8047.03 | 30265.5 | 1.2 | 4.73 | 15.457 | 87.343 | 1 | 1 | 1400 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 819959.7678 | 66058.5754 | 1908.931 | 10581.6762 | 55476.8991 | 91869.5632 | 0.053341 | -709392.4148 | 709392.4148
C | Xist Rating 3459 | -81.47 | 352.855 | 150.285 | 35.7 | 2357.13 | 8080.38 | 29957.7 | 1.18 | 4.67 | 15.44 | 85.357 | 1 | 1 | 1410 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 831725.1062 | 66929.5163 | 1936.2988 | 10657.2596 | 56272.2567 | 89794.6132 | 0.053722 | -693370.2012 | 693370.2012
C | Xist Rating 3460 | -80.77 | 367.077 | 150.285 | 35.7 | 2352.27 | 8101.34 | 29052.1 | 1.18 | 4.49 | 15.499 | 79.463 | 1 | 1 | 1420 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 863464.2148 | 67806.1182 | 1963.8614 | 10732.843 | 57073.2752 | 83686.3016 | 0.054103 | -646203.4382 | 646203.4382
C | Xist Rating 3461 | -80.66 | 369.887 | 150.285 | 35.7 | 2349.38 | 8079.68 | 28911.2 | 1.15 | 4.47 | 15.44 | 78.679 | 1 | 1 | 1430 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 869005.1201 | 68688.381 | 1991.6188 | 10808.4264 | 57879.9546 | 82846.1634 | 0.054484 | -639716.1135 | 639716.1135
C | Xist Rating 3462 | -80.35 | 376.329 | 150.284 | 35.7 | 2347.4 | 8089.88 | 28542.4 | 1.13 | 4.39 | 15.427 | 76.429 | 1 | 1 | 1440 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 883394.6946 | 69576.3048 | 2019.571 | 10884.0098 | 58692.2949 | 80496.6205 | 0.054865 | -621573.5664 | 621573.5664
C | Xist Rating 3463 | -80.14 | 380.506 | 150.284 | 35.7 | 2347.13 | 8107.71 | 28317.1 | 1.11 | 4.35 | 15.406 | 75.108 | 1 | 1 | 1450 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 893097.0478 | 70469.8894 | 2047.718 | 10959.5932 | 59510.2961 | 79111.0093 | 0.055246 | -610874.2441 | 610874.2441
C | Xist Rating 3464 | -79.96 | 382.957 | 150.284 | 35.7 | 2354.28 | 8206.62 | 28183.9 | 1.1 | 4.32 | 15.42 | 74.332 | 1 | 1 | 1460 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 901588.006 | 71369.1349 | 2076.0598 | 11035.1767 | 60333.9582 | 78303.7254 | 0.055627 | -604640.6116 | 604640.6116
C | Xist Rating 3465 | -79.27 | 399.158 | 150.284 | 35.7 | 2338.32 | 8100.55 | 27310.5 | 1.09 | 4.16 | 15.419 | 69.171 | 1 | 1 | 1470 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 933359.1346 | 72274.0413 | 2104.5964 | 11110.7601 | 61163.2813 | 72941.4058 | 0.056008 | -563234.2012 | 563234.2012
C | Xist Rating 3466 | -79.02 | 404.093 | 150.284 | 35.7 | 2338.61 | 8129.1 | 27066.5 | 1.07 | 4.11 | 15.407 | 67.81 | 1 | 1 | 1480 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 945015.9307 | 73184.6087 | 2133.3277 | 11186.3435 | 61998.2652 | 71514.2331 | 0.056389 | -552213.952 | 552213.952
C | Xist Rating 3467 | -78.78 | 408.272 | 150.284 | 35.7 | 2341.74 | 8188.2 | 26867.1 | 1.05 | 4.07 | 15.402 | 66.723 | 1 | 1 | 1490 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 956066.8733 | 74100.8369 | 2162.2539 | 11261.9269 | 62838.9101 | 70371.844 | 0.05677 | -543392.7259 | 543392.7259
C | Xist Rating 3468 | -78.54 | 412.544 | 150.284 | 35.7 | 2344.96 | 8249.08 | 26670.6 | 1.03 | 4.03 | 15.387 | 65.676 | 1 | 1 | 1500 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 967399.1782 | 75022.7261 | 2191.3748 | 11337.5103 | 63685.2158 | 69270.0348 | 0.057151 | -534884.8469 | 534884.8469
C | Xist Rating 3469 | -78.24 | 417.505 | 150.284 | 35.7 | 2350.61 | 8345.56 | 26439.1 | 1.01 | 3.99 | 15.389 | 64.43 | 1 | 1 | 1510 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 981391.428 | 75950.2762 | 2220.6906 | 11413.0937 | 64537.1825 | 67962.4771 | 0.057532 | -524788.2332 | 524788.2332
C | Xist Rating 3470 | -77.44 | 433.389 | 150.285 | 35.7 | 2348.35 | 8407.02 | 25681.3 | 1.02 | 3.85 | 15.457 | 60.279 | 1 | 1 | 1520 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1017749.0581 | 76883.4871 | 2250.2011 | 11488.6771 | 65394.8101 | 63673.848 | 0.057913 | -491672.5761 | 491672.5761
C | Xist Rating 3471 | -77.24 | 438.694 | 150.284 | 35.7 | 2341.84 | 8350.05 | 25468.7 | 0.99 | 3.8 | 15.407 | 59.233 | 1 | 1 | 1530 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1027351.157 | 77822.359 | 2279.9064 | 11564.2605 | 66258.0985 | 62559.4489 | 0.058294 | -483067.482 | 483067.482
C | Xist Rating 3472 | -77.06 | 441.42 | 150.284 | 35.7 | 2346.94 | 8428.59 | 25363.8 | 0.97 | 3.79 | 15.398 | 58.739 | 1 | 1 | 1540 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1035986.2548 | 78766.8918 | 2309.8065 | 11639.8439 | 67127.0479 | 62031.3943 | 0.058675 | -478989.9838 | 478989.9838
C | Xist Rating 3473 | -76.66 | 449.538 | 150.284 | 35.7 | 2345.78 | 8457.78 | 25021.4 | 0.96 | 3.72 | 15.394 | 56.995 | 1 | 1 | 1550 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1054517.2496 | 79717.0855 | 2339.9013 | 11715.4273 | 68001.6582 | 60215.983 | 0.059056 | -464971.8593 | 464971.8593
C | Xist Rating 3474 | -76.44 | 452.039 | 150.285 | 35.7 | 2356.48 | 8612.3 | 24920.7 | 0.95 | 3.7 | 15.414 | 56.508 | 1 | 1 | 1560 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1065220.8627 | 80672.9401 | 2370.191 | 11791.0107 | 68881.9294 | 59707.4227 | 0.059437 | -461044.8914 | 461044.8914
C | Xist Rating 3475 | -75.67 | 470.874 | 150.284 | 35.7 | 2337.01 | 8460.26 | 24162.3 | 0.94 | 3.56 | 15.412 | 52.737 | 1 | 1 | 1570 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1100437.2467 | 81634.4556 | 2400.6755 | 11866.5941 | 69767.8616 | 55786.8291 | 0.059818 | -430771.1069 | 430771.1069
C | Xist Rating 3476 | -75.43 | 475.174 | 150.284 | 35.7 | 2339.71 | 8518.01 | 24007.6 | 0.92 | 3.53 | 15.404 | 52.028 | 1 | 1 | 1580 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1111769.3595 | 82601.632 | 2431.3547 | 11942.1775 | 70659.4546 | 55034.6759 | 0.0602 | -424963.1791 | 424963.1791
C | Xist Rating 3477 | -75.2 | 479.509 | 150.284 | 35.7 | 2341.38 | 8562.49 | 23855.3 | 0.91 | 3.5 | 15.392 | 51.338 | 1 | 1 | 1590 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1122712.7824 | 83574.4694 | 2462.2288 | 12017.7609 | 71556.7085 | 54312.7075 | 0.060581 | -419388.3305 | 419388.3305
C | Xist Rating 3478 | -74.86 | 485.252 | 150.285 | 35.7 | 2346.09 | 8657.72 | 23645.6 | 0.9 | 3.46 | 15.4 | 50.363 | 1 | 1 | 1600 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1138444.8647 | 84552.9676 | 2493.2976 | 12093.3443 | 72459.6233 | 53295.9273 | 0.060962 | -411537.0235 | 411537.0235
C | Xist Rating 3479 | -74.71 | 488.173 | 150.284 | 35.7 | 2347.22 | 8686.98 | 23556.9 | 0.87 | 3.45 | 15.38 | 50.003 | 1 | 1 | 1610 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1145849.4291 | 85537.1268 | 2524.5612 | 12168.9277 | 73368.1991 | 52893.6834 | 0.061343 | -408431.0025 | 408431.0025
C | Xist Rating 3480 | -73.79 | 509.173 | 150.285 | 35.7 | 2333.08 | 8614.17 | 22805.3 | 0.88 | 3.31 | 15.398 | 46.518 | 1 | 1 | 1620 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1187941.3428 | 86526.9468 | 2556.0196 | 12244.5111 | 74282.4357 | 49292.8328 | 0.061724 | -380626.1886 | 380626.1886
C | Xist Rating 3481 | -73.57 | 511.749 | 150.285 | 35.7 | 2342.23 | 8754.06 | 22723.7 | 0.87 | 3.29 | 15.421 | 46.177 | 1 | 1 | 1630 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1198633.8603 | 87522.4278 | 2587.6728 | 12320.0945 | 75202.3333 | 48934.9903 | 0.062105 | -377863.0235 | 377863.0235
C | Xist Rating 3482 | -73.36 | 516.232 | 150.285 | 35.7 | 2341.22 | 8763.08 | 22589 | 0.85 | 3.27 | 15.401 | 45.623 | 1 | 1 | 1640 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1208612.683 | 88523.5697 | 2619.5208 | 12395.6779 | 76127.8918 | 48341.7535 | 0.062486 | -373282.2066 | 373282.2066
C | Xist Rating 3483 | -73.1 | 522.332 | 150.285 | 35.7 | 2337.8 | 8747.55 | 22403.3 | 0.83 | 3.24 | 15.368 | 44.847 | 1 | 1 | 1650 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1221107.7496 | 89530.3724 | 2651.5635 | 12471.2613 | 77059.1111 | 47516.9395 | 0.062867 | -366913.2116 | 366913.2116
C | Xist Rating 3484 | -72.79 | 528.189 | 150.285 | 35.7 | 2339.13 | 8798.69 | 22221.2 | 0.82 | 3.2 | 15.368 | 44.076 | 1 | 1 | 1660 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1235502.7356 | 90542.8361 | 2683.8011 | 12546.8447 | 77995.9914 | 46710.5397 | 0.063248 | -360686.4056 | 360686.4056
C | Xist Rating 3485 | -71.97 | 547.068 | 150.285 | 35.7 | 2327.52 | 8742.95 | 21633.2 | 0.82 | 3.1 | 15.395 | 41.565 | 1 | 1 | 1670 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1273311.7114 | 91560.9607 | 2716.2334 | 12622.4281 | 78938.5326 | 44110.1762 | 0.063629 | -340607.0879 | 340607.0879
C | Xist Rating 3486 | -71.79 | 549.755 | 150.285 | 35.7 | 2332.86 | 8832.74 | 21560.7 | 0.81 | 3.08 | 15.398 | 41.291 | 1 | 1 | 1680 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1282501.4493 | 92584.7462 | 2748.8606 | 12698.0115 | 79886.7347 | 43819.8759 | 0.06401 | -338365.4666 | 338365.4666
C | Xist Rating 3487 | -71.46 | 557.523 | 150.285 | 35.7 | 2327.57 | 8798.54 | 21346.3 | 0.79 | 3.04 | 15.374 | 40.443 | 1 | 1 | 1690 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1297673.8091 | 93614.1926 | 2781.6825 | 12773.5949 | 80840.5977 | 42920.0546 | 0.064391 | -331417.2847 | 331417.2847
C | Xist Rating 3488 | -71.19 | 562.64 | 150.285 | 35.7 | 2329.31 | 8851.27 | 21206.1 | 0.78 | 3.02 | 15.373 | 39.895 | 1 | 1 | 1700 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1310562.9784 | 94649.3 | 2814.6992 | 12849.1783 | 81800.1217 | 42344.6269 | 0.064772 | -326973.9845 | 326973.9845
C | Xist Rating 3489 | -70.91 | 568.69 | 150.285 | 35.7 | 2328.36 | 8870.13 | 21045 | 0.77 | 2.99 | 15.364 | 39.274 | 1 | 1 | 1710 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1324115.0484 | 95690.0682 | 2847.9107 | 12924.7617 | 82765.3065 | 41692.7797 | 0.065153 | -321940.593 | 321940.593
C | Xist Rating 3490 | -70.15 | 586.105 | 150.285 | 35.7 | 2318.72 | 8829.69 | 20567.5 | 0.77 | 2.9 | 15.395 | 37.38 | 1 | 1 | 1720 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1359013.3856 | 96736.4973 | 2881.317 | 13000.3451 | 83736.1522 | 39733.0069 | 0.065534 | -306807.747 | 306807.747
C | Xist Rating 3491 | -69.81 | 593.743 | 150.285 | 35.6 | 2316.85 | 8843.95 | 20374.5 | 0.76 | 2.87 | 15.387 | 36.658 | 1 | 1 | 1730 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1375613.4696 | 97788.5874 | 2914.9181 | 13075.9285 | 84712.6589 | 38976.1148 | 0.065915 | -300963.2271 | 300963.2271
C | Xist Rating 3492 | -69.58 | 597.334 | 150.285 | 35.7 | 2320.97 | 8922.85 | 20290.5 | 0.75 | 2.85 | 15.386 | 36.362 | 1 | 1 | 1740 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1386394.294 | 98846.3383 | 2948.714 | 13151.5119 | 85694.8264 | 38661.9016 | 0.066296 | -298536.9557 | 298536.9557
C | Xist Rating 3493 | -69.34 | 604.347 | 150.285 | 35.6 | 2315.05 | 8873.01 | 20123 | 0.74 | 2.82 | 15.363 | 35.759 | 1 | 1 | 1750 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1399093.5223 | 99909.7502 | 2982.7046 | 13227.0953 | 86682.6549 | 38027.4552 | 0.066677 | -293637.929 | 293637.929
C | Xist Rating 3494 | -69.07 | 609.582 | 150.285 | 35.6 | 2314.7 | 8895.2 | 20001.2 | 0.73 | 2.8 | 15.365 | 35.323 | 1 | 1 | 1760 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1410999.4554 | 100978.8229 | 3016.8901 | 13302.6787 | 87676.1442 | 37567.7609 | 0.067058 | -290088.2917 | 290088.2917
C | Xist Rating 3495 | -68.19 | 630.216 | 150.285 | 35.6 | 2303.56 | 8847.69 | 19497.8 | 0.73 | 2.71 | 15.402 | 33.457 | 1 | 1 | 1770 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1451740.369 | 102053.5566 | 3051.2703 | 13378.2621 | 88675.2945 | 35637.0936 | 0.067439 | -275180.1901 | 275180.1901
C | Xist Rating 3496 | -68.1 | 635.56 | 150.285 | 35.6 | 2293.36 | 8725.44 | 19383.7 | 0.71 | 2.69 | 15.552 | 33.064 | 1 | 1 | 1780 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1457567.8816 | 103133.9512 | 3085.8453 | 13453.8455 | 89680.1057 | 35217.9231 | 0.06782 | -271943.4668 | 271943.4668
C | Xist Rating 3497 | -67.94 | 638.506 | 150.285 | 35.6 | 2293.74 | 8744.15 | 19327.5 | 0.7 | 2.68 | 15.548 | 32.893 | 1 | 1 | 1790 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1464566.7524 | 104220.0067 | 3120.6151 | 13529.4289 | 90690.5778 | 35032.5864 | 0.068201 | -270512.3458 | 270512.3458
C | Xist Rating 3498 | -67.56 | 647.849 | 150.285 | 35.6 | 2291.45 | 8759.75 | 19122 | 0.69 | 2.65 | 15.532 | 32.184 | 1 | 1 | 1800 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1484513.591 | 105311.7231 | 3155.5797 | 13605.0123 | 91706.7108 | 34287.734 | 0.068582 | -264760.793 | 264760.793
C | Xist Rating 3499 | -67.32 | 653.066 | 150.285 | 35.6 | 2290.92 | 8778.66 | 19012.5 | 0.69 | 2.63 | 15.529 | 31.819 | 1 | 1 | 1810 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1496121.9607 | 106409.1004 | 3190.7391 | 13680.5957 | 92728.5047 | 33913.318 | 0.068963 | -261869.6521 | 261869.6521
C | Xist Rating 3500 | -66.45 | 673.958 | 150.285 | 35.6 | 2279.91 | 8729.38 | 18562.8 | 0.68 | 2.55 | 15.564 | 30.269 | 1 | 1 | 1820 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 16 | E | Rod | 1536563.5838 | 107512.1386 | 3226.0933 | 13756.1791 | 93755.9595 | 32297.7213 | 0.069344 | -249394.443 | 249394.443
C | Xist Rating 3501 | -66.42 | 670.622 | 150.285 | 35.6 | 2293.63 | 8915.87 | 18631.6 | 0.68 | 2.56 | 15.575 | 30.515 | 1 | 1 | 1830 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1538158.7379 | 108620.8377 | 3261.6423 | 13831.7625 | 94789.0752 | 32558.5496 | 0.069725 | -251408.4893 | 251408.4893
C | Xist Rating 3502 | -66.09 | 674.883 | 150.285 | 35.6 | 2301.81 | 9064.1 | 18545.7 | 0.67 | 2.55 | 15.593 | 30.237 | 1 | 1 | 1840 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1553452.4382 | 109735.1978 | 3297.386 | 13907.3459 | 95827.8519 | 32262.7432 | 0.070106 | -249124.3511 | 249124.3511
C | Xist Rating 3503 | -65.79 | 682.013 | 150.285 | 35.6 | 2298.31 | 9047.42 | 18409.8 | 0.66 | 2.52 | 15.586 | 29.807 | 1 | 1 | 1850 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1567477.298 | 110855.2187 | 3333.3246 | 13982.9293 | 96872.2894 | 31807.5581 | 0.070487 | -245609.5327 | 245609.5327
C | Xist Rating 3504 | -65.44 | 689.993 | 150.285 | 35.6 | 2296 | 9053.59 | 18259.8 | 0.65 | 2.5 | 15.577 | 29.333 | 1 | 1 | 1860 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1584223.928 | 111980.9006 | 3369.4579 | 14058.5127 | 97922.3879 | 31306.4385 | 0.070868 | -241740.0198 | 241740.0198
C | Xist Rating 3505 | -64.58 | 709.151 | 150.285 | 35.6 | 2290.52 | 9077.96 | 17880.2 | 0.65 | 2.43 | 15.625 | 28.089 | 1 | 1 | 1870 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1624324.5485 | 113112.2433 | 3405.7861 | 14134.0961 | 98978.1472 | 30021.7002 | 0.071249 | -231819.6114 | 231819.6114
C | Xist Rating 3506 | -64.24 | 717.116 | 150.285 | 35.6 | 2287.33 | 9069.68 | 17739.5 | 0.64 | 2.41 | 15.617 | 27.662 | 1 | 1 | 1880 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1640280.9403 | 114249.247 | 3442.309 | 14209.6795 | 100039.5675 | 29569.2152 | 0.07163 | -228325.642 | 228325.642
C | Xist Rating 3507 | -63.91 | 722.381 | 150.285 | 35.6 | 2291.85 | 9169.55 | 17647.4 | 0.63 | 2.39 | 15.631 | 27.387 | 1 | 1 | 1890 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1655588.8948 | 115391.9116 | 3479.0267 | 14285.2629 | 101106.6486 | 29275.625 | 0.072011 | -226058.6165 | 226058.6165
C | Xist Rating 3508 | -63.7 | 728.103 | 150.285 | 35.6 | 2288.28 | 9141.02 | 17556 | 0.62 | 2.38 | 15.609 | 27.129 | 1 | 1 | 1900 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1666103.5328 | 116540.2371 | 3515.9392 | 14360.8463 | 102179.3907 | 28997.6325 | 0.072392 | -223912.0315 | 223912.0315
C | Xist Rating 3509 | -63.46 | 733.547 | 150.285 | 35.6 | 2286.75 | 9144.9 | 17465.6 | 0.61 | 2.36 | 15.612 | 26.868 | 1 | 1 | 1910 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1677438.6022 | 117694.2234 | 3553.0464 | 14436.4297 | 103257.7937 | 28717.7153 | 0.072773 | -221750.5856 | 221750.5856
C | Xist Rating 3510 | -62.47 | 756.825 | 150.285 | 35.6 | 2277.85 | 9136.01 | 17050.6 | 0.61 | 2.29 | 15.654 | 25.586 | 1 | 1 | 1920 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1723933.8262 | 118853.8707 | 3590.3485 | 14512.0131 | 104341.8576 | 27392.8341 | 0.073154 | -211520.2039 | 211520.2039
C | Xist Rating 3511 | -62.14 | 764.868 | 150.285 | 35.6 | 2274.53 | 9124.56 | 16924.3 | 0.6 | 2.27 | 15.647 | 25.228 | 1 | 1 | 1930 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1739715.212 | 120019.1789 | 3627.8454 | 14587.5965 | 105431.5824 | 27011.4261 | 0.073535 | -208575.0722 | 208575.0722
C | Xist Rating 3512 | -61.89 | 767.453 | 150.285 | 35.6 | 2282.38 | 9266.78 | 16882.4 | 0.6 | 2.26 | 15.663 | 25.115 | 1 | 1 | 1940 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1751619.3781 | 121190.1481 | 3665.537 | 14663.1799 | 106526.9681 | 26899.1188 | 0.073916 | -207707.8652 | 207707.8652
C | Xist Rating 3513 | -61.65 | 775.154 | 150.285 | 35.6 | 2274.83 | 9181.04 | 16772.4 | 0.58 | 2.24 | 15.646 | 24.822 | 1 | 1 | 1950 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1763343.5738 | 122366.7781 | 3703.4235 | 14738.7633 | 107628.0147 | 26570.808 | 0.074297 | -205172.7362 | 205172.7362
C | Xist Rating 3514 | -61.27 | 783.926 | 150.285 | 35.6 | 2272.11 | 9183.65 | 16637.3 | 0.57 | 2.22 | 15.661 | 24.442 | 1 | 1 | 1960 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1781166.1039 | 123549.069 | 3741.5047 | 14814.3467 | 108734.7223 | 26167.2515 | 0.074678 | -202056.5796 | 202056.5796
C | Xist Rating 3515 | -60.38 | 804.947 | 150.285 | 35.6 | 2264.65 | 9180.86 | 16303.4 | 0.57 | 2.16 | 15.718 | 23.476 | 1 | 1 | 1970 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1822923.2235 | 124737.0208 | 3779.7807 | 14889.9301 | 109847.0907 | 25170.9324 | 0.075059 | -194363.2679 | 194363.2679
C | Xist Rating 3516 | -60.08 | 811.221 | 150.285 | 35.6 | 2265.09 | 9220.94 | 16214.4 | 0.57 | 2.15 | 15.731 | 23.241 | 1 | 1 | 1980 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1837488.5749 | 125930.6336 | 3818.2515 | 14965.5135 | 110965.1201 | 24931.5589 | 0.07544 | -192514.8891 | 192514.8891
C | Xist Rating 3517 | -59.76 | 819.457 | 150.285 | 35.6 | 2260.86 | 9193 | 16101.6 | 0.56 | 2.13 | 15.736 | 22.946 | 1 | 1 | 1990 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1852677.553 | 127129.9072 | 3856.9171 | 15041.0969 | 112088.8103 | 24615.4387 | 0.075821 | -190073.8926 | 190073.8926
C | Xist Rating 3518 | -59.47 | 825.856 | 150.285 | 35.6 | 2260.09 | 9212.83 | 16015.1 | 0.55 | 2.12 | 15.735 | 22.723 | 1 | 1 | 2000 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1866508.887 | 128334.8418 | 3895.7775 | 15116.6803 | 113218.1615 | 24373.647 | 0.076202 | -188206.8416 | 188206.8416
C | Xist Rating 3519 | -59.24 | 830.59 | 150.285 | 35.6 | 2260.68 | 9246.08 | 15954 | 0.54 | 2.11 | 15.739 | 22.573 | 1 | 1 | 2010 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1877698.2012 | 129545.4373 | 3934.8326 | 15192.2637 | 114353.1735 | 24207.7693 | 0.076583 | -186925.9775 | 186925.9775
C | Xist Rating 3520 | -58.28 | 854.317 | 150.285 | 35.6 | 2250.49 | 9208.82 | 15615.1 | 0.54 | 2.05 | 15.776 | 21.649 | 1 | 1 | 2020 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1922631.8653 | 130761.6937 | 3974.0826 | 15267.8471 | 115493.8465 | 23253.8155 | 0.076964 | -179559.7994 | 179559.7994
C | Xist Rating 3521 | -57.89 | 863.033 | 150.285 | 35.6 | 2249.57 | 9240 | 15499.9 | 0.53 | 2.03 | 15.779 | 21.354 | 1 | 1 | 2030 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1941453.1458 | 131983.6109 | 4013.5273 | 15343.4305 | 116640.1804 | 22937.0666 | 0.077345 | -177113.948 | 177113.948
C | Xist Rating 3522 | -57.67 | 868.955 | 150.285 | 35.6 | 2246.37 | 9213.97 | 15431.8 | 0.52 | 2.02 | 15.77 | 21.196 | 1 | 1 | 2040 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1951994.4434 | 133211.1891 | 4053.1669 | 15419.014 | 117792.1752 | 22761.8758 | 0.077726 | -175761.1715 | 175761.1715
C | Xist Rating 3523 | -57.39 | 874.061 | 150.285 | 35.6 | 2249.34 | 9292.35 | 15364.3 | 0.52 | 2.01 | 15.779 | 21.027 | 1 | 1 | 2050 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1966060.3697 | 134444.4282 | 4093.0012 | 15494.5974 | 118949.8309 | 22590.4754 | 0.078107 | -174437.6632 | 174437.6632
C | Xist Rating 3524 | -57.1 | 882.693 | 150.285 | 35.6 | 2242.93 | 9225.39 | 15264.4 | 0.51 | 1.99 | 15.77 | 20.79 | 1 | 1 | 2060 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 1979818.6105 | 135683.3283 | 4133.0303 | 15570.1808 | 120113.1475 | 22333.0352 | 0.078488 | -172449.7782 | 172449.7782
C | Xist Rating 3525 | -56.09 | 908.187 | 150.285 | 35.6 | 2232.47 | 9188.6 | 14936.3 | 0.51 | 1.94 | 15.808 | 19.947 | 1 | 1 | 2070 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2027500.2319 | 136927.8892 | 4173.2542 | 15645.7642 | 121282.125 | 21462.9844 | 0.078869 | -165731.4762 | 165731.4762
C | Xist Rating 3526 | -55.85 | 913.911 | 150.285 | 35.6 | 2231.4 | 9197.86 | 14873.5 | 0.5 | 1.93 | 15.805 | 19.806 | 1 | 1 | 2080 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2039301.0054 | 138178.111 | 4213.6729 | 15721.3476 | 122456.7634 | 21305.2914 | 0.07925 | -164513.813 | 164513.813
C | Xist Rating 3527 | -55.55 | 921.241 | 150.285 | 35.6 | 2229.5 | 9202.22 | 14790.9 | 0.5 | 1.91 | 15.802 | 19.614 | 1 | 1 | 2090 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2053906.8095 | 139433.9937 | 4254.2864 | 15796.931 | 123637.0628 | 21109.3015 | 0.079631 | -163000.4305 | 163000.4305
C | Xist Rating 3528 | -55.25 | 928.579 | 150.285 | 35.6 | 2227.63 | 9206.79 | 14709.3 | 0.49 | 1.9 | 15.8 | 19.426 | 1 | 1 | 2100 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2068530.4378 | 140695.5374 | 4295.0947 | 15872.5144 | 124823.023 | 20902.6384 | 0.080012 | -161404.6331 | 161404.6331
C | Xist Rating 3529 | -54.96 | 935.072 | 150.285 | 35.6 | 2226.65 | 9221.98 | 14639 | 0.48 | 1.89 | 15.802 | 19.266 | 1 | 1 | 2110 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2082078.0688 | 141962.7419 | 4336.0977 | 15948.0978 | 126014.6442 | 20725.0961 | 0.080393 | -160033.6988 | 160033.6988
C | Xist Rating 3530 | -54.05 | 959.238 | 150.285 | 35.6 | 2215.75 | 9164.81 | 14358.9 | 0.48 | 1.84 | 15.833 | 18.589 | 1 | 1 | 2120 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2125431.5985 | 143235.6074 | 4377.2956 | 16023.6812 | 127211.9262 | 20026.8467 | 0.080774 | -154642.0014 | 154642.0014
C | Xist Rating 3531 | -53.67 | 968.297 | 150.285 | 35.6 | 2213.55 | 9171.84 | 14264 | 0.48 | 1.83 | 15.834 | 18.375 | 1 | 1 | 2130 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2143373.8244 | 144514.1338 | 4418.6882 | 16099.2646 | 128414.8692 | 19808.0604 | 0.081155 | -152952.5921 | 152952.5921
C | Xist Rating 3532 | -53.36 | 977.382 | 150.285 | 35.6 | 2209.1 | 9140.5 | 14170 | 0.47 | 1.81 | 15.829 | 18.166 | 1 | 1 | 2140 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2159134.5762 | 145798.321 | 4460.2756 | 16174.848 | 129623.4731 | 19579.0069 | 0.081536 | -151183.9017 | 151183.9017
C | Xist Rating 3533 | -53.13 | 982.266 | 150.285 | 35.6 | 2209.8 | 9174.96 | 14123.5 | 0.47 | 1.8 | 15.826 | 18.072 | 1 | 1 | 2150 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2170611.4068 | 147088.1692 | 4502.0578 | 16250.4314 | 130837.7378 | 19484.587 | 0.081917 | -150454.8159 | 150454.8159
C | Xist Rating 3534 | -52.87 | 988.704 | 150.285 | 35.6 | 2208.43 | 9182.72 | 14059.1 | 0.46 | 1.79 | 15.824 | 17.933 | 1 | 1 | 2160 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2183483.5747 | 148383.6783 | 4544.0348 | 16326.0148 | 132057.6635 | 19328.1579 | 0.082298 | -149246.9116 | 149246.9116
C | Xist Rating 3535 | -51.87 | 1014.85 | 150.285 | 35.6 | 2197.65 | 9132.23 | 13786 | 0.46 | 1.75 | 15.86 | 17.309 | 1 | 1 | 2170 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2230285.1025 | 149684.8483 | 4586.2066 | 16401.5982 | 133283.2501 | 18685.0084 | 0.082679 | -144280.6822 | 144280.6822
C | Xist Rating 3536 | -51.51 | 1023.68 | 150.285 | 35.6 | 2195.78 | 9144.24 | 13699.1 | 0.46 | 1.74 | 15.857 | 17.121 | 1 | 1 | 2180 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2247776.0704 | 150991.6792 | 4628.5732 | 16477.1816 | 134514.4976 | 18492.9061 | 0.08306 | -142797.319 | 142797.319
C | Xist Rating 3537 | -51.25 | 1030.36 | 150.285 | 35.6 | 2194.19 | 9147.54 | 13639 | 0.45 | 1.73 | 15.854 | 17 | 1 | 1 | 2190 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2260805.6084 | 152304.171 | 4671.1346 | 16552.765 | 135751.4061 | 18354.8187 | 0.083441 | -141731.0447 | 141731.0447
C | Xist Rating 3538 | -51.04 | 1037.44 | 150.285 | 35.6 | 2189.62 | 9099.07 | 13579.4 | 0.44 | 1.72 | 15.847 | 16.885 | 1 | 1 | 2200 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2271599.3728 | 153622.3238 | 4713.8907 | 16628.3484 | 136993.9754 | 18222.6513 | 0.083822 | -140710.4828 | 140710.4828
C | Xist Rating 3539 | -50.69 | 1046.53 | 150.285 | 35.6 | 2186.93 | 9096.28 | 13495.3 | 0.44 | 1.7 | 15.846 | 16.71 | 1 | 1 | 2210 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2288687.8529 | 154946.1374 | 4756.8417 | 16703.9318 | 138242.2056 | 18043.9959 | 0.084203 | -139330.9537 | 139330.9537
C | Xist Rating 3540 | -49.69 | 1072.54 | 150.286 | 35.6 | 2177.71 | 9068.91 | 13246.2 | 0.44 | 1.66 | 15.884 | 16.168 | 1 | 1 | 2220 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2335681.0834 | 156275.6119 | 4799.9874 | 16779.5152 | 139496.0967 | 17485.9189 | 0.084584 | -135021.6307 | 135021.6307
C | Xist Rating 3541 | -49.39 | 1079.84 | 150.285 | 35.6 | 2176.96 | 9090.37 | 13182.5 | 0.43 | 1.65 | 15.883 | 16.041 | 1 | 1 | 2230 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2350768.4864 | 157610.7474 | 4843.3279 | 16855.0986 | 140755.6488 | 17341.2419 | 0.084965 | -133904.4734 | 133904.4734
C | Xist Rating 3542 | -49.11 | 1088.44 | 150.285 | 35.6 | 2172.63 | 9053.92 | 13111.7 | 0.43 | 1.64 | 15.88 | 15.904 | 1 | 1 | 2240 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2364777.3972 | 158951.5437 | 4886.8633 | 16930.682 | 142020.8617 | 17201.8995 | 0.085346 | -132828.5081 | 132828.5081
C | Xist Rating 3543 | -48.77 | 1097.84 | 150.285 | 35.6 | 2169.15 | 9036.16 | 13034 | 0.42 | 1.63 | 15.877 | 15.752 | 1 | 1 | 2250 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2381379.636 | 160298.001 | 4930.5934 | 17006.2654 | 143291.7356 | 17030.9656 | 0.085727 | -131508.602 | 131508.602
C | Xist Rating 3544 | -48.56 | 1102.69 | 150.285 | 35.6 | 2169.04 | 9055.67 | 12995.6 | 0.42 | 1.62 | 15.876 | 15.682 | 1 | 1 | 2260 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2391778.7176 | 161650.1192 | 4974.5182 | 17081.8488 | 144568.2704 | 16961.2172 | 0.086108 | -130970.0235 | 130970.0235
C | Xist Rating 3545 | -47.53 | 1130.78 | 150.286 | 35.6 | 2158.43 | 9008.87 | 12751.8 | 0.42 | 1.59 | 15.913 | 15.18 | 1 | 1 | 2270 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2440709.4754 | 163007.8982 | 5018.6379 | 17157.4322 | 145850.4661 | 16444.4611 | 0.086489 | -126979.7699 | 126979.7699
C | Xist Rating 3546 | -47.22 | 1139.32 | 150.286 | 35.6 | 2155.71 | 8999.27 | 12686.2 | 0.41 | 1.58 | 15.909 | 15.058 | 1 | 1 | 2280 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2456043.5172 | 164371.3382 | 5062.9524 | 17233.0156 | 147138.3226 | 16304.3294 | 0.08687 | -125897.71 | 125897.71
C | Xist Rating 3547 | -46.83 | 1149.31 | 150.286 | 35.6 | 2153.71 | 9010.65 | 12606.9 | 0.41 | 1.56 | 15.907 | 14.906 | 1 | 1 | 2290 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2475280.4401 | 165740.4391 | 5107.4617 | 17308.599 | 148431.8401 | 16149.3173 | 0.087251 | -124700.7472 | 124700.7472
C | Xist Rating 3548 | -46.58 | 1156.15 | 150.286 | 35.6 | 2151.49 | 9001.12 | 12557 | 0.4 | 1.56 | 15.904 | 14.817 | 1 | 1 | 2300 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2487445.1635 | 167115.2009 | 5152.1657 | 17384.1824 | 149731.0185 | 16043.291 | 0.087632 | -123882.0406 | 123882.0406
| Xist Rating 3549 | -46.36 | 1163.25 | 150.286 | 35.6 | 2148.3 | 8974.66 | 12507.6 | 0.4 | 1.55 | 15.901 | 14.732 | 1 | 1 | 2310 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2499009.975 | 168495.6236 | 5197.0645 | 17459.7658 | 151035.8579 | 15957.746 | 0.088013 | -123221.4843 | 123221.4843
| Xist Rating 3550 | -45.28 | 1192.02 | 150.286 | 35.6 | 2139.21 | 8954.31 | 12277.1 | 0.4 | 1.51 | 15.938 | 14.278 | 1 | 1 | 2320 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2549981.1042 | 169881.7073 | 5242.1582 | 17535.3492 | 152346.3581 | 15490.6578 | 0.088394 | -119614.7534 | 119614.7534
| Xist Rating 3551 | -44.97 | 1200.6 | 150.286 | 35.6 | 2136.67 | 8946.99 | 12216.8 | 0.39 | 1.5 | 15.933 | 14.171 | 1 | 1 | 2330 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2565286.002 | 171273.4518 | 5287.4466 | 17610.9326 | 153662.5192 | 15365.5466 | 0.088775 | -118648.6778 | 118648.6778
| Xist Rating 3552 | -44.68 | 1209.15 | 150.286 | 35.6 | 2133.81 | 8933.76 | 12157.2 | 0.39 | 1.49 | 15.928 | 14.067 | 1 | 1 | 2340 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2580096.3615 | 172670.8572 | 5332.9298 | 17686.516 | 154984.3412 | 15260.1236 | 0.089156 | -117834.6292 | 117834.6292
| Xist Rating 3553 | -44.41 | 1216.95 | 150.286 | 35.6 | 2131.03 | 8917.74 | 12104.7 | 0.38 | 1.49 | 15.923 | 13.977 | 1 | 1 | 2350 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2593356.9585 | 174073.9236 | 5378.6078 | 17762.0994 | 156311.8242 | 15152.4648 | 0.089537 | -117003.3168 | 117003.3168
| Xist Rating 3554 | -44.1 | 1226.4 | 150.286 | 35.6 | 2127.26 | 8892.38 | 12039.9 | 0.38 | 1.48 | 15.917 | 13.863 | 1 | 1 | 2360 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2608871.664 | 175482.6508 | 5424.4805 | 17837.6828 | 157644.968 | 15036.547 | 0.089918 | -116108.2304 | 116108.2304
| Xist Rating 3555 | -43.14 | 1252.84 | 150.286 | 35.6 | 2119.15 | 8873.25 | 11846.8 | 0.38 | 1.45 | 15.951 | 13.502 | 1 | 1 | 2370 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2654955.886 | 176897.039 | 5470.5481 | 17913.2662 | 158983.7728 | 14665.7328 | 0.090299 | -113244.9016 | 113244.9016
| Xist Rating 3556 | -42.85 | 1261.64 | 150.286 | 35.6 | 2115.9 | 8852.22 | 11791.2 | 0.37 | 1.44 | 15.945 | 13.41 | 1 | 1 | 2380 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2669504.076 | 178317.0881 | 5516.8105 | 17988.8496 | 160328.2385 | 14555.6542 | 0.09068 | -112394.9034 | 112394.9034
| Xist Rating 3557 | -42.51 | 1270.64 | 150.286 | 35.6 | 2114.06 | 8859.87 | 11730 | 0.37 | 1.43 | 15.938 | 13.303 | 1 | 1 | 2390 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 2686209.1984 | 179742.798 | 5563.2676 | 18064.433 | 161678.365 | 14446.9019 | 0.091061 | -111555.147 | 111555.147
C | Xist Rating 3561 | -35.76 | 1460.92 | 150.286 | 35.6 | 2057.38 | 8710.33 | 10537.9 | 0.39 | 1.25 | 15.97 | 11.255 | 1 | 1 | 2430 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3005667.5896 | 185502.247 | 5751.0441 | 18366.7666 | 167135.4804 | 12366.7104 | 0.092585 | -95492.4599 | 95492.4599
C | Xist Rating 3562 | -35.72 | 1462.29 | 150.286 | 35.6 | 2057.55 | 8713.39 | 10537.9 | 0.38 | 1.25 | 15.962 | 11.266 | 1 | 1 | 2440 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3008734.7895 | 186956.2615 | 5798.4752 | 18442.35 | 168513.9115 | 12363.1265 | 0.092966 | -95464.7857 | 95464.7857
C | Xist Rating 3563 | -35.72 | 1463.61 | 150.286 | 35.6 | 2056.55 | 8695.5 | 10537.9 | 0.38 | 1.25 | 15.955 | 11.276 | 1 | 1 | 2450 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3009987.1455 | 188415.937 | 5846.1011 | 18517.9334 | 169898.0036 | 12375.9382 | 0.093347 | -95563.7145 | 95563.7145
C | Xist Rating 3564 | -35.71 | 1465.09 | 150.286 | 35.6 | 2055.65 | 8679.4 | 10537.9 | 0.37 | 1.25 | 15.95 | 11.288 | 1 | 1 | 2460 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3011712.2585 | 189881.2733 | 5893.9217 | 18593.5168 | 171287.7565 | 12373.3205 | 0.093728 | -95543.5013 | 95543.5013
C | Xist Rating 3565 | -35.69 | 1466.44 | 150.286 | 35.6 | 2055.15 | 8670.65 | 10537.9 | 0.36 | 1.25 | 15.987 | 11.298 | 1 | 1 | 2470 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3013754.166 | 191352.2705 | 5941.9372 | 18669.1002 | 172683.1703 | 12370.1662 | 0.094109 | -95519.1448 | 95519.1448
C | Xist Rating 3566 | -35.67 | 1467.79 | 150.286 | 35.6 | 2054.56 | 8660.12 | 10537.9 | 0.36 | 1.25 | 15.981 | 11.309 | 1 | 1 | 2480 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3015662.6224 | 192828.9287 | 5990.1474 | 18744.6836 | 174084.2451 | 12383.9294 | 0.09449 | -95625.4203 | 95625.4203
C | Xist Rating 3567 | -35.64 | 1469.18 | 150.286 | 35.6 | 2054.35 | 8656.32 | 10537.8 | 0.35 | 1.25 | 15.974 | 11.32 | 1 | 1 | 2490 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3018209.933 | 194311.2478 | 6038.5525 | 18820.267 | 175490.9807 | 12379.8213 | 0.094871 | -95593.6989 | 95593.6989
C | Xist Rating 3568 | -35.62 | 1470.17 | 150.286 | 35.6 | 2054.56 | 8660.19 | 10537.8 | 0.35 | 1.25 | 15.969 | 11.328 | 1 | 1 | 2500 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3020552.4752 | 195799.2277 | 6087.1523 | 18895.8504 | 176903.3773 | 12390.4393 | 0.095252 | -95675.6881 | 95675.6881
C | Xist Rating 3569 | -35.59 | 1472.02 | 150.286 | 35.6 | 2053.6 | 8643.04 | 10537.9 | 0.34 | 1.25 | 15.963 | 11.341 | 1 | 1 | 2510 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3022940.272 | 197292.8686 | 6135.9469 | 18971.4338 | 178321.4348 | 12388.2489 | 0.095633 | -95658.7742 | 95658.7742
C | Xist Rating 3570 | -35.58 | 1473.47 | 150.286 | 35.6 | 2052.85 | 8629.87 | 10537.8 | 0.34 | 1.25 | 16.003 | 11.352 | 1 | 1 | 2520 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3024812.8895 | 198792.1704 | 6184.9363 | 19047.0172 | 179745.1531 | 12403.6414 | 0.096014 | -95777.6313 | 95777.6313
C | Xist Rating 3571 | -35.59 | 1474.81 | 150.286 | 35.6 | 2051.13 | 8599.51 | 10537.8 | 0.33 | 1.25 | 16 | 11.362 | 1 | 1 | 2530 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3025027.0353 | 200297.1331 | 6234.1205 | 19122.6006 | 181174.5324 | 12398.2046 | 0.096395 | -95735.6498 | 95735.6498
C | Xist Rating 3572 | -35.57 | 1475.96 | 150.286 | 35.6 | 2050.98 | 8596.79 | 10537.8 | 0.33 | 1.25 | 15.996 | 11.372 | 1 | 1 | 2540 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3027164.4408 | 201807.7567 | 6283.4995 | 19198.184 | 182609.5726 | 12410.8061 | 0.096776 | -95832.9548 | 95832.9548
C | Xist Rating 3573 | -35.55 | 1477.51 | 150.286 | 35.6 | 2050.2 | 8583.24 | 10537.8 | 0.32 | 1.25 | 15.991 | 11.383 | 1 | 1 | 2550 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3029191.002 | 203324.0412 | 6333.0732 | 19273.7674 | 184050.2737 | 12406.1289 | 0.097157 | -95796.8392 | 95796.8392
C | Xist Rating 3574 | -35.53 | 1478.96 | 150.286 | 35.6 | 2049.92 | 8578.31 | 10537.8 | 0.32 | 1.25 | 16 | 11.393 | 1 | 1 | 2560 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3031749.6832 | 204845.9866 | 6382.8418 | 19349.3508 | 185496.6357 | 12419.1381 | 0.097538 | -95897.2928 | 95897.2928
C | Xist Rating 3575 | -35.51 | 1480.35 | 150.286 | 35.6 | 2049.43 | 8569.8 | 10537.8 | 0.31 | 1.25 | 15.997 | 11.404 | 1 | 1 | 2570 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3033873.7005 | 206373.5929 | 6432.8051 | 19424.9342 | 186948.6587 | 12414.3176 | 0.097919 | -95860.0699 | 95860.0699
C | Xist Rating 3576 | -35.48 | 1481.71 | 150.286 | 35.6 | 2049.25 | 8566.54 | 10537.7 | 0.31 | 1.25 | 16.033 | 11.414 | 1 | 1 | 2580 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3036394.2175 | 207906.8601 | 6482.9633 | 19500.5176 | 188406.3425 | 12428.2161 | 0.0983 | -95967.3904 | 95967.3904
C | Xist Rating 3577 | -35.46 | 1483.07 | 150.286 | 35.6 | 2048.78 | 8558.49 | 10537.7 | 0.3 | 1.25 | 16.027 | 11.424 | 1 | 1 | 2590 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3038484.1546 | 209445.7883 | 6533.3162 | 19576.101 | 189869.6872 | 12422.0064 | 0.098681 | -95919.4404 | 95919.4404
C | Xist Rating 3578 | -35.42 | 1484.25 | 150.286 | 35.6 | 2048.93 | 8560.98 | 10537.7 | 0.3 | 1.25 | 16.028 | 11.433 | 1 | 1 | 2600 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3041124.3525 | 210990.3773 | 6583.8639 | 19651.6844 | 191338.6929 | 12433.543 | 0.099062 | -96008.5235 | 96008.5235
C | Xist Rating 3579 | -35.4 | 1485.94 | 150.286 | 35.6 | 2048.08 | 8546.27 | 10537.7 | 0.29 | 1.25 | 16.027 | 11.445 | 1 | 1 | 2610 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3043323.9952 | 212540.6273 | 6634.6064 | 19727.2678 | 192813.3594 | 12429.3749 | 0.099443 | -95976.3383 | 95976.3383
C | Xist Rating 3580 | -35.39 | 1487.33 | 150.286 | 35.6 | 2047.06 | 8528.57 | 10537.7 | 0.29 | 1.25 | 16.025 | 11.455 | 1 | 1 | 2620 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3044653.7498 | 214096.5381 | 6685.5437 | 19802.8513 | 194293.6869 | 12441.7751 | 0.099824 | -96072.0897 | 96072.0897
C | Xist Rating 3581 | -35.35 | 1488.76 | 150.286 | 35.6 | 2047.33 | 8533.23 | 10537.7 | 0.29 | 1.25 | 16.06 | 11.465 | 1 | 1 | 2630 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3047983.0108 | 215658.1099 | 6736.6758 | 19878.4347 | 195779.6753 | 12455.4398 | 0.10021 | -96177.6046 | 96177.6046
C | Xist Rating 3582 | -35.32 | 1490.01 | 150.286 | 35.6 | 2047.52 | 8536.52 | 10537.7 | 0.28 | 1.25 | 16.055 | 11.474 | 1 | 1 | 2640 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3050825.2752 | 217225.3426 | 6788.0027 | 19954.0181 | 197271.3245 | 12447.7034 | 0.10059 | -96117.8657 | 96117.8657
C | Xist Rating 3583 | -35.3 | 1491.51 | 150.286 | 35.6 | 2046.91 | 8525.98 | 10537.7 | 0.28 | 1.25 | 16.049 | 11.485 | 1 | 1 | 2650 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3052986.7341 | 218798.2362 | 6839.5243 | 20029.6015 | 198768.6347 | 12460.9423 | 0.10097 | -96220.0936 | 96220.0936
C | Xist Rating 3584 | -35.28 | 1492.85 | 150.286 | 35.6 | 2046.54 | 8519.45 | 10537.6 | 0.28 | 1.25 | 16.048 | 11.495 | 1 | 1 | 2660 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3055177.239 | 220376.7907 | 6891.2408 | 20105.1849 | 200271.6058 | 12473.3082 | 0.10135 | -96315.5797 | 96315.5797
C | Xist Rating 3585 | -35.24 | 1494.24 | 150.286 | 35.6 | 2046.82 | 8524.43 | 10537.6 | 0.27 | 1.25 | 16.045 | 11.505 | 1 | 1 | 2670 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3058440.3168 | 221961.0061 | 6943.152 | 20180.7683 | 201780.2378 | 12466.4039 | 0.10173 | -96262.2663 | 96262.2663
C | Xist Rating 3586 | -35.23 | 1495.65 | 150.286 | 35.6 | 2046.09 | 8511.74 | 10537.5 | 0.27 | 1.25 | 16.081 | 11.515 | 1 | 1 | 2680 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3060234.5085 | 223550.8824 | 6995.258 | 20256.3517 | 203294.5307 | 12479.8984 | 0.10211 | -96366.4674 | 96366.4674
C | Xist Rating 3587 | -35.18 | 1497.03 | 150.286 | 35.6 | 2046.49 | 8518.7 | 10537.5 | 0.26 | 1.25 | 16.079 | 11.525 | 1 | 1 | 2690 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3063656.9247 | 225146.4196 | 7047.5588 | 20331.9351 | 204814.4845 | 12472.7767 | 0.10249 | -96311.4757 | 96311.4757
C | Xist Rating 3588 | -35.16 | 1498.23 | 150.286 | 35.6 | 2046.34 | 8516.19 | 10537.5 | 0.26 | 1.25 | 16.07 | 11.534 | 1 | 1 | 2700 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3065887.9782 | 226747.6177 | 7100.0544 | 20407.5185 | 206340.0993 | 12483.7139 | 0.10287 | -96395.9298 | 96395.9298
C | Xist Rating 3589 | -35.14 | 1499.89 | 150.286 | 35.6 | 2045.21 | 8496.62 | 10537.6 | 0.26 | 1.25 | 16.068 | 11.545 | 1 | 1 | 2710 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3067590.0269 | 228354.4768 | 7152.7448 | 20483.1019 | 207871.3749 | 12496.9471 | 0.10325 | -96498.1129 | 96498.1129
C | Xist Rating 3590 | -35.14 | 1501.23 | 150.286 | 35.6 | 2043.95 | 8474.83 | 10537.6 | 0.26 | 1.25 | 16.062 | 11.554 | 1 | 1 | 2720 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3068439.0585 | 229966.9967 | 7205.63 | 20558.6853 | 209408.3114 | 12507.976 | 0.10363 | -96583.2753 | 96583.2753
C | Xist Rating 3591 | -35.12 | 1502.55 | 150.286 | 35.6 | 2043.53 | 8467.59 | 10537.6 | 0.25 | 1.25 | 16.099 | 11.564 | 1 | 1 | 2730 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3070506.0015 | 231585.1776 | 7258.71 | 20634.2687 | 210950.9089 | 12501.7096 | 0.10402 | -96534.8876 | 96534.8876
C | Xist Rating 3592 | -35.09 | 1503.84 | 150.286 | 35.6 | 2043.57 | 8468.25 | 10537.7 | 0.25 | 1.25 | 16.097 | 11.573 | 1 | 1 | 2740 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3073202.3088 | 233209.0193 | 7311.9847 | 20709.8521 | 212499.1673 | 12512.7987 | 0.1044 | -96620.5151 | 96620.5151
C | Xist Rating 3593 | -35.08 | 1505.38 | 150.286 | 35.6 | 2042.43 | 8448.69 | 10537.6 | 0.25 | 1.25 | 16.087 | 11.583 | 1 | 1 | 2750 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3074633.2734 | 234838.522 | 7365.4543 | 20785.4355 | 214053.0865 | 12524.6794 | 0.10478 | -96712.2545 | 96712.2545
C | Xist Rating 3594 | -35.06 | 1506.81 | 150.286 | 35.6 | 2042.08 | 8442.71 | 10537.6 | 0.24 | 1.25 | 16.087 | 11.593 | 1 | 1 | 2760 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3077026.5648 | 236473.6856 | 7419.1186 | 20861.0189 | 215612.6667 | 12516.9649 | 0.10516 | -96652.6853 | 96652.6853
C | Xist Rating 3595 | -35.05 | 1508.04 | 150.286 | 35.6 | 2041.35 | 8430.28 | 10537.6 | 0.24 | 1.25 | 16.082 | 11.602 | 1 | 1 | 2770 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3078437.454 | 238114.5101 | 7472.9777 | 20936.6023 | 217177.9078 | 12527.893 | 0.10554 | -96737.0693 | 96737.0693
C | Xist Rating 3596 | -34.99 | 1509.59 | 150.286 | 35.6 | 2041.83 | 8438.52 | 10537.7 | 0.24 | 1.25 | 16.126 | 11.613 | 1 | 1 | 2780 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3082326.1497 | 239760.9954 | 7527.0316 | 21012.1857 | 218748.8098 | 12542.3625 | 0.10592 | -96848.7988 | 96848.7988
C | Xist Rating 3597 | -34.93 | 1511 | 150.286 | 35.6 | 2042.72 | 8453.66 | 10537.7 | 0.23 | 1.25 | 16.129 | 11.622 | 1 | 1 | 2790 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3086549.92 | 241413.1418 | 7581.2803 | 21087.7691 | 220325.3727 | 12533.3628 | 0.1063 | -96779.3055 | 96779.3055
C | Xist Rating 3598 | -34.82 | 1511.97 | 150.286 | 35.6 | 2045.69 | 8504.74 | 10537.8 | 0.23 | 1.25 | 16.136 | 11.63 | 1 | 1 | 2800 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3093021.9093 | 243070.949 | 7635.7238 | 21163.3525 | 221907.5965 | 12543.5357 | 0.10668 | -96857.858 | 96857.858
C | Xist Rating 3599 | -34.72 | 1513.72 | 150.286 | 35.6 | 2047.17 | 8530.29 | 10537.9 | 0.23 | 1.25 | 16.143 | 11.642 | 1 | 1 | 2810 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3098842.1724 | 244734.4171 | 7690.3621 | 21238.9359 | 223495.4812 | 12557.8641 | 0.10706 | -96968.4976 | 96968.4976
C | Xist Rating 3600 | -34.38 | 1515.19 | 150.286 | 35.6 | 2056.79 | 8699.69 | 10538.1 | 0.22 | 1.25 | 16.197 | 11.652 | 1 | 1 | 2820 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3116427.6401 | 246403.5461 | 7745.1952 | 21314.5193 | 225089.0268 | 12551.0094 | 0.10744 | -96915.5677 | 96915.5677
C | Xist Rating 3601 | -34.65 | 1516.57 | 150.286 | 35.6 | 2047.09 | 8528.93 | 10537.9 | 0.22 | 1.25 | 16.186 | 11.661 | 1 | 1 | 2830 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3104555.2813 | 248078.336 | 7800.223 | 21390.1027 | 226688.2333 | 12561.6462 | 0.10783 | -96997.7019 | 96997.7019
C | Xist Rating 3602 | -34.14 | 1517.88 | 150.286 | 35.6 | 2062.37 | 8800.36 | 10538.1 | 0.22 | 1.25 | 16.266 | 11.671 | 1 | 1 | 2840 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3130430.1756 | 249758.7869 | 7855.4457 | 21465.6861 | 228293.1008 | 12575.8678 | 0.10821 | -97107.5178 | 97107.5178
C | Xist Rating 3603 | -33.78 | 1519.33 | 150.286 | 35.6 | 2072.83 | 8993.99 | 10538.1 | 0.21 | 1.25 | 16.326 | 11.681 | 1 | 1 | 2850 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3149312.8039 | 251444.8986 | 7910.8631 | 21541.2695 | 229903.6291 | 12568.6867 | 0.10859 | -97052.0668 | 97052.0668
C | Xist Rating 3604 | -33.55 | 1520.73 | 150.286 | 35.6 | 2078.87 | 9108.82 | 10538.2 | 0.21 | 1.25 | 16.351 | 11.691 | 1 | 1 | 2860 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3161399.9751 | 253136.6713 | 7966.4753 | 21616.8529 | 231519.8184 | 12581.2815 | 0.10897 | -97149.3207 | 97149.3207
C | Xist Rating 3605 | -33.36 | 1521.92 | 150.286 | 35.6 | 2083.88 | 9205.68 | 10538.1 | 0.21 | 1.25 | 16.367 | 11.7 | 1 | 1 | 2870 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3171498.6496 | 254834.1048 | 8022.2824 | 21692.4363 | 233141.6685 | 12592.5994 | 0.10935 | -97236.7144 | 97236.7144
C | Xist Rating 3606 | -33.25 | 1523.43 | 150.286 | 35.6 | 2086.19 | 9251.04 | 10538.1 | 0.21 | 1.25 | 16.415 | 11.71 | 1 | 1 | 2880 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 15 | E | Rod | 3178164.4317 | 256537.1993 | 8078.2842 | 21768.0197 | 234769.1796 | 12605.8263 | 0.10973 | -97338.8492 | 97338.8492
C | Xist Rating 3607 | -33.13 | 1524.78 | 150.286 | 35.6 | 2088.75 | 9301.66 | 10538.1 | 0.2 | 1.25 | 16.42 | 11.719 | 1 | 1 | 2890 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 14 | E | Rod | 3184884.225 | 258245.9547 | 8134.4807 | 21843.6031 | 236402.3516 | 12595.583 | 0.11011 | -97259.7529 | 97259.7529
C | Xist Rating 3608 | -33 | 1526.16 | 150.286 | 35.6 | 2091.83 | 9363.03 | 10538.2 | 0.2 | 1.25 | 16.428 | 11.729 | 1 | 1 | 2900 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 14 | E | Rod | 3192467.2728 | 259960.371 | 8190.8721 | 21919.1865 | 238041.1845 | 12607.648 | 0.11049 | -97352.9158 | 97352.9158
C | Xist Rating 3609 | -32.91 | 1527.7 | 150.286 | 35.6 | 2093.22 | 9390.95 | 10538.1 | 0.2 | 1.25 | 16.434 | 11.739 | 1 | 1 | 2910 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 14 | E | Rod | 3197812.194 | 261680.4482 | 8247.4583 | 21994.7699 | 239685.6783 | 12619.6622 | 0.11087 | -97445.6868 | 97445.6868
C | Xist Rating 3610 | -32.8 | 1529.09 | 150.286 | 35.5 | 2095.77 | 9442.56 | 10538 | 0.2 | 1.25 | 16.439 | 11.748 | 1 | 1 | 2920 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 14 | E | Rod | 3204620.9493 | 263406.1863 | 8304.2393 | 22070.3533 | 241335.833 | 12630.6129 | 0.11125 | -97530.245 | 97530.245
C | Xist Rating 3611 | -32.67 | 1530.48 | 150.286 | 35.5 | 2098.54 | 9499.02 | 10538 | 0.19 | 1.25 | 16.486 | 11.758 | 1 | 1 | 2930 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 14 | E | Rod | 3211773.4992 | 265137.5853 | 8361.215 | 22145.9367 | 242991.6486 | 12622.0541 | 0.11164 | -97464.1562 | 97464.1562
C | Xist Rating 3612 | -32.43 | 1531.84 | 150.286 | 35.5 | 2105.48 | 9642.92 | 10537.9 | 0.19 | 1.25 | 16.496 | 11.767 | 1 | 1 | 2940 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 14 | E | Rod | 3225258.4832 | 266874.6452 | 8418.3855 | 22221.5201 | 244653.1251 | 12633.0551 | 0.11202 | -97549.1025 | 97549.1025
C | Xist Rating 3613 | -32.41 | 1533.25 | 150.286 | 35.5 | 2104.79 | 9628.54 | 10537.9 | 0.19 | 1.25 | 16.492 | 11.777 | 1 | 1 | 2950 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 14 | E | Rod | 3227169.2675 | 268617.3661 | 8475.7509 | 22297.1035 | 246320.2625 | 12644.7445 | 0.1124 | -97639.3649 | 97639.3649
C | Xist Rating 3614 | -32.4 | 1534.62 | 150.286 | 35.5 | 2104.12 | 9614.56 | 10537.9 | 0.19 | 1.25 | 16.488 | 11.786 | 1 | 1 | 2960 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 14 | E | Rod | 3229024.6344 | 270365.7478 | 8533.311 | 22372.6869 | 247993.0609 | 12655.3947 | 0.11278 | -97721.6031 | 97721.6031
C | Xist Rating 3615 | -32.38 | 1536.01 | 150.286 | 35.5 | 2103.46 | 9600.9 | 10537.9 | 0.18 | 1.25 | 16.485 | 11.795 | 1 | 1 | 2970 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 14 | E | Rod | 3230935.5946 | 272119.7904 | 8591.0659 | 22448.2703 | 249671.5201 | 12644.1232 | 0.11316 | -97634.5674 | 97634.5674
C | Xist Rating 3616 | -32.37 | 1537.23 | 150.286 | 35.5 | 2102.88 | 9588.65 | 10537.9 | 0.18 | 1.25 | 16.521 | 11.803 | 1 | 1 | 2980 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 14 | E | Rod | 3232610.2224 | 273879.494 | 8649.0156 | 22523.8537 | 251355.6403 | 12654.6268 | 0.11354 | -97715.6738 | 97715.6738
C | Xist Rating 3617 | -32.35 | 1538.79 | 150.286 | 35.5 | 2102.15 | 9573.48 | 10537.9 | 0.18 | 1.25 | 16.517 | 11.813 | 1 | 1 | 2990 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 14 | E | Rod | 3234767.3985 | 275644.8584 | 8707.16 | 22599.4371 | 253045.4213 | 12666.2483 | 0.11392 | -97805.4118 | 97805.4118
C | Xist Rating 3618 | -32.33 | 1540.22 | 150.286 | 35.5 | 2101.47 | 9559.57 | 10537.9 | 0.18 | 1.25 | 16.514 | 11.822 | 1 | 1 | 3000 | 152.4 | 2 | 2.7 | 19.05 | 1.3333 | 14 | E | Rod | 3236726.1234 | 277415.8838 | 8765.4993 | 22675.0205 | 254740.8633 | 12676.8548 | 0.1143 | -97887.3126 | 97887.3126
C | Xist Rating 3619 | -91.87 | 148.87 | 150.289 | 35.8 | 2396.13 | 7370.93 | 58745.8 | 2.45 | 10.95 | 17.541 | 425.378 | 1 | 1 | 1000 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 356711.8731 | 37191.1354 | 973.9444 | 7838.2787 | 29352.8567 | 443680.7399 | 0.038101 | -3425985.067 | 3425985.067
C | Xist Rating 3620 | -91.8 | 150.433 | 150.29 | 35.8 | 2393.2 | 7351.61 | 58284.3 | 2.43 | 10.85 | 17.577 | 417.419 | 1 | 1 | 1010 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 360016.2556 | 37859.5106 | 993.5206 | 7916.6615 | 29942.8491 | 435422.6725 | 0.038482 | -3362218.4589 | 3362218.4589
C | Xist Rating 3621 | -91.19 | 162.176 | 150.29 | 35.8 | 2386.52 | 7352.73 | 54967.6 | 2.44 | 10.07 | 17.628 | 361.732 | 1 | 1 | 1020 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 387036.2675 | 38533.7564 | 1013.2917 | 7995.0443 | 30538.7121 | 377624.6825 | 0.038863 | -2915917.701 | 2915917.701
C | Xist Rating 3622 | -91.09 | 165.449 | 150.289 | 35.8 | 2366.37 | 7180.47 | 54179.2 | 2.36 | 9.89 | 17.271 | 349.681 | 1 | 1 | 1030 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 391513.5501 | 39213.8727 | 1033.2576 | 8073.4271 | 31140.4456 | 365025.0096 | 0.039244 | -2818626.3668 | 2818626.3668
C | Xist Rating 3623 | -91.03 | 167.088 | 150.289 | 35.8 | 2360.7 | 7136.29 | 53793.7 | 2.32 | 9.8 | 17.178 | 343.909 | 1 | 1 | 1040 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 394444.6416 | 39899.8596 | 1053.4182 | 8151.8098 | 31748.0498 | 359006.8035 | 0.039625 | -2772155.3746 | 2772155.3746
C | Xist Rating 3624 | -90.83 | 170.239 | 150.289 | 35.8 | 2367.99 | 7218.99 | 53043.4 | 2.26 | 9.63 | 17.139 | 332.561 | 1 | 1 | 1050 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 403124.2496 | 40591.7171 | 1073.7737 | 8230.1926 | 32361.5245 | 347187.1292 | 0.040006 | -2680886.9823 | 2680886.9823
C | Xist Rating 3625 | -90.7 | 171.858 | 150.289 | 35.8 | 2382.06 | 7359.54 | 52677.2 | 2.21 | 9.54 | 17.131 | 327.202 | 1 | 1 | 1060 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 409376.0675 | 41289.4452 | 1094.3239 | 8308.5754 | 32980.8698 | 341597.6213 | 0.040387 | -2637726.2842 | 2637726.2842
C | Xist Rating 3626 | -90.1 | 184.537 | 150.288 | 35.8 | 2362.07 | 7236.11 | 49857.4 | 2.2 | 8.9 | 17.011 | 286.328 | 1 | 1 | 1070 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 435889.3116 | 41993.0438 | 1115.0689 | 8386.9582 | 33606.0856 | 299146.1288 | 0.040768 | -2309927.1119 | 2309927.1119
C | Xist Rating 3627 | -89.94 | 186.969 | 150.288 | 35.8 | 2368.8 | 7311.6 | 49381.1 | 2.14 | 8.79 | 16.938 | 279.952 | 1 | 1 | 1080 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 442892.1672 | 42702.513 | 1136.0087 | 8465.341 | 34237.172 | 292484.4647 | 0.041149 | -2258487.5071 | 2258487.5071
C | Xist Rating 3628 | -89.76 | 190.201 | 150.288 | 35.8 | 2371.27 | 7351.08 | 48762.2 | 2.09 | 8.65 | 16.826 | 271.756 | 1 | 1 | 1090 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 451017.9253 | 43417.8528 | 1157.1433 | 8543.7238 | 34874.129 | 283936.3639 | 0.04153 | -2192481.3389 | 2192481.3389
C | Xist Rating 3629 | -89.62 | 192.601 | 150.288 | 35.8 | 2376.7 | 7415.69 | 48308.7 | 2.05 | 8.55 | 16.816 | 265.827 | 1 | 1 | 1100 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 457754.7967 | 44139.0631 | 1178.4727 | 8622.1066 | 35516.9566 | 277760.6735 | 0.041911 | -2144794.2947 | 2144794.2947
C | Xist Rating 3630 | -89.55 | 194.407 | 150.287 | 35.8 | 2371 | 7368.48 | 48010.8 | 1.98 | 8.49 | 16.589 | 262.239 | 1 | 1 | 1110 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 460938.997 | 44866.1441 | 1199.9969 | 8700.4894 | 36165.6547 | 273969.0624 | 0.042292 | -2115516.4789 | 2115516.4789
C | Xist Rating 3631 | -88.81 | 208.475 | 150.288 | 35.8 | 2368.84 | 7421.31 | 45448.1 | 2.02 | 7.92 | 16.792 | 229.46 | 1 | 1 | 1120 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 493843.919 | 45599.0956 | 1221.7158 | 8778.8721 | 36820.2234 | 239996.7456 | 0.042673 | -1853191.253 | 1853191.253
C | Xist Rating 3632 | -88.73 | 210.235 | 150.287 | 35.8 | 2366.86 | 7409.91 | 45189 | 1.96 | 7.86 | 16.644 | 226.562 | 1 | 1 | 1130 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 497596.8121 | 46337.9176 | 1243.6296 | 8857.2549 | 37480.6627 | 236936.6557 | 0.043054 | -1829562.0506 | 1829562.0506
C | Xist Rating 3633 | -88.58 | 213.538 | 150.287 | 35.8 | 2362.64 | 7384.41 | 44681.1 | 1.9 | 7.75 | 16.51 | 220.695 | 1 | 1 | 1140 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 504513.4203 | 47082.6103 | 1265.7381 | 8935.6377 | 38146.9725 | 230794.3676 | 0.043435 | -1782132.93 | 1782132.93
C | Xist Rating 3634 | -88.4 | 216.777 | 150.287 | 35.8 | 2365.93 | 7432.53 | 44186.8 | 1.86 | 7.64 | 16.386 | 215.012 | 1 | 1 | 1150 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 512879.2076 | 47833.1735 | 1288.0414 | 9014.0205 | 38819.153 | 224860.7105 | 0.043816 | -1736314.8026 | 1736314.8026
C | Xist Rating 3635 | -88.22 | 220.095 | 150.286 | 35.8 | 2366.9 | 7458.06 | 43704.1 | 1.81 | 7.53 | 16.281 | 209.614 | 1 | 1 | 1160 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 520942.8555 | 48589.6072 | 1310.5395 | 9092.4033 | 39497.2039 | 219216.0749 | 0.044197 | -1692728.4228 | 1692728.4228
C | Xist Rating 3636 | -87.55 | 232.761 | 150.287 | 35.8 | 2366 | 7515 | 41833.1 | 1.83 | 7.13 | 16.4 | 188.571 | 1 | 1 | 1170 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 550712.526 | 49351.9116 | 1333.2324 | 9170.7861 | 40181.1255 | 197404.6599 | 0.044578 | -1524306.4576 | 1524306.4576
C | Xist Rating 3637 | -87.46 | 233.734 | 150.287 | 35.8 | 2374.53 | 7605.86 | 41725.4 | 1.77 | 7.11 | 16.341 | 187.586 | 1 | 1 | 1180 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 555008.395 | 50120.0865 | 1356.1201 | 9249.1689 | 40870.9176 | 196337.6213 | 0.044959 | -1516067.0684 | 1516067.0684
C | Xist Rating 3638 | -87.18 | 240.198 | 150.286 | 35.8 | 2364.04 | 7531.18 | 40886.4 | 1.73 | 6.93 | 16.218 | 178.839 | 1 | 1 | 1190 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 567837.6799 | 50894.132 | 1379.2026 | 9327.5516 | 41566.5803 | 187220.624 | 0.04534 | -1445668.0318 | 1445668.0318
C | Xist Rating 3639 | -87.03 | 241.85 | 150.286 | 35.8 | 2375.87 | 7660.93 | 40682.6 | 1.7 | 6.88 | 16.239 | 176.805 | 1 | 1 | 1200 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 574604.1595 | 51674.0481 | 1402.4799 | 9405.9344 | 42268.1136 | 185096.6442 | 0.045721 | -1429267.2231 | 1429267.2231
C | Xist Rating 3640 | -86.88 | 245.238 | 150.286 | 35.8 | 2372.17 | 7638.98 | 40281.7 | 1.65 | 6.8 | 16.132 | 172.854 | 1 | 1 | 1210 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 581746.2265 | 52459.8347 | 1425.9519 | 9484.3172 | 42975.5175 | 180952.2973 | 0.046102 | -1397265.6747 | 1397265.6747
C | Xist Rating 3641 | -86.19 | 259.66 | 150.286 | 35.8 | 2359.3 | 7580.55 | 38538.3 | 1.65 | 6.43 | 16.15 | 155.478 | 1 | 1 | 1220 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 612615.838 | 53251.4919 | 1449.6188 | 9562.7 | 43688.7919 | 162920.9043 | 0.046483 | -1258032.0375 | 1258032.0375
C | Xist Rating 3642 | -85.99 | 262.897 | 150.286 | 35.8 | 2365.18 | 7657.84 | 38183.2 | 1.62 | 6.35 | 16.154 | 152.167 | 1 | 1 | 1230 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 621798.7265 | 54049.0197 | 1473.4804 | 9641.0828 | 44407.9369 | 159468.0254 | 0.046864 | -1231369.8217 | 1231369.8217
C | Xist Rating 3643 | -85.82 | 266.275 | 150.286 | 35.8 | 2364.82 | 7670.29 | 37835.7 | 1.58 | 6.28 | 16.082 | 149.033 | 1 | 1 | 1240 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 629692.4455 | 54852.418 | 1497.5369 | 9719.4656 | 45132.9524 | 156182.8634 | 0.047245 | -1206002.6717 | 1206002.6717
C | Xist Rating 3644 | -85.72 | 268.071 | 150.286 | 35.8 | 2367.16 | 7703.25 | 37664.7 | 1.54 | 6.24 | 16.029 | 147.571 | 1 | 1 | 1250 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 634566.9484 | 55661.6869 | 1521.7881 | 9797.8484 | 45863.8386 | 154635.3517 | 0.047626 | -1194053.1968 | 1194053.1968
C | Xist Rating 3645 | -85.48 | 272.951 | 150.286 | 35.8 | 2364.8 | 7702.7 | 37162 | 1.51 | 6.14 | 15.994 | 143.021 | 1 | 1 | 1260 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 645474.5248 | 56476.8264 | 1546.2341 | 9876.2312 | 46600.5953 | 149891.1047 | 0.048007 | -1157419.379 | 1157419.379
C | Xist Rating 3646 | -84.8 | 286.616 | 150.286 | 35.8 | 2358.12 | 7702.69 | 35778.1 | 1.52 | 5.85 | 16.051 | 130.651 | 1 | 1 | 1270 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 675874.9219 | 57297.8365 | 1570.8749 | 9954.6139 | 47343.2225 | 137069.742 | 0.048388 | -1058416.2146 | 1058416.2146
C | Xist Rating 3647 | -84.65 | 290.062 | 150.286 | 35.8 | 2353.86 | 7673.35 | 35477.7 | 1.48 | 5.79 | 15.975 | 128.204 | 1 | 1 | 1280 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 682765.3393 | 58124.7171 | 1595.7105 | 10032.9967 | 48091.7204 | 134496.1815 | 0.048769 | -1038543.8623 | 1038543.8623
C | Xist Rating 3648 | -84.46 | 293.456 | 150.286 | 35.8 | 2357.08 | 7723.84 | 35183.4 | 1.44 | 5.73 | 15.963 | 125.813 | 1 | 1 | 1290 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 691699.2685 | 58957.4683 | 1620.7408 | 10111.3795 | 48846.0888 | 131985.781 | 0.04915 | -1019159.2156 | 1019159.2156
C | Xist Rating 3649 | -84.17 | 298.313 | 150.286 | 35.8 | 2363.59 | 7818.9 | 34751.8 | 1.42 | 5.64 | 15.98 | 122.256 | 1 | 1 | 1300 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 705089.6237 | 59796.0901 | 1645.966 | 10189.7623 | 49606.3278 | 128284.9486 | 0.049531 | -990582.3688 | 990582.3688
C | Xist Rating 3650 | -84.01 | 300.938 | 150.286 | 35.8 | 2367.9 | 7878.9 | 34540.6 | 1.38 | 5.59 | 15.942 | 120.619 | 1 | 1 | 1310 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 712591.0902 | 60640.5824 | 1671.3859 | 10268.1451 | 50372.4373 | 126554.4849 | 0.049912 | -977220.1862 | 977220.1862
C | Xist Rating 3651 | -83.32 | 314.701 | 150.286 | 35.8 | 2362.93 | 7896.68 | 33363.8 | 1.39 | 5.35 | 15.991 | 111.118 | 1 | 1 | 1320 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 743616.4339 | 61490.9454 | 1697.0007 | 10346.5279 | 51144.4175 | 116711.0354 | 0.050293 | -901211.6787 | 901211.6787
C | Xist Rating 3652 | -83.09 | 319.776 | 150.285 | 35.8 | 2358.75 | 7874.98 | 32980.7 | 1.35 | 5.28 | 15.884 | 108.252 | 1 | 1 | 1330 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 754271.64 | 62347.1788 | 1722.8102 | 10424.9107 | 51922.2682 | 113697.9174 | 0.050674 | -877945.1802 | 877945.1802
C | Xist Rating 3653 | -82.83 | 324.749 | 150.285 | 35.7 | 2359.34 | 7906.42 | 32607.5 | 1.32 | 5.2 | 15.857 | 105.473 | 1 | 1 | 1340 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 766193.3057 | 63209.2829 | 1748.8145 | 10503.2935 | 52705.9894 | 110790.7793 | 0.051055 | -855497.0305 | 855497.0305
C | Xist Rating 3654 | -82.67 | 327.39 | 150.285 | 35.7 | 2363.48 | 7965.66 | 32424.4 | 1.29 | 5.16 | 15.828 | 104.182 | 1 | 1 | 1350 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 773779.7172 | 64077.2575 | 1775.0136 | 10581.6762 | 53495.5813 | 109428.4096 | 0.051436 | -844977.173 | 844977.173
C | Xist Rating 3655 | -82.48 | 328.989 | 150.286 | 35.7 | 2379.66 | 8161.31 | 32304 | 1.28 | 5.14 | 15.88 | 103.301 | 1 | 1 | 1360 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 782881.9637 | 64951.1027 | 1801.4075 | 10660.059 | 54291.0437 | 108517.0535 | 0.051817 | -837939.9224 | 837939.9224
C | Xist Rating 3656 | -81.65 | 348.63 | 150.285 | 35.7 | 2352.21 | 7947.94 | 30903.2 | 1.27 | 4.86 | 15.844 | 93.143 | 1 | 1 | 1370 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 820050.9723 | 65830.8185 | 1827.9962 | 10738.4418 | 55092.3767 | 97964.5383 | 0.052198 | -756456.1969 | 756456.1969
C | Xist Rating 3657 | -81.57 | 350.49 | 150.285 | 35.7 | 2352.05 | 7954.47 | 30794.4 | 1.25 | 4.84 | 15.809 | 92.463 | 1 | 1 | 1380 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 824370.0045 | 66716.4049 | 1854.7797 | 10816.8246 | 55899.5803 | 97245.071 | 0.052579 | -750900.6618 | 750900.6618
C | Xist Rating 3658 | -81.34 | 354.753 | 150.285 | 35.7 | 2352.92 | 7985.11 | 30527.8 | 1.22 | 4.79 | 15.785 | 90.683 | 1 | 1 | 1390 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 834705.4288 | 67607.8618 | 1881.7579 | 10895.2074 | 56712.6544 | 95374.0275 | 0.05296 | -736452.9591 | 736452.9591
C | Xist Rating 3659 | -81.12 | 359.012 | 150.285 | 35.7 | 2354.18 | 8020.61 | 30265.5 | 1.2 | 4.73 | 15.757 | 88.954 | 1 | 1 | 1400 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 845178.8702 | 68505.1893 | 1908.931 | 10973.5902 | 57531.5991 | 93565.1757 | 0.053341 | -722485.4856 | 722485.4856
C | Xist Rating 3660 | -80.86 | 364.046 | 150.285 | 35.7 | 2355.09 | 8056.44 | 29957.8 | 1.18 | 4.67 | 15.74 | 86.929 | 1 | 1 | 1410 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 857361.0941 | 69408.3873 | 1936.2988 | 11051.973 | 58356.4144 | 91449.5065 | 0.053722 | -706148.8486 | 706148.8486
C | Xist Rating 3661 | -80.14 | 378.711 | 150.285 | 35.7 | 2350.19 | 8076.75 | 29052.3 | 1.18 | 4.49 | 15.8 | 80.923 | 1 | 1 | 1420 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 890042.8051 | 70317.456 | 1963.8614 | 11130.3558 | 59187.1002 | 85225.1169 | 0.054103 | -658085.7617 | 658085.7617
C | Xist Rating 3662 | -80.02 | 381.593 | 150.285 | 35.7 | 2346.95 | 8051.05 | 28911.2 | 1.15 | 4.47 | 15.739 | 80.121 | 1 | 1 | 1430 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 895579.6913 | 71232.3952 | 1991.6188 | 11208.7385 | 60023.6566 | 84365.7186 | 0.054484 | -651449.7163 | 651449.7163
C | Xist Rating 3663 | -79.7 | 388.226 | 150.285 | 35.7 | 2344.98 | 8061.24 | 28542.3 | 1.13 | 4.39 | 15.724 | 77.827 | 1 | 1 | 1440 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 910382.2055 | 72153.2049 | 2019.571 | 11287.1213 | 60866.0836 | 81970.1041 | 0.054865 | -632951.416 | 632951.416
C | Xist Rating 3664 | -79.49 | 392.523 | 150.285 | 35.7 | 2344.99 | 8082.23 | 28317.1 | 1.11 | 4.35 | 15.705 | 76.48 | 1 | 1 | 1450 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 920462.5098 | 73079.8853 | 2047.718 | 11365.5041 | 61714.3812 | 80557.4006 | 0.055246 | -622042.8941 | 622042.8941
C | Xist Rating 3665 | -79.31 | 395.046 | 150.285 | 35.7 | 2351.75 | 8175.92 | 28183.8 | 1.1 | 4.32 | 15.718 | 75.689 | 1 | 1 | 1460 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 17 | E | Rod | 929049.4305 | 74012.4362 | 2076.0598 | 11443.8869 | 62568.5493 | 79734.4203 | 0.055627 | -615688.0584 | 615688.0584
C | Xist Rating 3666 | -78.59 | 411.738 | 150.285 | 35.7 | 2336.04 | 8073.27 | 27310.5 | 1.09 | 4.16 | 15.688 | 70.428 | 1 | 1 | 1470 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 961836.4375 | 74950.8577 | 2104.5964 | 11522.2697 | 63428.588 | 74266.1186 | 0.056008 | -573463.2821 | 573463.2821
C | Xist Rating 3667 | -78.33 | 416.816 | 150.285 | 35.7 | 2336.15 | 8099.4 | 27066.5 | 1.07 | 4.11 | 15.675 | 69.041 | 1 | 1 | 1480 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 973744.6984 | 75895.1497 | 2133.3277 | 11600.6525 | 64294.4973 | 72811.6485 | 0.056389 | -562232.2494 | 562232.2494
C | Xist Rating 3668 | -78.09 | 421.115 | 150.285 | 35.7 | 2339.26 | 8157.88 | 26866.8 | 1.05 | 4.07 | 15.669 | 67.931 | 1 | 1 | 1490 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 985097.4749 | 76845.3124 | 2162.2539 | 11679.0353 | 65166.2771 | 71645.0743 | 0.05677 | -553224.2728 | 553224.2728
C | Xist Rating 3669 | -77.84 | 425.506 | 150.285 | 35.7 | 2342.25 | 8215.7 | 26670.3 | 1.03 | 4.03 | 15.654 | 66.863 | 1 | 1 | 1500 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 996641.4285 | 77801.3456 | 2191.3748 | 11757.418 | 66043.9275 | 70521.2232 | 0.057151 | -544546.1926 | 544546.1926
C | Xist Rating 3670 | -77.54 | 430.611 | 150.285 | 35.7 | 2347.28 | 8303.77 | 26439 | 1.01 | 3.99 | 15.657 | 65.592 | 1 | 1 | 1510 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1010764.5881 | 78763.2493 | 2220.6906 | 11835.8008 | 66927.4485 | 69187.5333 | 0.057532 | -534247.7924 | 534247.7924
C | Xist Rating 3671 | -76.72 | 446.986 | 150.285 | 35.7 | 2344.95 | 8363.48 | 25681.3 | 1.02 | 3.85 | 15.725 | 61.363 | 1 | 1 | 1520 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1048159.8207 | 79731.0237 | 2250.2011 | 11914.1836 | 67816.8401 | 64818.2052 | 0.057913 | -500508.9994 | 500508.9994
C | Xist Rating 3672 | -76.51 | 452.435 | 150.285 | 35.7 | 2338.33 | 8305.59 | 25468.6 | 0.99 | 3.8 | 15.675 | 60.296 | 1 | 1 | 1530 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1057942.3335 | 80704.6686 | 2279.9064 | 11992.5664 | 68712.1022 | 63681.5689 | 0.058294 | -491732.1946 | 491732.1946
C | Xist Rating 3673 | -76.31 | 455.233 | 150.285 | 35.7 | 2344.83 | 8401.43 | 25364 | 0.97 | 3.79 | 15.669 | 59.791 | 1 | 1 | 1540 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1067443.9954 | 81684.1841 | 2309.8065 | 12070.9492 | 69613.2349 | 63142.0405 | 0.058675 | -487566.0997 | 487566.0997
C | Xist Rating 3674 | -75.9 | 463.59 | 150.285 | 35.7 | 2343.35 | 8426.26 | 25021.5 | 0.96 | 3.72 | 15.664 | 58.014 | 1 | 1 | 1550 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1086353.6265 | 82669.5701 | 2339.9013 | 12149.332 | 70520.2382 | 61292.2217 | 0.059056 | -473282.2888 | 473282.2888
C | Xist Rating 3675 | -75.67 | 466.163 | 150.285 | 35.7 | 2354.28 | 8582.94 | 24920.7 | 0.95 | 3.7 | 15.686 | 57.517 | 1 | 1 | 1560 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1097478.2276 | 83660.8268 | 2370.191 | 12227.7148 | 71433.112 | 60773.3366 | 0.059437 | -469275.596 | 469275.596
C | Xist Rating 3676 | -74.88 | 485.56 | 150.285 | 35.7 | 2334.63 | 8429.16 | 24162.4 | 0.94 | 3.56 | 15.682 | 53.673 | 1 | 1 | 1570 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1133602.9428 | 84657.954 | 2400.6755 | 12306.0976 | 72351.8564 | 56776.7247 | 0.059818 | -438414.8185 | 438414.8185
C | Xist Rating 3677 | -74.63 | 489.98 | 150.285 | 35.7 | 2337.57 | 8489.62 | 24007.6 | 0.92 | 3.53 | 15.674 | 52.95 | 1 | 1 | 1580 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1145362.5486 | 85660.9517 | 2431.3547 | 12384.4803 | 73276.4714 | 56009.7638 | 0.0602 | -432492.5498 | 432492.5498
C | Xist Rating 3678 | -74.39 | 494.435 | 150.285 | 35.7 | 2339.26 | 8534.17 | 23855.3 | 0.91 | 3.5 | 15.663 | 52.247 | 1 | 1 | 1590 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1156612.0181 | 86669.8201 | 2462.2288 | 12462.8631 | 74206.957 | 55274.2787 | 0.060581 | -426813.3288 | 426813.3288
C | Xist Rating 3679 | -74.05 | 500.345 | 150.285 | 35.7 | 2343.2 | 8618.6 | 23645.6 | 0.9 | 3.46 | 15.671 | 51.252 | 1 | 1 | 1600 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1172408.404 | 87684.559 | 2493.2976 | 12541.2459 | 75143.3131 | 54236.6448 | 0.060962 | -418800.9944 | 418800.9944
C | Xist Rating 3680 | -73.89 | 503.339 | 150.285 | 35.7 | 2345.08 | 8657.77 | 23556.9 | 0.88 | 3.45 | 15.652 | 50.884 | 1 | 1 | 1610 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1180370.2221 | 88705.1685 | 2524.5612 | 12619.6287 | 76085.5398 | 53836.9739 | 0.061343 | -415714.8422 | 415714.8422
C | Xist Rating 3681 | -72.93 | 524.972 | 150.285 | 35.7 | 2331.13 | 8587.62 | 22805.3 | 0.88 | 3.31 | 15.669 | 47.333 | 1 | 1 | 1620 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1223777.9784 | 89731.6486 | 2556.0196 | 12698.0115 | 77033.6371 | 50156.5264 | 0.061724 | -387295.4021 | 387295.4021
C | Xist Rating 3682 | -72.72 | 527.62 | 150.285 | 35.7 | 2339.09 | 8710.47 | 22723.6 | 0.87 | 3.29 | 15.694 | 46.986 | 1 | 1 | 1630 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1234150.6658 | 90763.9992 | 2587.6728 | 12776.3943 | 77987.6049 | 49792.4889 | 0.062105 | -384484.4011 | 384484.4011
C | Xist Rating 3683 | -72.5 | 532.223 | 150.285 | 35.7 | 2338.59 | 8726.42 | 22589 | 0.85 | 3.27 | 15.673 | 46.42 | 1 | 1 | 1640 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1244651.3856 | 91802.2204 | 2619.5208 | 12854.7771 | 78947.4433 | 49186.4328 | 0.062486 | -379804.5964 | 379804.5964
C | Xist Rating 3684 | -72.22 | 538.491 | 150.285 | 35.7 | 2335.65 | 8717.6 | 22403.3 | 0.83 | 3.24 | 15.64 | 45.628 | 1 | 1 | 1650 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1257726.5041 | 92846.3122 | 2651.5635 | 12933.1599 | 79913.1523 | 48344.7041 | 0.062867 | -373304.9906 | 373304.9906
C | Xist Rating 3685 | -71.91 | 544.515 | 150.285 | 35.7 | 2337.38 | 8773.98 | 22221 | 0.82 | 3.2 | 15.642 | 44.842 | 1 | 1 | 1660 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1272738.4707 | 93896.2745 | 2683.8011 | 13011.5426 | 80884.7319 | 47522.7476 | 0.063248 | -366958.0604 | 366958.0604
C | Xist Rating 3686 | -71.07 | 563.956 | 150.285 | 35.7 | 2325.04 | 8708 | 21633.3 | 0.82 | 3.1 | 15.667 | 42.283 | 1 | 1 | 1670 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1311220.2582 | 94952.1074 | 2716.2334 | 13089.9254 | 81862.182 | 44872.5142 | 0.063629 | -346493.66 | 346493.66
C | Xist Rating 3687 | -70.87 | 566.716 | 150.285 | 35.7 | 2330.58 | 8800.05 | 21560.7 | 0.81 | 3.08 | 15.669 | 42.004 | 1 | 1 | 1680 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1320776.9753 | 96013.8109 | 2748.8606 | 13168.3082 | 82845.5027 | 44576.8556 | 0.06401 | -344210.6629 | 344210.6629
C | Xist Rating 3688 | -70.54 | 574.699 | 150.285 | 35.7 | 2325.42 | 8767.98 | 21346.3 | 0.8 | 3.04 | 15.647 | 41.139 | 1 | 1 | 1690 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1336416.5486 | 97081.385 | 2781.6825 | 13246.691 | 83834.694 | 43671.0405 | 0.064391 | -337216.1984 | 337216.1984
C | Xist Rating 3689 | -70.26 | 579.96 | 150.285 | 35.7 | 2327.31 | 8822.51 | 21206.1 | 0.79 | 3.02 | 15.646 | 40.58 | 1 | 1 | 1700 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1349746.7076 | 98154.8296 | 2814.6992 | 13325.0738 | 84829.7558 | 43084.1473 | 0.064772 | -332684.3651 | 332684.3651
C | Xist Rating 3690 | -69.97 | 586.177 | 150.285 | 35.7 | 2326.33 | 8840.84 | 21045 | 0.77 | 2.99 | 15.637 | 39.947 | 1 | 1 | 1710 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1363641.1404 | 99234.1448 | 2847.9107 | 13403.4566 | 85830.6882 | 42407.8017 | 0.065153 | -327461.8038 | 327461.8038
C | Xist Rating 3691 | -69.19 | 604.107 | 150.285 | 35.7 | 2316.49 | 8797.41 | 20567.6 | 0.77 | 2.9 | 15.668 | 38.017 | 1 | 1 | 1720 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1399407.8244 | 100319.3306 | 2881.317 | 13481.8394 | 86837.4912 | 40410.7372 | 0.065534 | -312041.0011 | 312041.0011
C | Xist Rating 3692 | -68.82 | 611.96 | 150.286 | 35.7 | 2314.95 | 8816.15 | 20374.8 | 0.76 | 2.87 | 15.661 | 37.281 | 1 | 1 | 1730 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1416656.802 | 101410.3869 | 2914.9181 | 13560.2221 | 87850.1647 | 39639.2476 | 0.065915 | -306083.763 | 306083.763
C | Xist Rating 3693 | -68.59 | 615.646 | 150.286 | 35.6 | 2319.31 | 8898.29 | 20290.3 | 0.75 | 2.85 | 15.661 | 36.978 | 1 | 1 | 1740 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1427873.9243 | 102507.3138 | 2948.714 | 13638.6049 | 88868.7089 | 39317.703 | 0.066296 | -303600.8808 | 303600.8808
C | Xist Rating 3694 | -68.35 | 622.852 | 150.286 | 35.6 | 2313.09 | 8844.27 | 20122.9 | 0.74 | 2.82 | 15.636 | 36.363 | 1 | 1 | 1750 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1440712.7327 | 103610.1113 | 2982.7046 | 13716.9877 | 89893.1236 | 38670.5553 | 0.066677 | -298603.7777 | 298603.7777
C | Xist Rating 3695 | -68.07 | 628.23 | 150.286 | 35.6 | 2312.69 | 8865.56 | 20001.2 | 0.73 | 2.8 | 15.639 | 35.919 | 1 | 1 | 1760 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1452901.2387 | 104718.7793 | 3016.8901 | 13795.3705 | 90923.4088 | 38202.4858 | 0.067058 | -294989.4692 | 294989.4692
C | Xist Rating 3696 | -67.16 | 649.474 | 150.286 | 35.6 | 2301.66 | 8819.71 | 19497.8 | 0.73 | 2.71 | 15.676 | 34.017 | 1 | 1 | 1770 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1494868.3268 | 105833.318 | 3051.2703 | 13873.7533 | 91959.5647 | 36234.5222 | 0.067439 | -279793.3756 | 279793.3756
C | Xist Rating 3697 | -66.9 | 654.962 | 150.286 | 35.6 | 2301.37 | 8842.62 | 19383.2 | 0.72 | 2.69 | 15.667 | 33.624 | 1 | 1 | 1780 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1507309.8979 | 106953.7272 | 3085.8453 | 13952.1361 | 93001.5911 | 35818.4972 | 0.06782 | -276580.9412 | 276580.9412
C | Xist Rating 3698 | -66.91 | 657.981 | 150.286 | 35.6 | 2291.82 | 8716.26 | 19327.4 | 0.7 | 2.68 | 15.827 | 33.441 | 1 | 1 | 1790 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1507974.0154 | 108080.0069 | 3120.6151 | 14030.5189 | 94049.4881 | 35617.3536 | 0.068201 | -275027.7635 | 275027.7635
C | Xist Rating 3699 | -66.52 | 667.586 | 150.286 | 35.6 | 2289.11 | 8725.72 | 19121.9 | 0.69 | 2.65 | 15.809 | 32.718 | 1 | 1 | 1800 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1528177.7885 | 109212.1573 | 3155.5797 | 14108.9017 | 95103.2556 | 34857.7133 | 0.068582 | -269162.0225 | 269162.0225
C | Xist Rating 3700 | -66.26 | 672.947 | 150.286 | 35.6 | 2289.04 | 8751.13 | 19012.5 | 0.69 | 2.63 | 15.808 | 32.347 | 1 | 1 | 1810 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1540402.6009 | 110350.1782 | 3190.7391 | 14187.2844 | 96162.8938 | 34477.264 | 0.068963 | -266224.2936 | 266224.2936
C | Xist Rating 3701 | -65.36 | 694.45 | 150.286 | 35.6 | 2278.12 | 8703.24 | 18562.8 | 0.68 | 2.55 | 15.844 | 30.767 | 1 | 1 | 1820 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1582040.434 | 111494.0697 | 3226.0933 | 14265.6672 | 97228.4025 | 32830.4265 | 0.069344 | -253507.8514 | 253507.8514
C | Xist Rating 3702 | -65.34 | 691.018 | 150.286 | 35.6 | 2291.36 | 8881.58 | 18631.6 | 0.68 | 2.56 | 15.866 | 31.017 | 1 | 1 | 1830 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1583371.0045 | 112643.8317 | 3261.6423 | 14344.05 | 98299.7817 | 33096.1077 | 0.069725 | -255559.3707 | 255559.3707
C | Xist Rating 3703 | -65 | 695.399 | 150.286 | 35.6 | 2299.75 | 9032.34 | 18545.7 | 0.67 | 2.55 | 15.886 | 30.735 | 1 | 1 | 1840 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1599243.8502 | 113799.4644 | 3297.386 | 14422.4328 | 99377.0316 | 32796.1065 | 0.070106 | -253242.8414 | 253242.8414
C | Xist Rating 3704 | -64.69 | 702.72 | 150.286 | 35.6 | 2296.48 | 9019.11 | 18409.7 | 0.66 | 2.52 | 15.877 | 30.295 | 1 | 1 | 1850 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1613782.4256 | 114960.9676 | 3333.3246 | 14500.8156 | 100460.152 | 32330.2721 | 0.070487 | -249645.7911 | 249645.7911
C | Xist Rating 3705 | -64.34 | 710.915 | 150.286 | 35.6 | 2293.32 | 9012.19 | 18259.6 | 0.65 | 2.5 | 15.869 | 29.812 | 1 | 1 | 1860 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1630355.5878 | 116128.3413 | 3369.4579 | 14579.1984 | 101549.143 | 31819.7036 | 0.070868 | -245703.3168 | 245703.3168
C | Xist Rating 3706 | -63.46 | 730.636 | 150.286 | 35.6 | 2287.06 | 9023.82 | 17880.1 | 0.65 | 2.43 | 15.915 | 28.544 | 1 | 1 | 1870 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1671008.3702 | 117301.5857 | 3405.7861 | 14657.5812 | 102644.0045 | 30510.0175 | 0.071249 | -235590.2678 | 235590.2678
C | Xist Rating 3707 | -63.03 | 738.816 | 150.286 | 35.6 | 2288.38 | 9086.25 | 17739.7 | 0.64 | 2.41 | 15.923 | 28.11 | 1 | 1 | 1880 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1690691.7581 | 118480.7006 | 3442.309 | 14735.964 | 103744.7366 | 30050.966 | 0.07163 | -232045.5939 | 232045.5939
C | Xist Rating 3708 | -62.76 | 744.225 | 150.286 | 35.6 | 2289.29 | 9128.81 | 17647.2 | 0.63 | 2.39 | 15.911 | 27.828 | 1 | 1 | 1890 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1703746.8503 | 119665.6861 | 3479.0267 | 14814.3467 | 104851.3393 | 29748.5472 | 0.072011 | -229710.396 | 229710.396
C | Xist Rating 3709 | -62.53 | 750.091 | 150.286 | 35.6 | 2286.26 | 9108.88 | 17556 | 0.62 | 2.38 | 15.901 | 27.565 | 1 | 1 | 1900 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1714903.0497 | 120856.5421 | 3515.9392 | 14892.7295 | 105963.8126 | 29465.8364 | 0.072392 | -227527.378 | 227527.378
C | Xist Rating 3710 | -62.29 | 755.678 | 150.286 | 35.6 | 2284.98 | 9116.66 | 17465.5 | 0.61 | 2.36 | 15.899 | 27.299 | 1 | 1 | 1910 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1726709.1164 | 122053.2688 | 3553.0464 | 14971.1123 | 107082.1564 | 29180.2968 | 0.072773 | -225322.517 | 225322.517
C | Xist Rating 3711 | -61.27 | 779.639 | 150.286 | 35.6 | 2275.67 | 9101.16 | 17050.5 | 0.61 | 2.29 | 15.946 | 25.992 | 1 | 1 | 1920 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1774201.0831 | 123255.866 | 3590.3485 | 15049.4951 | 108206.3709 | 27829.7941 | 0.073154 | -214894.2929 | 214894.2929
C | Xist Rating 3712 | -60.94 | 787.897 | 150.286 | 35.6 | 2272.07 | 9085.29 | 16924 | 0.6 | 2.27 | 15.938 | 25.628 | 1 | 1 | 1930 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1790157.1368 | 124464.3337 | 3627.8454 | 15127.8779 | 109336.4558 | 27441.9304 | 0.073535 | -211899.3122 | 211899.3122
C | Xist Rating 3713 | -60.66 | 790.554 | 150.286 | 35.6 | 2281.28 | 9248.58 | 16882.5 | 0.6 | 2.26 | 15.959 | 25.512 | 1 | 1 | 1940 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1803475.0291 | 125678.6721 | 3665.537 | 15206.2607 | 110472.4114 | 27326.8467 | 0.073916 | -211010.6669 | 211010.6669
C | Xist Rating 3714 | -60.43 | 798.446 | 150.286 | 35.6 | 2272.79 | 9147.96 | 16772.3 | 0.58 | 2.24 | 15.937 | 25.213 | 1 | 1 | 1950 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1814700.0843 | 126898.881 | 3703.4235 | 15284.6435 | 111614.2375 | 26991.6136 | 0.074297 | -208422.0856 | 208422.0856
C | Xist Rating 3715 | -60.04 | 807.457 | 150.286 | 35.6 | 2270.02 | 9149.57 | 16637.2 | 0.57 | 2.22 | 15.953 | 24.825 | 1 | 1 | 1960 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1832943.5391 | 128124.9605 | 3741.5047 | 15363.0262 | 112761.9342 | 26579.6192 | 0.074678 | -205240.7737 | 205240.7737
C | Xist Rating 3716 | -59.12 | 829.089 | 150.286 | 35.6 | 2262.56 | 9146.6 | 16303.4 | 0.57 | 2.16 | 16.01 | 23.842 | 1 | 1 | 1970 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1875863.6078 | 129356.9105 | 3779.7807 | 15441.409 | 113915.5015 | 25565.7202 | 0.075059 | -197411.7149 | 197411.7149
C | Xist Rating 3717 | -58.8 | 835.53 | 150.286 | 35.6 | 2263.01 | 9186.55 | 16214.4 | 0.57 | 2.15 | 16.024 | 23.602 | 1 | 1 | 1980 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1890812.7453 | 130594.7311 | 3818.2515 | 15519.7918 | 115074.9393 | 25321.2794 | 0.07544 | -195524.2078 | 195524.2078
C | Xist Rating 3718 | -58.48 | 843.982 | 150.286 | 35.6 | 2258.8 | 9159.03 | 16101.6 | 0.56 | 2.13 | 16.029 | 23.301 | 1 | 1 | 1990 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1906386.5416 | 131838.4223 | 3856.9171 | 15598.1746 | 116240.2477 | 24998.7417 | 0.075821 | -193033.6572 | 193033.6572
C | Xist Rating 3719 | -58.18 | 850.549 | 150.286 | 35.6 | 2257.83 | 9175.5 | 16015.1 | 0.55 | 2.12 | 16.028 | 23.074 | 1 | 1 | 2000 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1920395.0487 | 133087.9841 | 3895.7775 | 15676.5574 | 117411.4267 | 24752.607 | 0.076202 | -191133.0697 | 191133.0697
C | Xist Rating 3720 | -57.95 | 855.403 | 150.286 | 35.6 | 2258.36 | 9207.51 | 15954 | 0.54 | 2.11 | 16.032 | 22.92 | 1 | 1 | 2010 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1931807.9191 | 134343.4164 | 3934.8326 | 15754.9402 | 118588.4763 | 24582.3834 | 0.076583 | -189818.6489 | 189818.6489
C | Xist Rating 3721 | -56.96 | 879.811 | 150.286 | 35.6 | 2248.21 | 9170.86 | 15615.1 | 0.54 | 2.05 | 16.069 | 21.979 | 1 | 1 | 2020 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1977999.8883 | 135604.7194 | 3974.0826 | 15833.323 | 119771.3964 | 23610.8461 | 0.076964 | -182316.6953 | 182316.6953
C | Xist Rating 3722 | -56.55 | 888.767 | 150.286 | 35.6 | 2247.46 | 9204.43 | 15499.9 | 0.53 | 2.03 | 16.073 | 21.678 | 1 | 1 | 2030 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 1997468.2818 | 136871.8928 | 4013.5273 | 15911.7058 | 120960.1871 | 23287.7187 | 0.077345 | -179821.5912 | 179821.5912
C | Xist Rating 3723 | -56.33 | 894.832 | 150.286 | 35.6 | 2244.28 | 9178.89 | 15431.7 | 0.52 | 2.02 | 16.064 | 21.517 | 1 | 1 | 2040 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2008253.561 | 138144.9369 | 4053.1669 | 15990.0885 | 122154.8483 | 23109.2135 | 0.077726 | -178443.2211 | 178443.2211
C | Xist Rating 3724 | -56.03 | 900.083 | 150.286 | 35.6 | 2247.17 | 9255.27 | 15364.4 | 0.52 | 2.01 | 16.077 | 21.344 | 1 | 1 | 2050 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2022639.5151 | 139423.8515 | 4093.0012 | 16068.4713 | 123355.3802 | 22933.9188 | 0.078107 | -177089.6417 | 177089.6417
C | Xist Rating 3725 | -55.74 | 908.93 | 150.286 | 35.6 | 2240.88 | 9190.79 | 15264.4 | 0.51 | 1.99 | 16.064 | 21.103 | 1 | 1 | 2060 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2036803.0584 | 140708.6367 | 4133.0303 | 16146.8541 | 124561.7826 | 22671.9305 | 0.078488 | -175066.6377 | 175066.6377
C | Xist Rating 3726 | -54.69 | 935.154 | 150.286 | 35.6 | 2230.42 | 9154.05 | 14936.3 | 0.51 | 1.94 | 16.101 | 20.244 | 1 | 1 | 2070 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2085786.1847 | 141999.2925 | 4173.2542 | 16225.2369 | 125774.0556 | 21785.2836 | 0.078869 | -168220.1852 | 168220.1852
C | Xist Rating 3727 | -54.45 | 941.022 | 150.286 | 35.6 | 2229.27 | 9161.84 | 14873.5 | 0.5 | 1.93 | 16.097 | 20.1 | 1 | 1 | 2080 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2097792.1139 | 143295.8188 | 4213.6729 | 16303.6197 | 126992.1991 | 21624.2223 | 0.07925 | -166976.5127 | 166976.5127
C | Xist Rating 3728 | -54.14 | 948.543 | 150.286 | 35.6 | 2227.47 | 9167.69 | 14790.9 | 0.5 | 1.91 | 16.095 | 19.904 | 1 | 1 | 2090 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2112851.0762 | 144598.2157 | 4254.2864 | 16382.0025 | 128216.2132 | 21424.1906 | 0.079631 | -165431.9212 | 165431.9212
C | Xist Rating 3729 | -53.83 | 956.073 | 150.286 | 35.6 | 2225.59 | 9172.03 | 14709.2 | 0.49 | 1.9 | 16.093 | 19.712 | 1 | 1 | 2100 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2127826.5081 | 145906.4832 | 4295.0947 | 16460.3853 | 129446.0979 | 21213.1635 | 0.080012 | -163802.4252 | 163802.4252
C | Xist Rating 3730 | -53.57 | 962.733 | 150.286 | 35.6 | 2223.72 | 9171.98 | 14638.7 | 0.48 | 1.89 | 16.094 | 19.549 | 1 | 1 | 2110 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2140848.6268 | 147220.6213 | 4336.0977 | 16538.7681 | 130681.8532 | 21032.2475 | 0.080393 | -162405.4404 | 162405.4404
C | Xist Rating 3731 | -52.59 | 987.582 | 150.286 | 35.6 | 2213.96 | 9134.1 | 14359 | 0.48 | 1.84 | 16.131 | 18.86 | 1 | 1 | 2120 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2186467.0447 | 148540.6299 | 4377.2956 | 16617.1508 | 131923.479 | 20321.8726 | 0.080774 | -156920.1133 | 156920.1133
C | Xist Rating 3732 | -52.24 | 996.88 | 150.286 | 35.6 | 2210.67 | 9122.82 | 14263.7 | 0.48 | 1.83 | 16.126 | 18.641 | 1 | 1 | 2130 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2203772.7096 | 149866.5091 | 4418.6882 | 16695.5336 | 133170.9755 | 20097.683 | 0.081155 | -155188.9808 | 155188.9808
C | Xist Rating 3733 | -51.87 | 1006.2 | 150.286 | 35.6 | 2208.04 | 9122.36 | 14170 | 0.47 | 1.81 | 16.124 | 18.429 | 1 | 1 | 2140 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2221729.848 | 151198.2588 | 4460.2756 | 16773.9164 | 134424.3424 | 19865.432 | 0.081536 | -153395.6 | 153395.6
C | Xist Rating 3734 | -51.64 | 1011.21 | 150.286 | 35.6 | 2208.18 | 9147.04 | 14123.5 | 0.47 | 1.8 | 16.12 | 18.332 | 1 | 1 | 2150 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2232933.6978 | 152535.8792 | 4502.0578 | 16852.2992 | 135683.58 | 19767.9134 | 0.081917 | -152642.5873 | 152642.5873
C | Xist Rating 3735 | -51.36 | 1017.81 | 150.286 | 35.6 | 2207.19 | 9161.26 | 14059.1 | 0.46 | 1.79 | 16.119 | 18.191 | 1 | 1 | 2160 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2246500.0539 | 153879.3701 | 4544.0348 | 16930.682 | 136948.6881 | 19609.2291 | 0.082298 | -151417.2692 | 151417.2692
C | Xist Rating 3736 | -50.34 | 1044.69 | 150.286 | 35.6 | 2196.22 | 9107.56 | 13786.1 | 0.46 | 1.75 | 16.154 | 17.555 | 1 | 1 | 2170 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2294369.0718 | 155228.7316 | 4586.2066 | 17009.0648 | 138219.6668 | 18953.6338 | 0.082679 | -146354.9359 | 146354.9359
C | Xist Rating 3737 | -49.97 | 1053.76 | 150.286 | 35.6 | 2194.46 | 9121.35 | 13699.1 | 0.46 | 1.74 | 16.152 | 17.363 | 1 | 1 | 2180 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2312434.1696 | 156583.9636 | 4628.5732 | 17087.4476 | 139496.5161 | 18757.483 | 0.08306 | -144840.3118 | 144840.3118
C | Xist Rating 3738 | -49.72 | 1060.6 | 150.286 | 35.6 | 2192.34 | 9115.48 | 13639 | 0.45 | 1.73 | 16.148 | 17.24 | 1 | 1 | 2190 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2325195.804 | 157945.0663 | 4671.1346 | 17165.8303 | 140779.2359 | 18617.0457 | 0.083441 | -143755.8919 | 143755.8919
C | Xist Rating 3739 | -49.48 | 1067.85 | 150.286 | 35.6 | 2188.22 | 9075.03 | 13579.4 | 0.44 | 1.72 | 16.143 | 17.122 | 1 | 1 | 2200 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2336690.727 | 159312.0394 | 4713.8907 | 17244.2131 | 142067.8263 | 18481.6189 | 0.083822 | -142710.1623 | 142710.1623
C | Xist Rating 3740 | -49.13 | 1077.18 | 150.286 | 35.6 | 2185.42 | 9070.28 | 13495.4 | 0.44 | 1.7 | 16.141 | 16.944 | 1 | 1 | 2210 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2354090.7156 | 160684.8832 | 4756.8417 | 17322.5959 | 143362.2873 | 18299.8629 | 0.084203 | -141306.6904 | 141306.6904
C | Xist Rating 3741 | -48.1 | 1103.92 | 150.286 | 35.6 | 2176.24 | 9043.46 | 13246.2 | 0.44 | 1.66 | 16.179 | 16.391 | 1 | 1 | 2220 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2402394.8608 | 162063.5976 | 4799.9874 | 17400.9787 | 144662.6188 | 17730.4205 | 0.084584 | -136909.6076 | 136909.6076
C | Xist Rating 3742 | -47.8 | 1111.42 | 150.286 | 35.6 | 2175.06 | 9057.39 | 13182.5 | 0.43 | 1.65 | 16.176 | 16.262 | 1 | 1 | 2230 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2417405.1852 | 163448.1825 | 4843.3279 | 17479.3615 | 145968.821 | 17583.3439 | 0.084965 | -135773.9207 | 135773.9207
C | Xist Rating 3743 | -47.49 | 1120.23 | 150.286 | 35.6 | 2171.66 | 9037.09 | 13111.7 | 0.43 | 1.64 | 16.176 | 16.122 | 1 | 1 | 2240 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2432758.6818 | 164838.6379 | 4886.8633 | 17557.7443 | 147280.8937 | 17441.072 | 0.085346 | -134675.3347 | 134675.3347
C | Xist Rating 3744 | -47.15 | 1129.87 | 150.286 | 35.6 | 2167.74 | 9011.78 | 13034.1 | 0.42 | 1.63 | 16.171 | 15.967 | 1 | 1 | 2250 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2449264.3938 | 166234.964 | 4930.5934 | 17636.1271 | 148598.8369 | 17266.6964 | 0.085727 | -133328.8527 | 133328.8527
C | Xist Rating 3745 | -46.94 | 1134.84 | 150.286 | 35.6 | 2167.62 | 9030.91 | 12995.6 | 0.42 | 1.62 | 16.171 | 15.896 | 1 | 1 | 2260 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2459901.8808 | 167637.1606 | 4974.5182 | 17714.5099 | 149922.6508 | 17196.0074 | 0.086108 | -132783.0112 | 132783.0112
C | Xist Rating 3746 | -45.87 | 1163.7 | 150.286 | 35.6 | 2157.06 | 8985.04 | 12751.9 | 0.42 | 1.59 | 16.207 | 15.384 | 1 | 1 | 2270 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2510170.722 | 169045.2278 | 5018.6379 | 17792.8926 | 151252.3352 | 16668.8791 | 0.086489 | -128712.6662 | 128712.6662
C | Xist Rating 3747 | -45.56 | 1172.46 | 150.286 | 35.6 | 2154.29 | 8974.61 | 12686.2 | 0.41 | 1.58 | 16.203 | 15.259 | 1 | 1 | 2280 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2525818.8534 | 170459.1656 | 5062.9524 | 17871.2754 | 152587.8901 | 16525.3868 | 0.08687 | -127604.6566 | 127604.6566
C | Xist Rating 3748 | -45.15 | 1182.72 | 150.286 | 35.6 | 2152.15 | 8983.4 | 12606.9 | 0.41 | 1.56 | 16.202 | 15.105 | 1 | 1 | 2290 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2545390.848 | 171878.9739 | 5107.4617 | 17949.6582 | 153929.3157 | 16368.3938 | 0.087251 | -126392.398 | 126392.398
C | Xist Rating 3749 | -44.9 | 1189.72 | 150.286 | 35.6 | 2150.25 | 8979.49 | 12557 | 0.4 | 1.56 | 16.199 | 15.014 | 1 | 1 | 2300 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2558195.43 | 173304.6528 | 5152.1657 | 18028.041 | 155276.6118 | 16260.0406 | 0.087632 | -125555.7235 | 125555.7235
| Xist Rating 3750 | -44.66 | 1196.99 | 150.286 | 35.6 | 2147.08 | 8953.3 | 12507.6 | 0.4 | 1.55 | 16.195 | 14.927 | 1 | 1 | 2310 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2570033.2892 | 174736.2023 | 5197.0645 | 18106.4238 | 156629.7785 | 16172.43 | 0.088013 | -124879.2179 | 124879.2179
| Xist Rating 3751 | -43.56 | 1226.57 | 150.286 | 35.6 | 2137.99 | 8933.04 | 12277.1 | 0.4 | 1.51 | 16.232 | 14.465 | 1 | 1 | 2320 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2622394.3943 | 176173.6224 | 5242.1582 | 18184.8066 | 157988.8158 | 15697.0866 | 0.088394 | -121208.7419 | 121208.7419
| Xist Rating 3752 | -43.25 | 1235.36 | 150.286 | 35.6 | 2135.03 | 8918.19 | 12216.8 | 0.39 | 1.5 | 16.226 | 14.356 | 1 | 1 | 2330 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2637530.6608 | 177616.913 | 5287.4466 | 18263.1894 | 159353.7236 | 15569.6033 | 0.088775 | -120224.3498 | 120224.3498
| Xist Rating 3753 | -42.93 | 1244.13 | 150.286 | 35.6 | 2132.62 | 8912.97 | 12157.2 | 0.39 | 1.49 | 16.222 | 14.249 | 1 | 1 | 2340 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2653256.5206 | 179066.0742 | 5332.9298 | 18341.5722 | 160724.502 | 15461.1569 | 0.089156 | -119386.9555 | 119386.9555
| Xist Rating 3754 | -42.66 | 1252.12 | 150.286 | 35.6 | 2129.85 | 8897.15 | 12104.7 | 0.38 | 1.49 | 16.217 | 14.158 | 1 | 1 | 2350 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2666827.782 | 180521.1059 | 5378.6078 | 18419.9549 | 162101.151 | 15352.2014 | 0.089537 | -118545.6296 | 118545.6296
| Xist Rating 3755 | -42.34 | 1261.81 | 150.286 | 35.6 | 2126.12 | 8872.5 | 12039.9 | 0.38 | 1.48 | 16.211 | 14.041 | 1 | 1 | 2360 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2682759.4772 | 181982.0083 | 5424.4805 | 18498.3377 | 163483.6705 | 15233.2182 | 0.089918 | -117626.8729 | 117626.8729
| Xist Rating 3756 | -41.35 | 1288.98 | 150.286 | 35.6 | 2118.02 | 8853.35 | 11846.8 | 0.38 | 1.45 | 16.245 | 13.674 | 1 | 1 | 2370 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2730085.4196 | 183448.7812 | 5470.5481 | 18576.7205 | 164872.0607 | 14856.2231 | 0.090299 | -114715.8167 | 114715.8167
| Xist Rating 3757 | -41.05 | 1297.99 | 150.286 | 35.6 | 2114.74 | 8831.95 | 11791.2 | 0.37 | 1.44 | 16.236 | 13.58 | 1 | 1 | 2380 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2744911.3726 | 184921.4247 | 5516.8105 | 18655.1033 | 166266.3214 | 14743.6854 | 0.09068 | -113846.8309 | 113846.8309
| Xist Rating 3758 | -40.71 | 1307.23 | 150.286 | 35.6 | 2112.77 | 8837.24 | 11730 | 0.37 | 1.43 | 16.235 | 13.471 | 1 | 1 | 2390 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 2761876.3271 | 186399.9387 | 5563.2676 | 18733.4861 | 167666.4526 | 14633.1422 | 0.091061 | -112993.2456 | 112993.2456
C | Xist Rating 3762 | -33.75 | 1502.81 | 150.286 | 35.6 | 2056.13 | 8687.96 | 10537.9 | 0.39 | 1.25 | 16.265 | 11.385 | 1 | 1 | 2430 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 3089972.7253 | 192372.7006 | 5751.0441 | 19047.0172 | 173325.6834 | 12514.2469 | 0.092585 | -96631.6975 | 96631.6975
C | Xist Rating 3763 | -33.71 | 1504.18 | 150.286 | 35.6 | 2056.41 | 8693.02 | 10537.9 | 0.38 | 1.25 | 16.256 | 11.396 | 1 | 1 | 2440 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 3093210.7938 | 193880.5675 | 5798.4752 | 19125.4 | 174755.1675 | 12510.3504 | 0.092966 | -96601.6093 | 96601.6093
C | Xist Rating 3764 | -33.71 | 1505.51 | 150.286 | 35.6 | 2055.39 | 8674.76 | 10537.9 | 0.38 | 1.25 | 16.249 | 11.407 | 1 | 1 | 2450 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 3094410.1989 | 195394.305 | 5846.1011 | 19203.7828 | 176190.5222 | 12524.2507 | 0.093347 | -96708.9438 | 96708.9438
C | Xist Rating 3765 | -33.69 | 1506.98 | 150.286 | 35.6 | 2054.6 | 8660.8 | 10537.8 | 0.37 | 1.25 | 16.244 | 11.418 | 1 | 1 | 2460 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 3096241.108 | 196913.9131 | 5893.9217 | 19282.1656 | 177631.7475 | 12520.3203 | 0.093728 | -96678.5949 | 96678.5949
C | Xist Rating 3766 | -33.67 | 1508.33 | 150.286 | 35.6 | 2054.25 | 8654.66 | 10537.8 | 0.36 | 1.25 | 16.28 | 11.429 | 1 | 1 | 2470 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 3098486.9025 | 198439.3917 | 5941.9372 | 19360.5484 | 179078.8433 | 12517.888 | 0.094109 | -96659.8126 | 96659.8126
C | Xist Rating 3767 | -33.65 | 1509.68 | 150.286 | 35.6 | 2053.77 | 8646.04 | 10537.8 | 0.36 | 1.25 | 16.273 | 11.439 | 1 | 1 | 2480 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 3100535.4936 | 199970.7409 | 5990.1474 | 19438.9312 | 180531.8097 | 12530.6199 | 0.09449 | -96758.1252 | 96758.1252
C | Xist Rating 3768 | -33.63 | 1511.08 | 150.286 | 35.6 | 2053.18 | 8635.59 | 10537.8 | 0.35 | 1.25 | 16.267 | 11.45 | 1 | 1 | 2490 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 3102519.2344 | 201507.9606 | 6038.5525 | 19517.314 | 181990.6467 | 12526.2721 | 0.094871 | -96724.5527 | 96724.5527
C | Xist Rating 3769 | -33.61 | 1512.06 | 150.286 | 35.6 | 2053.27 | 8637.14 | 10537.8 | 0.35 | 1.25 | 16.266 | 11.459 | 1 | 1 | 2500 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 3104667.4362 | 203051.051 | 6087.1523 | 19595.6967 | 183455.3542 | 12538.1314 | 0.095252 | -96816.1273 | 96816.1273
C | Xist Rating 3770 | -33.63 | 1513.91 | 150.286 | 35.6 | 2050.91 | 8595.53 | 10537.9 | 0.34 | 1.25 | 16.264 | 11.471 | 1 | 1 | 2510 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 3104893.1581 | 204600.0119 | 6135.9469 | 19674.0795 | 184925.9323 | 12534.768 | 0.095633 | -96790.1555 | 96790.1555
C | Xist Rating 3771 | -33.6 | 1515.37 | 150.286 | 35.6 | 2050.42 | 8586.99 | 10537.8 | 0.34 | 1.25 | 16.301 | 11.482 | 1 | 1 | 2520 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 16 | E | Rod | 3107144.9554 | 206154.8434 | 6184.9363 | 19752.4623 | 186402.381 | 12550.0911 | 0.096014 | -96908.4771 | 96908.4771
C | Xist Rating 3772 | -33.58 | 1516.7 | 150.286 | 35.6 | 2050.15 | 8582.3 | 10537.9 | 0.33 | 1.25 | 16.291 | 11.493 | 1 | 1 | 2530 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3109462.505 | 207715.5454 | 6234.1205 | 19830.8451 | 187884.7003 | 12545.1383 | 0.096395 | -96870.233 | 96870.233
C | Xist Rating 3773 | -33.56 | 1517.85 | 150.286 | 35.6 | 2050.06 | 8580.68 | 10537.8 | 0.33 | 1.25 | 16.285 | 11.502 | 1 | 1 | 2540 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3111683.571 | 209282.118 | 6283.4995 | 19909.2279 | 189372.8901 | 12556.6692 | 0.096776 | -96959.2711 | 96959.2711
C | Xist Rating 3774 | -33.54 | 1519.4 | 150.286 | 35.6 | 2049.32 | 8567.8 | 10537.8 | 0.32 | 1.25 | 16.28 | 11.513 | 1 | 1 | 2550 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3113736.808 | 210854.5612 | 6333.0732 | 19987.6107 | 190866.9505 | 12551.7045 | 0.097157 | -96920.9348 | 96920.9348
C | Xist Rating 3775 | -33.51 | 1520.85 | 150.286 | 35.6 | 2049.13 | 8564.5 | 10537.8 | 0.32 | 1.25 | 16.29 | 11.524 | 1 | 1 | 2560 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3116419.3605 | 212432.875 | 6382.8418 | 20065.9935 | 192366.8815 | 12565.8303 | 0.097538 | -97030.011 | 97030.011
C | Xist Rating 3776 | -33.49 | 1522.24 | 150.287 | 35.6 | 2048.59 | 8555.04 | 10537.8 | 0.31 | 1.25 | 16.287 | 11.534 | 1 | 1 | 2570 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3118445.6416 | 214017.0593 | 6432.8051 | 20144.3763 | 193872.6831 | 12559.6788 | 0.097919 | -96982.5107 | 96982.5107
C | Xist Rating 3777 | -33.47 | 1523.6 | 150.287 | 35.6 | 2048.36 | 8550.97 | 10537.7 | 0.31 | 1.25 | 16.324 | 11.544 | 1 | 1 | 2580 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3120881.296 | 215607.1142 | 6482.9633 | 20222.759 | 195384.3552 | 12573.6535 | 0.0983 | -97090.4192 | 97090.4192
C | Xist Rating 3778 | -33.44 | 1524.96 | 150.287 | 35.6 | 2048.07 | 8546.08 | 10537.7 | 0.3 | 1.25 | 16.318 | 11.554 | 1 | 1 | 2590 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3123224.8272 | 217203.0397 | 6533.3162 | 20301.1418 | 196901.8979 | 12567.1463 | 0.098681 | -97040.1727 | 97040.1727
C | Xist Rating 3779 | -33.42 | 1526.14 | 150.287 | 35.6 | 2047.93 | 8543.7 | 10537.6 | 0.3 | 1.25 | 16.314 | 11.563 | 1 | 1 | 2600 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3125427.8902 | 218804.8357 | 6583.8639 | 20379.5246 | 198425.3111 | 12578.5473 | 0.099062 | -97128.2081 | 97128.2081
C | Xist Rating 3780 | -33.4 | 1527.83 | 150.287 | 35.6 | 2047.16 | 8530.26 | 10537.6 | 0.3 | 1.25 | 16.313 | 11.575 | 1 | 1 | 2610 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3127712.4628 | 220412.5024 | 6634.6064 | 20457.9074 | 199954.595 | 12593.168 | 0.099443 | -97241.1052 | 97241.1052
C | Xist Rating 3781 | -33.37 | 1529.22 | 150.287 | 35.6 | 2046.9 | 8525.78 | 10537.6 | 0.29 | 1.25 | 16.314 | 11.585 | 1 | 1 | 2620 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3130160.418 | 222026.0396 | 6685.5437 | 20536.2902 | 201489.7494 | 12586.6226 | 0.099824 | -97190.5636 | 97190.5636
C | Xist Rating 3782 | -33.35 | 1530.65 | 150.287 | 35.6 | 2046.53 | 8519.34 | 10537.6 | 0.29 | 1.25 | 16.35 | 11.595 | 1 | 1 | 2630 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3132521.1445 | 223645.4473 | 6736.6758 | 20614.673 | 203030.7743 | 12600.3591 | 0.10021 | -97296.6326 | 97296.6326
C | Xist Rating 3783 | -33.33 | 1531.9 | 150.287 | 35.6 | 2046.08 | 8511.54 | 10537.7 | 0.28 | 1.25 | 16.346 | 11.605 | 1 | 1 | 2640 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3134389.952 | 225270.7257 | 6788.0027 | 20693.0558 | 204577.6699 | 12593.3887 | 0.10059 | -97242.8098 | 97242.8098
C | Xist Rating 3784 | -33.29 | 1533.4 | 150.287 | 35.6 | 2046.17 | 8513.1 | 10537.7 | 0.28 | 1.25 | 16.343 | 11.615 | 1 | 1 | 2650 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3137597.078 | 226901.8746 | 6839.5243 | 20771.4385 | 206130.436 | 12605.7255 | 0.10097 | -97338.0711 | 97338.0711
C | Xist Rating 3785 | -33.26 | 1534.74 | 150.287 | 35.6 | 2046.02 | 8510.39 | 10537.7 | 0.28 | 1.25 | 16.34 | 11.625 | 1 | 1 | 2660 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3140108.7348 | 228538.894 | 6891.2408 | 20849.8213 | 207689.0727 | 12618.0615 | 0.10135 | -97433.3266 | 97433.3266
C | Xist Rating 3786 | -33.24 | 1536.13 | 150.287 | 35.6 | 2045.64 | 8503.91 | 10537.6 | 0.27 | 1.25 | 16.336 | 11.635 | 1 | 1 | 2670 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3142368.9732 | 230181.7841 | 6943.152 | 20928.2041 | 209253.58 | 12610.8121 | 0.10173 | -97377.3481 | 97377.3481
C | Xist Rating 3787 | -33.23 | 1537.55 | 150.287 | 35.6 | 2044.88 | 8490.94 | 10537.6 | 0.27 | 1.25 | 16.375 | 11.645 | 1 | 1 | 2680 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3144105.244 | 231830.5447 | 6995.258 | 21006.5869 | 210823.9578 | 12624.4391 | 0.10211 | -97482.5726 | 97482.5726
C | Xist Rating 3788 | -33.19 | 1538.92 | 150.287 | 35.6 | 2045.02 | 8493.27 | 10537.6 | 0.26 | 1.25 | 16.371 | 11.655 | 1 | 1 | 2690 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3147122.1784 | 233485.1759 | 7047.5588 | 21084.9697 | 212400.2062 | 12616.9358 | 0.10249 | -97424.634 | 97424.634
C | Xist Rating 3789 | -33.18 | 1540.12 | 150.287 | 35.6 | 2044.49 | 8484.15 | 10537.6 | 0.26 | 1.25 | 16.364 | 11.664 | 1 | 1 | 2700 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3148759.9388 | 235145.6777 | 7100.0544 | 21163.3525 | 213982.3252 | 12627.97 | 0.10287 | -97509.8369 | 97509.8369
C | Xist Rating 3790 | -33.14 | 1541.78 | 150.287 | 35.6 | 2044.13 | 8477.84 | 10537.6 | 0.26 | 1.25 | 16.36 | 11.675 | 1 | 1 | 2710 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3151598.7514 | 236812.05 | 7152.7448 | 21241.7353 | 215570.3147 | 12641.1743 | 0.10325 | -97611.7968 | 97611.7968
C | Xist Rating 3791 | -33.1 | 1543.12 | 150.287 | 35.6 | 2044.1 | 8477.39 | 10537.6 | 0.26 | 1.25 | 16.356 | 11.685 | 1 | 1 | 2720 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3154291.592 | 238484.2929 | 7205.63 | 21320.1181 | 217164.1748 | 12653.3391 | 0.10363 | -97705.7305 | 97705.7305
C | Xist Rating 3792 | -33.1 | 1544.44 | 150.287 | 35.6 | 2043.28 | 8463.25 | 10537.6 | 0.25 | 1.25 | 16.389 | 11.694 | 1 | 1 | 2730 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3155723.3632 | 240162.4064 | 7258.71 | 21398.5008 | 218763.9055 | 12645.5863 | 0.10402 | -97645.8654 | 97645.8654
C | Xist Rating 3793 | -33.08 | 1545.73 | 150.287 | 35.6 | 2043.01 | 8458.71 | 10537.6 | 0.25 | 1.25 | 16.385 | 11.703 | 1 | 1 | 2740 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3157941.8473 | 241846.3904 | 7311.9847 | 21476.8836 | 220369.5068 | 12656.6465 | 0.1044 | -97731.2697 | 97731.2697
C | Xist Rating 3794 | -33.08 | 1547.28 | 150.287 | 35.6 | 2041.71 | 8436.44 | 10537.6 | 0.25 | 1.25 | 16.379 | 11.714 | 1 | 1 | 2750 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3159097.0488 | 243536.245 | 7365.4543 | 21555.2664 | 221980.9786 | 12669.7213 | 0.10478 | -97832.2291 | 97832.2291
C | Xist Rating 3795 | -33.05 | 1548.7 | 150.287 | 35.6 | 2041.32 | 8429.8 | 10537.6 | 0.24 | 1.25 | 16.379 | 11.724 | 1 | 1 | 2760 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3161392.284 | 245231.9702 | 7419.1186 | 21633.6492 | 223598.321 | 12661.6782 | 0.10516 | -97770.1232 | 97770.1232
C | Xist Rating 3796 | -33.01 | 1549.94 | 150.287 | 35.6 | 2041.71 | 8436.36 | 10537.7 | 0.24 | 1.25 | 16.381 | 11.733 | 1 | 1 | 2770 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3164527.9974 | 246933.566 | 7472.9777 | 21712.032 | 225221.534 | 12672.8464 | 0.10554 | -97856.3605 | 97856.3605
C | Xist Rating 3797 | -33.01 | 1551.48 | 150.287 | 35.6 | 2040.32 | 8412.69 | 10537.6 | 0.24 | 1.25 | 16.414 | 11.743 | 1 | 1 | 2780 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3165515.6736 | 248641.0323 | 7527.0316 | 21790.4148 | 226850.6175 | 12685.9805 | 0.10592 | -97957.779 | 97957.779
C | Xist Rating 3798 | -32.95 | 1552.89 | 150.287 | 35.6 | 2041.05 | 8425.1 | 10537.7 | 0.23 | 1.25 | 16.417 | 11.753 | 1 | 1 | 2790 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3169526.1345 | 250354.3692 | 7581.2803 | 21868.7976 | 228485.5717 | 12677.6901 | 0.1063 | -97893.7628 | 97893.7628
C | Xist Rating 3799 | -32.76 | 1553.87 | 150.287 | 35.6 | 2046.36 | 8516.31 | 10537.8 | 0.23 | 1.25 | 16.435 | 11.761 | 1 | 1 | 2800 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3179777.4132 | 252073.5767 | 7635.7238 | 21947.1804 | 230126.3963 | 12688.2103 | 0.10668 | -97974.9965 | 97974.9965
C | Xist Rating 3800 | -32.82 | 1555.61 | 150.287 | 35.6 | 2042.97 | 8457.79 | 10537.8 | 0.23 | 1.25 | 16.423 | 11.772 | 1 | 1 | 2810 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3178064.5617 | 253798.6547 | 7690.3621 | 22025.5631 | 231773.0916 | 12700.9805 | 0.10706 | -98073.6048 | 98073.6048
C | Xist Rating 3801 | -32.54 | 1557.09 | 150.287 | 35.6 | 2050.33 | 8585.28 | 10538 | 0.22 | 1.25 | 16.463 | 11.782 | 1 | 1 | 2820 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3192548.3397 | 255529.6034 | 7745.1952 | 22103.9459 | 233425.6574 | 12693.4114 | 0.10744 | -98015.1585 | 98015.1585
C | Xist Rating 3802 | -32.79 | 1558.46 | 150.287 | 35.6 | 2041.57 | 8433.9 | 10537.8 | 0.22 | 1.25 | 16.46 | 11.791 | 1 | 1 | 2830 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3181705.1822 | 257266.4226 | 7800.223 | 22182.3287 | 235084.0938 | 12704.2977 | 0.10783 | -98099.2192 | 98099.2192
C | Xist Rating 3803 | -32.44 | 1559.78 | 150.287 | 35.6 | 2051.68 | 8608.97 | 10538 | 0.22 | 1.25 | 16.511 | 11.801 | 1 | 1 | 2840 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3200169.4304 | 259009.1123 | 7855.4457 | 22260.7115 | 236748.4008 | 12717.7342 | 0.10821 | -98202.9723 | 98202.9723
C | Xist Rating 3804 | -31.99 | 1561.22 | 150.287 | 35.6 | 2064.42 | 8837.84 | 10538.1 | 0.22 | 1.25 | 16.582 | 11.811 | 1 | 1 | 2850 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3223013.7924 | 260757.6726 | 7910.8631 | 22339.0943 | 238418.5784 | 12731.7429 | 0.10859 | -98311.1435 | 98311.1435
C | Xist Rating 3805 | -31.6 | 1562.63 | 150.287 | 35.6 | 2075.45 | 9043.44 | 10538.1 | 0.21 | 1.25 | 16.64 | 11.821 | 1 | 1 | 2860 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3243160.4335 | 262512.1035 | 7966.4753 | 22417.4771 | 240094.6265 | 12724.0666 | 0.10897 | -98251.8699 | 98251.8699
C | Xist Rating 3806 | -31.37 | 1563.82 | 150.287 | 35.6 | 2081.43 | 9158.2 | 10538.1 | 0.21 | 1.25 | 16.66 | 11.83 | 1 | 1 | 2870 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3254981.8626 | 264272.405 | 8022.2824 | 22495.8599 | 241776.5452 | 12735.5198 | 0.10935 | -98340.3081 | 98340.3081
C | Xist Rating 3807 | -31.25 | 1565.32 | 150.287 | 35.6 | 2083.85 | 9205.27 | 10538.1 | 0.21 | 1.25 | 16.709 | 11.84 | 1 | 1 | 2880 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3261892.082 | 266038.5771 | 8078.2842 | 22574.2426 | 243464.3344 | 12748.8014 | 0.10973 | -98442.8651 | 98442.8651
C | Xist Rating 3808 | -31.11 | 1566.67 | 150.287 | 35.6 | 2087.27 | 9272.38 | 10538.1 | 0.2 | 1.25 | 16.718 | 11.85 | 1 | 1 | 2890 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3270063.2909 | 267810.6197 | 8134.4807 | 22652.6254 | 245157.9942 | 12739.347 | 0.11011 | -98369.861 | 98369.861
C | Xist Rating 3809 | -30.99 | 1568.05 | 150.287 | 35.6 | 2089.72 | 9320.87 | 10538.1 | 0.2 | 1.25 | 16.725 | 11.859 | 1 | 1 | 2900 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3276785.446 | 269588.5329 | 8190.8721 | 22731.0082 | 246857.5247 | 12750.3743 | 0.11049 | -98455.0103 | 98455.0103
C | Xist Rating 3810 | -30.9 | 1569.59 | 150.287 | 35.6 | 2091.16 | 9349.53 | 10538.1 | 0.2 | 1.25 | 16.73 | 11.869 | 1 | 1 | 2910 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3282263.8244 | 271372.3166 | 8247.4583 | 22809.391 | 248562.9256 | 12762.3891 | 0.11087 | -98547.7855 | 98547.7855
C | Xist Rating 3811 | -30.76 | 1570.98 | 150.287 | 35.5 | 2094.46 | 9416.03 | 10538 | 0.2 | 1.25 | 16.739 | 11.879 | 1 | 1 | 2920 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3290354.7708 | 273161.971 | 8304.2393 | 22887.7738 | 250274.1972 | 12774.5095 | 0.11125 | -98641.3761 | 98641.3761
C | Xist Rating 3812 | -30.63 | 1572.37 | 150.287 | 35.5 | 2097.16 | 9470.91 | 10538.1 | 0.19 | 1.25 | 16.787 | 11.888 | 1 | 1 | 2930 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3297511.4692 | 274957.4959 | 8361.215 | 22966.1566 | 251991.3393 | 12764.57 | 0.11164 | -98564.6263 | 98564.6263
C | Xist Rating 3813 | -30.36 | 1573.74 | 150.287 | 35.5 | 2104.8 | 9628.71 | 10537.9 | 0.19 | 1.25 | 16.799 | 11.898 | 1 | 1 | 2940 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3312407.952 | 276758.8913 | 8418.3855 | 23044.5394 | 253714.352 | 12776.6852 | 0.11202 | -98658.1762 | 98658.1762
C | Xist Rating 3814 | -30.34 | 1575.15 | 150.287 | 35.5 | 2104.12 | 9614.57 | 10537.9 | 0.19 | 1.25 | 16.795 | 11.907 | 1 | 1 | 2950 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3314304.618 | 278566.1574 | 8475.7509 | 23122.9222 | 255443.2352 | 12787.3619 | 0.1124 | -98740.6189 | 98740.6189
C | Xist Rating 3815 | -30.33 | 1576.52 | 150.287 | 35.5 | 2103.46 | 9600.75 | 10537.9 | 0.19 | 1.25 | 16.791 | 11.916 | 1 | 1 | 2960 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3316146.7592 | 280379.294 | 8533.311 | 23201.3049 | 257177.9891 | 12798.0379 | 0.11278 | -98823.0564 | 98823.0564
C | Xist Rating 3816 | -30.31 | 1577.9 | 150.287 | 35.5 | 2102.79 | 9586.97 | 10537.9 | 0.18 | 1.25 | 16.788 | 11.925 | 1 | 1 | 2970 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3317992.341 | 282198.3012 | 8591.0659 | 23279.6877 | 258918.6135 | 12786.3888 | 0.11316 | -98733.1052 | 98733.1052
C | Xist Rating 3817 | -30.31 | 1579.12 | 150.287 | 35.5 | 2102.16 | 9573.85 | 10537.9 | 0.18 | 1.25 | 16.824 | 11.933 | 1 | 1 | 2980 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3319562.8992 | 284023.1789 | 8649.0156 | 23358.0705 | 260665.1084 | 12796.9169 | 0.11354 | -98814.4003 | 98814.4003
C | Xist Rating 3818 | -30.29 | 1580.68 | 150.287 | 35.5 | 2101.39 | 9557.74 | 10537.9 | 0.18 | 1.25 | 16.821 | 11.943 | 1 | 1 | 2990 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3321625.1452 | 285853.9273 | 8707.16 | 23436.4533 | 262417.474 | 12808.587 | 0.11392 | -98904.5133 | 98904.5133
C | Xist Rating 3819 | -30.27 | 1582.11 | 150.287 | 35.5 | 2100.81 | 9545.92 | 10537.9 | 0.18 | 1.25 | 16.816 | 11.952 | 1 | 1 | 3000 | 152.4 | 2 | 2.8 | 19.05 | 1.3333 | 15 | E | Rod | 3323712.5091 | 287690.5462 | 8765.4993 | 23514.8361 | 264175.7101 | 12819.1696 | 0.1143 | -98986.2298 | 98986.2298
C | Xist Rating 3820 | -91.6 | 153.645 | 150.29 | 35.8 | 2394.15 | 7352.26 | 58745.8 | 2.45 | 10.95 | 17.938 | 433.447 | 1 | 1 | 1000 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 18 | E | Rod | 367849.1768 | 38519.3902 | 973.9444 | 8118.2172 | 30401.173 | 452103.9824 | 0.038101 | -3491027.1124 | 3491027.1124
C | Xist Rating 3821 | -91.53 | 155.257 | 150.29 | 35.8 | 2391.38 | 7334.49 | 58284.2 | 2.43 | 10.85 | 17.978 | 425.333 | 1 | 1 | 1010 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 18 | E | Rod | 371278.4847 | 39211.636 | 993.5206 | 8199.3994 | 31012.2366 | 443685.4642 | 0.038482 | -3426021.5466 | 3426021.5466
C | Xist Rating 3822 | -90.9 | 167.371 | 150.291 | 35.8 | 2384.81 | 7336.59 | 54967.7 | 2.44 | 10.07 | 18.03 | 368.592 | 1 | 1 | 1020 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 18 | E | Rod | 399148.0345 | 39909.9619 | 1013.2917 | 8280.5816 | 31629.3804 | 384793.6286 | 0.038863 | -2971274.4026 | 2971274.4026
C | Xist Rating 3823 | -90.8 | 170.739 | 150.29 | 35.8 | 2364.7 | 7165.12 | 54179.2 | 2.36 | 9.89 | 17.655 | 356.303 | 1 | 1 | 1030 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 18 | E | Rod | 403746.5133 | 40614.3682 | 1033.2576 | 8361.7637 | 32252.6044 | 371943.7867 | 0.039244 | -2872051.3295 | 2872051.3295
C | Xist Rating 3824 | -90.73 | 172.426 | 150.29 | 35.8 | 2358.79 | 7118.84 | 53793.7 | 2.32 | 9.8 | 17.558 | 350.417 | 1 | 1 | 1040 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 18 | E | Rod | 406716.7245 | 41324.8546 | 1053.4182 | 8442.9459 | 32881.9087 | 365806.4494 | 0.039625 | -2824660.4373 | 2824660.4373
C | Xist Rating 3825 | -90.54 | 175.673 | 150.289 | 35.8 | 2364.11 | 7183.07 | 53043.4 | 2.27 | 9.63 | 17.515 | 338.849 | 1 | 1 | 1050 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 18 | E | Rod | 415310.296 | 42041.4213 | 1073.7737 | 8524.1281 | 33517.2932 | 353765.4455 | 0.040006 | -2731682.9975 | 2731682.9975
C | Xist Rating 3826 | -90.4 | 177.34 | 150.289 | 35.8 | 2378.55 | 7326.16 | 52676.8 | 2.22 | 9.54 | 17.507 | 333.384 | 1 | 1 | 1060 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 18 | E | Rod | 421812.057 | 42764.0682 | 1094.3239 | 8605.3103 | 34158.758 | 348065.4192 | 0.040387 | -2687668.9049 | 2687668.9049
C | Xist Rating 3827 | -89.78 | 190.414 | 150.289 | 35.8 | 2358.66 | 7204.18 | 49857.4 | 2.2 | 8.9 | 17.379 | 291.735 | 1 | 1 | 1070 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 18 | E | Rod | 449121.8852 | 43492.7954 | 1115.0689 | 8686.4924 | 34806.303 | 304800.1201 | 0.040768 | -2353585.7339 | 2353585.7339
C | Xist Rating 3828 | -89.62 | 192.918 | 150.289 | 35.8 | 2365.73 | 7282.41 | 49380.8 | 2.15 | 8.79 | 17.303 | 285.234 | 1 | 1 | 1080 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 18 | E | Rod | 456391.9001 | 44227.6028 | 1136.0087 | 8767.6746 | 35459.9282 | 298016.0034 | 0.041149 | -2301200.5826 | 2301200.5826
C | Xist Rating 3829 | -89.44 | 196.245 | 150.289 | 35.8 | 2366.86 | 7308.81 | 48762.1 | 2.09 | 8.65 | 17.185 | 276.874 | 1 | 1 | 1090 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 18 | E | Rod | 464484.4407 | 44968.4904 | 1157.1433 | 8848.8568 | 36119.6336 | 289288.0581 | 0.04153 | -2233805.703 | 2233805.703
C | Xist Rating 3830 | -89.28 | 198.717 | 150.288 | 35.8 | 2374.61 | 7395.35 | 48308.6 | 2.05 | 8.55 | 17.08 | 270.834 | 1 | 1 | 1100 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 471875.3754 | 45715.4583 | 1178.4727 | 8930.0389 | 36785.4193 | 282987.1201 | 0.041911 | -2185151.5299 | 2185151.5299
C | Xist Rating 3831 | -89.21 | 200.571 | 150.288 | 35.8 | 2368.68 | 7346.07 | 48011.5 | 1.98 | 8.49 | 16.854 | 267.176 | 1 | 1 | 1110 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 475088.5163 | 46468.5064 | 1199.9969 | 9011.2211 | 37457.2852 | 279122.2358 | 0.042292 | -2155307.9174 | 2155307.9174
C | Xist Rating 3832 | -88.45 | 215.082 | 150.288 | 35.8 | 2366.64 | 7399.79 | 45448.1 | 2.02 | 7.92 | 17.056 | 233.776 | 1 | 1 | 1120 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 509021.6645 | 47227.6347 | 1221.7158 | 9092.4033 | 38135.2314 | 244505.6773 | 0.042673 | -1888008.0289 | 1888008.0289
C | Xist Rating 3833 | -88.36 | 216.89 | 150.288 | 35.8 | 2364.95 | 7391.16 | 45189.1 | 1.96 | 7.86 | 16.909 | 230.818 | 1 | 1 | 1130 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 512934.0055 | 47992.8432 | 1243.6296 | 9173.5855 | 38819.2578 | 241382.8136 | 0.043054 | -1863894.103 | 1863894.103
C | Xist Rating 3834 | -88.21 | 220.288 | 150.288 | 35.8 | 2360.17 | 7360.36 | 44681.2 | 1.9 | 7.75 | 16.773 | 224.834 | 1 | 1 | 1140 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 519917.129 | 48764.132 | 1265.7381 | 9254.7676 | 39509.3644 | 235118.2473 | 0.043435 | -1815520.7827 | 1815520.7827
C | Xist Rating 3835 | -88.03 | 223.624 | 150.287 | 35.8 | 2362.41 | 7397.85 | 44186.8 | 1.86 | 7.64 | 16.647 | 219.041 | 1 | 1 | 1150 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 528291.5738 | 49541.5011 | 1288.0414 | 9335.9498 | 40205.5513 | 229069.8453 | 0.043816 | -1768816.6258 | 1768816.6258
C | Xist Rating 3836 | -87.84 | 227.038 | 150.287 | 35.8 | 2363.9 | 7428.32 | 43704.1 | 1.81 | 7.53 | 16.543 | 213.537 | 1 | 1 | 1160 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 536695.1282 | 50324.9503 | 1310.5395 | 9417.132 | 40907.8184 | 223314.7621 | 0.044197 | -1724377.3984 | 1724377.3984
C | Xist Rating 3837 | -87.16 | 240.098 | 150.287 | 35.8 | 2362.59 | 7480.76 | 41833.1 | 1.83 | 7.13 | 16.662 | 192.098 | 1 | 1 | 1170 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 567253.1338 | 51114.4799 | 1333.2324 | 9498.3141 | 41616.1657 | 201092.589 | 0.044578 | -1552783.6687 | 1552783.6687
C | Xist Rating 3838 | -87.06 | 241.095 | 150.287 | 35.8 | 2371.44 | 7574.29 | 41725.4 | 1.77 | 7.11 | 16.604 | 191.092 | 1 | 1 | 1180 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 571742.3268 | 51910.0896 | 1356.1201 | 9579.4963 | 42330.5933 | 200003.219 | 0.044959 | -1544371.8424 | 1544371.8424
C | Xist Rating 3839 | -86.77 | 247.751 | 150.287 | 35.8 | 2361.13 | 7501.78 | 40886.4 | 1.73 | 6.93 | 16.481 | 182.176 | 1 | 1 | 1190 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 584972.3186 | 52711.7796 | 1379.2026 | 9660.6785 | 43051.1011 | 190710.363 | 0.04534 | -1472614.8713 | 1472614.8713
C | Xist Rating 3840 | -86.62 | 249.451 | 150.287 | 35.8 | 2372.81 | 7629.13 | 40682.6 | 1.7 | 6.88 | 16.503 | 180.102 | 1 | 1 | 1200 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 591899.8273 | 53519.5498 | 1402.4799 | 9741.8607 | 43777.6891 | 188544.7143 | 0.045721 | -1455892.306 | 1455892.306
C | Xist Rating 3841 | -86.46 | 252.934 | 150.287 | 35.8 | 2369.23 | 7608.56 | 40281.7 | 1.65 | 6.8 | 16.395 | 176.073 | 1 | 1 | 1210 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 599258.8208 | 54333.4002 | 1425.9519 | 9823.0428 | 44510.3574 | 184318.7602 | 0.046102 | -1423260.609 | 1423260.609
C | Xist Rating 3842 | -85.75 | 267.799 | 150.287 | 35.8 | 2356.36 | 7550.28 | 38538.8 | 1.65 | 6.43 | 16.419 | 158.372 | 1 | 1 | 1220 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 631030.8516 | 55153.3309 | 1449.6188 | 9904.225 | 45249.1059 | 165950.5911 | 0.046483 | -1281426.4762 | 1281426.4762
C | Xist Rating 3843 | -85.54 | 271.132 | 150.287 | 35.8 | 2362.56 | 7630.48 | 38183.4 | 1.62 | 6.35 | 16.42 | 154.994 | 1 | 1 | 1230 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 640565.6179 | 55979.3418 | 1473.4804 | 9985.4072 | 45993.9346 | 162427.6189 | 0.046864 | -1254223.0183 | 1254223.0183
C | Xist Rating 3844 | -85.37 | 274.605 | 150.287 | 35.8 | 2361.75 | 7638.13 | 37835.7 | 1.58 | 6.28 | 16.345 | 151.798 | 1 | 1 | 1240 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 648548.3588 | 56811.4329 | 1497.5369 | 10066.5894 | 46744.8436 | 159077.4083 | 0.047245 | -1228353.5803 | 1228353.5803
C | Xist Rating 3845 | -85.26 | 276.45 | 150.286 | 35.8 | 2364.54 | 7675.46 | 37664.6 | 1.54 | 6.24 | 16.294 | 150.306 | 1 | 1 | 1250 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 653677.083 | 57649.6043 | 1521.7881 | 10147.7715 | 47501.8328 | 157498.5111 | 0.047626 | -1216161.7543 | 1216161.7543
C | Xist Rating 3846 | -85.01 | 281.473 | 150.286 | 35.8 | 2362.6 | 7679.42 | 37161.7 | 1.51 | 6.14 | 16.259 | 145.669 | 1 | 1 | 1260 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 665008.1098 | 58493.8559 | 1546.2341 | 10228.9537 | 48264.9022 | 152663.6486 | 0.048007 | -1178828.2282 | 1178828.2282
C | Xist Rating 3847 | -84.32 | 295.557 | 150.286 | 35.8 | 2355.4 | 7673.7 | 35777.9 | 1.52 | 5.85 | 16.316 | 133.065 | 1 | 1 | 1270 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 696154.9578 | 59344.1878 | 1570.8749 | 10310.1359 | 49034.0519 | 139599.6075 | 0.048388 | -1077951.1654 | 1077951.1654
C | Xist Rating 3848 | -84.16 | 299.099 | 150.286 | 35.8 | 2351.98 | 7653.42 | 35477.7 | 1.48 | 5.79 | 16.242 | 130.571 | 1 | 1 | 1280 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 703474.866 | 60200.5999 | 1595.7105 | 10391.318 | 49809.2818 | 136976.9798 | 0.048769 | -1057699.9291 | 1057699.9291
C | Xist Rating 3849 | -83.98 | 302.588 | 150.286 | 35.8 | 2352.65 | 7676.52 | 35183.3 | 1.45 | 5.73 | 16.222 | 128.13 | 1 | 1 | 1290 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 711883.6582 | 61063.0922 | 1620.7408 | 10472.5002 | 50590.592 | 134422.928 | 0.04915 | -1037978.2186 | 1037978.2186
C | Xist Rating 3850 | -83.67 | 307.59 | 150.286 | 35.8 | 2360.59 | 7786.27 | 34751.8 | 1.42 | 5.64 | 16.247 | 124.506 | 1 | 1 | 1300 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 726093.8781 | 61931.6647 | 1645.966 | 10553.6824 | 51377.9823 | 130643.6633 | 0.049531 | -1008795.7385 | 1008795.7385
C | Xist Rating 3851 | -83.5 | 310.286 | 150.286 | 35.8 | 2365.57 | 7853.11 | 34540.4 | 1.39 | 5.59 | 16.209 | 122.837 | 1 | 1 | 1310 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 734003.253 | 62806.3175 | 1671.3859 | 10634.8646 | 52171.453 | 128889.0284 | 0.049912 | -995246.9126 | 995246.9126
C | Xist Rating 3852 | -82.79 | 324.468 | 150.286 | 35.8 | 2360.26 | 7866.94 | 33363.8 | 1.39 | 5.35 | 16.258 | 113.157 | 1 | 1 | 1320 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 765828.8417 | 63687.0505 | 1697.0007 | 10716.0467 | 52971.0038 | 118850.4929 | 0.050293 | -917732.0023 | 917732.0023
C | Xist Rating 3853 | -82.55 | 329.686 | 150.286 | 35.8 | 2356.41 | 7848.88 | 32980.7 | 1.35 | 5.28 | 16.151 | 110.235 | 1 | 1 | 1330 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 776875.3873 | 64573.8638 | 1722.8102 | 10797.2289 | 53776.6349 | 115778.7486 | 0.050674 | -894012.8074 | 894012.8074
C | Xist Rating 3854 | -82.28 | 334.803 | 150.286 | 35.7 | 2356.96 | 7879.73 | 32607.5 | 1.33 | 5.2 | 16.124 | 107.402 | 1 | 1 | 1340 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 789117.2789 | 65466.7573 | 1748.8145 | 10878.4111 | 54588.3462 | 112824.897 | 0.051055 | -871203.9478 | 871203.9478
C | Xist Rating 3855 | -82.12 | 337.516 | 150.286 | 35.7 | 2360.44 | 7931.29 | 32424.4 | 1.3 | 5.16 | 16.094 | 106.085 | 1 | 1 | 1350 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 796686.267 | 66365.731 | 1775.0136 | 10959.5932 | 55406.1378 | 111435.1757 | 0.051436 | -860472.8883 | 860472.8883
C | Xist Rating 3856 | -81.92 | 339.163 | 150.286 | 35.7 | 2376.89 | 8128.86 | 32303.8 | 1.28 | 5.14 | 16.148 | 105.187 | 1 | 1 | 1360 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 806153.1431 | 67270.785 | 1801.4075 | 11040.7754 | 56230.0096 | 110496.5738 | 0.051817 | -853225.2531 | 853225.2531
C | Xist Rating 3857 | -81.06 | 359.39 | 150.286 | 35.7 | 2350.26 | 7925.73 | 30903.2 | 1.28 | 4.86 | 16.111 | 94.836 | 1 | 1 | 1370 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 844659.9414 | 68181.9192 | 1827.9962 | 11121.9576 | 57059.9616 | 99753.4333 | 0.052198 | -770269.5699 | 770269.5699
C | Xist Rating 3858 | -80.98 | 361.298 | 150.286 | 35.7 | 2349.35 | 7923.6 | 30794.9 | 1.25 | 4.84 | 16.081 | 94.144 | 1 | 1 | 1380 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 848815.4563 | 69099.1336 | 1854.7797 | 11203.1398 | 57895.9938 | 99011.8186 | 0.052579 | -764543.0182 | 764543.0182
C | Xist Rating 3859 | -80.75 | 365.681 | 150.286 | 35.7 | 2350.4 | 7956.11 | 30527.9 | 1.22 | 4.78 | 16.052 | 92.328 | 1 | 1 | 1390 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 859496.6224 | 70022.4283 | 1881.7579 | 11284.3219 | 58738.1063 | 97102.653 | 0.05296 | -749800.9473 | 749800.9473
C | Xist Rating 3860 | -80.52 | 370.06 | 150.286 | 35.7 | 2351.31 | 7987.27 | 30266 | 1.2 | 4.73 | 16.029 | 90.566 | 1 | 1 | 1400 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 870125.7786 | 70951.8032 | 1908.931 | 11365.5041 | 59586.2991 | 95259.7183 | 0.053341 | -735570.2938 | 735570.2938
C | Xist Rating 3861 | -80.25 | 375.237 | 150.286 | 35.7 | 2352.65 | 8027.96 | 29957.8 | 1.18 | 4.67 | 16.008 | 88.501 | 1 | 1 | 1410 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 882801.3281 | 71887.2583 | 1936.2988 | 11446.6863 | 60440.572 | 93102.0132 | 0.053722 | -718909.0677 | 718909.0677
C | Xist Rating 3862 | -79.5 | 390.345 | 150.286 | 35.7 | 2348.09 | 8051.91 | 29052.3 | 1.18 | 4.49 | 16.07 | 82.382 | 1 | 1 | 1420 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 916565.1911 | 72828.7937 | 1963.8614 | 11527.8685 | 61300.9252 | 86760.5653 | 0.054103 | -669942.0872 | 669942.0872
C | Xist Rating 3863 | -79.39 | 393.299 | 150.286 | 35.7 | 2344.59 | 8023.36 | 28911.1 | 1.15 | 4.47 | 16.007 | 81.564 | 1 | 1 | 1430 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 922124.9024 | 73776.4093 | 1991.6188 | 11609.0506 | 62167.3586 | 85884.0272 | 0.054484 | -663173.6929 | 663173.6929
C | Xist Rating 3864 | -79.06 | 400.124 | 150.286 | 35.7 | 2342.64 | 8033.65 | 28542.3 | 1.13 | 4.39 | 15.993 | 79.226 | 1 | 1 | 1440 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 937346.4874 | 74730.1051 | 2019.571 | 11690.2328 | 63039.8723 | 83442.5839 | 0.054865 | -644321.5146 | 644321.5146
C | Xist Rating 3865 | -78.84 | 404.541 | 150.286 | 35.7 | 2342.64 | 8054.31 | 28317.1 | 1.11 | 4.35 | 15.973 | 77.852 | 1 | 1 | 1450 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 947693.9282 | 75689.8812 | 2047.718 | 11771.415 | 63918.4662 | 82001.5554 | 0.055246 | -633194.2744 | 633194.2744
C | Xist Rating 3866 | -78.65 | 407.135 | 150.286 | 35.7 | 2349.54 | 8149.27 | 28183.9 | 1.1 | 4.32 | 15.988 | 77.046 | 1 | 1 | 1460 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 956579.9679 | 76655.7375 | 2076.0598 | 11852.5971 | 64803.1403 | 81163.0995 | 0.055627 | -626719.9406 | 626719.9406
C | Xist Rating 3867 | -77.91 | 424.318 | 150.286 | 35.7 | 2333.73 | 8045.84 | 27310.5 | 1.09 | 4.16 | 15.984 | 71.686 | 1 | 1 | 1470 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 990243.6461 | 77627.674 | 2104.5964 | 11933.7793 | 65693.8947 | 75593.8091 | 0.056008 | -583715.356 | 583715.356
C | Xist Rating 3868 | -77.65 | 429.54 | 150.286 | 35.7 | 2333.83 | 8071.67 | 27066.3 | 1.07 | 4.11 | 15.971 | 70.271 | 1 | 1 | 1480 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1002473.3382 | 78605.6908 | 2133.3277 | 12014.9615 | 66590.7293 | 74110.0129 | 0.056389 | -572257.8752 | 572257.8752
C | Xist Rating 3869 | -77.4 | 433.958 | 150.286 | 35.7 | 2336.4 | 8123.2 | 26866.7 | 1.06 | 4.07 | 15.963 | 69.14 | 1 | 1 | 1490 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1013899.4712 | 79589.7878 | 2162.2539 | 12096.1437 | 67493.6441 | 72931.8981 | 0.05677 | -563160.7847 | 563160.7847
C | Xist Rating 3870 | -77.14 | 438.469 | 150.286 | 35.7 | 2339.42 | 8180.9 | 26670.5 | 1.03 | 4.03 | 15.95 | 68.051 | 1 | 1 | 1500 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1025763.148 | 80579.9651 | 2191.3748 | 12177.3258 | 68402.6392 | 71775.4585 | 0.057151 | -554231.0653 | 554231.0653
C | Xist Rating 3871 | -76.83 | 443.718 | 150.286 | 35.7 | 2344.6 | 8270.37 | 26439.1 | 1.02 | 3.99 | 15.952 | 66.756 | 1 | 1 | 1510 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1040341.2228 | 81576.2225 | 2220.6906 | 12258.508 | 69317.7145 | 70427.3094 | 0.057532 | -543821.015 | 543821.015
C | Xist Rating 3872 | -75.99 | 460.583 | 150.286 | 35.7 | 2342.05 | 8326.72 | 25681.3 | 1.02 | 3.85 | 16.02 | 62.447 | 1 | 1 | 1520 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1078708.4152 | 82578.5602 | 2250.2011 | 12339.6902 | 70238.8701 | 65964.4389 | 0.057913 | -509359.9118 | 509359.9118
C | Xist Rating 3873 | -75.77 | 466.176 | 150.286 | 35.7 | 2335.53 | 8270.5 | 25468.6 | 0.99 | 3.8 | 15.968 | 61.359 | 1 | 1 | 1530 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1088768.0333 | 83586.9782 | 2279.9064 | 12420.8723 | 71166.1058 | 64805.3862 | 0.058294 | -500410.014 | 500410.014
C | Xist Rating 3874 | -75.58 | 469.045 | 150.286 | 35.7 | 2340.64 | 8347.89 | 25363.8 | 0.97 | 3.78 | 15.96 | 60.844 | 1 | 1 | 1540 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1097865.4888 | 84601.4764 | 2309.8065 | 12502.0545 | 72099.4219 | 64255.0644 | 0.058675 | -496160.5754 | 496160.5754
C | Xist Rating 3875 | -75.15 | 477.642 | 150.286 | 35.7 | 2340.7 | 8392.05 | 25021.5 | 0.96 | 3.72 | 15.957 | 59.033 | 1 | 1 | 1550 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1118016.6294 | 85622.0548 | 2339.9013 | 12583.2367 | 73038.8181 | 62369.9944 | 0.059056 | -481604.5641 | 481604.5641
C | Xist Rating 3876 | -74.9 | 480.287 | 150.286 | 35.7 | 2352.03 | 8553.23 | 24920.6 | 0.95 | 3.7 | 15.98 | 58.526 | 1 | 1 | 1560 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1129649.4326 | 86648.7134 | 2370.191 | 12664.4189 | 73984.2946 | 61840.712 | 0.059437 | -477517.5856 | 477517.5856
C | Xist Rating 3877 | -74.09 | 500.247 | 150.286 | 35.7 | 2332 | 8394.93 | 24162.4 | 0.94 | 3.56 | 15.973 | 54.61 | 1 | 1 | 1570 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1166576.004 | 87681.4523 | 2400.6755 | 12745.601 | 74935.8513 | 57769.048 | 0.059818 | -446077.2761 | 446077.2761
C | Xist Rating 3878 | -73.83 | 504.786 | 150.286 | 35.7 | 2335.23 | 8458.84 | 24007.7 | 0.92 | 3.53 | 15.965 | 53.872 | 1 | 1 | 1580 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1178791.4108 | 88720.2715 | 2431.3547 | 12826.7832 | 75893.4882 | 56986.2201 | 0.0602 | -440032.4863 | 440032.4863
C | Xist Rating 3879 | -73.58 | 509.361 | 150.286 | 35.7 | 2337.33 | 8508.58 | 23855.4 | 0.91 | 3.5 | 15.954 | 53.155 | 1 | 1 | 1590 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1190544.7461 | 89765.1708 | 2462.2288 | 12907.9654 | 76857.2054 | 56236.1086 | 0.060581 | -434240.3242 | 434240.3242
C | Xist Rating 3880 | -73.23 | 515.439 | 150.286 | 35.7 | 2341.05 | 8589.59 | 23645.6 | 0.9 | 3.46 | 15.963 | 52.141 | 1 | 1 | 1600 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1206668.4709 | 90816.1504 | 2493.2976 | 12989.1476 | 77827.0028 | 55178.7177 | 0.060962 | -426075.4321 | 426075.4321
C | Xist Rating 3881 | -73.07 | 518.504 | 150.286 | 35.7 | 2342.39 | 8621.15 | 23556.9 | 0.88 | 3.45 | 15.941 | 51.765 | 1 | 1 | 1610 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1214538.5846 | 91873.2102 | 2524.5612 | 13070.3297 | 78802.8805 | 54770.2447 | 0.061343 | -422921.3119 | 422921.3119
C | Xist Rating 3882 | -72.09 | 540.772 | 150.286 | 35.7 | 2328.75 | 8555.48 | 22805.3 | 0.88 | 3.31 | 15.958 | 48.148 | 1 | 1 | 1620 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1259322.795 | 92936.3503 | 2556.0196 | 13151.5119 | 79784.8384 | 51021.3703 | 0.061724 | -393973.4974 | 393973.4974
C | Xist Rating 3883 | -71.86 | 543.492 | 150.286 | 35.7 | 2336.86 | 8679.57 | 22723.4 | 0.87 | 3.29 | 15.986 | 47.793 | 1 | 1 | 1630 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1270064.7151 | 94005.5706 | 2587.6728 | 13232.6941 | 80772.8765 | 50649.1184 | 0.062105 | -391099.0666 | 391099.0666
C | Xist Rating 3884 | -71.64 | 548.214 | 150.286 | 35.7 | 2336.49 | 8697.33 | 22588.7 | 0.85 | 3.27 | 15.954 | 47.216 | 1 | 1 | 1640 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1280896.5289 | 95080.8711 | 2619.5208 | 13313.8762 | 81766.9949 | 50030.636 | 0.062486 | -386323.3096 | 386323.3096
C | Xist Rating 3885 | -71.36 | 554.649 | 150.286 | 35.7 | 2332.99 | 8680.73 | 22403.1 | 0.83 | 3.24 | 15.93 | 46.409 | 1 | 1 | 1650 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1293990.5705 | 96162.2519 | 2651.5635 | 13395.0584 | 82767.1935 | 49173.5737 | 0.062867 | -379705.3019 | 379705.3019
C | Xist Rating 3886 | -71.02 | 560.841 | 150.286 | 35.7 | 2335.34 | 8745.41 | 22221 | 0.82 | 3.2 | 15.931 | 45.608 | 1 | 1 | 1660 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1309754.4209 | 97249.7129 | 2683.8011 | 13476.2406 | 83773.4723 | 48335.8709 | 0.063248 | -373236.7823 | 373236.7823
C | Xist Rating 3887 | -70.17 | 580.845 | 150.286 | 35.7 | 2322.43 | 8671.57 | 21633.2 | 0.82 | 3.1 | 15.955 | 43.002 | 1 | 1 | 1670 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1348971.8533 | 98343.2541 | 2716.2334 | 13557.4228 | 84785.8313 | 45636.8728 | 0.063629 | -352395.8347 | 352395.8347
C | Xist Rating 3888 | -69.96 | 583.676 | 150.286 | 35.7 | 2328.32 | 8767.9 | 21560.7 | 0.81 | 3.08 | 15.957 | 42.717 | 1 | 1 | 1680 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1358984.5043 | 99442.8756 | 2748.8606 | 13638.6049 | 85804.2706 | 45334.8722 | 0.06401 | -350063.8663 | 350063.8663
C | Xist Rating 3889 | -69.62 | 591.875 | 150.286 | 35.7 | 2323.32 | 8738.19 | 21346.1 | 0.8 | 3.04 | 15.933 | 41.834 | 1 | 1 | 1690 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1375115.025 | 100548.5773 | 2781.6825 | 13719.7871 | 86828.7902 | 44410.1293 | 0.064391 | -342923.2465 | 342923.2465
C | Xist Rating 3890 | -69.33 | 597.28 | 150.286 | 35.7 | 2325.31 | 8793.88 | 21206.1 | 0.79 | 3.02 | 15.933 | 41.265 | 1 | 1 | 1700 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1388861.1568 | 101660.3592 | 2814.6992 | 13800.9693 | 87859.3899 | 43812.796 | 0.064772 | -338310.797 | 338310.797
C | Xist Rating 3891 | -69.02 | 603.664 | 150.286 | 35.7 | 2324.73 | 8817.73 | 21045 | 0.77 | 2.99 | 15.926 | 40.619 | 1 | 1 | 1710 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1403355.8107 | 102778.2214 | 2847.9107 | 13882.1514 | 88896.0699 | 43122.7296 | 0.065153 | -332982.2875 | 332982.2875
C | Xist Rating 3892 | -68.23 | 622.109 | 150.286 | 35.7 | 2314.41 | 8767.58 | 20567.5 | 0.77 | 2.9 | 15.956 | 38.654 | 1 | 1 | 1720 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1439815.2907 | 103902.1638 | 2881.317 | 13963.3336 | 89938.8302 | 41089.3581 | 0.065534 | -317281.1313 | 317281.1313
C | Xist Rating 3893 | -67.85 | 630.177 | 150.286 | 35.7 | 2313.1 | 8789.5 | 20374.6 | 0.76 | 2.87 | 15.949 | 37.903 | 1 | 1 | 1730 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1457662.4187 | 105032.1864 | 2914.9181 | 14044.5158 | 90987.6706 | 40302.1671 | 0.065915 | -311202.6511 | 311202.6511
C | Xist Rating 3894 | -67.61 | 633.96 | 150.286 | 35.6 | 2317.48 | 8871.53 | 20290.2 | 0.75 | 2.85 | 15.949 | 37.594 | 1 | 1 | 1740 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1469189.6208 | 106168.2893 | 2948.714 | 14125.698 | 92042.5913 | 39974.2649 | 0.066296 | -308670.6779 | 308670.6779
C | Xist Rating 3895 | -67.33 | 641.356 | 150.286 | 35.6 | 2312.61 | 8837.13 | 20123.3 | 0.74 | 2.82 | 15.929 | 36.968 | 1 | 1 | 1750 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1483206.2992 | 107310.4724 | 2982.7046 | 14206.8801 | 93103.5923 | 39315.8549 | 0.066677 | -303586.61 | 303586.61
C | Xist Rating 3896 | -67.07 | 646.878 | 150.286 | 35.6 | 2310.73 | 8836.87 | 20001.3 | 0.73 | 2.8 | 15.926 | 36.514 | 1 | 1 | 1760 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1494760.4009 | 108458.7358 | 3016.8901 | 14288.0623 | 94170.6734 | 38836.9209 | 0.067058 | -299888.4088 | 299888.4088
C | Xist Rating 3897 | -66.13 | 668.733 | 150.286 | 35.6 | 2299.77 | 8792.04 | 19497.8 | 0.73 | 2.71 | 15.963 | 34.578 | 1 | 1 | 1770 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1537932.0914 | 109613.0793 | 3051.2703 | 14369.2445 | 95243.8348 | 36833.7423 | 0.067439 | -284420.3941 | 284420.3941
C | Xist Rating 3898 | -66.01 | 674.364 | 150.286 | 35.6 | 2291.55 | 8699.39 | 19383.6 | 0.71 | 2.69 | 16.129 | 34.169 | 1 | 1 | 1780 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1545338.8242 | 110773.5031 | 3085.8453 | 14450.4267 | 96323.0765 | 36398.1505 | 0.06782 | -281056.8703 | 281056.8703
C | Xist Rating 3899 | -65.89 | 677.455 | 150.286 | 35.6 | 2290.02 | 8690.39 | 19327.1 | 0.7 | 2.68 | 16.113 | 33.989 | 1 | 1 | 1790 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1551385.4991 | 111940.0072 | 3120.6151 | 14531.6088 | 97408.3984 | 36202.514 | 0.068201 | -279546.217 | 279546.217
C | Xist Rating 3900 | -65.47 | 687.324 | 150.286 | 35.6 | 2287.7 | 8705.24 | 19121.9 | 0.69 | 2.65 | 16.102 | 33.253 | 1 | 1 | 1800 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1572391.1148 | 113112.5915 | 3155.5797 | 14612.791 | 98499.8005 | 35429.6219 | 0.068582 | -273578.1492 | 273578.1492
C | Xist Rating 3901 | -65.21 | 692.828 | 150.286 | 35.6 | 2287.13 | 8723.17 | 19012.5 | 0.69 | 2.63 | 16.099 | 32.874 | 1 | 1 | 1810 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1584587.7036 | 114291.256 | 3190.7391 | 14693.9732 | 99597.2828 | 35040.8433 | 0.068963 | -270576.1035 | 270576.1035
C | Xist Rating 3902 | -64.29 | 714.941 | 150.286 | 35.6 | 2276.2 | 8675.26 | 18562.8 | 0.68 | 2.55 | 16.134 | 31.265 | 1 | 1 | 1820 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1627348.7042 | 115476.0007 | 3226.0933 | 14775.1553 | 100700.8454 | 33363.6865 | 0.069344 | -257625.5435 | 257625.5435
C | Xist Rating 3903 | -64.28 | 711.413 | 150.286 | 35.6 | 2288.56 | 8839.64 | 18631.5 | 0.68 | 2.56 | 16.156 | 31.52 | 1 | 1 | 1830 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1628111.3353 | 116666.8257 | 3261.6423 | 14856.3375 | 101810.4882 | 33634.6485 | 0.069725 | -259717.8403 | 259717.8403
C | Xist Rating 3904 | -63.91 | 715.914 | 150.286 | 35.6 | 2297.69 | 9000.58 | 18545.7 | 0.67 | 2.55 | 16.179 | 31.232 | 1 | 1 | 1840 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1644948.4387 | 117863.731 | 3297.386 | 14937.5197 | 102926.2113 | 33328.4314 | 0.070106 | -257353.3128 | 257353.3128
C | Xist Rating 3905 | -63.58 | 723.427 | 150.286 | 35.6 | 2295.38 | 9002.15 | 18409.8 | 0.66 | 2.52 | 16.17 | 30.784 | 1 | 1 | 1850 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1660539.8673 | 119066.7164 | 3333.3246 | 15018.7019 | 104048.0145 | 32854.1339 | 0.070487 | -253690.9136 | 253690.9136
C | Xist Rating 3906 | -63.24 | 731.838 | 150.286 | 35.6 | 2291.01 | 8976.51 | 18259.5 | 0.65 | 2.5 | 16.16 | 30.291 | 1 | 1 | 1860 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1676648.1764 | 120275.7821 | 3369.4579 | 15099.884 | 105175.8981 | 32332.9145 | 0.070868 | -249666.1954 | 249666.1954
C | Xist Rating 3907 | -62.33 | 752.121 | 150.286 | 35.6 | 2285.15 | 8994.17 | 17880.1 | 0.65 | 2.43 | 16.207 | 28.999 | 1 | 1 | 1870 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1718709.3032 | 121490.928 | 3405.7861 | 15181.0662 | 106309.8618 | 30998.4437 | 0.071249 | -239361.7655 | 239361.7655
C | Xist Rating 3908 | -61.95 | 760.517 | 150.286 | 35.6 | 2283.39 | 9008.25 | 17739.1 | 0.64 | 2.41 | 16.192 | 28.556 | 1 | 1 | 1880 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1736556.9126 | 122712.1542 | 3442.309 | 15262.2484 | 107449.9058 | 30528.6443 | 0.07163 | -235734.099 | 235734.099
C | Xist Rating 3909 | -61.61 | 766.069 | 150.286 | 35.6 | 2287.24 | 9096.36 | 17647 | 0.63 | 2.39 | 16.199 | 28.269 | 1 | 1 | 1890 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1752183.6596 | 123939.4606 | 3479.0267 | 15343.4305 | 108596.03 | 30221.8963 | 0.072011 | -233365.4726 | 233365.4726
C | Xist Rating 3910 | -61.37 | 772.078 | 150.286 | 35.6 | 2284.24 | 9077 | 17555.8 | 0.62 | 2.38 | 16.189 | 28.001 | 1 | 1 | 1900 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1763611.4507 | 125172.8472 | 3515.9392 | 15424.6127 | 109748.2345 | 29933.8291 | 0.072392 | -231141.0936 | 231141.0936
C | Xist Rating 3911 | -61.12 | 777.809 | 150.286 | 35.6 | 2282.9 | 9083.68 | 17465.3 | 0.61 | 2.36 | 16.192 | 27.729 | 1 | 1 | 1910 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1775660.1661 | 126412.3141 | 3553.0464 | 15505.7949 | 110906.5192 | 29642.1531 | 0.072773 | -228888.8489 | 228888.8489
C | Xist Rating 3912 | -60.07 | 802.452 | 150.286 | 35.6 | 2273.73 | 9070.27 | 17050.5 | 0.61 | 2.29 | 16.237 | 26.399 | 1 | 1 | 1920 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1824559.186 | 127657.8612 | 3590.3485 | 15586.9771 | 112070.8841 | 28267.74 | 0.073154 | -218275.9955 | 218275.9955
C | Xist Rating 3913 | -59.72 | 810.926 | 150.286 | 35.6 | 2270.08 | 9053.45 | 16924.2 | 0.6 | 2.27 | 16.234 | 26.027 | 1 | 1 | 1930 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1840866.8941 | 128909.4885 | 3627.8454 | 15668.1592 | 113241.3293 | 27871.6557 | 0.073535 | -215217.5373 | 215217.5373
C | Xist Rating 3914 | -59.44 | 813.655 | 150.286 | 35.6 | 2279.31 | 9216.35 | 16882.3 | 0.6 | 2.26 | 16.247 | 25.909 | 1 | 1 | 1940 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1854571.978 | 130167.1961 | 3665.537 | 15749.3414 | 114417.8547 | 27754.1573 | 0.073916 | -214310.2456 | 214310.2456
C | Xist Rating 3915 | -59.2 | 821.738 | 150.286 | 35.6 | 2270.74 | 9114.85 | 16772.3 | 0.58 | 2.24 | 16.228 | 25.604 | 1 | 1 | 1950 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1865953.3461 | 131430.9839 | 3703.4235 | 15830.5236 | 115600.4603 | 27412.4192 | 0.074297 | -211671.435 | 211671.435
C | Xist Rating 3916 | -58.8 | 830.989 | 150.286 | 35.6 | 2268.09 | 9118.37 | 16637.3 | 0.57 | 2.22 | 16.244 | 25.209 | 1 | 1 | 1960 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1884757.841 | 132700.8519 | 3741.5047 | 15911.7058 | 116789.1461 | 26992.9753 | 0.074678 | -208432.6001 | 208432.6001
C | Xist Rating 3917 | -57.86 | 853.231 | 150.286 | 35.6 | 2260.65 | 9115.42 | 16303.3 | 0.57 | 2.16 | 16.302 | 24.207 | 1 | 1 | 1970 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1928856.6602 | 133976.8002 | 3779.7807 | 15992.8879 | 117983.9122 | 25959.4696 | 0.075059 | -200452.1429 | 200452.1429
C | Xist Rating 3918 | -57.53 | 859.84 | 150.286 | 35.6 | 2261.01 | 9153.64 | 16214.3 | 0.57 | 2.15 | 16.317 | 23.963 | 1 | 1 | 1980 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1944106.8384 | 135258.8287 | 3818.2515 | 16074.0701 | 119184.7586 | 25711 | 0.07544 | -198533.5264 | 198533.5264
C | Xist Rating 3919 | -57.2 | 868.508 | 150.286 | 35.6 | 2256.72 | 9124.84 | 16101.6 | 0.56 | 2.13 | 16.322 | 23.656 | 1 | 1 | 1990 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1959979.3738 | 136546.9374 | 3856.9171 | 16155.2523 | 120391.6851 | 25382.0448 | 0.075821 | -195993.4217 | 195993.4217
C | Xist Rating 3920 | -56.9 | 875.242 | 150.286 | 35.6 | 2255.71 | 9140.47 | 16015 | 0.55 | 2.12 | 16.321 | 23.424 | 1 | 1 | 2000 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1974292.1318 | 137841.1264 | 3895.7775 | 16236.4344 | 121604.6919 | 25130.5284 | 0.076202 | -194051.2788 | 194051.2788
C | Xist Rating 3921 | -56.67 | 880.215 | 150.286 | 35.6 | 2255.72 | 9163.73 | 15953.9 | 0.54 | 2.11 | 16.326 | 23.267 | 1 | 1 | 2010 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 1985518.5798 | 139141.3956 | 3934.8326 | 16317.6166 | 122823.779 | 24957.0463 | 0.076583 | -192711.696 | 192711.696
C | Xist Rating 3922 | -55.65 | 905.306 | 150.287 | 35.6 | 2245.61 | 9127.77 | 15615 | 0.54 | 2.05 | 16.363 | 22.309 | 1 | 1 | 2020 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2032964.2067 | 140447.745 | 3974.0826 | 16398.7988 | 124048.9463 | 23967.9257 | 0.076964 | -185073.9688 | 185073.9688
C | Xist Rating 3923 | -55.23 | 914.501 | 150.287 | 35.6 | 2244.92 | 9161.96 | 15499.9 | 0.54 | 2.03 | 16.366 | 22.002 | 1 | 1 | 2030 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2052981.5849 | 141760.1747 | 4013.5273 | 16479.981 | 125280.1938 | 23653.2148 | 0.077345 | -182643.8547 | 182643.8547
C | Xist Rating 3924 | -54.99 | 920.71 | 150.287 | 35.6 | 2242.28 | 9145.54 | 15431.7 | 0.53 | 2.02 | 16.357 | 21.838 | 1 | 1 | 2040 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2064489.6188 | 143078.6846 | 4053.1669 | 16561.1631 | 126517.5215 | 23471.4609 | 0.077726 | -181240.3991 | 181240.3991
C | Xist Rating 3925 | -54.68 | 926.104 | 150.287 | 35.6 | 2245.12 | 9220.62 | 15364.4 | 0.52 | 2.01 | 16.37 | 21.662 | 1 | 1 | 2050 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2079214.6125 | 144403.2748 | 4093.0012 | 16642.3453 | 127760.9295 | 23278.1617 | 0.078107 | -179747.7944 | 179747.7944
C | Xist Rating 3926 | -54.38 | 935.166 | 150.287 | 35.6 | 2238.92 | 9157.96 | 15264.4 | 0.51 | 1.99 | 16.357 | 21.415 | 1 | 1 | 2060 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2093761.8607 | 145733.9452 | 4133.0303 | 16723.5275 | 129010.4177 | 23009.7402 | 0.078488 | -177675.1146 | 177675.1146
C | Xist Rating 3927 | -53.3 | 962.121 | 150.287 | 35.6 | 2228.58 | 9123.05 | 14936.2 | 0.51 | 1.94 | 16.395 | 20.541 | 1 | 1 | 2070 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2144163.6182 | 147070.6958 | 4173.2542 | 16804.7096 | 130265.9861 | 22107.6301 | 0.078869 | -170709.2595 | 170709.2595
C | Xist Rating 3928 | -53.05 | 968.132 | 150.287 | 35.6 | 2227.32 | 9128.95 | 14873.5 | 0.5 | 1.93 | 16.391 | 20.394 | 1 | 1 | 2080 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2156339.7662 | 148413.5266 | 4213.6729 | 16885.8918 | 131527.6348 | 21943.2464 | 0.07925 | -169439.9324 | 169439.9324
C | Xist Rating 3929 | -52.73 | 975.845 | 150.287 | 35.6 | 2225.59 | 9135.93 | 14790.9 | 0.5 | 1.91 | 16.389 | 20.194 | 1 | 1 | 2090 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2171830.8736 | 149762.4377 | 4254.2864 | 16967.074 | 132795.3637 | 21739.1267 | 0.079631 | -167863.7737 | 167863.7737
C | Xist Rating 3930 | -52.42 | 983.566 | 150.287 | 35.6 | 2223.62 | 9138.71 | 14709.2 | 0.49 | 1.9 | 16.386 | 19.999 | 1 | 1 | 2100 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2187077.0289 | 151117.429 | 4295.0947 | 17048.2562 | 134069.1729 | 21524.727 | 0.080012 | -166208.2363 | 166208.2363
C | Xist Rating 3931 | -52.13 | 990.394 | 150.287 | 35.6 | 2222.23 | 9146.81 | 14638.7 | 0.48 | 1.89 | 16.389 | 19.832 | 1 | 1 | 2110 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2200883.2586 | 152478.5006 | 4336.0977 | 17129.4383 | 135349.0623 | 21339.5351 | 0.080393 | -164778.2336 | 164778.2336
C | Xist Rating 3932 | -51.14 | 1015.93 | 150.287 | 35.6 | 2212.11 | 9102.71 | 14359 | 0.48 | 1.84 | 16.425 | 19.13 | 1 | 1 | 2120 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2247348.9123 | 153845.6524 | 4377.2956 | 17210.6205 | 136635.0319 | 20615.6775 | 0.080774 | -159188.7974 | 159188.7974
C | Xist Rating 3933 | -50.76 | 1025.46 | 150.287 | 35.6 | 2209.22 | 9098.18 | 14263.7 | 0.48 | 1.83 | 16.421 | 18.908 | 1 | 1 | 2130 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2265466.7412 | 155218.8844 | 4418.6882 | 17291.8027 | 137927.0817 | 20388.4816 | 0.081155 | -157434.4502 | 157434.4502
C | Xist Rating 3934 | -50.41 | 1035.03 | 150.287 | 35.6 | 2205.69 | 9082.45 | 14169.8 | 0.47 | 1.81 | 16.413 | 18.691 | 1 | 1 | 2140 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2282955.3207 | 156598.1967 | 4460.2756 | 17372.9849 | 139225.2118 | 20150.548 | 0.081536 | -155597.1906 | 155597.1906
C | Xist Rating 3935 | -50.16 | 1040.15 | 150.287 | 35.6 | 2206.58 | 9119.61 | 14123.5 | 0.47 | 1.8 | 16.414 | 18.592 | 1 | 1 | 2150 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 17 | E | Rod | 2295174.187 | 157983.5892 | 4502.0578 | 17454.167 | 140529.4221 | 20051.2398 | 0.081917 | -154830.3588 | 154830.3588
C | Xist Rating 3936 | -49.87 | 1046.92 | 150.287 | 35.6 | 2205.83 | 9137.79 | 14059.1 | 0.46 | 1.79 | 16.408 | 18.448 | 1 | 1 | 2160 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2309327.5436 | 159375.0619 | 4544.0348 | 17535.3492 | 141839.7127 | 19888.9946 | 0.082298 | -153577.5443 | 153577.5443
C | Xist Rating 3937 | -48.82 | 1074.53 | 150.287 | 35.6 | 2194.58 | 9079.56 | 13786.1 | 0.46 | 1.75 | 16.442 | 17.801 | 1 | 1 | 2170 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2358142.0474 | 160772.6148 | 4586.2066 | 17616.5314 | 143156.0835 | 19221.9906 | 0.082679 | -148427.1165 | 148427.1165
C | Xist Rating 3938 | -48.43 | 1083.84 | 150.287 | 35.6 | 2193.21 | 9099.73 | 13699.1 | 0.46 | 1.74 | 16.441 | 17.605 | 1 | 1 | 2180 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2377088.7264 | 162176.248 | 4628.5732 | 17697.7135 | 144478.5345 | 19021.7902 | 0.08306 | -146881.222 | 146881.222
C | Xist Rating 3939 | -48.18 | 1090.85 | 150.287 | 35.6 | 2190.56 | 9084.71 | 13639 | 0.45 | 1.73 | 16.436 | 17.479 | 1 | 1 | 2190 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2389572.376 | 163585.9615 | 4671.1346 | 17778.8957 | 145807.0658 | 18877.9691 | 0.083441 | -145770.6735 | 145770.6735
C | Xist Rating 3940 | -47.94 | 1098.26 | 150.287 | 35.6 | 2186.41 | 9043.95 | 13579.4 | 0.44 | 1.72 | 16.431 | 17.359 | 1 | 1 | 2200 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2401246.6466 | 165001.7551 | 4713.8907 | 17860.0779 | 147141.6773 | 18740.2394 | 0.083822 | -144707.1614 | 144707.1614
C | Xist Rating 3941 | -47.57 | 1107.83 | 150.287 | 35.6 | 2184.04 | 9046.53 | 13495.4 | 0.44 | 1.7 | 16.429 | 17.177 | 1 | 1 | 2210 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2419545.0332 | 166423.629 | 4756.8417 | 17941.2601 | 148482.369 | 18554.3862 | 0.084203 | -143272.0521 | 143272.0521
C | Xist Rating 3942 | -46.52 | 1135.31 | 150.287 | 35.6 | 2174.45 | 9012.64 | 13246.2 | 0.44 | 1.66 | 16.467 | 16.615 | 1 | 1 | 2220 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2468674.8295 | 167851.5832 | 4799.9874 | 18022.4422 | 149829.1409 | 17975.6542 | 0.084584 | -138803.2368 | 138803.2368
C | Xist Rating 3943 | -46.21 | 1142.99 | 150.287 | 35.6 | 2173.36 | 9027.93 | 13182.6 | 0.43 | 1.65 | 16.469 | 16.483 | 1 | 1 | 2230 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2484128.7464 | 169285.6176 | 4843.3279 | 18103.6244 | 151181.9931 | 17825.4459 | 0.084965 | -137643.368 | 137643.368
C | Xist Rating 3944 | -45.89 | 1152.02 | 150.287 | 35.6 | 2169.95 | 9007.48 | 13111.7 | 0.43 | 1.64 | 16.464 | 16.34 | 1 | 1 | 2240 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2499825.799 | 170725.7322 | 4886.8633 | 18184.8066 | 152540.9256 | 17679.8991 | 0.085346 | -136519.4941 | 136519.4941
C | Xist Rating 3945 | -45.52 | 1161.9 | 150.287 | 35.6 | 2166.85 | 8996.34 | 13034.1 | 0.42 | 1.63 | 16.461 | 16.182 | 1 | 1 | 2250 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2517663.015 | 172171.927 | 4930.5934 | 18265.9887 | 153905.9382 | 17502.2578 | 0.085727 | -135147.7951 | 135147.7951
C | Xist Rating 3946 | -45.32 | 1166.98 | 150.287 | 35.6 | 2166.27 | 9007.5 | 12995.6 | 0.42 | 1.62 | 16.46 | 16.109 | 1 | 1 | 2260 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2527993.7646 | 173624.2021 | 4974.5182 | 18347.1709 | 155277.0311 | 17429.5038 | 0.086108 | -134586.0085 | 134586.0085
C | Xist Rating 3947 | -44.22 | 1196.63 | 150.287 | 35.6 | 2155.69 | 8961.22 | 12751.9 | 0.42 | 1.59 | 16.497 | 15.588 | 1 | 1 | 2270 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2579563.3247 | 175082.5574 | 5018.6379 | 18428.3531 | 156654.2043 | 16893.1262 | 0.086489 | -130444.2426 | 130444.2426
C | Xist Rating 3948 | -43.89 | 1205.61 | 150.287 | 35.6 | 2152.94 | 8951.26 | 12686.1 | 0.41 | 1.58 | 16.492 | 15.461 | 1 | 1 | 2280 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2595605.9934 | 176546.9929 | 5062.9524 | 18509.5353 | 158037.4577 | 16747.2732 | 0.08687 | -129318.0045 | 129318.0045
C | Xist Rating 3949 | -43.48 | 1216.13 | 150.287 | 35.6 | 2150.71 | 8958.25 | 12606.9 | 0.41 | 1.56 | 16.491 | 15.303 | 1 | 1 | 2290 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2615542.9523 | 178017.5087 | 5107.4617 | 18590.7174 | 159426.7913 | 16586.1793 | 0.087251 | -128074.0799 | 128074.0799
C | Xist Rating 3950 | -43.21 | 1223.3 | 150.287 | 35.6 | 2149.06 | 8958.69 | 12557 | 0.4 | 1.56 | 16.489 | 15.211 | 1 | 1 | 2300 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2628945.098 | 179494.1047 | 5152.1657 | 18671.8996 | 160822.2051 | 16476.584 | 0.087632 | -127227.8143 | 127227.8143
| Xist Rating 3951 | -42.97 | 1230.73 | 150.287 | 35.6 | 2145.87 | 8932.39 | 12507.6 | 0.4 | 1.55 | 16.485 | 15.122 | 1 | 1 | 2310 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2640986.5851 | 180976.781 | 5197.0645 | 18753.0818 | 162223.6992 | 16386.9484 | 0.088013 | -126535.6721 | 126535.6721
| Xist Rating 3952 | -41.83 | 1261.11 | 150.287 | 35.6 | 2136.8 | 8912.38 | 12277.1 | 0.4 | 1.51 | 16.521 | 14.651 | 1 | 1 | 2320 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2694739.848 | 182465.5374 | 5242.1582 | 18834.264 | 163631.2735 | 15902.2689 | 0.088394 | -122793.1054 | 122793.1054
| Xist Rating 3953 | -41.52 | 1270.12 | 150.287 | 35.6 | 2133.85 | 8897.79 | 12216.8 | 0.39 | 1.5 | 16.515 | 14.54 | 1 | 1 | 2330 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2710245.562 | 183960.3742 | 5287.4466 | 18915.4461 | 165044.928 | 15772.4586 | 0.088775 | -121790.7447 | 121790.7447
| Xist Rating 3954 | -41.19 | 1279.1 | 150.287 | 35.6 | 2131.49 | 8893.13 | 12157.2 | 0.39 | 1.49 | 16.511 | 14.431 | 1 | 1 | 2340 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2726388.859 | 185461.2911 | 5332.9298 | 18996.6283 | 166464.6628 | 15661.9858 | 0.089156 | -120937.7025 | 120937.7025
| Xist Rating 3955 | -40.91 | 1287.28 | 150.287 | 35.6 | 2128.72 | 8877.3 | 12104.7 | 0.38 | 1.49 | 16.507 | 14.338 | 1 | 1 | 2350 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2740258.6816 | 186968.2883 | 5378.6078 | 19077.8105 | 167890.4778 | 15550.7393 | 0.089537 | -120078.6871 | 120078.6871
| Xist Rating 3956 | -40.55 | 1297.21 | 150.287 | 35.6 | 2125.89 | 8868.4 | 12039.9 | 0.38 | 1.48 | 16.505 | 14.22 | 1 | 1 | 2360 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2757725.7669 | 188481.3657 | 5424.4805 | 19158.9926 | 169322.3731 | 15430.9278 | 0.089918 | -119153.5344 | 119153.5344
| Xist Rating 3957 | -39.53 | 1325.12 | 150.287 | 35.6 | 2117.81 | 8849.72 | 11846.8 | 0.38 | 1.45 | 16.535 | 13.845 | 1 | 1 | 2370 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2806352.3872 | 190000.5234 | 5470.5481 | 19240.1748 | 170760.3485 | 15045.5133 | 0.090299 | -116177.4659 | 116177.4659
| Xist Rating 3958 | -39.24 | 1334.34 | 150.287 | 35.6 | 2114.28 | 8823.97 | 11791.1 | 0.38 | 1.44 | 16.524 | 13.749 | 1 | 1 | 2380 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2821168.3752 | 191525.7613 | 5516.8105 | 19321.357 | 172204.4043 | 14948.188 | 0.09068 | -115425.9456 | 115425.9456
| Xist Rating 3959 | -38.88 | 1343.82 | 150.287 | 35.6 | 2112.48 | 8832.29 | 11730 | 0.37 | 1.43 | 16.519 | 13.639 | 1 | 1 | 2390 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 2838792.8736 | 193057.0794 | 5563.2676 | 19402.5392 | 173654.5402 | 14818.8673 | 0.091061 | -114427.3652 | 114427.3652
C | Xist Rating 3960 | -35.06 | 1540.5 | 150.287 | 35.6 | 1963.06 | 7237.55 | 10538.8 | 0.41 | 1.25 | 16.447 | 11.494 | 1 | 1 | 2400 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3024093.93 | 194594.4777 | 5609.9196 | 19483.7213 | 175110.7564 | 12661.9361 | 0.091442 | -97772.1146 | 97772.1146
C | Xist Rating 3963 | -31.74 | 1544.7 | 150.287 | 35.6 | 2054.98 | 8667.56 | 10537.9 | 0.39 | 1.25 | 16.554 | 11.516 | 1 | 1 | 2430 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3174327.606 | 199243.1542 | 5751.0441 | 19727.2678 | 179515.8864 | 12662.567 | 0.092585 | -97776.9861 | 97776.9861
C | Xist Rating 3964 | -31.71 | 1546.07 | 150.287 | 35.6 | 2054.84 | 8665.14 | 10537.8 | 0.38 | 1.25 | 16.547 | 11.526 | 1 | 1 | 2440 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3176926.4788 | 200804.8735 | 5798.4752 | 19808.45 | 180996.4235 | 12657.4495 | 0.092966 | -97737.4701 | 97737.4701
C | Xist Rating 3965 | -31.71 | 1547.4 | 150.287 | 35.6 | 2053.98 | 8649.86 | 10537.8 | 0.38 | 1.25 | 16.539 | 11.537 | 1 | 1 | 2450 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3178328.652 | 202372.673 | 5846.1011 | 19889.6322 | 182483.0409 | 12671.3577 | 0.093347 | -97844.865 | 97844.865
C | Xist Rating 3966 | -31.69 | 1548.87 | 150.287 | 35.6 | 2053.31 | 8637.85 | 10537.8 | 0.37 | 1.25 | 16.535 | 11.548 | 1 | 1 | 2460 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3180310.2597 | 203946.5528 | 5893.9217 | 19970.8144 | 183975.7384 | 12667.1978 | 0.093728 | -97812.7434 | 97812.7434
C | Xist Rating 3967 | -31.66 | 1550.22 | 150.287 | 35.6 | 2052.98 | 8632.06 | 10537.8 | 0.36 | 1.25 | 16.57 | 11.559 | 1 | 1 | 2470 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3182570.6556 | 205526.5128 | 5941.9372 | 20051.9965 | 185474.5163 | 12664.4516 | 0.094109 | -97791.5382 | 97791.5382
C | Xist Rating 3968 | -31.67 | 1551.57 | 150.287 | 35.6 | 2051.58 | 8607.33 | 10537.9 | 0.36 | 1.25 | 16.57 | 11.569 | 1 | 1 | 2480 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3183169.9806 | 207112.553 | 5990.1474 | 20133.1787 | 186979.3743 | 12677.5105 | 0.09449 | -97892.3753 | 97892.3753
C | Xist Rating 3969 | -31.65 | 1552.97 | 150.287 | 35.6 | 2051.03 | 8597.64 | 10537.9 | 0.35 | 1.25 | 16.564 | 11.58 | 1 | 1 | 2490 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3185188.0591 | 208704.6735 | 6038.5525 | 20214.3609 | 188490.3126 | 12672.8791 | 0.094871 | -97856.6131 | 97856.6131
C | Xist Rating 3970 | -31.62 | 1553.95 | 150.287 | 35.6 | 2051.31 | 8602.63 | 10537.9 | 0.35 | 1.25 | 16.56 | 11.589 | 1 | 1 | 2500 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3187633.1745 | 210302.8742 | 6087.1523 | 20295.5431 | 190007.3312 | 12684.6674 | 0.095252 | -97947.639 | 97947.639
C | Xist Rating 3971 | -31.61 | 1555.8 | 150.287 | 35.6 | 2050 | 8579.7 | 10537.9 | 0.34 | 1.25 | 16.554 | 11.602 | 1 | 1 | 2510 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3189390 | 211907.1552 | 6135.9469 | 20376.7252 | 191530.4299 | 12681.9047 | 0.095633 | -97926.3066 | 97926.3066
C | Xist Rating 3972 | -31.59 | 1557.26 | 150.287 | 35.6 | 2049.52 | 8571.3 | 10537.8 | 0.34 | 1.25 | 16.59 | 11.612 | 1 | 1 | 2520 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3191635.5152 | 213517.5163 | 6184.9363 | 20457.9074 | 193059.6089 | 12696.1952 | 0.096014 | -98036.654 | 98036.654
C | Xist Rating 3973 | -31.57 | 1558.6 | 150.287 | 35.6 | 2049.17 | 8565.14 | 10537.8 | 0.33 | 1.25 | 16.584 | 11.623 | 1 | 1 | 2530 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3193836.362 | 215133.9577 | 6234.1205 | 20539.0896 | 194594.8682 | 12691.1084 | 0.096395 | -97997.375 | 97997.375
C | Xist Rating 3974 | -31.54 | 1559.75 | 150.287 | 35.6 | 2049.12 | 8564.35 | 10537.8 | 0.33 | 1.25 | 16.578 | 11.632 | 1 | 1 | 2540 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3196114.92 | 216756.4794 | 6283.4995 | 20620.2717 | 196136.2076 | 12702.6826 | 0.096776 | -98086.7478 | 98086.7478
C | Xist Rating 3975 | -31.53 | 1561.29 | 150.287 | 35.6 | 2048.42 | 8552.1 | 10537.7 | 0.32 | 1.25 | 16.573 | 11.643 | 1 | 1 | 2550 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3198177.6618 | 218385.0813 | 6333.0732 | 20701.4539 | 197683.6273 | 12697.4263 | 0.097157 | -98046.1601 | 98046.1601
C | Xist Rating 3976 | -31.49 | 1562.74 | 150.287 | 35.6 | 2048.45 | 8552.65 | 10537.8 | 0.32 | 1.25 | 16.583 | 11.654 | 1 | 1 | 2560 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3201194.753 | 220019.7634 | 6382.8418 | 20782.6361 | 199237.1273 | 12711.5942 | 0.097538 | -98155.5609 | 98155.5609
C | Xist Rating 3977 | -31.5 | 1564.13 | 150.287 | 35.6 | 2047.35 | 8533.47 | 10537.7 | 0.31 | 1.25 | 16.581 | 11.664 | 1 | 1 | 2570 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3202321.5555 | 221660.5257 | 6432.8051 | 20863.8183 | 200796.7075 | 12705.1829 | 0.097919 | -98106.0545 | 98106.0545
C | Xist Rating 3978 | -31.47 | 1565.5 | 150.287 | 35.6 | 2046.98 | 8527.07 | 10537.7 | 0.31 | 1.25 | 16.618 | 11.674 | 1 | 1 | 2580 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3204547.19 | 223307.3683 | 6482.9633 | 20945.0004 | 202362.3679 | 12719.1984 | 0.0983 | -98214.2785 | 98214.2785
C | Xist Rating 3979 | -31.44 | 1566.86 | 150.287 | 35.6 | 2046.95 | 8526.62 | 10537.7 | 0.3 | 1.25 | 16.614 | 11.684 | 1 | 1 | 2590 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3207284.077 | 224960.2911 | 6533.3162 | 21026.1826 | 203934.1085 | 12712.4604 | 0.098681 | -98162.2497 | 98162.2497
C | Xist Rating 3980 | -31.42 | 1568.03 | 150.287 | 35.6 | 2046.9 | 8525.66 | 10537.7 | 0.3 | 1.25 | 16.609 | 11.694 | 1 | 1 | 2600 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3209600.607 | 226619.2942 | 6583.8639 | 21107.3648 | 205511.9294 | 12724.9047 | 0.099062 | -98258.3415 | 98258.3415
C | Xist Rating 3981 | -31.39 | 1569.72 | 150.287 | 35.6 | 2046.32 | 8515.64 | 10537.7 | 0.29 | 1.25 | 16.607 | 11.705 | 1 | 1 | 2610 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3212149.4304 | 228284.3775 | 6634.6064 | 21188.5469 | 207095.8305 | 12719.0626 | 0.099443 | -98213.2299 | 98213.2299
C | Xist Rating 3982 | -31.36 | 1571.12 | 150.287 | 35.6 | 2046.1 | 8511.8 | 10537.7 | 0.29 | 1.25 | 16.606 | 11.715 | 1 | 1 | 2620 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3214668.632 | 229955.541 | 6685.5437 | 21269.7291 | 208685.8118 | 12731.5723 | 0.099824 | -98309.8265 | 98309.8265
C | Xist Rating 3983 | -31.32 | 1572.54 | 150.287 | 35.6 | 2046.13 | 8512.4 | 10537.7 | 0.29 | 1.25 | 16.643 | 11.726 | 1 | 1 | 2630 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3217621.2702 | 231632.7847 | 6736.6758 | 21350.9113 | 210281.8734 | 12746.4194 | 0.10021 | -98424.4716 | 98424.4716
C | Xist Rating 3984 | -31.28 | 1573.79 | 150.287 | 35.6 | 2046.39 | 8516.77 | 10537.7 | 0.28 | 1.25 | 16.638 | 11.735 | 1 | 1 | 2640 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3220588.1181 | 233316.1087 | 6788.0027 | 21432.0935 | 211884.0152 | 12738.0688 | 0.10059 | -98359.9906 | 98359.9906
C | Xist Rating 3985 | -31.3 | 1575.29 | 150.287 | 35.6 | 2045 | 8492.85 | 10537.6 | 0.28 | 1.25 | 16.637 | 11.746 | 1 | 1 | 2650 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3221468.05 | 235005.5129 | 6839.5243 | 21513.2756 | 213492.2373 | 12751.5472 | 0.10097 | -98464.0676 | 98464.0676
C | Xist Rating 3986 | -31.27 | 1576.63 | 150.287 | 35.6 | 2044.72 | 8488.13 | 10537.6 | 0.28 | 1.25 | 16.635 | 11.755 | 1 | 1 | 2660 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3223766.8936 | 236700.9974 | 6891.2408 | 21594.4578 | 215106.5396 | 12762.915 | 0.10135 | -98551.8468 | 98551.8468
C | Xist Rating 3987 | -31.26 | 1578.02 | 150.287 | 35.6 | 2043.9 | 8474.01 | 10537.6 | 0.27 | 1.25 | 16.632 | 11.765 | 1 | 1 | 2670 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3225315.078 | 238402.5621 | 6943.152 | 21675.64 | 216726.9221 | 12755.3818 | 0.10173 | -98493.6775 | 98493.6775
C | Xist Rating 3988 | -31.21 | 1579.44 | 150.287 | 35.6 | 2044.16 | 8478.37 | 10537.6 | 0.27 | 1.25 | 16.672 | 11.775 | 1 | 1 | 2680 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3228628.0704 | 240110.207 | 6995.258 | 21756.8222 | 218353.3849 | 12769.0771 | 0.10211 | -98599.429 | 98599.429
C | Xist Rating 3989 | -31.16 | 1580.82 | 150.287 | 35.6 | 2044.53 | 8484.74 | 10537.6 | 0.26 | 1.25 | 16.665 | 11.785 | 1 | 1 | 2690 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3232033.9146 | 241823.9322 | 7047.5588 | 21838.0043 | 219985.9278 | 12761.1576 | 0.10249 | -98538.2765 | 98538.2765
C | Xist Rating 3990 | -31.11 | 1582.02 | 150.287 | 35.6 | 2045.31 | 8498.36 | 10537.5 | 0.26 | 1.25 | 16.659 | 11.794 | 1 | 1 | 2700 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3235721.3262 | 243543.7376 | 7100.0544 | 21919.1865 | 221624.5511 | 12772.2575 | 0.10287 | -98623.987 | 98623.987
C | Xist Rating 3991 | -31.11 | 1583.67 | 150.287 | 35.6 | 2043.92 | 8474.39 | 10537.6 | 0.26 | 1.25 | 16.651 | 11.805 | 1 | 1 | 2710 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3236894.7864 | 245269.6232 | 7152.7448 | 22000.3687 | 223269.2545 | 12785.3698 | 0.10325 | -98725.2368 | 98725.2368
C | Xist Rating 3992 | -31.09 | 1585.02 | 150.287 | 35.6 | 2043.53 | 8467.58 | 10537.6 | 0.26 | 1.25 | 16.65 | 11.815 | 1 | 1 | 2720 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3239035.9206 | 247001.5891 | 7205.63 | 22081.5508 | 224920.0382 | 12797.6637 | 0.10363 | -98820.1668 | 98820.1668
C | Xist Rating 3993 | -31.1 | 1586.34 | 150.288 | 35.6 | 2042.38 | 8447.88 | 10537.6 | 0.25 | 1.25 | 16.681 | 11.824 | 1 | 1 | 2730 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3239909.0892 | 248739.6352 | 7258.71 | 22162.733 | 226576.9022 | 12789.5242 | 0.10402 | -98757.3157 | 98757.3157
C | Xist Rating 3994 | -31.08 | 1587.62 | 150.288 | 35.6 | 2042.13 | 8443.56 | 10537.6 | 0.25 | 1.25 | 16.678 | 11.833 | 1 | 1 | 2740 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3242126.4306 | 250483.7615 | 7311.9847 | 22243.9152 | 228239.8463 | 12800.6479 | 0.1044 | -98843.2098 | 98843.2098
C | Xist Rating 3995 | -31.05 | 1589.17 | 150.288 | 35.6 | 2041.66 | 8435.67 | 10537.6 | 0.25 | 1.25 | 16.677 | 11.844 | 1 | 1 | 2750 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3244544.8222 | 252233.9681 | 7365.4543 | 22325.0974 | 229908.8707 | 12813.9095 | 0.10478 | -98945.6125 | 98945.6125
C | Xist Rating 3996 | -31.06 | 1590.59 | 150.288 | 35.6 | 2040.3 | 8412.47 | 10537.6 | 0.24 | 1.25 | 16.671 | 11.854 | 1 | 1 | 2760 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3245280.777 | 253990.2549 | 7419.1186 | 22406.2795 | 231583.9753 | 12805.3531 | 0.10516 | -98879.542 | 98879.542
C | Xist Rating 3997 | -31.02 | 1591.83 | 150.288 | 35.6 | 2040.61 | 8417.72 | 10537.6 | 0.24 | 1.25 | 16.673 | 11.863 | 1 | 1 | 2770 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3248304.2163 | 255752.6219 | 7472.9777 | 22487.4617 | 233265.1602 | 12816.5526 | 0.10554 | -98966.0218 | 98966.0218
C | Xist Rating 3998 | -30.96 | 1593.38 | 150.288 | 35.6 | 2040.99 | 8424.14 | 10537.7 | 0.24 | 1.25 | 16.717 | 11.873 | 1 | 1 | 2780 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3252072.6462 | 257521.0692 | 7527.0316 | 22568.6439 | 234952.4253 | 12830.0472 | 0.10592 | -99070.2233 | 99070.2233
C | Xist Rating 3999 | -30.97 | 1594.79 | 150.288 | 35.6 | 2039.72 | 8402.48 | 10537.7 | 0.23 | 1.25 | 16.709 | 11.883 | 1 | 1 | 2790 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3252925.0588 | 259295.5967 | 7581.2803 | 22649.826 | 236645.7706 | 12821.094 | 0.1063 | -99001.0895 | 99001.0895
C | Xist Rating 4000 | -30.81 | 1595.76 | 150.288 | 35.6 | 2043.91 | 8474.05 | 10537.8 | 0.23 | 1.25 | 16.723 | 11.891 | 1 | 1 | 2800 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3261589.8216 | 261076.2044 | 7635.7238 | 22731.0082 | 238345.1962 | 12831.5288 | 0.10668 | -99081.664 | 99081.664
C | Xist Rating 4001 | -30.88 | 1597.5 | 150.288 | 35.6 | 2040.2 | 8410.66 | 10537.7 | 0.23 | 1.25 | 16.71 | 11.902 | 1 | 1 | 2810 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3259219.5 | 262862.8924 | 7690.3621 | 22812.1904 | 240050.702 | 12844.2997 | 0.10706 | -99180.278 | 99180.278
C | Xist Rating 4002 | -30.71 | 1598.98 | 150.288 | 35.6 | 2044.34 | 8481.39 | 10537.8 | 0.23 | 1.25 | 16.735 | 11.912 | 1 | 1 | 2820 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3268858.7732 | 264655.6606 | 7745.1952 | 22893.3726 | 241762.2881 | 12857.1343 | 0.10744 | -99279.3831 | 99279.3831
C | Xist Rating 4003 | -30.3 | 1600.35 | 150.288 | 35.6 | 2055.43 | 8675.44 | 10538 | 0.22 | 1.25 | 16.837 | 11.922 | 1 | 1 | 2830 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3289407.4005 | 266454.5091 | 7800.223 | 22974.5547 | 243479.9543 | 12850.8622 | 0.10783 | -99230.9518 | 99230.9518
C | Xist Rating 4004 | -30.63 | 1601.67 | 150.288 | 35.6 | 2044.68 | 8487.24 | 10537.9 | 0.22 | 1.25 | 16.778 | 11.93 | 1 | 1 | 2840 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3274902.6156 | 268259.4378 | 7855.4457 | 23055.7369 | 245203.7008 | 12859.1782 | 0.10821 | -99295.1655 | 99295.1655
C | Xist Rating 4005 | -30.22 | 1603.11 | 150.288 | 35.6 | 2055.9 | 8683.74 | 10538 | 0.22 | 1.25 | 16.842 | 11.941 | 1 | 1 | 2850 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3295833.849 | 270070.4467 | 7910.8631 | 23136.9191 | 246933.5276 | 12874.055 | 0.10859 | -99410.0399 | 99410.0399
C | Xist Rating 4006 | -29.68 | 1604.52 | 150.288 | 35.6 | 2071.17 | 8962.85 | 10538.1 | 0.21 | 1.25 | 16.925 | 11.951 | 1 | 1 | 2860 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3323233.6884 | 271887.5358 | 7966.4753 | 23218.1013 | 248669.4346 | 12866.7441 | 0.10897 | -99353.5875 | 99353.5875
C | Xist Rating 4007 | -29.39 | 1605.71 | 150.288 | 35.6 | 2078.83 | 9108.06 | 10538.1 | 0.21 | 1.25 | 16.954 | 11.96 | 1 | 1 | 2870 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3337998.1193 | 273710.7052 | 8022.2824 | 23299.2834 | 250411.4218 | 12878.4672 | 0.10935 | -99444.1104 | 99444.1104
C | Xist Rating 4008 | -29.23 | 1607.22 | 150.288 | 35.6 | 2082.28 | 9174.57 | 10538.1 | 0.21 | 1.25 | 17.007 | 11.971 | 1 | 1 | 2880 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3346682.0616 | 275539.9548 | 8078.2842 | 23380.4656 | 252159.4892 | 12892.9235 | 0.10973 | -99555.7375 | 99555.7375
C | Xist Rating 4009 | -29.11 | 1608.56 | 150.288 | 35.6 | 2085.05 | 9228.64 | 10538.1 | 0.2 | 1.25 | 17.014 | 11.98 | 1 | 1 | 2890 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3353928.028 | 277375.2847 | 8134.4807 | 23461.6478 | 253913.6369 | 12882.0208 | 0.11011 | -99471.5499 | 99471.5499
C | Xist Rating 4010 | -28.99 | 1609.95 | 150.288 | 35.6 | 2087.55 | 9277.94 | 10538.1 | 0.2 | 1.25 | 17.021 | 11.989 | 1 | 1 | 2900 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3360851.1225 | 279216.6948 | 8190.8721 | 23542.8299 | 255673.8648 | 12893.0746 | 0.11049 | -99556.9042 | 99556.9042
C | Xist Rating 4011 | -28.87 | 1611.48 | 150.288 | 35.6 | 2089.75 | 9321.58 | 10538.1 | 0.2 | 1.25 | 17.03 | 11.999 | 1 | 1 | 2910 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3367590.33 | 281064.1851 | 8247.4583 | 23624.0121 | 257440.173 | 12905.2203 | 0.11087 | -99650.69 | 99650.69
C | Xist Rating 4012 | -28.72 | 1612.88 | 150.288 | 35.6 | 2093.15 | 9389.52 | 10538 | 0.2 | 1.25 | 17.039 | 12.009 | 1 | 1 | 2920 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3375999.772 | 282917.7556 | 8304.2393 | 23705.1943 | 259212.5614 | 12917.3676 | 0.11125 | -99744.4883 | 99744.4883
C | Xist Rating 4013 | -28.59 | 1614.26 | 150.288 | 35.5 | 2095.88 | 9444.77 | 10538.1 | 0.19 | 1.25 | 17.087 | 12.018 | 1 | 1 | 2930 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3383295.2488 | 284777.4064 | 8361.215 | 23786.3765 | 260991.03 | 12907.061 | 0.11164 | -99664.9037 | 99664.9037
C | Xist Rating 4014 | -28.29 | 1615.63 | 150.288 | 35.5 | 2104.14 | 9614.99 | 10537.9 | 0.19 | 1.25 | 17.102 | 12.028 | 1 | 1 | 2940 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3399511.7082 | 286643.1375 | 8418.3855 | 23867.5586 | 262775.5788 | 12919.2768 | 0.11202 | -99759.231 | 99759.231
C | Xist Rating 4015 | -28.28 | 1617.04 | 150.288 | 35.5 | 2103.42 | 9600.07 | 10537.9 | 0.19 | 1.25 | 17.098 | 12.037 | 1 | 1 | 2950 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3401314.2768 | 288514.9487 | 8475.7509 | 23948.7408 | 264566.2079 | 12929.9793 | 0.1124 | -99841.8729 | 99841.8729
C | Xist Rating 4016 | -28.26 | 1618.41 | 150.288 | 35.5 | 2102.74 | 9585.85 | 10537.9 | 0.19 | 1.25 | 17.094 | 12.046 | 1 | 1 | 2960 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3403095.4434 | 290392.8402 | 8533.311 | 24029.923 | 266362.9172 | 12940.6812 | 0.11278 | -99924.5096 | 99924.5096
C | Xist Rating 4017 | -28.25 | 1619.79 | 150.288 | 35.5 | 2102.04 | 9571.34 | 10537.9 | 0.18 | 1.25 | 17.092 | 12.055 | 1 | 1 | 2970 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3404863.3716 | 292276.8119 | 8591.0659 | 24111.1051 | 268165.7068 | 12928.6784 | 0.11316 | -99831.8279 | 99831.8279
C | Xist Rating 4018 | -28.24 | 1621.02 | 150.288 | 35.5 | 2101.43 | 9558.74 | 10537.9 | 0.18 | 1.25 | 17.128 | 12.063 | 1 | 1 | 2980 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3406460.0586 | 294166.8639 | 8649.0156 | 24192.2873 | 269974.5766 | 12939.2311 | 0.11354 | -99913.3125 | 99913.3125
C | Xist Rating 4019 | -28.22 | 1622.58 | 150.288 | 35.5 | 2100.69 | 9543.47 | 10537.9 | 0.18 | 1.25 | 17.124 | 12.073 | 1 | 1 | 2990 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3408537.5802 | 296062.9961 | 8707.16 | 24273.4695 | 271789.5266 | 12950.9015 | 0.11392 | -100003.4286 | 100003.4286
C | Xist Rating 4020 | -28.2 | 1624.01 | 150.288 | 35.5 | 2100.11 | 9531.45 | 10537.9 | 0.18 | 1.25 | 17.119 | 12.082 | 1 | 1 | 3000 | 152.4 | 2 | 2.9 | 19.05 | 1.3333 | 16 | E | Rod | 3410599.6411 | 297965.2085 | 8765.4993 | 24354.6517 | 273610.5569 | 12961.5086 | 0.1143 | -100085.3338 | 100085.3338
C | Xist Rating 4021 | -91.34 | 158.421 | 150.291 | 35.8 | 2392.4 | 7335.71 | 58745.8 | 2.45 | 10.95 | 18.204 | 441.517 | 1 | 1 | 1000 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 379006.4004 | 39847.645 | 973.9444 | 8398.1557 | 31449.4893 | 460513.8768 | 0.038101 | -3555966.0882 | 3555966.0882
C | Xist Rating 4022 | -91.26 | 160.081 | 150.291 | 35.8 | 2389.43 | 7316.12 | 58284.2 | 2.43 | 10.85 | 18.243 | 433.249 | 1 | 1 | 1010 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 382502.3438 | 40563.7613 | 993.5206 | 8482.1373 | 32081.624 | 451935.3712 | 0.038482 | -3489725.1414 | 3489725.1414
C | Xist Rating 4023 | -90.61 | 172.565 | 150.291 | 35.8 | 2382.87 | 7318.24 | 54967.7 | 2.44 | 10.07 | 18.296 | 375.451 | 1 | 1 | 1020 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 411199.9615 | 41286.1675 | 1013.2917 | 8566.1189 | 32720.0487 | 391946.3641 | 0.038863 | -3026505.9302 | 3026505.9302
C | Xist Rating 4024 | -90.5 | 176.03 | 150.29 | 35.8 | 2362.96 | 7149.19 | 54179.2 | 2.36 | 9.89 | 17.919 | 362.925 | 1 | 1 | 1030 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 415951.8488 | 42014.8636 | 1033.2576 | 8650.1004 | 33364.7632 | 378849.4886 | 0.039244 | -2925375.3291 | 2925375.3291
C | Xist Rating 4025 | -90.44 | 177.764 | 150.29 | 35.8 | 2357.22 | 7104.57 | 53793.7 | 2.32 | 9.8 | 17.823 | 356.924 | 1 | 1 | 1040 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 419028.8561 | 42749.8496 | 1053.4182 | 8734.082 | 34015.7676 | 372592.6191 | 0.039625 | -2877061.4411 | 2877061.4411
C | Xist Rating 4026 | -90.25 | 181.107 | 150.29 | 35.8 | 2360.47 | 7149.56 | 53043.5 | 2.27 | 9.63 | 17.776 | 345.136 | 1 | 1 | 1050 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 427497.6403 | 43491.1255 | 1073.7737 | 8818.0635 | 34673.0619 | 360322.3702 | 0.040006 | -2782313.8318 | 2782313.8318
C | Xist Rating 4027 | -90.1 | 182.822 | 150.29 | 35.8 | 2374.76 | 7290.38 | 52676.9 | 2.22 | 9.54 | 17.769 | 339.567 | 1 | 1 | 1060 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 434158.3727 | 44238.6913 | 1094.3239 | 8902.0451 | 35336.6462 | 354514.091 | 0.040387 | -2737463.8395 | 2737463.8395
C | Xist Rating 4028 | -89.46 | 196.291 | 150.29 | 35.8 | 2355.21 | 7172.14 | 49857.3 | 2.21 | 8.9 | 17.641 | 297.141 | 1 | 1 | 1070 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 462306.5261 | 44992.5469 | 1115.0689 | 8986.0266 | 36006.5203 | 310450.3491 | 0.040768 | -2397215.3046 | 2397215.3046
C | Xist Rating 4029 | -89.3 | 198.867 | 150.29 | 35.8 | 2362.17 | 7248.79 | 49380.8 | 2.15 | 8.79 | 17.565 | 290.515 | 1 | 1 | 1080 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 469757.6614 | 45752.6925 | 1136.0087 | 9070.0082 | 36682.6843 | 303527.5832 | 0.041149 | -2343759.5412 | 2343759.5412
C | Xist Rating 4030 | -89.11 | 202.29 | 150.289 | 35.8 | 2364.04 | 7281.99 | 48761.7 | 2.09 | 8.65 | 17.447 | 281.996 | 1 | 1 | 1090 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 478221.6516 | 46519.128 | 1157.1433 | 9153.9898 | 37365.1382 | 294634.0012 | 0.04153 | -2275085.6581 | 2275085.6581
C | Xist Rating 4031 | -88.94 | 204.833 | 150.289 | 35.8 | 2372.26 | 7372.66 | 48308.1 | 2.05 | 8.55 | 17.439 | 275.836 | 1 | 1 | 1100 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 485917.1326 | 47291.8534 | 1178.4727 | 9237.9713 | 38053.882 | 288217.9768 | 0.041911 | -2225542.8185 | 2225542.8185
C | Xist Rating 4032 | -88.87 | 206.735 | 150.289 | 35.8 | 2366.56 | 7325.74 | 48011.4 | 1.98 | 8.49 | 17.205 | 272.109 | 1 | 1 | 1110 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 489250.7816 | 48070.8686 | 1199.9969 | 9321.9529 | 38748.9158 | 284279.7274 | 0.042292 | -2195132.701 | 2195132.701
C | Xist Rating 4033 | -88.09 | 221.689 | 150.289 | 35.8 | 2364.1 | 7375.02 | 45448.1 | 2.02 | 7.92 | 17.414 | 238.092 | 1 | 1 | 1120 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 524094.9649 | 48856.1738 | 1221.7158 | 9405.9344 | 39450.2394 | 249024.1417 | 0.042673 | -1922898.4134 | 1922898.4134
C | Xist Rating 4034 | -88 | 223.545 | 150.289 | 35.8 | 2362.85 | 7370.71 | 45189.1 | 1.96 | 7.86 | 17.261 | 235.074 | 1 | 1 | 1130 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 528203.3032 | 49647.7689 | 1243.6296 | 9489.916 | 40157.8529 | 245837.6086 | 0.043054 | -1898292.8491 | 1898292.8491
C | Xist Rating 4035 | -87.84 | 227.039 | 150.288 | 35.8 | 2358.25 | 7341.69 | 44681.2 | 1.91 | 7.75 | 17.12 | 228.975 | 1 | 1 | 1140 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 535414.7218 | 50445.6538 | 1265.7381 | 9573.8976 | 40871.7563 | 239461.1079 | 0.043435 | -1849055.201 | 1849055.201
C | Xist Rating 4036 | -87.66 | 230.47 | 150.288 | 35.8 | 2359.11 | 7365.65 | 44186.9 | 1.87 | 7.64 | 16.985 | 223.069 | 1 | 1 | 1150 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 543704.0817 | 51249.8287 | 1288.0414 | 9657.8791 | 41591.9496 | 233294.0798 | 0.043816 | -1801435.0451 | 1801435.0451
C | Xist Rating 4037 | -87.47 | 233.98 | 150.288 | 35.8 | 2360.27 | 7392.59 | 43704.1 | 1.81 | 7.53 | 16.874 | 217.46 | 1 | 1 | 1160 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 552255.9746 | 52060.2935 | 1310.5395 | 9741.8607 | 42318.4328 | 227419.943 | 0.044197 | -1756076.5177 | 1756076.5177
C | Xist Rating 4038 | -86.76 | 247.435 | 150.288 | 35.8 | 2359.1 | 7445.83 | 41833.1 | 1.83 | 7.13 | 16.997 | 195.625 | 1 | 1 | 1170 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 583723.9085 | 52877.0481 | 1333.2324 | 9825.8422 | 43051.2059 | 204787.5243 | 0.044578 | -1581314.9792 | 1581314.9792
C | Xist Rating 4039 | -86.66 | 248.456 | 150.288 | 35.8 | 2368.42 | 7543.5 | 41725.4 | 1.78 | 7.11 | 16.937 | 194.597 | 1 | 1 | 1180 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 588448.1595 | 53700.0927 | 1356.1201 | 9909.8238 | 43790.2689 | 203683.2902 | 0.044959 | -1572788.3765 | 1572788.3765
C | Xist Rating 4040 | -86.36 | 255.303 | 150.288 | 35.8 | 2357.98 | 7470.11 | 40886.4 | 1.73 | 6.93 | 16.809 | 185.513 | 1 | 1 | 1190 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 601999.3679 | 54529.4271 | 1379.2026 | 9993.8053 | 44535.6218 | 194206.1002 | 0.04534 | -1499608.0276 | 1499608.0276
C | Xist Rating 4041 | -86.2 | 257.051 | 150.288 | 35.8 | 2369.86 | 7598.76 | 40682.6 | 1.7 | 6.88 | 16.832 | 183.398 | 1 | 1 | 1200 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 609174.8829 | 55365.0515 | 1402.4799 | 10077.7869 | 45287.2646 | 191997.6896 | 0.045721 | -1482555.266 | 1482555.266
C | Xist Rating 4042 | -86.04 | 260.63 | 150.287 | 35.8 | 2366.33 | 7578.73 | 40281.7 | 1.65 | 6.8 | 16.719 | 179.291 | 1 | 1 | 1210 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 616736.5879 | 56206.9657 | 1425.9519 | 10161.7685 | 46045.1973 | 187689.6437 | 0.046102 | -1449289.6775 | 1449289.6775
C | Xist Rating 4043 | -85.31 | 275.938 | 150.287 | 35.8 | 2353 | 7515.95 | 38538.4 | 1.65 | 6.43 | 16.742 | 161.263 | 1 | 1 | 1220 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 649282.114 | 57055.1699 | 1449.6188 | 10245.75 | 46809.4199 | 168982.035 | 0.046483 | -1304834.4822 | 1304834.4822
C | Xist Rating 4044 | -85.09 | 279.367 | 150.287 | 35.8 | 2359.66 | 7600.28 | 38183.4 | 1.62 | 6.35 | 16.744 | 157.821 | 1 | 1 | 1230 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 659211.1352 | 57909.6639 | 1473.4804 | 10329.7316 | 47579.9324 | 165392.3928 | 0.046864 | -1277116.2167 | 1277116.2167
C | Xist Rating 4045 | -84.92 | 282.936 | 150.287 | 35.8 | 2358.75 | 7606.88 | 37835.7 | 1.58 | 6.28 | 16.666 | 154.562 | 1 | 1 | 1240 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 667375.29 | 58770.4479 | 1497.5369 | 10413.7131 | 48356.7347 | 161976.0083 | 0.047245 | -1250735.8011 | 1250735.8011
C | Xist Rating 4046 | -84.8 | 284.828 | 150.287 | 35.8 | 2361.91 | 7647.92 | 37664.6 | 1.54 | 6.24 | 16.613 | 153.041 | 1 | 1 | 1250 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 672738.1015 | 59637.5217 | 1521.7881 | 10497.6947 | 49139.827 | 160366.33 | 0.047626 | -1238306.2915 | 1238306.2915
C | Xist Rating 4047 | -84.55 | 289.995 | 150.287 | 35.8 | 2360.17 | 7653.8 | 37161.6 | 1.52 | 6.14 | 16.577 | 148.316 | 1 | 1 | 1260 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 684437.4992 | 60510.8854 | 1546.2341 | 10581.6762 | 49929.2092 | 155449.0366 | 0.048007 | -1200336.2557 | 1200336.2557
C | Xist Rating 4048 | -83.83 | 304.498 | 150.287 | 35.8 | 2353.08 | 7649.11 | 35777.9 | 1.52 | 5.85 | 16.635 | 135.48 | 1 | 1 | 1270 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 716508.1538 | 61390.5391 | 1570.8749 | 10665.6578 | 50724.8813 | 142135.1841 | 0.048388 | -1097530.2157 | 1097530.2157
C | Xist Rating 4049 | -83.67 | 308.135 | 150.287 | 35.8 | 2349.48 | 7627.03 | 35477.6 | 1.48 | 5.79 | 16.557 | 132.936 | 1 | 1 | 1280 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 723957.0198 | 62276.4826 | 1595.7105 | 10749.6394 | 51526.8433 | 139459.777 | 0.048769 | -1076871.4313 | 1076871.4313
C | Xist Rating 4050 | -83.48 | 311.721 | 150.287 | 35.8 | 2349.99 | 7648.31 | 35183.2 | 1.45 | 5.73 | 16.533 | 130.449 | 1 | 1 | 1290 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 732541.2328 | 63168.7161 | 1620.7408 | 10833.6209 | 52335.0951 | 136857.2815 | 0.04915 | -1056775.6508 | 1056775.6508
C | Xist Rating 4051 | -83.17 | 316.866 | 150.287 | 35.8 | 2356.26 | 7739.27 | 34751.8 | 1.42 | 5.64 | 16.56 | 126.756 | 1 | 1 | 1300 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 746618.6812 | 64067.2394 | 1645.966 | 10917.6025 | 53149.6369 | 133006.1844 | 0.049531 | -1027038.4997 | 1027038.4997
C | Xist Rating 4052 | -82.99 | 319.634 | 150.287 | 35.8 | 2362.8 | 7822.69 | 34540.4 | 1.39 | 5.59 | 16.521 | 125.054 | 1 | 1 | 1310 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 755231.2152 | 64972.0526 | 1671.3859 | 11001.584 | 53970.4686 | 131216.8452 | 0.049912 | -1013221.697 | 1013221.697
C | Xist Rating 4053 | -82.26 | 334.235 | 150.287 | 35.8 | 2357.02 | 7831.02 | 33363.8 | 1.39 | 5.35 | 16.57 | 115.196 | 1 | 1 | 1320 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 787798.5797 | 65883.1557 | 1697.0007 | 11085.5656 | 54797.5902 | 120993.6514 | 0.050293 | -934280.9041 | 934280.9041
C | Xist Rating 4054 | -82.01 | 339.597 | 150.287 | 35.8 | 2353.78 | 7819.78 | 32980.7 | 1.35 | 5.28 | 16.459 | 112.218 | 1 | 1 | 1330 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 799336.6267 | 66800.5488 | 1722.8102 | 11169.5471 | 55631.0016 | 117862.8797 | 0.050674 | -910105.9147 | 910105.9147
C | Xist Rating 4055 | -81.74 | 344.857 | 150.287 | 35.7 | 2354.62 | 7853.64 | 32607.4 | 1.33 | 5.2 | 16.43 | 109.331 | 1 | 1 | 1340 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 812007.1893 | 67724.2317 | 1748.8145 | 11253.5287 | 56470.703 | 114852.6057 | 0.051055 | -886861.3771 | 886861.3771
C | Xist Rating 4056 | -81.57 | 347.642 | 150.287 | 35.7 | 2358.06 | 7904.5 | 32424.2 | 1.3 | 5.16 | 16.399 | 107.987 | 1 | 1 | 1350 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 819760.6945 | 68654.2045 | 1775.0136 | 11337.5103 | 57316.6942 | 113434.3932 | 0.051436 | -875910.3159 | 875910.3159
C | Xist Rating 4057 | -81.37 | 349.337 | 150.287 | 35.7 | 2373.81 | 8092.93 | 32303.7 | 1.29 | 5.14 | 16.455 | 107.072 | 1 | 1 | 1360 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 829259.664 | 69590.4672 | 1801.4075 | 11421.4918 | 58168.9754 | 112488.1299 | 0.051817 | -868603.522 | 868603.522
C | Xist Rating 4058 | -80.48 | 370.151 | 150.287 | 35.7 | 2348.29 | 7903.31 | 30902.9 | 1.28 | 4.86 | 16.413 | 96.529 | 1 | 1 | 1370 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 869221.8918 | 70533.0198 | 1827.9962 | 11505.4734 | 59027.5465 | 101535.3496 | 0.052198 | -784029.0559 | 784029.0559
C | Xist Rating 4059 | -80.39 | 372.107 | 150.287 | 35.7 | 2347.06 | 7897.65 | 30794.8 | 1.25 | 4.84 | 16.383 | 95.823 | 1 | 1 | 1380 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 873357.4554 | 71481.8623 | 1854.7797 | 11589.4549 | 59892.4074 | 100778.8089 | 0.052579 | -778187.2485 | 778187.2485
C | Xist Rating 4060 | -80.16 | 376.609 | 150.287 | 35.7 | 2347.35 | 7921.26 | 30527.9 | 1.23 | 4.78 | 16.353 | 93.972 | 1 | 1 | 1390 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 884033.1361 | 72436.9948 | 1881.7579 | 11673.4365 | 60763.5583 | 98843.0134 | 0.05296 | -763239.5494 | 763239.5494
C | Xist Rating 4061 | -79.92 | 381.107 | 150.286 | 35.7 | 2349.1 | 7962 | 30265.6 | 1.2 | 4.73 | 16.327 | 92.176 | 1 | 1 | 1400 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 895258.4537 | 73398.4171 | 1908.931 | 11757.418 | 61640.999 | 96954.1417 | 0.053341 | -748654.1827 | 748654.1827
C | Xist Rating 4062 | -79.64 | 386.429 | 150.286 | 35.7 | 2350.29 | 8000.51 | 29957.8 | 1.18 | 4.67 | 16.309 | 90.072 | 1 | 1 | 1410 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 908220.2144 | 74366.1293 | 1936.2988 | 11841.3996 | 62524.7297 | 94755.9426 | 0.053722 | -731680.2719 | 731680.2719
C | Xist Rating 4063 | -78.87 | 401.979 | 150.287 | 35.7 | 2345.35 | 8019.85 | 29052.3 | 1.19 | 4.49 | 16.371 | 83.842 | 1 | 1 | 1420 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 942781.4476 | 75340.1314 | 1963.8614 | 11925.3812 | 63414.7502 | 88309.8008 | 0.054103 | -681904.8736 | 681904.8736
C | Xist Rating 4064 | -78.76 | 405.005 | 150.286 | 35.7 | 2341.93 | 7992.26 | 28911.1 | 1.15 | 4.47 | 16.304 | 83.006 | 1 | 1 | 1430 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 948493.3596 | 76320.4234 | 1991.6188 | 12009.3627 | 64311.0607 | 87403.435 | 0.054484 | -674906.1573 | 674906.1573
C | Xist Rating 4065 | -78.41 | 412.021 | 150.286 | 35.7 | 2340.32 | 8006.44 | 28542.3 | 1.13 | 4.39 | 16.29 | 80.624 | 1 | 1 | 1440 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 964260.9867 | 77307.0053 | 2019.571 | 12093.3443 | 65213.661 | 84916.0675 | 0.054865 | -655699.3642 | 655699.3642
C | Xist Rating 4066 | -78.19 | 416.558 | 150.286 | 35.7 | 2340.52 | 8029.29 | 28317.1 | 1.11 | 4.35 | 16.271 | 79.225 | 1 | 1 | 1450 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 974962.3302 | 78299.8771 | 2047.718 | 12177.3258 | 66122.5512 | 83448.913 | 0.055246 | -644370.3863 | 644370.3863
C | Xist Rating 4067 | -78 | 419.224 | 150.286 | 35.7 | 2347.15 | 8120.59 | 28183.9 | 1.1 | 4.32 | 16.286 | 78.402 | 1 | 1 | 1460 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 983981.6116 | 79299.0388 | 2076.0598 | 12261.3074 | 67037.7314 | 82592.7559 | 0.055627 | -637759.3683 | 637759.3683
C | Xist Rating 4068 | -77.23 | 436.898 | 150.286 | 35.7 | 2331.46 | 8018.85 | 27310.5 | 1.09 | 4.16 | 16.279 | 72.943 | 1 | 1 | 1470 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1018610.2111 | 80304.4904 | 2104.5964 | 12345.2889 | 67959.2014 | 76920.3892 | 0.056008 | -593958.8564 | 593958.8564
C | Xist Rating 4069 | -76.96 | 442.263 | 150.286 | 35.7 | 2331.56 | 8044.61 | 27066.3 | 1.08 | 4.11 | 16.266 | 71.502 | 1 | 1 | 1480 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1031162.7203 | 81316.2319 | 2133.3277 | 12429.2705 | 68886.9614 | 75420.1358 | 0.056389 | -582374.2968 | 582374.2968
C | Xist Rating 4070 | -76.71 | 446.801 | 150.286 | 35.7 | 2333.68 | 8090.45 | 26867.1 | 1.06 | 4.07 | 16.26 | 70.35 | 1 | 1 | 1490 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1042690.5577 | 82334.2633 | 2162.2539 | 12513.2521 | 69821.0112 | 74209.5076 | 0.05677 | -573026.1468 | 573026.1468
C | Xist Rating 4071 | -76.45 | 451.432 | 150.286 | 35.7 | 2336.61 | 8146.67 | 26670.5 | 1.03 | 4.03 | 16.244 | 69.239 | 1 | 1 | 1500 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1054820.5255 | 83358.5845 | 2191.3748 | 12597.2336 | 70761.3509 | 73029.5554 | 0.057151 | -563914.8686 | 563914.8686
C | Xist Rating 4072 | -76.12 | 456.824 | 150.286 | 35.7 | 2341.98 | 8237.84 | 26439 | 1.02 | 3.99 | 16.245 | 67.919 | 1 | 1 | 1510 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1069872.6715 | 84389.1957 | 2220.6906 | 12681.2152 | 71707.9805 | 71655.3115 | 0.057532 | -553303.3214 | 553303.3214
C | Xist Rating 4073 | -75.25 | 474.181 | 150.286 | 35.7 | 2339.67 | 8296.8 | 25681.2 | 1.02 | 3.85 | 16.316 | 63.532 | 1 | 1 | 1520 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1109427.0603 | 85426.0968 | 2250.2011 | 12765.1967 | 72660.9001 | 67111.7805 | 0.057913 | -518219.3799 | 518219.3799
C | Xist Rating 4074 | -75.04 | 479.917 | 150.286 | 35.7 | 2332.93 | 8238 | 25468.5 | 1 | 3.8 | 16.261 | 62.422 | 1 | 1 | 1530 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1119612.7668 | 86469.2878 | 2279.9064 | 12849.1783 | 73620.1095 | 65940.3556 | 0.058294 | -509173.9468 | 509173.9468
C | Xist Rating 4075 | -74.83 | 482.858 | 150.286 | 35.7 | 2338.53 | 8321.11 | 25363.8 | 0.97 | 3.78 | 16.252 | 61.896 | 1 | 1 | 1540 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1129177.9187 | 87518.7687 | 2309.8065 | 12933.1599 | 74585.6088 | 65367.1168 | 0.058675 | -504747.5491 | 504747.5491
C | Xist Rating 4076 | -74.4 | 491.694 | 150.286 | 35.7 | 2337.25 | 8347.93 | 25021.3 | 0.96 | 3.72 | 16.248 | 60.051 | 1 | 1 | 1550 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1149211.8015 | 88574.5394 | 2339.9013 | 13017.1414 | 75557.398 | 63446.5952 | 0.059056 | -489917.7902 | 489917.7902
C | Xist Rating 4077 | -74.13 | 494.411 | 150.286 | 35.7 | 2349.35 | 8517.82 | 24920.9 | 0.95 | 3.7 | 16.273 | 59.535 | 1 | 1 | 1560 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1161544.4829 | 89636.6001 | 2370.191 | 13101.123 | 76535.4772 | 62908.0209 | 0.059437 | -485759.0623 | 485759.0623
C | Xist Rating 4078 | -73.31 | 514.933 | 150.286 | 35.7 | 2328.6 | 8351.09 | 24162.3 | 0.94 | 3.56 | 16.262 | 55.546 | 1 | 1 | 1570 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1199072.9838 | 90704.9507 | 2400.6755 | 13185.1045 | 77519.8462 | 58760.2006 | 0.059818 | -453730.6931 | 453730.6931
C | Xist Rating 4079 | -73.03 | 519.592 | 150.286 | 35.7 | 2332.37 | 8421.39 | 24007.8 | 0.93 | 3.53 | 16.255 | 54.795 | 1 | 1 | 1580 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1211880.793 | 91779.5912 | 2431.3547 | 13269.0861 | 78510.5051 | 57975.162 | 0.0602 | -447668.8333 | 447668.8333
C | Xist Rating 4080 | -72.78 | 524.286 | 150.286 | 35.7 | 2334.75 | 8474.5 | 23855.4 | 0.91 | 3.5 | 16.244 | 54.063 | 1 | 1 | 1590 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1224076.7385 | 92860.5215 | 2462.2288 | 13353.0676 | 79507.4539 | 57197.8737 | 0.060581 | -441666.8189 | 441666.8189
C | Xist Rating 4081 | -72.41 | 530.532 | 150.286 | 35.7 | 2339.11 | 8563.48 | 23645.6 | 0.9 | 3.46 | 16.254 | 53.031 | 1 | 1 | 1600 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1240972.7065 | 93947.7418 | 2493.2976 | 13437.0492 | 80510.6926 | 56121.7647 | 0.060962 | -433357.3904 | 433357.3904
C | Xist Rating 4082 | -72.25 | 533.669 | 150.286 | 35.7 | 2340.48 | 8595.38 | 23556.9 | 0.88 | 3.45 | 16.232 | 52.647 | 1 | 1 | 1610 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1249041.6211 | 95041.252 | 2524.5612 | 13521.0308 | 81520.2212 | 55704.681 | 0.061343 | -430136.7813 | 430136.7813
C | Xist Rating 4083 | -71.24 | 556.571 | 150.286 | 35.7 | 2326.38 | 8523.53 | 22805.4 | 0.88 | 3.31 | 16.246 | 48.964 | 1 | 1 | 1620 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1294795.643 | 96141.052 | 2556.0196 | 13605.0123 | 82536.0397 | 51887.1888 | 0.061724 | -400659.1183 | 400659.1183
C | Xist Rating 4084 | -71.01 | 559.363 | 150.286 | 35.7 | 2334.89 | 8652.55 | 22723.4 | 0.87 | 3.29 | 16.263 | 48.602 | 1 | 1 | 1630 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1306051.0751 | 97247.142 | 2587.6728 | 13688.9939 | 83558.1481 | 51506.8713 | 0.062105 | -397722.4076 | 397722.4076
C | Xist Rating 4085 | -70.78 | 564.205 | 150.286 | 35.7 | 2333.85 | 8660.87 | 22588.7 | 0.85 | 3.27 | 16.242 | 48.013 | 1 | 1 | 1640 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1316769.8392 | 98359.5218 | 2619.5208 | 13772.9754 | 84586.5464 | 50876.3151 | 0.062486 | -392853.4193 | 392853.4193
C | Xist Rating 4086 | -70.49 | 570.808 | 150.286 | 35.7 | 2330.48 | 8646.02 | 22403.1 | 0.83 | 3.24 | 16.218 | 47.19 | 1 | 1 | 1650 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1330256.6278 | 99478.1916 | 2651.5635 | 13856.957 | 85621.2346 | 50002.3206 | 0.062867 | -386104.6652 | 386104.6652
C | Xist Rating 4087 | -70.15 | 577.167 | 150.286 | 35.7 | 2332.45 | 8704.94 | 22220.9 | 0.82 | 3.2 | 16.22 | 46.375 | 1 | 1 | 1660 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1346213.1691 | 100603.1512 | 2683.8011 | 13940.9385 | 86662.2127 | 49150.0326 | 0.063248 | -379523.5232 | 379523.5232
C | Xist Rating 4088 | -69.27 | 597.734 | 150.286 | 35.7 | 2319.76 | 8634.49 | 21633.1 | 0.82 | 3.1 | 16.241 | 43.72 | 1 | 1 | 1670 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1386599.4238 | 101734.4008 | 2716.2334 | 14024.9201 | 87709.4807 | 46400.0702 | 0.063629 | -358289.0425 | 358289.0425
C | Xist Rating 4089 | -69.05 | 600.637 | 150.286 | 35.7 | 2326.12 | 8736.82 | 21560.7 | 0.81 | 3.08 | 16.246 | 43.429 | 1 | 1 | 1680 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1397153.7384 | 102871.9402 | 2748.8606 | 14108.9017 | 88763.0386 | 46091.9113 | 0.06401 | -355909.5217 | 355909.5217
C | Xist Rating 4090 | -68.7 | 609.051 | 150.287 | 35.7 | 2320.8 | 8702.65 | 21346.5 | 0.8 | 3.04 | 16.221 | 42.531 | 1 | 1 | 1690 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1413485.5608 | 104015.7696 | 2781.6825 | 14192.8832 | 89822.8864 | 45151.4163 | 0.064391 | -348647.2686 | 348647.2686
C | Xist Rating 4091 | -68.4 | 614.599 | 150.287 | 35.7 | 2323.01 | 8761.1 | 21206.1 | 0.79 | 3.02 | 16.22 | 41.95 | 1 | 1 | 1700 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1427719.623 | 105165.8888 | 2814.6992 | 14276.8648 | 90889.0241 | 44541.4446 | 0.064772 | -343937.2289 | 343937.2289
C | Xist Rating 4092 | -68.09 | 621.151 | 150.287 | 35.7 | 2322.1 | 8780 | 21045.1 | 0.77 | 2.99 | 16.211 | 41.292 | 1 | 1 | 1710 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1442374.7371 | 106322.298 | 2847.9107 | 14360.8463 | 91961.4517 | 43838.4599 | 0.065153 | -338508.9673 | 338508.9673
C | Xist Rating 4093 | -67.26 | 640.111 | 150.287 | 35.7 | 2312.63 | 8742.02 | 20567.5 | 0.77 | 2.9 | 16.244 | 39.29 | 1 | 1 | 1720 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1480339.9019 | 107484.997 | 2881.317 | 14444.8279 | 93040.1691 | 41766.9404 | 0.065534 | -322513.2425 | 322513.2425
C | Xist Rating 4094 | -66.89 | 648.395 | 150.287 | 35.6 | 2310.18 | 8747.59 | 20374.4 | 0.76 | 2.87 | 16.233 | 38.525 | 1 | 1 | 1730 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1497909.1611 | 108653.986 | 2914.9181 | 14528.8094 | 94125.1765 | 40964.8507 | 0.065915 | -316319.7189 | 316319.7189
C | Xist Rating 4095 | -66.63 | 652.273 | 150.287 | 35.6 | 2315.59 | 8843.9 | 20290.1 | 0.75 | 2.85 | 16.236 | 38.21 | 1 | 1 | 1740 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1510396.8361 | 109829.2648 | 2948.714 | 14612.791 | 95216.4738 | 40630.7684 | 0.066296 | -313740.0234 | 313740.0234
C | Xist Rating 4096 | -66.33 | 659.861 | 150.287 | 35.6 | 2310.72 | 8809.56 | 20123.5 | 0.74 | 2.82 | 16.215 | 37.573 | 1 | 1 | 1750 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1524754.0099 | 111010.8335 | 2982.7046 | 14696.7726 | 96314.061 | 39960.7481 | 0.066677 | -308566.3048 | 308566.3048
C | Xist Rating 4097 | -66.07 | 665.526 | 150.287 | 35.7 | 2308.87 | 8809.79 | 20001.2 | 0.73 | 2.8 | 16.212 | 37.11 | 1 | 1 | 1760 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1536613.0156 | 112198.6922 | 3016.8901 | 14780.7541 | 97417.938 | 39472.3369 | 0.067058 | -304794.9227 | 304794.9227
C | Xist Rating 4098 | -65.1 | 687.991 | 150.287 | 35.7 | 2298.05 | 8766.92 | 19497.8 | 0.73 | 2.71 | 16.25 | 35.138 | 1 | 1 | 1770 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1581037.7176 | 113392.8407 | 3051.2703 | 14864.7357 | 98528.105 | 37431.9238 | 0.067439 | -289039.3936 | 289039.3936
C | Xist Rating 4099 | -65.01 | 693.766 | 150.287 | 35.6 | 2287.75 | 8644.82 | 19383.8 | 0.71 | 2.69 | 16.414 | 34.721 | 1 | 1 | 1780 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1587163.1665 | 114593.2791 | 3085.8453 | 14948.7172 | 99644.5619 | 36987.5467 | 0.06782 | -285608.0316 | 285608.0316
C | Xist Rating 4100 | -64.86 | 696.929 | 150.287 | 35.6 | 2288.23 | 8664.62 | 19327.1 | 0.7 | 2.68 | 16.404 | 34.537 | 1 | 1 | 1790 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 18 | E | Rod | 1594733.8457 | 115800.0074 | 3120.6151 | 15032.6988 | 100767.3087 | 36787.9553 | 0.068201 | -284066.8391 | 284066.8391
C | Xist Rating 4101 | -64.42 | 707.061 | 150.287 | 35.6 | 2285.83 | 8678.25 | 19121.9 | 0.69 | 2.65 | 16.381 | 33.788 | 1 | 1 | 1800 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1616221.2456 | 117013.0257 | 3155.5797 | 15116.6803 | 101896.3453 | 36000.7511 | 0.068582 | -277988.2575 | 277988.2575
C | Xist Rating 4102 | -64.15 | 712.709 | 150.287 | 35.6 | 2285.79 | 8703.74 | 19012.5 | 0.69 | 2.63 | 16.38 | 33.402 | 1 | 1 | 1810 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1629103.1051 | 118232.3338 | 3190.7391 | 15200.6619 | 103031.6719 | 35604.9012 | 0.068963 | -274931.6096 | 274931.6096
C | Xist Rating 4103 | -63.21 | 735.433 | 150.287 | 35.6 | 2274.36 | 8648.66 | 18562.8 | 0.68 | 2.55 | 16.413 | 31.764 | 1 | 1 | 1820 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1672639.3979 | 119457.9318 | 3226.0933 | 15284.6435 | 104173.2883 | 33897.3747 | 0.069344 | -261746.5425 | 261746.5425
C | Xist Rating 4104 | -63.19 | 731.809 | 150.287 | 35.6 | 2286.87 | 8814.53 | 18631.6 | 0.68 | 2.56 | 16.438 | 32.022 | 1 | 1 | 1830 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1673552.0478 | 120689.8197 | 3261.6423 | 15368.625 | 105321.1947 | 34171.7046 | 0.069725 | -263864.8452 | 263864.8452
C | Xist Rating 4105 | -62.83 | 736.429 | 150.287 | 35.6 | 2295.38 | 8965.26 | 18545.6 | 0.67 | 2.55 | 16.459 | 31.729 | 1 | 1 | 1840 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1690384.398 | 121927.9975 | 3297.386 | 15452.6066 | 106475.391 | 33860.0379 | 0.070106 | -261458.237 | 261458.237
C | Xist Rating 4106 | -62.48 | 744.134 | 150.287 | 35.6 | 2293.18 | 8968.4 | 18409.8 | 0.66 | 2.52 | 16.451 | 31.272 | 1 | 1 | 1850 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1706433.2061 | 123172.4652 | 3333.3246 | 15536.5881 | 107635.8771 | 33376.3006 | 0.070487 | -257722.9458 | 257722.9458
C | Xist Rating 4107 | -62.12 | 752.76 | 150.287 | 35.6 | 2289.94 | 8960.14 | 18259.6 | 0.65 | 2.5 | 16.441 | 30.77 | 1 | 1 | 1860 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1723775.2344 | 124423.2229 | 3369.4579 | 15620.5697 | 108802.6532 | 32845.5835 | 0.070868 | -253624.8893 | 253624.8893
C | Xist Rating 4108 | -61.17 | 773.605 | 150.287 | 35.6 | 2284.75 | 8987.97 | 17879.8 | 0.65 | 2.43 | 16.483 | 29.455 | 1 | 1 | 1870 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1767494.0237 | 125680.2704 | 3405.7861 | 15704.5512 | 109975.7191 | 31487.0367 | 0.071249 | -243134.5509 | 243134.5509
C | Xist Rating 4109 | -60.81 | 782.217 | 150.287 | 35.6 | 2281.34 | 8976.46 | 17739.1 | 0.64 | 2.41 | 16.472 | 29.003 | 1 | 1 | 1880 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1784502.9308 | 126943.6078 | 3442.309 | 15788.5328 | 111155.075 | 31007.9543 | 0.07163 | -239435.204 | 239435.204
C | Xist Rating 4110 | -60.46 | 787.913 | 150.287 | 35.6 | 2285.55 | 9069.77 | 17647 | 0.63 | 2.39 | 16.48 | 28.711 | 1 | 1 | 1890 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1800814.5572 | 128213.2351 | 3479.0267 | 15872.5144 | 112340.7207 | 30695.9104 | 0.072011 | -237025.6834 | 237025.6834
C | Xist Rating 4111 | -60.22 | 794.066 | 150.287 | 35.6 | 2281.86 | 9039.45 | 17555.6 | 0.62 | 2.38 | 16.466 | 28.437 | 1 | 1 | 1900 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1811947.4428 | 129489.1523 | 3515.9392 | 15956.4959 | 113532.6564 | 30401.2409 | 0.072392 | -234750.3241 | 234750.3241
C | Xist Rating 4112 | -59.96 | 799.94 | 150.287 | 35.6 | 2280.6 | 9047.48 | 17465.3 | 0.61 | 2.36 | 16.473 | 28.16 | 1 | 1 | 1910 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1824343.164 | 130771.3594 | 3553.0464 | 16040.4775 | 114730.8819 | 30104.4212 | 0.072773 | -232458.3606 | 232458.3606
C | Xist Rating 4113 | -58.87 | 825.266 | 150.287 | 35.6 | 2271.52 | 9035.02 | 17050.7 | 0.61 | 2.29 | 16.522 | 26.806 | 1 | 1 | 1920 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1874608.2243 | 132059.8564 | 3590.3485 | 16124.459 | 115935.3973 | 28705.371 | 0.073154 | -221655.2658 | 221655.2658
C | Xist Rating 4114 | -58.52 | 833.954 | 150.287 | 35.6 | 2267.76 | 9016.74 | 16924.2 | 0.6 | 2.27 | 16.516 | 26.427 | 1 | 1 | 1930 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1891207.523 | 133354.6433 | 3627.8454 | 16208.4406 | 117146.2027 | 28301.6928 | 0.073535 | -218538.17 | 218538.17
C | Xist Rating 4115 | -58.23 | 836.755 | 150.287 | 35.6 | 2277.27 | 9183.2 | 16882.1 | 0.6 | 2.26 | 16.529 | 26.307 | 1 | 1 | 1940 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1905517.0588 | 134655.7201 | 3665.537 | 16292.4221 | 118363.2979 | 28182.1932 | 0.073916 | -217615.4259 | 217615.4259
C | Xist Rating 4116 | -57.98 | 845.031 | 150.287 | 35.6 | 2268.75 | 9082.91 | 16772.2 | 0.58 | 2.24 | 16.51 | 25.995 | 1 | 1 | 1950 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1917164.0812 | 135963.0868 | 3703.4235 | 16376.4037 | 119586.683 | 27832.7686 | 0.074297 | -214917.2613 | 214917.2613
C | Xist Rating 4117 | -57.57 | 854.521 | 150.287 | 35.6 | 2266.17 | 9087.41 | 16637.2 | 0.57 | 2.22 | 16.527 | 25.593 | 1 | 1 | 1960 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1936489.8546 | 137276.7433 | 3741.5047 | 16460.3853 | 120816.3581 | 27405.9308 | 0.074678 | -211621.333 | 211621.333
C | Xist Rating 4118 | -56.59 | 877.373 | 150.287 | 35.6 | 2258.72 | 9084.16 | 16303.3 | 0.58 | 2.16 | 16.585 | 24.573 | 1 | 1 | 1970 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1981739.9426 | 138596.6898 | 3779.7807 | 16544.3668 | 122052.323 | 26368.4497 | 0.075059 | -203610.1791 | 203610.1791
C | Xist Rating 4119 | -56.27 | 884.149 | 150.287 | 35.6 | 2258.89 | 9118.87 | 16214.4 | 0.57 | 2.15 | 16.611 | 24.324 | 1 | 1 | 1980 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 1997195.3346 | 139922.9262 | 3818.2515 | 16628.3484 | 123294.5778 | 26100.7711 | 0.07544 | -201543.2357 | 201543.2357
C | Xist Rating 4120 | -55.92 | 893.033 | 150.287 | 35.6 | 2254.68 | 9091.58 | 16101.6 | 0.56 | 2.13 | 16.607 | 24.011 | 1 | 1 | 1990 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2013503.6444 | 141255.4525 | 3856.9171 | 16712.3299 | 124543.1226 | 25764.9482 | 0.075821 | -198950.1005 | 198950.1005
C | Xist Rating 4121 | -55.61 | 899.934 | 150.287 | 35.6 | 2253.69 | 9107.4 | 16015 | 0.55 | 2.12 | 16.606 | 23.775 | 1 | 1 | 2000 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2028172.2565 | 142594.2687 | 3895.7775 | 16796.3115 | 125797.9572 | 25509.0939 | 0.076202 | -196974.4611 | 196974.4611
C | Xist Rating 4122 | -55.38 | 905.027 | 150.287 | 35.6 | 2253.62 | 9129.2 | 15953.9 | 0.54 | 2.11 | 16.611 | 23.615 | 1 | 1 | 2010 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2039586.9477 | 143939.3748 | 3934.8326 | 16880.2931 | 127059.0817 | 25332.3097 | 0.076583 | -195609.381 | 195609.381
C | Xist Rating 4123 | -54.33 | 930.801 | 150.287 | 35.6 | 2243.57 | 9094.09 | 15615 | 0.54 | 2.05 | 16.648 | 22.639 | 1 | 1 | 2020 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2088317.1996 | 145290.7707 | 3974.0826 | 16964.2746 | 128326.4961 | 24324.5651 | 0.076964 | -187827.8443 | 187827.8443
C | Xist Rating 4124 | -53.9 | 940.235 | 150.287 | 35.6 | 2242.69 | 9125.05 | 15499.9 | 0.54 | 2.03 | 16.65 | 22.327 | 1 | 1 | 2030 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2108655.6321 | 146648.4566 | 4013.5273 | 17048.2562 | 129600.2004 | 24004.6816 | 0.077345 | -185357.7884 | 185357.7884
C | Xist Rating 4125 | -53.65 | 946.587 | 150.287 | 35.6 | 2240.3 | 9112.8 | 15431.7 | 0.53 | 2.02 | 16.643 | 22.159 | 1 | 1 | 2040 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2120638.8561 | 148012.4324 | 4053.1669 | 17132.2377 | 130880.1947 | 23818.6797 | 0.077726 | -183921.5308 | 183921.5308
C | Xist Rating 4126 | -53.33 | 952.125 | 150.287 | 35.6 | 2243.27 | 9189.64 | 15364.3 | 0.52 | 2.01 | 16.657 | 21.979 | 1 | 1 | 2050 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2135873.4487 | 149382.698 | 4093.0012 | 17216.2193 | 132166.4788 | 23621.0795 | 0.078107 | -182395.7143 | 182395.7143
C | Xist Rating 4127 | -53.02 | 961.403 | 150.287 | 35.6 | 2237.11 | 9127.79 | 15264.3 | 0.51 | 1.99 | 16.644 | 21.728 | 1 | 1 | 2060 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2150764.2653 | 150759.2536 | 4133.0303 | 17300.2008 | 133459.0528 | 23348.3058 | 0.078488 | -180289.4287 | 180289.4287
C | Xist Rating 4128 | -51.91 | 989.088 | 150.287 | 35.6 | 2226.71 | 9091.89 | 14936.2 | 0.51 | 1.94 | 16.682 | 20.838 | 1 | 1 | 2070 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2202412.1405 | 152142.0991 | 4173.2542 | 17384.1824 | 134757.9167 | 22429.6454 | 0.078869 | -173195.7761 | 173195.7761
C | Xist Rating 4129 | -51.65 | 995.243 | 150.287 | 35.6 | 2225.51 | 9098.68 | 14873.5 | 0.5 | 1.93 | 16.678 | 20.688 | 1 | 1 | 2080 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2214923.2489 | 153531.2344 | 4213.6729 | 17468.164 | 136063.0705 | 22261.9442 | 0.07925 | -171900.8323 | 171900.8323
C | Xist Rating 4130 | -51.33 | 1003.15 | 150.287 | 35.6 | 2223.69 | 9103.99 | 14790.9 | 0.5 | 1.91 | 16.675 | 20.484 | 1 | 1 | 2090 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2230694.6235 | 154926.6597 | 4254.2864 | 17552.1455 | 137374.5142 | 22053.6879 | 0.079631 | -170292.7326 | 170292.7326
C | Xist Rating 4131 | -51 | 1011.06 | 150.287 | 35.6 | 2221.8 | 9108.08 | 14709.2 | 0.49 | 1.9 | 16.673 | 20.285 | 1 | 1 | 2100 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2246373.108 | 156328.3749 | 4295.0947 | 17636.1271 | 138692.2478 | 21834.9753 | 0.080012 | -168603.8914 | 168603.8914
C | Xist Rating 4132 | -50.71 | 1018.05 | 150.287 | 35.6 | 2220.33 | 9114.66 | 14638.7 | 0.48 | 1.89 | 16.676 | 20.116 | 1 | 1 | 2110 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2260406.9565 | 157736.3799 | 4336.0977 | 17720.1086 | 140016.2713 | 21647.498 | 0.080393 | -167156.2415 | 167156.2415
C | Xist Rating 4133 | -49.69 | 1044.27 | 150.287 | 35.6 | 2210.27 | 9071.74 | 14359 | 0.48 | 1.84 | 16.712 | 19.401 | 1 | 1 | 2120 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2308118.6529 | 159150.6749 | 4377.2956 | 17804.0902 | 141346.5847 | 20910.2017 | 0.080774 | -161463.0349 | 161463.0349
C | Xist Rating 4134 | -49.3 | 1054.05 | 150.287 | 35.6 | 2207.35 | 9066.57 | 14263.7 | 0.48 | 1.83 | 16.708 | 19.174 | 1 | 1 | 2130 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2326657.2675 | 160571.2597 | 4418.6882 | 17888.0717 | 142683.188 | 20677.875 | 0.081155 | -159669.0695 | 159669.0695
C | Xist Rating 4135 | -48.92 | 1063.85 | 150.287 | 35.6 | 2204.45 | 9061.47 | 14169.8 | 0.47 | 1.81 | 16.701 | 18.953 | 1 | 1 | 2140 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2345204.1325 | 161998.1345 | 4460.2756 | 17972.0533 | 144026.0812 | 20435.619 | 0.081536 | -157798.4329 | 157798.4329
C | Xist Rating 4136 | -48.68 | 1069.09 | 150.287 | 35.6 | 2204.51 | 9084.38 | 14123.6 | 0.47 | 1.8 | 16.7 | 18.852 | 1 | 1 | 2150 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2356819.5959 | 163431.2991 | 4502.0578 | 18056.0349 | 145375.2643 | 20334.2039 | 0.081917 | -157015.3321 | 157015.3321
C | Xist Rating 4137 | -48.37 | 1076.03 | 150.287 | 35.6 | 2204.36 | 9112.7 | 14059.1 | 0.46 | 1.79 | 16.702 | 18.705 | 1 | 1 | 2160 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2371957.4908 | 164870.7537 | 4544.0348 | 18140.0164 | 146730.7373 | 20168.9828 | 0.082298 | -155739.539 | 155739.539
C | Xist Rating 4138 | -47.31 | 1104.37 | 150.287 | 35.6 | 2192.56 | 9045.04 | 13786.1 | 0.46 | 1.75 | 16.735 | 18.046 | 1 | 1 | 2170 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2421397.4872 | 166316.4981 | 4586.2066 | 18223.998 | 148092.5001 | 19489.5327 | 0.082679 | -150493.0057 | 150493.0057
C | Xist Rating 4139 | -46.9 | 1113.92 | 150.287 | 35.6 | 2191.73 | 9074.32 | 13699.1 | 0.46 | 1.74 | 16.736 | 17.847 | 1 | 1 | 2180 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2441411.8816 | 167768.5325 | 4628.5732 | 18307.9795 | 149460.5529 | 19286.3671 | 0.08306 | -148924.2148 | 148924.2148
C | Xist Rating 4140 | -46.64 | 1121.1 | 150.287 | 35.6 | 2189.15 | 9060.56 | 13639 | 0.45 | 1.73 | 16.732 | 17.719 | 1 | 1 | 2190 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2454256.065 | 169226.8567 | 4671.1346 | 18391.9611 | 150834.8956 | 19140.2844 | 0.083441 | -147796.2029 | 147796.2029
C | Xist Rating 4141 | -46.39 | 1128.68 | 150.287 | 35.6 | 2185.17 | 9022.84 | 13579.4 | 0.44 | 1.72 | 16.725 | 17.596 | 1 | 1 | 2200 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2466357.6756 | 170691.4708 | 4713.8907 | 18475.9426 | 152215.5282 | 18999.1203 | 0.083822 | -146706.1708 | 146706.1708
C | Xist Rating 4142 | -46.02 | 1138.49 | 150.287 | 35.6 | 2182.36 | 9017.71 | 13495.4 | 0.44 | 1.7 | 16.723 | 17.411 | 1 | 1 | 2210 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2484595.0364 | 172162.3749 | 4756.8417 | 18559.9242 | 153602.4507 | 18810.2096 | 0.084203 | -145247.4522 | 145247.4522
C | Xist Rating 4143 | -44.93 | 1166.69 | 150.287 | 35.6 | 2173.27 | 8992.34 | 13246.1 | 0.44 | 1.66 | 16.761 | 16.838 | 1 | 1 | 2220 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2535532.3763 | 173639.5688 | 4799.9874 | 18643.9058 | 154995.663 | 18220.112 | 0.084584 | -140690.8755 | 140690.8755
C | Xist Rating 4144 | -44.61 | 1174.57 | 150.287 | 35.6 | 2171.99 | 9004.39 | 13182.5 | 0.43 | 1.65 | 16.764 | 16.703 | 1 | 1 | 2230 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2551154.2943 | 175123.0526 | 4843.3279 | 18727.8873 | 156395.1653 | 18066.5953 | 0.084965 | -139505.4602 | 139505.4602
C | Xist Rating 4145 | -44.28 | 1183.81 | 150.287 | 35.6 | 2168.63 | 8984.78 | 13111.7 | 0.43 | 1.64 | 16.759 | 16.558 | 1 | 1 | 2240 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2567245.8803 | 176612.8264 | 4886.8633 | 18811.8689 | 157800.9575 | 17919.0284 | 0.085346 | -138365.9873 | 138365.9873
C | Xist Rating 4146 | -43.91 | 1193.93 | 150.287 | 35.6 | 2165.04 | 8965.33 | 13034 | 0.42 | 1.63 | 16.755 | 16.397 | 1 | 1 | 2250 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2584906.2072 | 178108.89 | 4930.5934 | 18895.8504 | 159213.0396 | 17737.9886 | 0.085727 | -136968.0458 | 136968.0458
C | Xist Rating 4147 | -43.69 | 1199.14 | 150.287 | 35.6 | 2164.93 | 8984.4 | 12995.6 | 0.42 | 1.62 | 16.755 | 16.323 | 1 | 1 | 2260 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2596054.1602 | 179611.2435 | 4974.5182 | 18979.832 | 160631.4115 | 17664.294 | 0.086108 | -136398.9962 | 136398.9962
C | Xist Rating 4148 | -42.55 | 1229.56 | 150.287 | 35.6 | 2154.82 | 8946.33 | 12751.9 | 0.42 | 1.59 | 16.792 | 15.792 | 1 | 1 | 2270 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2649480.4792 | 181119.8869 | 5018.6379 | 19063.8135 | 162056.0734 | 17117.5869 | 0.086489 | -132177.469 | 132177.469
C | Xist Rating 4149 | -42.23 | 1238.75 | 150.287 | 35.6 | 2151.61 | 8928.26 | 12686.1 | 0.41 | 1.58 | 16.787 | 15.663 | 1 | 1 | 2280 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2665306.8875 | 182634.8203 | 5062.9524 | 19147.7951 | 163487.0252 | 16969.411 | 0.08687 | -131033.2936 | 131033.2936
C | Xist Rating 4150 | -41.81 | 1249.53 | 150.287 | 35.6 | 2149.29 | 8933.78 | 12606.9 | 0.41 | 1.56 | 16.785 | 15.502 | 1 | 1 | 2290 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2685602.3337 | 184156.0435 | 5107.4617 | 19231.7767 | 164924.2668 | 16805.2137 | 0.087251 | -129765.4057 | 129765.4057
C | Xist Rating 4151 | -41.53 | 1256.87 | 150.287 | 35.6 | 2147.88 | 8938.31 | 12557 | 0.4 | 1.56 | 16.783 | 15.408 | 1 | 1 | 2300 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2699605.9356 | 185683.5566 | 5152.1657 | 19315.7582 | 166367.7984 | 16693.2924 | 0.087632 | -128901.1788 | 128901.1788
| Xist Rating 4152 | -41.28 | 1264.47 | 150.287 | 35.6 | 2144.7 | 8912.15 | 12507.5 | 0.4 | 1.55 | 16.779 | 15.317 | 1 | 1 | 2310 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2711908.809 | 187217.3596 | 5197.0645 | 19399.7398 | 167817.6198 | 16601.6325 | 0.088013 | -128193.4057 | 128193.4057
| Xist Rating 4153 | -40.11 | 1295.65 | 150.288 | 35.6 | 2135.63 | 8892.07 | 12277.1 | 0.4 | 1.51 | 16.815 | 14.838 | 1 | 1 | 2320 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2767029.0095 | 188757.4525 | 5242.1582 | 19483.7213 | 169273.7312 | 16108.6977 | 0.088394 | -124387.0939 | 124387.0939
| Xist Rating 4154 | -39.78 | 1304.88 | 150.287 | 35.6 | 2133.04 | 8883.6 | 12216.8 | 0.39 | 1.5 | 16.808 | 14.725 | 1 | 1 | 2330 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2783361.2352 | 190303.8353 | 5287.4466 | 19567.7029 | 170736.1324 | 15976.5154 | 0.088775 | -123366.4167 | 123366.4167
| Xist Rating 4155 | -39.44 | 1314.08 | 150.287 | 35.6 | 2130.79 | 8881.05 | 12157.1 | 0.39 | 1.49 | 16.804 | 14.614 | 1 | 1 | 2340 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2800028.5232 | 191856.508 | 5332.9298 | 19651.6844 | 172204.8236 | 15864.0167 | 0.089156 | -122497.732 | 122497.732
| Xist Rating 4156 | -39.15 | 1322.45 | 150.287 | 35.6 | 2128.11 | 8866.73 | 12104.7 | 0.38 | 1.49 | 16.799 | 14.519 | 1 | 1 | 2350 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2814319.0695 | 193415.4706 | 5378.6078 | 19735.666 | 173679.8046 | 15750.3958 | 0.089537 | -121620.3817 | 121620.3817
| Xist Rating 4157 | -38.8 | 1332.62 | 150.287 | 35.6 | 2124.99 | 8852.92 | 12039.8 | 0.38 | 1.48 | 16.794 | 14.398 | 1 | 1 | 2360 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2831804.1738 | 194980.7231 | 5424.4805 | 19819.6476 | 175161.0756 | 15627.398 | 0.089918 | -120670.6248 | 120670.6248
| Xist Rating 4158 | -37.75 | 1361.25 | 150.288 | 35.6 | 2116.74 | 8831.14 | 11846.7 | 0.38 | 1.45 | 16.828 | 14.017 | 1 | 1 | 2370 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2881412.325 | 196552.2655 | 5470.5481 | 19903.6291 | 176648.6364 | 15235.9632 | 0.090299 | -117648.0693 | 117648.0693
| Xist Rating 4159 | -37.43 | 1370.69 | 150.287 | 35.6 | 2113.56 | 8811.62 | 11791.1 | 0.37 | 1.44 | 16.819 | 13.919 | 1 | 1 | 2380 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2897035.5564 | 198130.0978 | 5516.8105 | 19987.6107 | 178142.4872 | 15118.7489 | 0.09068 | -116742.9717 | 116742.9717
| Xist Rating 4160 | -37.08 | 1380.41 | 150.287 | 35.6 | 2111.27 | 8811.05 | 11730 | 0.37 | 1.43 | 16.813 | 13.806 | 1 | 1 | 2390 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 2914418.2207 | 199714.22 | 5563.2676 | 20071.5922 | 179642.6278 | 15003.9502 | 0.091061 | -115856.5266 | 115856.5266
C | Xist Rating 4161 | -32.59 | 1582.39 | 150.288 | 35.6 | 1976.45 | 7422.97 | 10538.7 | 0.4 | 1.25 | 16.764 | 11.623 | 1 | 1 | 2400 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3127514.7155 | 201304.6321 | 5609.9196 | 20155.5738 | 181149.0583 | 12791.8499 | 0.091442 | -98775.2745 | 98775.2745
C | Xist Rating 4163 | -30.44 | 1585.24 | 150.288 | 35.6 | 2035.81 | 8336.69 | 10537.4 | 0.39 | 1.25 | 16.86 | 11.637 | 1 | 1 | 2420 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3227247.4444 | 204504.326 | 5703.8078 | 20323.5369 | 184180.7891 | 12798.2769 | 0.092204 | -98824.9018 | 98824.9018
C | Xist Rating 4164 | -29.72 | 1586.59 | 150.288 | 35.6 | 2054.17 | 8653.26 | 10537.8 | 0.39 | 1.25 | 16.847 | 11.646 | 1 | 1 | 2430 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3259125.5803 | 206113.6078 | 5751.0441 | 20407.5185 | 185706.0893 | 12810.0186 | 0.092585 | -98915.5677 | 98915.5677
C | Xist Rating 4165 | -29.72 | 1587.96 | 150.288 | 35.6 | 2053.2 | 8636.02 | 10537.8 | 0.38 | 1.25 | 16.839 | 11.657 | 1 | 1 | 2440 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3260399.472 | 207729.1795 | 5798.4752 | 20491.5 | 187237.6795 | 12805.6287 | 0.092966 | -98881.6708 | 98881.6708
C | Xist Rating 4166 | -29.7 | 1589.29 | 150.288 | 35.6 | 2052.8 | 8628.9 | 10537.8 | 0.38 | 1.25 | 16.834 | 11.667 | 1 | 1 | 2450 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3262494.512 | 209351.0411 | 5846.1011 | 20575.4816 | 188775.5595 | 12818.6733 | 0.093347 | -98982.3975 | 98982.3975
C | Xist Rating 4167 | -29.7 | 1590.76 | 150.288 | 35.6 | 2051.31 | 8602.65 | 10537.9 | 0.37 | 1.25 | 16.831 | 11.679 | 1 | 1 | 2460 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3263141.8956 | 210979.1926 | 5893.9217 | 20659.4631 | 190319.7294 | 12815.3177 | 0.093728 | -98956.4861 | 98956.4861
C | Xist Rating 4168 | -29.68 | 1592.12 | 150.288 | 35.6 | 2051.05 | 8598.08 | 10537.9 | 0.36 | 1.25 | 16.867 | 11.689 | 1 | 1 | 2470 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3265517.726 | 212613.6339 | 5941.9372 | 20743.4447 | 191870.1892 | 12811.2942 | 0.094109 | -98925.4182 | 98925.4182
C | Xist Rating 4169 | -29.66 | 1593.46 | 150.288 | 35.6 | 2050.58 | 8589.79 | 10537.9 | 0.36 | 1.25 | 16.864 | 11.7 | 1 | 1 | 2480 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3267517.2068 | 214254.3652 | 5990.1474 | 20827.4263 | 193426.939 | 12825.3195 | 0.09449 | -99033.7173 | 99033.7173
C | Xist Rating 4170 | -29.64 | 1594.86 | 150.288 | 35.6 | 2050.13 | 8581.86 | 10537.9 | 0.35 | 1.25 | 16.857 | 11.71 | 1 | 1 | 2490 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3269670.3318 | 215901.3864 | 6038.5525 | 20911.4078 | 194989.9786 | 12819.3298 | 0.094871 | -98987.467 | 98987.467
C | Xist Rating 4171 | -29.61 | 1595.85 | 150.288 | 35.6 | 2050.45 | 8587.49 | 10537.8 | 0.35 | 1.25 | 16.853 | 11.719 | 1 | 1 | 2500 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3272210.6325 | 217554.6975 | 6087.1523 | 20995.3894 | 196559.3081 | 12831.1641 | 0.095252 | -99078.8478 | 99078.8478
C | Xist Rating 4172 | -29.6 | 1597.7 | 150.288 | 35.6 | 2049.16 | 8564.91 | 10537.8 | 0.34 | 1.25 | 16.847 | 11.732 | 1 | 1 | 2510 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3273942.932 | 219214.2984 | 6135.9469 | 21079.3709 | 198134.9275 | 12828.1177 | 0.095633 | -99055.3249 | 99055.3249
C | Xist Rating 4173 | -29.6 | 1599.15 | 150.288 | 35.6 | 2047.98 | 8544.37 | 10537.8 | 0.34 | 1.25 | 16.885 | 11.743 | 1 | 1 | 2520 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3275027.217 | 220880.1893 | 6184.9363 | 21163.3525 | 199716.8368 | 12843.5682 | 0.096014 | -99174.6291 | 99174.6291
C | Xist Rating 4174 | -29.57 | 1600.49 | 150.288 | 35.6 | 2047.7 | 8539.48 | 10537.8 | 0.33 | 1.25 | 16.879 | 11.753 | 1 | 1 | 2530 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3277323.373 | 222552.3701 | 6234.1205 | 21247.334 | 201305.036 | 12837.1533 | 0.096395 | -99125.0951 | 99125.0951
C | Xist Rating 4175 | -29.55 | 1601.64 | 150.288 | 35.6 | 2047.79 | 8541.09 | 10537.8 | 0.33 | 1.25 | 16.873 | 11.762 | 1 | 1 | 2540 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3279822.3756 | 224230.8407 | 6283.4995 | 21331.3156 | 202899.5251 | 12848.7711 | 0.096776 | -99214.8048 | 99214.8048
C | Xist Rating 4176 | -29.52 | 1603.19 | 150.288 | 35.6 | 2047.29 | 8532.46 | 10537.8 | 0.32 | 1.25 | 16.867 | 11.773 | 1 | 1 | 2550 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3282194.8551 | 225915.6013 | 6333.0732 | 21415.2972 | 204500.3042 | 12843.1847 | 0.097157 | -99171.6679 | 99171.6679
C | Xist Rating 4177 | -29.49 | 1604.63 | 150.288 | 35.6 | 2047.33 | 8533.15 | 10537.8 | 0.32 | 1.25 | 16.875 | 11.784 | 1 | 1 | 2560 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3285207.1379 | 227606.6518 | 6382.8418 | 21499.2787 | 206107.3731 | 12857.3213 | 0.097538 | -99280.8272 | 99280.8272
C | Xist Rating 4178 | -29.46 | 1606.02 | 150.288 | 35.6 | 2047.2 | 8530.88 | 10537.8 | 0.31 | 1.25 | 16.875 | 11.794 | 1 | 1 | 2570 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3287844.144 | 229303.9921 | 6432.8051 | 21583.2603 | 207720.7319 | 12850.687 | 0.097919 | -99229.5983 | 99229.5983
C | Xist Rating 4179 | -29.43 | 1607.39 | 150.288 | 35.6 | 2047.06 | 8528.49 | 10537.8 | 0.31 | 1.25 | 16.91 | 11.804 | 1 | 1 | 2580 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3290423.7734 | 231007.6224 | 6482.9633 | 21667.2418 | 209340.3806 | 12864.6716 | 0.0983 | -99337.5841 | 99337.5841
C | Xist Rating 4180 | -29.41 | 1608.75 | 150.288 | 35.6 | 2046.83 | 8524.48 | 10537.7 | 0.3 | 1.25 | 16.903 | 11.814 | 1 | 1 | 2590 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3292837.7625 | 232717.5425 | 6533.3162 | 21751.2234 | 210966.3191 | 12857.5307 | 0.098681 | -99282.4442 | 99282.4442
C | Xist Rating 4181 | -29.38 | 1609.93 | 150.288 | 35.6 | 2047.1 | 8529.18 | 10537.7 | 0.3 | 1.25 | 16.9 | 11.824 | 1 | 1 | 2600 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3295687.703 | 234433.7526 | 6583.8639 | 21835.2049 | 212598.5476 | 12870.0838 | 0.099062 | -99379.3759 | 99379.3759
C | Xist Rating 4182 | -29.36 | 1611.61 | 150.288 | 35.6 | 2046.25 | 8514.46 | 10537.6 | 0.29 | 1.25 | 16.903 | 11.835 | 1 | 1 | 2610 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3297756.9625 | 236156.2525 | 6634.6064 | 21919.1865 | 214237.066 | 12864.11 | 0.099443 | -99333.2476 | 99333.2476
C | Xist Rating 4183 | -29.38 | 1613.01 | 150.288 | 35.6 | 2044.86 | 8490.55 | 10537.6 | 0.29 | 1.25 | 16.901 | 11.846 | 1 | 1 | 2620 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3298379.6286 | 237885.0424 | 6685.5437 | 22003.1681 | 215881.8743 | 12877.6626 | 0.099824 | -99437.8973 | 99437.8973
C | Xist Rating 4184 | -29.35 | 1614.44 | 150.288 | 35.6 | 2044.36 | 8481.87 | 10537.6 | 0.29 | 1.25 | 16.94 | 11.856 | 1 | 1 | 2630 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3300496.5584 | 239620.1221 | 6736.6758 | 22087.1496 | 217532.9725 | 12891.5779 | 0.10021 | -99545.3475 | 99545.3475
C | Xist Rating 4185 | -29.3 | 1615.68 | 150.288 | 35.6 | 2044.88 | 8490.82 | 10537.7 | 0.28 | 1.25 | 16.936 | 11.865 | 1 | 1 | 2640 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3303871.7184 | 241361.4918 | 6788.0027 | 22171.1312 | 219190.3606 | 12882.9476 | 0.10059 | -99478.7066 | 99478.7066
C | Xist Rating 4186 | -29.3 | 1617.19 | 150.288 | 35.6 | 2043.58 | 8468.45 | 10537.7 | 0.28 | 1.25 | 16.932 | 11.876 | 1 | 1 | 2650 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3304857.1402 | 243109.1513 | 6839.5243 | 22255.1127 | 220854.0386 | 12896.3637 | 0.10097 | -99582.3019 | 99582.3019
C | Xist Rating 4187 | -29.24 | 1618.53 | 150.288 | 35.6 | 2044.25 | 8479.94 | 10537.7 | 0.28 | 1.25 | 16.93 | 11.886 | 1 | 1 | 2660 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3308679.9525 | 244863.1008 | 6891.2408 | 22339.0943 | 222524.0065 | 12908.807 | 0.10135 | -99678.386 | 99678.386
C | Xist Rating 4188 | -29.22 | 1619.91 | 150.288 | 35.6 | 2044.03 | 8476.15 | 10537.6 | 0.27 | 1.25 | 16.928 | 11.896 | 1 | 1 | 2670 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3311144.6373 | 246623.3401 | 6943.152 | 22423.0758 | 224200.2642 | 12900.9901 | 0.10173 | -99618.026 | 99618.026
C | Xist Rating 4189 | -29.19 | 1621.33 | 150.288 | 35.6 | 2043.92 | 8474.28 | 10537.6 | 0.27 | 1.25 | 16.963 | 11.906 | 1 | 1 | 2680 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3313868.8136 | 248389.8693 | 6995.258 | 22507.0574 | 225882.8119 | 12914.5591 | 0.10211 | -99722.8018 | 99722.8018
C | Xist Rating 4190 | -29.17 | 1622.71 | 150.288 | 35.6 | 2043.31 | 8463.81 | 10537.6 | 0.26 | 1.25 | 16.957 | 11.915 | 1 | 1 | 2690 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3315699.5701 | 250162.6885 | 7047.5588 | 22591.039 | 227571.6495 | 12905.3167 | 0.10249 | -99651.4349 | 99651.4349
C | Xist Rating 4191 | -29.1 | 1623.91 | 150.288 | 35.6 | 2044.71 | 8487.92 | 10537.5 | 0.26 | 1.25 | 16.954 | 11.924 | 1 | 1 | 2700 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3320425.0161 | 251941.7975 | 7100.0544 | 22675.0205 | 229266.777 | 12916.545 | 0.10287 | -99738.137 | 99738.137
C | Xist Rating 4192 | -29.1 | 1625.56 | 150.288 | 35.6 | 2043.4 | 8465.41 | 10537.6 | 0.26 | 1.25 | 16.946 | 11.936 | 1 | 1 | 2710 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3321669.304 | 253727.1964 | 7152.7448 | 22759.0021 | 230968.1943 | 12930.7302 | 0.10325 | -99847.6714 | 99847.6714
C | Xist Rating 4193 | -29.09 | 1626.91 | 150.288 | 35.6 | 2042.69 | 8453.19 | 10537.6 | 0.26 | 1.25 | 16.942 | 11.945 | 1 | 1 | 2720 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3323272.7879 | 255518.8852 | 7205.63 | 22842.9836 | 232675.9016 | 12941.9249 | 0.10363 | -99934.1134 | 99934.1134
C | Xist Rating 4194 | -29.09 | 1628.23 | 150.288 | 35.6 | 2041.68 | 8436.02 | 10537.6 | 0.25 | 1.25 | 16.974 | 11.954 | 1 | 1 | 2730 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3324324.6264 | 257316.864 | 7258.71 | 22926.9652 | 234389.8988 | 12933.4927 | 0.10402 | -99869.0022 | 99869.0022
C | Xist Rating 4195 | -29.07 | 1629.51 | 150.288 | 35.6 | 2041.48 | 8432.45 | 10537.6 | 0.25 | 1.25 | 16.972 | 11.964 | 1 | 1 | 2740 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3326612.0748 | 259121.1326 | 7311.9847 | 23010.9467 | 236110.1858 | 12945.7184 | 0.1044 | -99963.4059 | 99963.4059
C | Xist Rating 4196 | -29.06 | 1631.06 | 150.288 | 35.6 | 2040.56 | 8416.83 | 10537.6 | 0.25 | 1.25 | 16.969 | 11.974 | 1 | 1 | 2750 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3328275.7936 | 260931.6911 | 7365.4543 | 23094.9283 | 237836.7628 | 12957.9128 | 0.10478 | -100057.5682 | 100057.5682
C | Xist Rating 4197 | -29.05 | 1632.49 | 150.288 | 35.6 | 2039.6 | 8400.65 | 10537.6 | 0.24 | 1.25 | 16.964 | 11.984 | 1 | 1 | 2760 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3329626.604 | 262748.5395 | 7419.1186 | 23178.9099 | 239569.6297 | 12949.0576 | 0.10516 | -99989.1901 | 99989.1901
C | Xist Rating 4198 | -29.02 | 1633.72 | 150.288 | 35.6 | 2039.74 | 8402.85 | 10537.6 | 0.24 | 1.25 | 16.965 | 11.993 | 1 | 1 | 2770 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3332364.0328 | 264571.6778 | 7472.9777 | 23262.8914 | 241308.7864 | 12960.2588 | 0.10554 | -100075.6832 | 100075.6832
C | Xist Rating 4199 | -28.99 | 1635.27 | 150.288 | 35.6 | 2039.41 | 8397.22 | 10537.6 | 0.24 | 1.25 | 17.007 | 12.003 | 1 | 1 | 2780 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3334985.9907 | 266401.1061 | 7527.0316 | 23346.873 | 243054.2331 | 12973.725 | 0.10592 | -100179.6654 | 100179.6654
C | Xist Rating 4200 | -29 | 1636.68 | 150.288 | 35.6 | 2038.11 | 8375.31 | 10537.6 | 0.23 | 1.25 | 16.999 | 12.013 | 1 | 1 | 2790 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3335733.8748 | 268236.8242 | 7581.2803 | 23430.8545 | 244805.9696 | 12964.4404 | 0.1063 | -100107.972 | 100107.972
C | Xist Rating 4201 | -28.86 | 1637.65 | 150.288 | 35.6 | 2041.49 | 8432.66 | 10537.7 | 0.23 | 1.25 | 17.012 | 12.021 | 1 | 1 | 2800 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3343246.0985 | 270078.8322 | 7635.7238 | 23514.8361 | 246563.9961 | 12974.8762 | 0.10668 | -100188.5545 | 100188.5545
C | Xist Rating 4202 | -28.92 | 1639.4 | 150.288 | 35.6 | 2038.25 | 8377.63 | 10537.7 | 0.23 | 1.25 | 17 | 12.032 | 1 | 1 | 2810 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3341507.05 | 271927.1301 | 7690.3621 | 23598.8176 | 248328.3124 | 12987.7059 | 0.10706 | -100287.6222 | 100287.6222
C | Xist Rating 4203 | -28.81 | 1640.87 | 150.288 | 35.6 | 2040.26 | 8411.71 | 10537.8 | 0.23 | 1.25 | 17.015 | 12.042 | 1 | 1 | 2820 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3347801.4262 | 273781.7179 | 7745.1952 | 23682.7992 | 250098.9187 | 13000.2796 | 0.10744 | -100384.7132 | 100384.7132
C | Xist Rating 4204 | -28.48 | 1642.24 | 150.289 | 35.6 | 2048.95 | 8561.21 | 10538 | 0.22 | 1.25 | 17.106 | 12.052 | 1 | 1 | 2830 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3364867.648 | 275642.5956 | 7800.223 | 23766.7808 | 251875.8148 | 12993.3742 | 0.10783 | -100331.3917 | 100331.3917
C | Xist Rating 4205 | -28.74 | 1643.56 | 150.288 | 35.6 | 2040.3 | 8412.25 | 10537.8 | 0.22 | 1.25 | 17.057 | 12.06 | 1 | 1 | 2840 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3353355.468 | 277509.7632 | 7855.4457 | 23850.7623 | 253659.0009 | 13001.9968 | 0.10821 | -100397.9729 | 100397.9729
C | Xist Rating 4206 | -28.37 | 1645.01 | 150.288 | 35.6 | 2050.1 | 8581.17 | 10538 | 0.22 | 1.25 | 17.114 | 12.071 | 1 | 1 | 2850 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 17 | E | Rod | 3372435.001 | 279383.2207 | 7910.8631 | 23934.7439 | 255448.4768 | 13016.7043 | 0.10859 | -100511.5405 | 100511.5405
C | Xist Rating 4207 | -27.9 | 1646.41 | 150.288 | 35.6 | 2062.92 | 8810.32 | 10538.1 | 0.21 | 1.25 | 17.19 | 12.081 | 1 | 1 | 2860 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3396412.1172 | 281262.9681 | 7966.4753 | 24018.7254 | 257244.2426 | 13008.8832 | 0.10897 | -100451.1475 | 100451.1475
C | Xist Rating 4208 | -27.44 | 1647.6 | 150.288 | 35.6 | 2075.47 | 9043.83 | 10538.1 | 0.21 | 1.25 | 17.242 | 12.091 | 1 | 1 | 2870 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3419544.372 | 283149.0054 | 8022.2824 | 24102.707 | 259046.2984 | 13022.2911 | 0.10935 | -100554.68 | 100554.68
C | Xist Rating 4209 | -27.25 | 1649.11 | 150.289 | 35.6 | 2079.77 | 9126.21 | 10538.1 | 0.21 | 1.25 | 17.299 | 12.101 | 1 | 1 | 2880 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3429769.5047 | 285041.3326 | 8078.2842 | 24186.6886 | 260854.644 | 13035.8444 | 0.10973 | -100659.3348 | 100659.3348
C | Xist Rating 4210 | -27.12 | 1650.45 | 150.289 | 35.6 | 2082.81 | 9185.02 | 10538.1 | 0.2 | 1.25 | 17.307 | 12.11 | 1 | 1 | 2890 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3437573.7645 | 286939.9497 | 8134.4807 | 24270.6701 | 262669.2796 | 13024.6168 | 0.11011 | -100572.6386 | 100572.6386
C | Xist Rating 4211 | -26.96 | 1651.84 | 150.289 | 35.6 | 2086.2 | 9251.29 | 10538.1 | 0.2 | 1.25 | 17.319 | 12.12 | 1 | 1 | 2900 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3446068.608 | 288844.8566 | 8190.8721 | 24354.6517 | 264490.205 | 13036.8653 | 0.11049 | -100667.2185 | 100667.2185
C | Xist Rating 4212 | -26.85 | 1653.38 | 150.289 | 35.6 | 2088.29 | 9292.49 | 10538.1 | 0.2 | 1.25 | 17.328 | 12.13 | 1 | 1 | 2910 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3452736.9202 | 290756.0535 | 8247.4583 | 24438.6332 | 266317.4203 | 13049.0378 | 0.11087 | -100761.2106 | 100761.2106
C | Xist Rating 4213 | -26.71 | 1654.77 | 150.289 | 35.6 | 2091.11 | 9348.72 | 10538.1 | 0.2 | 1.25 | 17.336 | 12.139 | 1 | 1 | 2920 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3460306.0947 | 292673.5403 | 8304.2393 | 24522.6148 | 268150.9255 | 13060.1471 | 0.11125 | -100846.9941 | 100846.9941
C | Xist Rating 4214 | -26.58 | 1656.16 | 150.289 | 35.6 | 2093.82 | 9403.11 | 10538.1 | 0.19 | 1.25 | 17.386 | 12.149 | 1 | 1 | 2930 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3467700.9312 | 294597.317 | 8361.215 | 24606.5963 | 269990.7207 | 13050.5655 | 0.11164 | -100773.0074 | 100773.0074
C | Xist Rating 4215 | -26.24 | 1657.52 | 150.289 | 35.5 | 2102.99 | 9591.01 | 10537.9 | 0.19 | 1.25 | 17.404 | 12.158 | 1 | 1 | 2940 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3485747.9848 | 296527.3836 | 8418.3855 | 24690.5779 | 271836.8057 | 13061.8434 | 0.11202 | -100860.0924 | 100860.0924
C | Xist Rating 4216 | -26.21 | 1658.93 | 150.289 | 35.5 | 2102.82 | 9587.52 | 10537.9 | 0.19 | 1.25 | 17.4 | 12.167 | 1 | 1 | 2950 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3488431.1826 | 298463.7401 | 8475.7509 | 24774.5595 | 273689.1806 | 13072.5716 | 0.1124 | -100942.9329 | 100942.9329
C | Xist Rating 4217 | -26.2 | 1660.3 | 150.289 | 35.5 | 2102.1 | 9572.44 | 10537.9 | 0.19 | 1.25 | 17.397 | 12.176 | 1 | 1 | 2960 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3490116.63 | 300406.3864 | 8533.311 | 24858.541 | 275547.8454 | 13083.3244 | 0.11278 | -101025.9629 | 101025.9629
C | Xist Rating 4218 | -26.18 | 1661.68 | 150.289 | 35.5 | 2101.44 | 9558.77 | 10537.9 | 0.18 | 1.25 | 17.394 | 12.185 | 1 | 1 | 2970 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3491920.8192 | 302355.3227 | 8591.0659 | 24942.5226 | 277412.8001 | 13070.9201 | 0.11316 | -100930.1806 | 100930.1806
C | Xist Rating 4219 | -26.18 | 1662.91 | 150.289 | 35.5 | 2100.82 | 9546.15 | 10537.9 | 0.18 | 1.25 | 17.43 | 12.194 | 1 | 1 | 2980 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3493474.5862 | 304310.5489 | 8649.0156 | 25026.5041 | 279284.0447 | 13082.5356 | 0.11354 | -101019.8724 | 101019.8724
C | Xist Rating 4220 | -26.15 | 1664.47 | 150.289 | 35.5 | 2100.17 | 9532.59 | 10537.9 | 0.18 | 1.25 | 17.425 | 12.204 | 1 | 1 | 2990 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3495669.9599 | 306272.0649 | 8707.16 | 25110.4857 | 281161.5793 | 13094.2063 | 0.11392 | -101109.9903 | 101109.9903
C | Xist Rating 4221 | -26.14 | 1665.9 | 150.289 | 35.5 | 2099.52 | 9519.23 | 10537.9 | 0.18 | 1.25 | 17.421 | 12.213 | 1 | 1 | 3000 | 152.4 | 2 | 3 | 19.05 | 1.3333 | 16 | E | Rod | 3497590.368 | 308239.8709 | 8765.4993 | 25194.4672 | 283045.4037 | 13104.8619 | 0.1143 | -101192.27 | 101192.27
C | Xist Rating 4222 | -91.07 | 163.197 | 150.292 | 35.8 | 2390.71 | 7319.89 | 58745.9 | 2.45 | 10.95 | 18.602 | 449.587 | 1 | 1 | 1000 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 390156.6999 | 41175.8999 | 973.9444 | 8678.0943 | 32497.8056 | 468938.2676 | 0.038101 | -3621017.0006 | 3621017.0006
C | Xist Rating 4223 | -90.99 | 164.904 | 150.292 | 35.8 | 2387.5 | 7298.07 | 58284.2 | 2.43 | 10.85 | 18.643 | 441.164 | 1 | 1 | 1010 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 393708.3 | 41915.8867 | 993.5206 | 8764.8752 | 33151.0115 | 460199.0914 | 0.038482 | -3553535.3986 | 3553535.3986
C | Xist Rating 4224 | -90.32 | 177.76 | 150.292 | 35.8 | 2380.94 | 7300.08 | 54967.7 | 2.44 | 10.07 | 18.696 | 382.311 | 1 | 1 | 1020 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 423235.8944 | 42662.3731 | 1013.2917 | 8851.6562 | 33810.717 | 399115.0871 | 0.038863 | -3081860.9089 | 3081860.9089
C | Xist Rating 4225 | -90.21 | 181.32 | 150.291 | 35.8 | 2361.56 | 7136.37 | 54178.5 | 2.36 | 9.89 | 18.301 | 369.54 | 1 | 1 | 1030 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 428198.0592 | 43415.3591 | 1033.2576 | 8938.4371 | 34476.922 | 385760.7783 | 0.039244 | -2978742.4759 | 2978742.4759
C | Xist Rating 4226 | -90.15 | 183.102 | 150.291 | 35.8 | 2355.49 | 7088.86 | 53793.7 | 2.32 | 9.8 | 18.203 | 363.432 | 1 | 1 | 1040 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 431294.93 | 44174.8446 | 1053.4182 | 9025.218 | 35149.6265 | 379392.2649 | 0.039625 | -2929566.5038 | 2929566.5038
C | Xist Rating 4227 | -89.96 | 186.541 | 150.291 | 35.8 | 2356.82 | 7116.21 | 53043.5 | 2.28 | 9.63 | 18.151 | 351.422 | 1 | 1 | 1050 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 439643.5596 | 44940.8297 | 1073.7737 | 9111.999 | 35828.8307 | 366898.979 | 0.040006 | -2833096.6619 | 2833096.6619
C | Xist Rating 4228 | -89.81 | 188.304 | 150.291 | 35.8 | 2371.11 | 7256.05 | 52676.8 | 2.22 | 9.54 | 18.146 | 345.749 | 1 | 1 | 1060 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 446489.4974 | 45713.3143 | 1094.3239 | 9198.7799 | 36514.5344 | 360973.8547 | 0.040387 | -2787344.4225 | 2787344.4225
C | Xist Rating 4229 | -89.15 | 202.168 | 150.291 | 35.8 | 2351.79 | 7140.54 | 49857.3 | 2.21 | 8.9 | 18.008 | 302.546 | 1 | 1 | 1070 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 475456.6807 | 46492.2985 | 1115.0689 | 9285.5609 | 37206.7376 | 316102.3339 | 0.040768 | -2440858.433 | 2440858.433
C | Xist Rating 4230 | -88.98 | 204.815 | 150.29 | 35.8 | 2358.92 | 7218.23 | 49380.8 | 2.15 | 8.79 | 17.93 | 295.796 | 1 | 1 | 1080 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 483142.1998 | 47277.7823 | 1136.0087 | 9372.3418 | 37905.4405 | 309049.8836 | 0.041149 | -2386401.281 | 2386401.281
C | Xist Rating 4231 | -88.78 | 208.334 | 150.29 | 35.8 | 2361.24 | 7255.55 | 48761.2 | 2.1 | 8.65 | 17.805 | 287.112 | 1 | 1 | 1090 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 491926.5742 | 48069.7656 | 1157.1433 | 9459.1228 | 38610.6428 | 299992.2156 | 0.04153 | -2316460.3695 | 2316460.3695
C | Xist Rating 4232 | -88.62 | 210.95 | 150.29 | 35.8 | 2367.41 | 7326 | 48308.9 | 2.06 | 8.55 | 17.802 | 280.848 | 1 | 1 | 1100 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 499405.1395 | 48868.2485 | 1178.4727 | 9545.9037 | 39322.3448 | 293468.4004 | 0.041911 | -2266085.1979 | 2266085.1979
C | Xist Rating 4233 | -88.53 | 212.899 | 150.289 | 35.8 | 2364.28 | 7303.91 | 48011.4 | 1.98 | 8.49 | 17.556 | 277.042 | 1 | 1 | 1110 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 503352.8477 | 49673.2309 | 1199.9969 | 9632.6846 | 40040.5463 | 289437.2191 | 0.042292 | -2234957.4847 | 2234957.4847
C | Xist Rating 4234 | -87.73 | 228.296 | 150.29 | 35.8 | 2359.77 | 7332.98 | 45448.7 | 2.02 | 7.92 | 17.774 | 242.41 | 1 | 1 | 1120 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 538726.0519 | 50484.7129 | 1221.7158 | 9719.4656 | 40765.2474 | 253544.886 | 0.042673 | -1957806.4021 | 1957806.4021
C | Xist Rating 4235 | -87.63 | 230.2 | 150.29 | 35.8 | 2360.51 | 7347.92 | 45189.7 | 1.96 | 7.86 | 17.616 | 239.336 | 1 | 1 | 1130 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 543389.402 | 51302.6945 | 1243.6296 | 9806.2465 | 41496.448 | 250298.9324 | 0.043054 | -1932742.0091 | 1932742.0091
C | Xist Rating 4236 | -87.47 | 233.79 | 150.289 | 35.8 | 2356.25 | 7322.38 | 44681.2 | 1.91 | 7.75 | 17.465 | 233.116 | 1 | 1 | 1140 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 550867.6875 | 52127.1756 | 1265.7381 | 9893.0275 | 42234.1482 | 243795.2023 | 0.043435 | -1882521.9288 | 1882521.9288
C | Xist Rating 4237 | -87.29 | 237.316 | 150.289 | 35.8 | 2356.21 | 7337.42 | 44186.8 | 1.87 | 7.64 | 17.323 | 227.098 | 1 | 1 | 1150 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 559166.3324 | 52958.1563 | 1288.0414 | 9979.8084 | 42978.3479 | 237510.7716 | 0.043816 | -1833995.2213 | 1833995.2213
C | Xist Rating 4238 | -87.1 | 240.922 | 150.289 | 35.8 | 2356.84 | 7359.08 | 43704.2 | 1.81 | 7.53 | 17.207 | 221.382 | 1 | 1 | 1160 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 567814.6065 | 53795.6366 | 1310.5395 | 10066.5894 | 43729.0472 | 231524.2737 | 0.044197 | -1787769.0715 | 1787769.0715
C | Xist Rating 4239 | -86.36 | 254.772 | 150.289 | 35.8 | 2356.34 | 7418.41 | 41832.8 | 1.83 | 7.13 | 17.333 | 199.152 | 1 | 1 | 1170 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 600329.4545 | 54639.6164 | 1333.2324 | 10153.3703 | 44486.2461 | 208482.5555 | 0.044578 | -1609847.0307 | 1609847.0307
C | Xist Rating 4240 | -86.26 | 255.817 | 150.289 | 35.8 | 2365.11 | 7510.08 | 41725.3 | 1.78 | 7.11 | 17.27 | 198.102 | 1 | 1 | 1180 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 605035.3449 | 55490.0958 | 1356.1201 | 10240.1512 | 45249.9445 | 207354.579 | 0.044959 | -1601137.0955 | 1601137.0955
C | Xist Rating 4241 | -85.95 | 262.856 | 150.288 | 35.8 | 2355.18 | 7442.05 | 40886.3 | 1.73 | 6.93 | 17.136 | 188.849 | 1 | 1 | 1190 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 619073.1941 | 56347.0747 | 1379.2026 | 10326.9322 | 46020.1425 | 197700.7067 | 0.04534 | -1526592.4523 | 1526592.4523
C | Xist Rating 4242 | -85.79 | 264.652 | 150.289 | 35.8 | 2366.97 | 7569.11 | 40682.5 | 1.7 | 6.88 | 17.161 | 186.695 | 1 | 1 | 1200 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 626423.3444 | 57210.5532 | 1402.4799 | 10413.7131 | 46796.8401 | 195451.7034 | 0.045721 | -1509226.245 | 1509226.245
C | Xist Rating 4243 | -85.63 | 268.327 | 150.288 | 35.8 | 2362.84 | 7543.06 | 40281.2 | 1.65 | 6.8 | 17.043 | 182.509 | 1 | 1 | 1210 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 634013.7687 | 58080.5313 | 1425.9519 | 10500.4941 | 47580.0372 | 191060.5271 | 0.046102 | -1475318.746 | 1475318.746
C | Xist Rating 4244 | -84.87 | 284.077 | 150.288 | 35.8 | 2350.44 | 7489.9 | 38538.1 | 1.65 | 6.43 | 17.062 | 164.152 | 1 | 1 | 1220 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 667705.9439 | 58957.0089 | 1449.6188 | 10587.275 | 48369.7339 | 172011.1312 | 0.046483 | -1328224.36 | 1328224.36
C | Xist Rating 4245 | -84.65 | 287.602 | 150.288 | 35.8 | 2356.92 | 7571.9 | 38183.4 | 1.63 | 6.35 | 17.067 | 160.648 | 1 | 1 | 1230 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 677854.9058 | 59839.9861 | 1473.4804 | 10674.056 | 49165.9301 | 168366.4872 | 0.046864 | -1300081.3852 | 1300081.3852
C | Xist Rating 4246 | -84.46 | 291.267 | 150.288 | 35.8 | 2356.22 | 7580.61 | 37835.8 | 1.58 | 6.28 | 16.988 | 157.327 | 1 | 1 | 1240 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 686289.1307 | 60729.4628 | 1497.5369 | 10760.8369 | 49968.6259 | 164875.7346 | 0.047245 | -1273126.7191 | 1273126.7191
C | Xist Rating 4247 | -84.35 | 293.207 | 150.288 | 35.8 | 2359.24 | 7619.97 | 37664.5 | 1.55 | 6.24 | 16.931 | 155.776 | 1 | 1 | 1250 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 691745.6827 | 61625.4391 | 1521.7881 | 10847.6178 | 50777.8213 | 163243.5491 | 0.047626 | -1260523.4152 | 1260523.4152
C | Xist Rating 4248 | -84.08 | 298.517 | 150.288 | 35.8 | 2357.62 | 7627 | 37161.5 | 1.52 | 6.14 | 16.894 | 150.963 | 1 | 1 | 1260 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 703789.6495 | 62527.915 | 1546.2341 | 10934.3988 | 51593.5162 | 158225.1558 | 0.048007 | -1221772.7122 | 1221772.7122
C | Xist Rating 4249 | -83.34 | 313.439 | 150.288 | 35.8 | 2350.64 | 7623.36 | 35778 | 1.52 | 5.85 | 16.954 | 137.894 | 1 | 1 | 1270 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 736782.251 | 63436.8904 | 1570.8749 | 11021.1797 | 52415.7107 | 144669.7222 | 0.048388 | -1117101.2471 | 1117101.2471
C | Xist Rating 4250 | -83.18 | 317.172 | 150.288 | 35.8 | 2347.02 | 7601.12 | 35477.6 | 1.48 | 5.79 | 16.87 | 135.302 | 1 | 1 | 1280 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 744409.0274 | 64352.3654 | 1595.7105 | 11107.9607 | 53244.4047 | 141943.4429 | 0.048769 | -1096049.6411 | 1096049.6411
C | Xist Rating 4251 | -82.99 | 320.853 | 150.288 | 35.8 | 2347.04 | 7617.12 | 35183 | 1.45 | 5.73 | 16.844 | 132.767 | 1 | 1 | 1290 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 753054.8251 | 65274.3399 | 1620.7408 | 11194.7416 | 54079.5983 | 139290.5965 | 0.04915 | -1075565.0641 | 1075565.0641
C | Xist Rating 4252 | -82.67 | 326.142 | 150.288 | 35.8 | 2353.54 | 7710.06 | 34751.6 | 1.43 | 5.64 | 16.871 | 129.005 | 1 | 1 | 1300 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 767588.2427 | 66202.814 | 1645.966 | 11281.5226 | 54921.2915 | 135377.3325 | 0.049531 | -1045347.877 | 1045347.877
C | Xist Rating 4253 | -82.48 | 328.982 | 150.287 | 35.8 | 2360.06 | 7792.68 | 34540.4 | 1.39 | 5.59 | 16.834 | 127.272 | 1 | 1 | 1310 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 776417.2589 | 67137.7877 | 1671.3859 | 11368.3035 | 55769.4842 | 133545.7821 | 0.049912 | -1031205.1306 | 1031205.1306
C | Xist Rating 4254 | -81.75 | 344.002 | 150.288 | 35.8 | 2352.74 | 7784.04 | 33363.4 | 1.39 | 5.35 | 16.881 | 117.234 | 1 | 1 | 1320 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 809347.2655 | 68079.2609 | 1697.0007 | 11455.0844 | 56624.1765 | 123135.6891 | 0.050293 | -950821.1518 | 950821.1518
C | Xist Rating 4255 | -81.48 | 349.507 | 150.287 | 35.8 | 2350.85 | 7787.57 | 32980.5 | 1.36 | 5.28 | 16.765 | 114.2 | 1 | 1 | 1330 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 821638.5309 | 69027.2337 | 1722.8102 | 11541.8654 | 57485.3683 | 119955.806 | 0.050674 | -926266.9369 | 926266.9369
C | Xist Rating 4256 | -81.19 | 354.912 | 150.287 | 35.8 | 2352.2 | 7826.73 | 32607.5 | 1.33 | 5.2 | 16.735 | 111.259 | 1 | 1 | 1340 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 834824.0064 | 69981.7061 | 1748.8145 | 11628.6463 | 58353.0597 | 116879.196 | 0.051055 | -902510.1704 | 902510.1704
C | Xist Rating 4257 | -81.02 | 357.768 | 150.287 | 35.7 | 2356.21 | 7883.76 | 32424.4 | 1.3 | 5.16 | 16.704 | 109.89 | 1 | 1 | 1350 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 842976.5393 | 70942.678 | 1775.0136 | 11715.4273 | 59227.2507 | 115434.6492 | 0.051436 | -891355.7626 | 891355.7626
C | Xist Rating 4258 | -80.82 | 359.511 | 150.287 | 35.7 | 2370.46 | 8054.14 | 32303.9 | 1.29 | 5.14 | 16.764 | 108.958 | 1 | 1 | 1360 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 852206.4451 | 71910.1495 | 1801.4075 | 11802.2082 | 60107.9412 | 114471.0378 | 0.051817 | -883915.0111 | 883915.0111
C | Xist Rating 4259 | -79.89 | 380.911 | 150.287 | 35.7 | 2346.03 | 7877.84 | 30902.9 | 1.28 | 4.86 | 16.717 | 98.224 | 1 | 1 | 1370 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 893628.6333 | 72884.1205 | 1827.9962 | 11888.9892 | 60995.1313 | 103319.5002 | 0.052198 | -797805.7938 | 797805.7938
C | Xist Rating 4260 | -79.81 | 382.915 | 150.287 | 35.7 | 2345.08 | 7875.21 | 30794.5 | 1.25 | 4.84 | 16.683 | 97.502 | 1 | 1 | 1380 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 897966.3082 | 73864.5911 | 1854.7797 | 11975.7701 | 61888.821 | 102545.6445 | 0.052579 | -791830.2847 | 791830.2847
C | Xist Rating 4261 | -79.57 | 387.537 | 150.287 | 35.7 | 2345.35 | 7898.64 | 30527.5 | 1.23 | 4.78 | 16.652 | 95.616 | 1 | 1 | 1390 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 908909.9029 | 74851.5613 | 1881.7579 | 12062.551 | 62789.0102 | 100573.2192 | 0.05296 | -776599.7398 | 776599.7398
C | Xist Rating 4262 | -79.33 | 392.155 | 150.287 | 35.7 | 2346.07 | 7927.22 | 30265.6 | 1.2 | 4.73 | 16.626 | 93.786 | 1 | 1 | 1400 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 920023.0809 | 75845.031 | 1908.931 | 12149.332 | 63695.699 | 98648.6405 | 0.053341 | -761738.653 | 761738.653
C | Xist Rating 4263 | -79.04 | 397.62 | 150.287 | 35.7 | 2347.54 | 7968.74 | 29957.8 | 1.18 | 4.67 | 16.609 | 91.644 | 1 | 1 | 1410 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 933428.8548 | 76845.0002 | 1936.2988 | 12236.1129 | 64608.8873 | 96410.8359 | 0.053722 | -744458.9192 | 744458.9192
C | Xist Rating 4264 | -78.25 | 413.613 | 150.287 | 35.7 | 2342.44 | 7985.91 | 29052.1 | 1.19 | 4.49 | 16.671 | 85.301 | 1 | 1 | 1420 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 19 | E | Rod | 968863.6357 | 77851.4691 | 1963.8614 | 12322.8939 | 65528.5752 | 89847.6934 | 0.054103 | -693780.0726 | 693780.0726
C | Xist Rating 4265 | -78.12 | 416.711 | 150.287 | 35.7 | 2339.97 | 7969.58 | 28911 | 1.15 | 4.47 | 16.574 | 84.449 | 1 | 1 | 1430 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 975091.2387 | 78864.4375 | 1991.6188 | 12409.6748 | 66454.7627 | 88921.8911 | 0.054484 | -686631.2724 | 686631.2724
C | Xist Rating 4266 | -77.78 | 423.919 | 150.287 | 35.7 | 2337.72 | 7976.01 | 28542.3 | 1.14 | 4.39 | 16.558 | 82.023 | 1 | 1 | 1440 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 991003.9247 | 79883.9055 | 2019.571 | 12496.4558 | 67387.4497 | 86399.1621 | 0.054865 | -667151.4278 | 667151.4278
C | Xist Rating 4267 | -77.54 | 428.575 | 150.287 | 35.7 | 2337.95 | 7999.18 | 28317.1 | 1.11 | 4.35 | 16.539 | 80.597 | 1 | 1 | 1450 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1001986.9212 | 80909.873 | 2047.718 | 12583.2367 | 68326.6363 | 84893.0678 | 0.055246 | -655521.7666 | 655521.7666
C | Xist Rating 4268 | -77.34 | 431.313 | 150.287 | 35.7 | 2345 | 8094.93 | 28183.9 | 1.1 | 4.32 | 16.555 | 79.759 | 1 | 1 | 1460 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1011428.985 | 81942.3401 | 2076.0598 | 12670.0176 | 69272.3224 | 84021.3632 | 0.055627 | -648790.6947 | 648790.6947
C | Xist Rating 4269 | -76.55 | 449.477 | 150.287 | 35.7 | 2329.19 | 7992.07 | 27310.5 | 1.09 | 4.16 | 16.549 | 74.201 | 1 | 1 | 1470 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1046917.3336 | 82981.3067 | 2104.5964 | 12756.7986 | 70224.5081 | 78246.2123 | 0.056008 | -604196.5109 | 604196.5109
C | Xist Rating 4270 | -76.27 | 454.986 | 150.287 | 35.7 | 2329.61 | 8021.35 | 27066.2 | 1.08 | 4.11 | 16.536 | 72.733 | 1 | 1 | 1480 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1059939.9355 | 84026.7729 | 2133.3277 | 12843.5795 | 71183.1934 | 76717.8722 | 0.056389 | -592395.0735 | 592395.0735
C | Xist Rating 4271 | -76.02 | 459.644 | 150.287 | 35.7 | 2331.09 | 8059.34 | 26867.1 | 1.06 | 4.07 | 16.528 | 71.559 | 1 | 1 | 1490 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1071471.532 | 85078.7387 | 2162.2539 | 12930.3605 | 72148.3782 | 75484.0255 | 0.05677 | -582867.6364 | 582867.6364
C | Xist Rating 4272 | -75.75 | 464.394 | 150.287 | 35.7 | 2334.01 | 8115.06 | 26670.5 | 1.04 | 4.03 | 16.512 | 70.427 | 1 | 1 | 1500 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1083900.2399 | 86137.204 | 2191.3748 | 13017.1414 | 73120.0626 | 74292.9538 | 0.057151 | -573670.496 | 573670.496
C | Xist Rating 4273 | -75.42 | 469.93 | 150.287 | 35.7 | 2339.47 | 8206.89 | 26439 | 1.02 | 3.99 | 16.515 | 69.082 | 1 | 1 | 1510 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1099387.1371 | 87202.1689 | 2220.6906 | 13103.9224 | 74098.2466 | 72881.7256 | 0.057532 | -562773.3666 | 562773.3666
C | Xist Rating 4274 | -74.52 | 487.778 | 150.287 | 35.7 | 2336.94 | 8262.49 | 25681.2 | 1.03 | 3.85 | 16.586 | 64.616 | 1 | 1 | 1520 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1139907.9193 | 88273.6334 | 2250.2011 | 13190.7033 | 75082.9301 | 68267.5774 | 0.057913 | -527144.1368 | 527144.1368
C | Xist Rating 4275 | -74.3 | 493.657 | 150.287 | 35.7 | 2330.66 | 8209.72 | 25468.5 | 1 | 3.8 | 16.531 | 63.485 | 1 | 1 | 1530 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1150546.6236 | 89351.5974 | 2279.9064 | 13277.4842 | 76074.1131 | 67062.7964 | 0.058294 | -517841.1378 | 517841.1378
C | Xist Rating 4276 | -74.09 | 496.67 | 150.287 | 35.7 | 2335.84 | 8287.14 | 25363.8 | 0.98 | 3.78 | 16.522 | 62.949 | 1 | 1 | 1540 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1160141.6528 | 90436.061 | 2309.8065 | 13364.2652 | 77071.7958 | 66490.1397 | 0.058675 | -513419.2344 | 513419.2344
C | Xist Rating 4277 | -73.65 | 505.746 | 150.287 | 35.7 | 2334.54 | 8313.48 | 25021.3 | 0.96 | 3.72 | 16.517 | 61.07 | 1 | 1 | 1550 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1180684.2668 | 91527.0241 | 2339.9013 | 13451.0461 | 78075.978 | 64522.7671 | 0.059056 | -498227.7047 | 498227.7047
C | Xist Rating 4278 | -73.37 | 508.534 | 150.287 | 35.7 | 2347.29 | 8490.86 | 24920.8 | 0.95 | 3.7 | 16.546 | 60.544 | 1 | 1 | 1560 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1193676.7729 | 92624.4868 | 2370.191 | 13537.8271 | 79086.6597 | 63974.0012 | 0.059437 | -493990.2798 | 493990.2798
C | Xist Rating 4279 | -72.53 | 529.619 | 150.287 | 35.7 | 2325.81 | 8315.28 | 24162.2 | 0.94 | 3.56 | 16.531 | 56.483 | 1 | 1 | 1570 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1231793.1664 | 93728.449 | 2400.6755 | 13624.608 | 80103.841 | 59751.0685 | 0.059818 | -461381.9128 | 461381.9128
C | Xist Rating 4280 | -72.25 | 534.398 | 150.287 | 35.7 | 2329.02 | 8378 | 24007.7 | 0.93 | 3.53 | 16.523 | 55.717 | 1 | 1 | 1580 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1244623.63 | 94838.9109 | 2431.3547 | 13711.3889 | 81127.5219 | 58950.3094 | 0.0602 | -455198.6634 | 455198.6634
C | Xist Rating 4281 | -71.97 | 539.212 | 150.287 | 35.7 | 2332.82 | 8449.19 | 23855.2 | 0.91 | 3.5 | 16.517 | 54.971 | 1 | 1 | 1590 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1257884.5378 | 95955.8722 | 2462.2288 | 13798.1699 | 82157.7024 | 58158.5361 | 0.060581 | -449084.7998 | 449084.7998
C | Xist Rating 4282 | -71.6 | 545.625 | 150.287 | 35.7 | 2336.56 | 8529.36 | 23645.6 | 0.9 | 3.46 | 16.524 | 53.92 | 1 | 1 | 1600 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1274885.55 | 97079.3332 | 2493.2976 | 13884.9508 | 83194.3824 | 57062.4176 | 0.060962 | -440620.8629 | 440620.8629
C | Xist Rating 4283 | -71.42 | 548.834 | 150.287 | 35.7 | 2338.71 | 8571.62 | 23556.9 | 0.88 | 3.45 | 16.503 | 53.528 | 1 | 1 | 1610 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1283563.5641 | 98209.2937 | 2524.5612 | 13971.7318 | 84237.5619 | 56636.8087 | 0.061343 | -437334.424 | 437334.424
C | Xist Rating 4284 | -70.39 | 572.371 | 150.287 | 35.7 | 2324.38 | 8496.77 | 22805.2 | 0.88 | 3.31 | 16.519 | 49.778 | 1 | 1 | 1620 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1330407.705 | 99345.7538 | 2556.0196 | 14058.5127 | 85287.241 | 52749.9718 | 0.061724 | -407321.2996 | 407321.2996
C | Xist Rating 4285 | -70.14 | 575.234 | 150.287 | 35.7 | 2333.49 | 8633.31 | 22723.8 | 0.87 | 3.29 | 16.532 | 49.41 | 1 | 1 | 1630 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1342302.7867 | 100488.7134 | 2587.6728 | 14145.2937 | 86343.4197 | 52363.0773 | 0.062105 | -404333.8029 | 404333.8029
C | Xist Rating 4286 | -69.92 | 580.196 | 150.287 | 35.7 | 2331.65 | 8630.62 | 22588.8 | 0.85 | 3.27 | 16.512 | 48.811 | 1 | 1 | 1640 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1352814.0034 | 101638.1726 | 2619.5208 | 14232.0746 | 87406.098 | 51721.9079 | 0.062486 | -399382.863 | 399382.863
C | Xist Rating 4287 | -69.62 | 586.966 | 150.287 | 35.7 | 2328.59 | 8620.13 | 22403 | 0.84 | 3.23 | 16.49 | 47.972 | 1 | 1 | 1650 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1366803.1579 | 102794.1313 | 2651.5635 | 14318.8555 | 88475.2758 | 50843.3198 | 0.062867 | -392598.6384 | 392598.6384
C | Xist Rating 4288 | -69.28 | 593.493 | 150.287 | 35.7 | 2329.77 | 8667.83 | 22220.9 | 0.83 | 3.2 | 16.491 | 47.141 | 1 | 1 | 1660 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1382702.1866 | 103956.5896 | 2683.8011 | 14405.6365 | 89550.9531 | 49974.3283 | 0.063248 | -385888.5162 | 385888.5162
C | Xist Rating 4289 | -68.36 | 614.622 | 150.287 | 35.7 | 2317.7 | 8605.97 | 21633.2 | 0.82 | 3.1 | 16.513 | 44.439 | 1 | 1 | 1670 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1424509.4094 | 105125.5475 | 2716.2334 | 14492.4174 | 90633.1301 | 47163.4467 | 0.063629 | -364183.6335 | 364183.6335
C | Xist Rating 4290 | -68.14 | 617.597 | 150.287 | 35.7 | 2323.96 | 8706.41 | 21560.6 | 0.81 | 3.08 | 16.52 | 44.142 | 1 | 1 | 1680 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1435270.7241 | 106301.0049 | 2748.8606 | 14579.1984 | 91721.8065 | 46849.074 | 0.06401 | -361756.131 | 361756.131
C | Xist Rating 4291 | -67.78 | 626.227 | 150.287 | 35.7 | 2318.52 | 8670.71 | 21346.2 | 0.8 | 3.04 | 16.494 | 43.227 | 1 | 1 | 1690 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1451919.824 | 107482.9619 | 2781.6825 | 14665.9793 | 92816.9826 | 45890.7558 | 0.064391 | -354356.2522 | 354356.2522
C | Xist Rating 4292 | -67.47 | 631.919 | 150.287 | 35.7 | 2320.89 | 8730.94 | 21206.1 | 0.79 | 3.02 | 16.493 | 42.635 | 1 | 1 | 1700 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1466614.4879 | 108671.4185 | 2814.6992 | 14752.7603 | 93918.6582 | 45269.2505 | 0.064772 | -349557.153 | 349557.153
C | Xist Rating 4293 | -67.15 | 638.638 | 150.287 | 35.7 | 2320.12 | 8751.79 | 21045 | 0.77 | 2.99 | 16.484 | 41.965 | 1 | 1 | 1710 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1481716.7966 | 109866.3746 | 2847.9107 | 14839.5412 | 95026.8334 | 44553.482 | 0.065153 | -344030.1781 | 344030.1781
C | Xist Rating 4294 | -66.3 | 658.113 | 150.287 | 35.7 | 2310.31 | 8709.01 | 20567.5 | 0.77 | 2.9 | 16.516 | 39.927 | 1 | 1 | 1720 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1520445.045 | 111067.8303 | 2881.317 | 14926.3221 | 96141.5081 | 42444.6114 | 0.065534 | -327746.0382 | 327746.0382
C | Xist Rating 4295 | -65.92 | 666.612 | 150.288 | 35.6 | 2308.14 | 8718.39 | 20374.4 | 0.76 | 2.87 | 16.507 | 39.147 | 1 | 1 | 1730 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1538633.8217 | 112275.7855 | 2914.9181 | 15013.1031 | 97262.6824 | 41626.9451 | 0.065915 | -321432.2358 | 321432.2358
C | Xist Rating 4296 | -65.66 | 670.586 | 150.287 | 35.7 | 2312.62 | 8800.7 | 20290.4 | 0.75 | 2.85 | 16.508 | 38.827 | 1 | 1 | 1740 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1550810.5953 | 113490.2403 | 2948.714 | 15099.884 | 98390.3563 | 41287.4329 | 0.066296 | -318810.6124 | 318810.6124
C | Xist Rating 4297 | -65.38 | 678.365 | 150.287 | 35.6 | 2307.52 | 8763.35 | 20122.9 | 0.74 | 2.82 | 16.483 | 38.176 | 1 | 1 | 1750 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1565340.8048 | 114711.1946 | 2982.7046 | 15186.665 | 99524.5297 | 40602.5195 | 0.066677 | -313521.8933 | 313521.8933
C | Xist Rating 4298 | -65.07 | 684.174 | 150.287 | 35.7 | 2307.16 | 8784.97 | 20001.2 | 0.73 | 2.8 | 16.487 | 37.705 | 1 | 1 | 1760 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1578498.8858 | 115938.6486 | 3016.8901 | 15273.4459 | 100665.2026 | 40106.0809 | 0.067058 | -309688.526 | 309688.526
C | Xist Rating 4299 | -64.08 | 707.25 | 150.287 | 35.7 | 2296.24 | 8740.71 | 19497.8 | 0.73 | 2.71 | 16.523 | 35.698 | 1 | 1 | 1770 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1624015.74 | 117172.602 | 3051.2703 | 15360.2269 | 101812.3752 | 38029.2945 | 0.067439 | -293652.1318 | 293652.1318
C | Xist Rating 4300 | -63.97 | 713.168 | 150.287 | 35.6 | 2287.8 | 8645.52 | 19383.4 | 0.71 | 2.69 | 16.695 | 35.273 | 1 | 1 | 1780 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1631585.7504 | 118413.0551 | 3085.8453 | 15447.0078 | 102966.0473 | 37576.7163 | 0.06782 | -290157.4431 | 290157.4431
C | Xist Rating 4301 | -63.82 | 716.403 | 150.287 | 35.6 | 2286.45 | 8639.14 | 19327.1 | 0.7 | 2.68 | 16.683 | 35.086 | 1 | 1 | 1790 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1638019.6393 | 119660.0077 | 3120.6151 | 15533.7887 | 104126.2189 | 37373.761 | 0.068201 | -288590.2758 | 288590.2758
C | Xist Rating 4302 | -63.39 | 726.798 | 150.287 | 35.6 | 2283.76 | 8648.5 | 19121.9 | 0.7 | 2.65 | 16.669 | 34.322 | 1 | 1 | 1800 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1659832.2005 | 120913.4599 | 3155.5797 | 15620.5697 | 105292.8902 | 36584.7922 | 0.068582 | -282498.0676 | 282498.0676
C | Xist Rating 4303 | -63.1 | 732.59 | 150.287 | 35.6 | 2283.96 | 8677.37 | 19012.5 | 0.69 | 2.63 | 16.67 | 33.929 | 1 | 1 | 1810 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1673206.2564 | 122173.4116 | 3190.7391 | 15707.3506 | 106466.0609 | 36168.4246 | 0.068963 | -279282.9872 | 279282.9872
C | Xist Rating 4304 | -62.12 | 755.924 | 150.287 | 35.6 | 2273.09 | 8630.28 | 18562.8 | 0.68 | 2.55 | 16.705 | 32.262 | 1 | 1 | 1820 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1718283.2852 | 123439.8629 | 3226.0933 | 15794.1316 | 107645.7313 | 34430.7456 | 0.069344 | -265865.0913 | 265865.0913
C | Xist Rating 4305 | -62.12 | 752.205 | 150.288 | 35.6 | 2284.7 | 8782.43 | 18631.5 | 0.68 | 2.56 | 16.728 | 32.525 | 1 | 1 | 1830 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1718562.7635 | 124712.8137 | 3261.6423 | 15880.9125 | 108831.9012 | 34710.2455 | 0.069725 | -268023.3149 | 268023.3149
C | Xist Rating 4306 | -61.76 | 756.945 | 150.288 | 35.6 | 2292.6 | 8922.96 | 18545.5 | 0.67 | 2.55 | 16.748 | 32.225 | 1 | 1 | 1840 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1735372.107 | 125992.2641 | 3297.386 | 15967.6935 | 110024.5707 | 34391.1032 | 0.070106 | -265558.9825 | 265558.9825
C | Xist Rating 4307 | -61.36 | 764.841 | 150.288 | 35.6 | 2292.83 | 8963.14 | 18409.6 | 0.66 | 2.52 | 16.74 | 31.761 | 1 | 1 | 1850 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1753650.39 | 127278.2141 | 3333.3246 | 16054.4744 | 111223.7397 | 33899.9435 | 0.070487 | -261766.3779 | 261766.3779
C | Xist Rating 4308 | -60.99 | 773.682 | 150.287 | 35.6 | 2289.56 | 8954.4 | 18259.3 | 0.65 | 2.5 | 16.729 | 31.249 | 1 | 1 | 1860 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1771391.3599 | 128570.6636 | 3369.4579 | 16141.2553 | 112429.4083 | 33358.6318 | 0.070868 | -257586.5125 | 257586.5125
C | Xist Rating 4309 | -60.04 | 795.09 | 150.288 | 35.6 | 2282.91 | 8959.7 | 17879.8 | 0.65 | 2.43 | 16.774 | 29.91 | 1 | 1 | 1870 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1815118.9119 | 129869.6127 | 3405.7861 | 16228.0363 | 113641.5764 | 31975.4084 | 0.071249 | -246905.6279 | 246905.6279
C | Xist Rating 4310 | -59.65 | 803.917 | 150.288 | 35.6 | 2279.77 | 8952.1 | 17739.2 | 0.64 | 2.41 | 16.766 | 29.45 | 1 | 1 | 1880 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1832745.8591 | 131175.0614 | 3442.309 | 16314.8172 | 114860.2441 | 31488.0194 | 0.07163 | -243142.1395 | 243142.1395
C | Xist Rating 4311 | -59.31 | 809.757 | 150.288 | 35.6 | 2283.64 | 9039.67 | 17646.9 | 0.63 | 2.39 | 16.77 | 29.152 | 1 | 1 | 1890 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1849193.4755 | 132487.0096 | 3479.0267 | 16401.5982 | 116085.4114 | 31169.3663 | 0.072011 | -240681.5842 | 240681.5842
C | Xist Rating 4312 | -59.06 | 816.054 | 150.288 | 35.6 | 2280.1 | 9011.93 | 17555.6 | 0.62 | 2.38 | 16.761 | 28.873 | 1 | 1 | 1900 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1860684.7254 | 133805.4574 | 3515.9392 | 16488.3791 | 117317.0782 | 30869.6033 | 0.072392 | -238366.8938 | 238366.8938
C | Xist Rating 4313 | -58.8 | 822.072 | 150.288 | 35.6 | 2278.48 | 9014.24 | 17465.1 | 0.61 | 2.36 | 16.764 | 28.591 | 1 | 1 | 1910 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1873074.6106 | 135130.4047 | 3553.0464 | 16575.1601 | 118555.2446 | 30567.2115 | 0.072773 | -236031.9051 | 236031.9051
C | Xist Rating 4314 | -57.69 | 848.079 | 150.288 | 35.6 | 2269.16 | 8997.9 | 17050.4 | 0.61 | 2.29 | 16.81 | 27.213 | 1 | 1 | 1920 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1924426.9436 | 136461.8516 | 3590.3485 | 16661.941 | 119799.9106 | 29143.1594 | 0.073154 | -225035.7522 | 225035.7522
C | Xist Rating 4315 | -57.32 | 856.983 | 150.288 | 35.6 | 2265.77 | 8985.37 | 16924.1 | 0.6 | 2.27 | 16.806 | 26.827 | 1 | 1 | 1930 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1941726.3719 | 137799.798 | 3627.8454 | 16748.7219 | 121051.0761 | 28732.1452 | 0.073535 | -221862.0092 | 221862.0092
C | Xist Rating 4316 | -57.01 | 859.856 | 150.288 | 35.6 | 2275.43 | 9153.4 | 16882.2 | 0.6 | 2.26 | 16.821 | 26.704 | 1 | 1 | 1940 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1956542.1381 | 139144.2441 | 3665.537 | 16835.5029 | 122308.7412 | 28609.7125 | 0.073916 | -220916.6161 | 220916.6161
C | Xist Rating 4317 | -56.76 | 868.323 | 150.288 | 35.6 | 2266.94 | 9053.92 | 16772.2 | 0.58 | 2.24 | 16.801 | 26.386 | 1 | 1 | 1950 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1968436.1416 | 140495.1896 | 3703.4235 | 16922.2838 | 123572.9058 | 28253.5742 | 0.074297 | -218166.6107 | 218166.6107
C | Xist Rating 4318 | -56.34 | 878.052 | 150.288 | 35.6 | 2264.26 | 9056.76 | 16637.2 | 0.57 | 2.22 | 16.818 | 25.977 | 1 | 1 | 1960 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 1988138.0215 | 141852.6348 | 3741.5047 | 17009.0648 | 124843.57 | 27819.2869 | 0.074678 | -214813.1593 | 214813.1593
C | Xist Rating 4319 | -55.33 | 901.515 | 150.288 | 35.6 | 2256.86 | 9054.21 | 16303.3 | 0.58 | 2.16 | 16.877 | 24.939 | 1 | 1 | 1970 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2034593.1429 | 143216.5795 | 3779.7807 | 17095.8457 | 126120.7338 | 26763.4954 | 0.075059 | -206660.6172 | 206660.6172
C | Xist Rating 4320 | -55 | 908.459 | 150.288 | 35.6 | 2256.92 | 9086.85 | 16214.4 | 0.57 | 2.15 | 16.904 | 24.685 | 1 | 1 | 1980 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2050319.2863 | 144587.0238 | 3818.2515 | 17182.6267 | 127404.3971 | 26490.4916 | 0.07544 | -204552.5544 | 204552.5544
C | Xist Rating 4321 | -54.65 | 917.558 | 150.288 | 35.6 | 2252.69 | 9059.33 | 16101.6 | 0.56 | 2.13 | 16.9 | 24.366 | 1 | 1 | 1990 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2066973.731 | 145963.9676 | 3856.9171 | 17269.4076 | 128694.56 | 26148.2512 | 0.075821 | -201909.865 | 201909.865
C | Xist Rating 4322 | -54.33 | 924.627 | 150.288 | 35.6 | 2251.52 | 9072.18 | 16015.1 | 0.55 | 2.12 | 16.901 | 24.125 | 1 | 1 | 2000 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2081816.183 | 147347.411 | 3895.7775 | 17356.1885 | 129991.2224 | 25887.1139 | 0.076202 | -199893.4317 | 199893.4317
C | Xist Rating 4323 | -54.09 | 929.84 | 150.288 | 35.6 | 2251.58 | 9095.88 | 15953.9 | 0.54 | 2.11 | 16.904 | 23.962 | 1 | 1 | 2010 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2093609.1472 | 148737.3539 | 3934.8326 | 17442.9695 | 131294.3844 | 25706.9239 | 0.076583 | -198502.0525 | 198502.0525
C | Xist Rating 4324 | -53.01 | 956.295 | 150.288 | 35.6 | 2241.59 | 9061.71 | 15615 | 0.54 | 2.05 | 16.941 | 22.969 | 1 | 1 | 2020 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2143621.3091 | 150133.7964 | 3974.0826 | 17529.7504 | 132604.046 | 24681.5958 | 0.076964 | -190584.7402 | 190584.7402
C | Xist Rating 4325 | -52.57 | 965.969 | 150.288 | 35.6 | 2240.6 | 9090.51 | 15499.9 | 0.54 | 2.03 | 16.943 | 22.651 | 1 | 1 | 2030 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2164350.1414 | 151536.7385 | 4013.5273 | 17616.5314 | 133920.2071 | 24355.5522 | 0.077345 | -188067.1179 | 188067.1179
C | Xist Rating 4326 | -52.31 | 972.465 | 150.288 | 35.6 | 2238.28 | 9079.33 | 15431.8 | 0.53 | 2.02 | 16.94 | 22.48 | 1 | 1 | 2040 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2176648.9602 | 152946.1801 | 4053.1669 | 17703.3123 | 135242.8678 | 24166.4316 | 0.077726 | -186606.7789 | 186606.7789
C | Xist Rating 4327 | -51.98 | 978.146 | 150.288 | 35.7 | 2241.42 | 9158.59 | 15364.3 | 0.52 | 2.01 | 16.951 | 22.297 | 1 | 1 | 2050 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2192436.0073 | 154362.1213 | 4093.0012 | 17790.0933 | 136572.0281 | 23965.3702 | 0.078107 | -185054.236 | 185054.236
C | Xist Rating 4328 | -51.67 | 987.64 | 150.288 | 35.6 | 2235.23 | 9096.61 | 15264.3 | 0.51 | 1.99 | 16.937 | 22.041 | 1 | 1 | 2060 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2207602.5572 | 155784.5621 | 4133.0303 | 17876.8742 | 137907.6879 | 23687.154 | 0.078488 | -182905.9246 | 182905.9246
C | Xist Rating 4329 | -50.52 | 1016.05 | 150.288 | 35.6 | 2224.85 | 9061.01 | 14936.2 | 0.51 | 1.94 | 16.975 | 21.135 | 1 | 1 | 2070 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2260558.8425 | 157213.5024 | 4173.2542 | 17963.6551 | 139249.8472 | 22751.9446 | 0.078869 | -175684.485 | 175684.485
C | Xist Rating 4330 | -50.26 | 1022.35 | 150.288 | 35.7 | 2223.66 | 9067.77 | 14873.5 | 0.5 | 1.93 | 16.971 | 20.982 | 1 | 1 | 2080 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2273358.801 | 158648.9423 | 4213.6729 | 18050.4361 | 140598.5062 | 22580.9217 | 0.07925 | -174363.892 | 174363.892
C | Xist Rating 4331 | -49.92 | 1030.45 | 150.288 | 35.6 | 2221.86 | 9073.47 | 14790.9 | 0.5 | 1.91 | 16.969 | 20.775 | 1 | 1 | 2090 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2289515.637 | 160090.8817 | 4254.2864 | 18137.217 | 141953.6647 | 22369.6625 | 0.079631 | -172732.604 | 172732.604
C | Xist Rating 4332 | -49.59 | 1038.55 | 150.288 | 35.7 | 2219.76 | 9073.8 | 14709.3 | 0.49 | 1.9 | 16.971 | 20.571 | 1 | 1 | 2100 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2305331.748 | 161539.3207 | 4295.0947 | 18223.998 | 143315.3227 | 22145.731 | 0.080012 | -171003.4643 | 171003.4643
C | Xist Rating 4333 | -49.29 | 1045.72 | 150.288 | 35.7 | 2218.54 | 9084.48 | 14638.7 | 0.49 | 1.89 | 16.97 | 20.399 | 1 | 1 | 2110 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2319971.6488 | 162994.2593 | 4336.0977 | 18310.7789 | 144683.4803 | 21970.7904 | 0.080393 | -169652.6198 | 169652.6198
C | Xist Rating 4334 | -48.24 | 1072.61 | 150.288 | 35.6 | 2208.46 | 9041.23 | 14359 | 0.48 | 1.84 | 17.006 | 19.671 | 1 | 1 | 2120 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2368816.2806 | 164455.6974 | 4377.2956 | 18397.5599 | 146058.1375 | 21204.0067 | 0.080774 | -163731.7189 | 163731.7189
C | Xist Rating 4335 | -47.82 | 1082.63 | 150.288 | 35.6 | 2206.82 | 9057.61 | 14263.7 | 0.48 | 1.83 | 17.004 | 19.44 | 1 | 1 | 2130 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2389169.5366 | 165923.6351 | 4418.6882 | 18484.3408 | 147439.2943 | 20967.6809 | 0.081155 | -161906.8736 | 161906.8736
C | Xist Rating 4336 | -47.45 | 1092.67 | 150.288 | 35.6 | 2202.76 | 9032.99 | 14169.9 | 0.47 | 1.81 | 16.994 | 19.215 | 1 | 1 | 2140 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2406889.7692 | 167398.0723 | 4460.2756 | 18571.1217 | 148826.9506 | 20720.9154 | 0.081536 | -160001.416 | 160001.416
C | Xist Rating 4337 | -47.21 | 1098.03 | 150.288 | 35.6 | 2202.71 | 9053.87 | 14123.4 | 0.47 | 1.8 | 16.993 | 19.112 | 1 | 1 | 2150 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2418641.6613 | 168879.0091 | 4502.0578 | 18657.9027 | 150221.1064 | 20617.485 | 0.081917 | -159202.7538 | 159202.7538
C | Xist Rating 4338 | -46.9 | 1105.14 | 150.288 | 35.6 | 2202.27 | 9077.09 | 14059.2 | 0.46 | 1.79 | 16.995 | 18.962 | 1 | 1 | 2160 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2433816.6678 | 170366.4455 | 4544.0348 | 18744.6836 | 151621.7618 | 20448.9265 | 0.082298 | -157901.1897 | 157901.1897
C | Xist Rating 4339 | -45.81 | 1134.21 | 150.288 | 35.6 | 2190.33 | 9007.23 | 13786 | 0.46 | 1.75 | 17.027 | 18.292 | 1 | 1 | 2170 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2484294.1893 | 171860.3814 | 4586.2066 | 18831.4646 | 153028.9168 | 19758.0686 | 0.082679 | -152566.5683 | 152566.5683
C | Xist Rating 4340 | -45.39 | 1144 | 150.288 | 35.7 | 2189.18 | 9030.77 | 13699.3 | 0.46 | 1.74 | 17.03 | 18.089 | 1 | 1 | 2180 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2504421.92 | 173360.8169 | 4628.5732 | 18918.2455 | 154442.5714 | 19550.8991 | 0.08306 | -150966.8605 | 150966.8605
C | Xist Rating 4341 | -45.1 | 1151.34 | 150.288 | 35.6 | 2187.69 | 9035.59 | 13639 | 0.45 | 1.73 | 17.027 | 17.958 | 1 | 1 | 2190 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2518775.0046 | 174867.7519 | 4671.1346 | 19005.0265 | 155862.7255 | 19401.5171 | 0.083441 | -149813.3723 | 149813.3723
C | Xist Rating 4342 | -44.84 | 1159.09 | 150.288 | 35.6 | 2183.9 | 9001.2 | 13579.4 | 0.44 | 1.72 | 17.019 | 17.833 | 1 | 1 | 2200 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2531336.651 | 176381.1865 | 4713.8907 | 19091.8074 | 157289.3791 | 19258.0012 | 0.083822 | -148705.1802 | 148705.1802
C | Xist Rating 4343 | -44.46 | 1169.14 | 150.288 | 35.6 | 2180.84 | 8991.81 | 13495.4 | 0.44 | 1.7 | 17.021 | 17.644 | 1 | 1 | 2210 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2549707.2776 | 177901.1207 | 4756.8417 | 19178.5883 | 158722.5324 | 19065.1688 | 0.084203 | -147216.1796 | 147216.1796
C | Xist Rating 4344 | -43.34 | 1198.07 | 150.288 | 35.6 | 2171.77 | 8966.73 | 13246.2 | 0.44 | 1.66 | 17.06 | 17.061 | 1 | 1 | 2220 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2601932.4839 | 179427.5544 | 4799.9874 | 19265.3693 | 160162.1852 | 18464.7888 | 0.084584 | -142580.2048 | 142580.2048
C | Xist Rating 4345 | -43.02 | 1206.14 | 150.288 | 35.6 | 2170.31 | 8975.58 | 13182.5 | 0.43 | 1.65 | 17.057 | 16.924 | 1 | 1 | 2230 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2617697.7034 | 180960.4877 | 4843.3279 | 19352.1502 | 161608.3375 | 18308.6973 | 0.084965 | -141374.9075 | 141374.9075
C | Xist Rating 4346 | -42.68 | 1215.6 | 150.288 | 35.6 | 2166.87 | 8954.65 | 13111.7 | 0.43 | 1.64 | 17.051 | 16.776 | 1 | 1 | 2240 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2634047.172 | 182499.9206 | 4886.8633 | 19438.9312 | 163060.9894 | 18158.0282 | 0.085346 | -140211.4803 | 140211.4803
C | Xist Rating 4347 | -42.3 | 1225.96 | 150.288 | 35.6 | 2163.75 | 8943.19 | 13034 | 0.42 | 1.63 | 17.049 | 16.612 | 1 | 1 | 2250 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2652670.95 | 184045.853 | 4930.5934 | 19525.7121 | 164520.1409 | 17973.7193 | 0.085727 | -138788.2965 | 138788.2965
C | Xist Rating 4348 | -42.06 | 1231.28 | 150.288 | 35.6 | 2164.09 | 8970.06 | 12995.6 | 0.42 | 1.62 | 17.05 | 16.536 | 1 | 1 | 2260 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2664600.7352 | 185598.285 | 4974.5182 | 19612.4931 | 165985.7919 | 17898.0457 | 0.086108 | -138203.9648 | 138203.9648
C | Xist Rating 4349 | -40.91 | 1262.48 | 150.288 | 35.6 | 2153.08 | 8916.34 | 12751.9 | 0.42 | 1.59 | 17.085 | 15.996 | 1 | 1 | 2270 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2718220.4384 | 187157.2165 | 5018.6379 | 19699.274 | 167457.9425 | 17341.9622 | 0.086489 | -133910.0354 | 133910.0354
C | Xist Rating 4350 | -40.56 | 1271.89 | 150.288 | 35.6 | 2150.84 | 8914.99 | 12686.1 | 0.41 | 1.58 | 17.082 | 15.865 | 1 | 1 | 2280 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2735631.8876 | 188722.6476 | 5062.9524 | 19786.0549 | 168936.5927 | 17191.5488 | 0.08687 | -132748.5828 | 132748.5828
C | Xist Rating 4351 | -40.14 | 1282.94 | 150.288 | 35.6 | 2148.01 | 8911.78 | 12606.8 | 0.41 | 1.56 | 17.079 | 15.701 | 1 | 1 | 2290 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2755767.9494 | 190294.5783 | 5107.4617 | 19872.8359 | 170421.7424 | 17024.2481 | 0.087251 | -131456.7315 | 131456.7315
C | Xist Rating 4352 | -39.84 | 1290.44 | 150.288 | 35.6 | 2146.96 | 8922.38 | 12556.9 | 0.4 | 1.56 | 17.077 | 15.605 | 1 | 1 | 2300 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2770523.0624 | 191873.0085 | 5152.1657 | 19959.6168 | 171913.3917 | 16910.0007 | 0.087632 | -130574.5433 | 130574.5433
| Xist Rating 4353 | -39.58 | 1298.21 | 150.288 | 35.6 | 2143.96 | 8899.47 | 12507.5 | 0.4 | 1.55 | 17.072 | 15.512 | 1 | 1 | 2310 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2783310.3116 | 193457.9383 | 5197.0645 | 20046.3978 | 173411.5405 | 16816.2752 | 0.088013 | -129850.8194 | 129850.8194
| Xist Rating 4354 | -38.39 | 1330.19 | 150.288 | 35.6 | 2134.59 | 8874.02 | 12277 | 0.4 | 1.51 | 17.109 | 15.025 | 1 | 1 | 2320 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2839410.2721 | 195049.3676 | 5242.1582 | 20133.1787 | 174916.1889 | 16315.1265 | 0.088394 | -125981.0824 | 125981.0824
| Xist Rating 4355 | -38.05 | 1339.63 | 150.288 | 35.6 | 2131.85 | 8862.98 | 12216.7 | 0.39 | 1.5 | 17.102 | 14.909 | 1 | 1 | 2330 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2855890.2155 | 196647.2965 | 5287.4466 | 20219.9597 | 176427.3369 | 16179.5743 | 0.088775 | -124934.3842 | 124934.3842
| Xist Rating 4356 | -37.7 | 1349.05 | 150.288 | 35.6 | 2129.64 | 8861.19 | 12157.1 | 0.39 | 1.49 | 17.097 | 14.796 | 1 | 1 | 2340 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2872990.842 | 198251.725 | 5332.9298 | 20306.7406 | 177944.9844 | 16065.0092 | 0.089156 | -124049.7424 | 124049.7424
| Xist Rating 4357 | -37.41 | 1357.62 | 150.288 | 35.6 | 2126.88 | 8845.44 | 12104.6 | 0.38 | 1.49 | 17.093 | 14.699 | 1 | 1 | 2350 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2887494.8256 | 199862.653 | 5378.6078 | 20393.5215 | 179469.1315 | 15949.0939 | 0.089537 | -123154.6756 | 123154.6756
| Xist Rating 4358 | -37.07 | 1368.02 | 150.288 | 35.6 | 2122.77 | 8814.34 | 12039.9 | 0.38 | 1.48 | 17.096 | 14.577 | 1 | 1 | 2360 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2903991.8154 | 201480.0806 | 5424.4805 | 20480.3025 | 180999.7781 | 15825.4292 | 0.089918 | -122199.7696 | 122199.7696
| Xist Rating 4359 | -35.99 | 1397.39 | 150.288 | 35.6 | 2114.55 | 8793.04 | 11846.8 | 0.38 | 1.45 | 17.129 | 14.189 | 1 | 1 | 2370 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2954851.0245 | 203104.0077 | 5470.5481 | 20567.0834 | 182536.9243 | 15426.736 | 0.090299 | -119121.1665 | 119121.1665
| Xist Rating 4360 | -35.66 | 1407.04 | 150.288 | 35.6 | 2111.46 | 8775.13 | 11791.2 | 0.37 | 1.44 | 17.12 | 14.089 | 1 | 1 | 2380 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2970908.6784 | 204734.4344 | 5516.8105 | 20653.8644 | 184080.5701 | 15307.1749 | 0.09068 | -118197.9472 | 118197.9472
| Xist Rating 4361 | -35.3 | 1417 | 150.288 | 35.6 | 2109.13 | 8773.96 | 11730.1 | 0.37 | 1.43 | 17.115 | 13.974 | 1 | 1 | 2390 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 2988637.21 | 206371.3607 | 5563.2676 | 20740.6453 | 185630.7154 | 15190.3888 | 0.091061 | -117296.1556 | 117296.1556
C | Xist Rating 4362 | -30.64 | 1624.28 | 150.288 | 35.6 | 1975.72 | 7412.61 | 10538.8 | 0.4 | 1.25 | 17.056 | 11.754 | 1 | 1 | 2400 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 3209122.4816 | 208014.7865 | 5609.9196 | 20827.4263 | 187187.3603 | 12940.4585 | 0.091442 | -99922.7902 | 99922.7902
C | Xist Rating 4364 | -27.56 | 1627.13 | 150.289 | 35.7 | 2055.94 | 8683.45 | 10539.3 | 0.39 | 1.25 | 17.158 | 11.767 | 1 | 1 | 2420 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 3345281.6522 | 211321.1369 | 5703.8078 | 21000.9881 | 190320.1488 | 12945.8887 | 0.092204 | -99964.7213 | 99964.7213
C | Xist Rating 4365 | -27.71 | 1628.49 | 150.288 | 35.6 | 2053.01 | 8632.61 | 10537.8 | 0.39 | 1.25 | 17.141 | 11.776 | 1 | 1 | 2430 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 3343306.2549 | 212984.0614 | 5751.0441 | 21087.7691 | 191896.2923 | 12957.5126 | 0.092585 | -100054.4773 | 100054.4773
C | Xist Rating 4366 | -27.73 | 1629.86 | 150.288 | 35.6 | 2051.26 | 8601.71 | 10537.9 | 0.38 | 1.25 | 17.136 | 11.787 | 1 | 1 | 2440 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 3343266.6236 | 214653.4855 | 5798.4752 | 21174.55 | 193478.9355 | 12952.9773 | 0.092966 | -100019.4571 | 100019.4571
C | Xist Rating 4367 | -27.71 | 1631.18 | 150.288 | 35.6 | 2050.96 | 8596.46 | 10537.9 | 0.38 | 1.25 | 17.131 | 11.798 | 1 | 1 | 2450 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 3345484.9328 | 216329.4091 | 5846.1011 | 21261.331 | 195068.0782 | 12967.1109 | 0.093347 | -100128.5935 | 100128.5935
C | Xist Rating 4368 | -27.69 | 1632.66 | 150.288 | 35.6 | 2050.4 | 8586.57 | 10537.9 | 0.37 | 1.25 | 17.125 | 11.809 | 1 | 1 | 2460 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 3347606.064 | 218011.8323 | 5893.9217 | 21348.1119 | 196663.7204 | 12962.3175 | 0.093728 | -100091.5798 | 100091.5798
C | Xist Rating 4369 | -27.66 | 1634.01 | 150.288 | 35.6 | 2050.18 | 8582.71 | 10537.8 | 0.36 | 1.25 | 17.161 | 11.819 | 1 | 1 | 2470 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 3350014.6218 | 219700.7551 | 5941.9372 | 21434.8929 | 198265.8622 | 12958.0173 | 0.094109 | -100058.3748 | 100058.3748
C | Xist Rating 4370 | -27.67 | 1635.36 | 150.288 | 35.6 | 2048.97 | 8561.57 | 10537.9 | 0.36 | 1.25 | 17.16 | 11.83 | 1 | 1 | 2480 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 18 | E | Rod | 3350803.5792 | 221396.1774 | 5990.1474 | 21521.6738 | 199874.5036 | 12972.17 | 0.09449 | -100167.6583 | 100167.6583
C | Xist Rating 4371 | -27.64 | 1636.75 | 150.288 | 35.6 | 2048.66 | 8556.25 | 10537.9 | 0.35 | 1.25 | 17.149 | 11.841 | 1 | 1 | 2490 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3353144.255 | 223098.0993 | 6038.5525 | 21608.4547 | 201489.6445 | 12966.78 | 0.094871 | -100126.0382 | 100126.0382
C | Xist Rating 4372 | -27.61 | 1637.74 | 150.288 | 35.6 | 2049.08 | 8563.57 | 10537.9 | 0.35 | 1.25 | 17.144 | 11.849 | 1 | 1 | 2500 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3355860.2792 | 224806.5207 | 6087.1523 | 21695.2357 | 203111.285 | 12977.5823 | 0.095252 | -100209.4509 | 100209.4509
C | Xist Rating 4373 | -27.59 | 1639.59 | 150.288 | 35.6 | 2048.06 | 8545.75 | 10537.9 | 0.34 | 1.25 | 17.138 | 11.862 | 1 | 1 | 2510 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3357978.6954 | 226521.4417 | 6135.9469 | 21782.0166 | 204739.4251 | 12974.2543 | 0.095633 | -100183.7523 | 100183.7523
C | Xist Rating 4374 | -27.57 | 1641.04 | 150.288 | 35.6 | 2047.83 | 8541.73 | 10537.9 | 0.34 | 1.25 | 17.173 | 11.873 | 1 | 1 | 2520 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3360570.9432 | 228242.8623 | 6184.9363 | 21868.7976 | 206374.0647 | 12989.6338 | 0.096014 | -100302.5094 | 100302.5094
C | Xist Rating 4375 | -27.54 | 1642.38 | 150.288 | 35.6 | 2047.68 | 8539.22 | 10537.8 | 0.33 | 1.25 | 17.165 | 11.883 | 1 | 1 | 2530 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3363068.6784 | 229970.7824 | 6234.1205 | 21955.5785 | 208015.2039 | 12982.8614 | 0.096395 | -100250.2143 | 100250.2143
C | Xist Rating 4376 | -27.51 | 1643.53 | 150.288 | 35.6 | 2047.82 | 8541.59 | 10537.8 | 0.33 | 1.25 | 17.159 | 11.892 | 1 | 1 | 2540 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3365653.6046 | 231705.2021 | 6283.4995 | 22042.3595 | 209662.8426 | 12994.5215 | 0.096776 | -100340.2507 | 100340.2507
C | Xist Rating 4377 | -27.49 | 1645.08 | 150.288 | 35.6 | 2047.35 | 8533.48 | 10537.8 | 0.32 | 1.25 | 17.153 | 11.904 | 1 | 1 | 2550 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3368054.538 | 233446.1213 | 6333.0732 | 22129.1404 | 211316.981 | 12989.689 | 0.097157 | -100302.9352 | 100302.9352
C | Xist Rating 4378 | -27.45 | 1646.53 | 150.289 | 35.6 | 2047.48 | 8535.75 | 10537.8 | 0.32 | 1.25 | 17.162 | 11.914 | 1 | 1 | 2560 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3371237.2444 | 235193.5402 | 6382.8418 | 22215.9213 | 212977.6188 | 13002.8649 | 0.097538 | -100404.6758 | 100404.6758
C | Xist Rating 4379 | -27.46 | 1647.92 | 150.289 | 35.6 | 2046.31 | 8515.55 | 10537.7 | 0.31 | 1.25 | 17.16 | 11.924 | 1 | 1 | 2570 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3372155.1752 | 236947.4585 | 6432.8051 | 22302.7023 | 214644.7562 | 12995.8696 | 0.097919 | -100350.6603 | 100350.6603
C | Xist Rating 4380 | -27.44 | 1649.28 | 150.289 | 35.6 | 2046.03 | 8510.71 | 10537.7 | 0.31 | 1.25 | 17.197 | 11.935 | 1 | 1 | 2580 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3374476.3584 | 238707.8765 | 6482.9633 | 22389.4832 | 216318.3932 | 13011.0041 | 0.0983 | -100467.5246 | 100467.5246
C | Xist Rating 4381 | -27.45 | 1650.64 | 150.289 | 35.6 | 2044.85 | 8490.2 | 10537.6 | 0.3 | 1.25 | 17.194 | 11.945 | 1 | 1 | 2590 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3375311.204 | 240474.794 | 6533.3162 | 22476.2642 | 217998.5298 | 13003.7092 | 0.098681 | -100411.1955 | 100411.1955
C | Xist Rating 4382 | -27.42 | 1651.82 | 150.289 | 35.6 | 2044.98 | 8492.5 | 10537.7 | 0.3 | 1.25 | 17.195 | 11.954 | 1 | 1 | 2600 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3377938.8636 | 242248.211 | 6583.8639 | 22563.0451 | 219685.1659 | 13015.4028 | 0.099062 | -100501.4903 | 100501.4903
C | Xist Rating 4383 | -27.41 | 1653.51 | 150.289 | 35.6 | 2043.77 | 8471.64 | 10537.6 | 0.3 | 1.25 | 17.19 | 11.966 | 1 | 1 | 2610 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3379394.1327 | 244028.1276 | 6634.6064 | 22649.826 | 221378.3016 | 13030.0016 | 0.099443 | -100614.2182 | 100614.2182
C | Xist Rating 4384 | -27.36 | 1654.9 | 150.289 | 35.6 | 2043.74 | 8471.15 | 10537.7 | 0.29 | 1.25 | 17.196 | 11.976 | 1 | 1 | 2620 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3382185.326 | 245814.5438 | 6685.5437 | 22736.607 | 223077.9368 | 13022.7145 | 0.099824 | -100557.9491 | 100557.9491
C | Xist Rating 4385 | -27.33 | 1656.33 | 150.289 | 35.6 | 2043.4 | 8465.28 | 10537.7 | 0.29 | 1.25 | 17.231 | 11.986 | 1 | 1 | 2630 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3384544.722 | 247607.4595 | 6736.6758 | 22823.3879 | 224784.0716 | 13036.5314 | 0.10021 | -100664.6395 | 100664.6395
C | Xist Rating 4386 | -27.31 | 1657.58 | 150.289 | 35.6 | 2043.44 | 8466.1 | 10537.6 | 0.28 | 1.25 | 17.226 | 11.996 | 1 | 1 | 2640 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3387165.2752 | 249406.8748 | 6788.0027 | 22910.1689 | 226496.706 | 13028.5999 | 0.10059 | -100603.3948 | 100603.3948
C | Xist Rating 4387 | -27.27 | 1659.08 | 150.289 | 35.6 | 2043.37 | 8464.81 | 10537.7 | 0.28 | 1.25 | 17.224 | 12.006 | 1 | 1 | 2650 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3390114.2996 | 251212.7897 | 6839.5243 | 22996.9498 | 228215.8399 | 13041.0804 | 0.10097 | -100699.7658 | 100699.7658
C | Xist Rating 4388 | -27.24 | 1660.42 | 150.289 | 35.6 | 2043.47 | 8466.55 | 10537.7 | 0.28 | 1.25 | 17.222 | 12.016 | 1 | 1 | 2660 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3393018.4574 | 253025.2041 | 6891.2408 | 23083.7308 | 229941.4733 | 13053.5603 | 0.10135 | -100796.1329 | 100796.1329
C | Xist Rating 4389 | -27.21 | 1661.81 | 150.289 | 35.6 | 2043.37 | 8464.92 | 10537.6 | 0.27 | 1.25 | 17.218 | 12.026 | 1 | 1 | 2670 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3395692.6997 | 254844.1181 | 6943.152 | 23170.5117 | 231673.6064 | 13045.366 | 0.10173 | -100732.8582 | 100732.8582
C | Xist Rating 4390 | -27.2 | 1663.22 | 150.289 | 35.6 | 2042.32 | 8446.77 | 10537.7 | 0.27 | 1.25 | 17.255 | 12.036 | 1 | 1 | 2680 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3396827.4704 | 256669.5316 | 6995.258 | 23257.2926 | 233412.239 | 13059.0349 | 0.10211 | -100838.406 | 100838.406
C | Xist Rating 4391 | -27.16 | 1664.6 | 150.289 | 35.6 | 2042.83 | 8455.65 | 10537.6 | 0.26 | 1.25 | 17.25 | 12.046 | 1 | 1 | 2690 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3400494.818 | 258501.4447 | 7047.5588 | 23344.0736 | 235157.3711 | 13050.5457 | 0.10249 | -100772.8543 | 100772.8543
C | Xist Rating 4392 | -27.12 | 1665.8 | 150.289 | 35.6 | 2043.42 | 8465.68 | 10537.5 | 0.26 | 1.25 | 17.245 | 12.055 | 1 | 1 | 2700 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3403929.036 | 260339.8574 | 7100.0544 | 23430.8545 | 236909.0029 | 13061.7452 | 0.10287 | -100859.3342 | 100859.3342
C | Xist Rating 4393 | -27.07 | 1667.46 | 150.289 | 35.6 | 2043.2 | 8462.03 | 10537.6 | 0.26 | 1.25 | 17.242 | 12.066 | 1 | 1 | 2710 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3406954.272 | 262184.7696 | 7152.7448 | 23517.6355 | 238667.1342 | 13075.0837 | 0.10325 | -100962.3308 | 100962.3308
C | Xist Rating 4394 | -27.08 | 1668.8 | 150.289 | 35.6 | 2042.03 | 8441.86 | 10537.6 | 0.26 | 1.25 | 17.234 | 12.075 | 1 | 1 | 2720 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3407739.664 | 264036.1814 | 7205.63 | 23604.4164 | 240431.765 | 13086.1861 | 0.10363 | -101048.0601 | 101048.0601
C | Xist Rating 4395 | -27.05 | 1670.12 | 150.289 | 35.6 | 2041.78 | 8437.58 | 10537.6 | 0.25 | 1.25 | 17.273 | 12.085 | 1 | 1 | 2730 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3410017.6136 | 265894.0928 | 7258.71 | 23691.1974 | 242202.8954 | 13078.6832 | 0.10402 | -100990.1252 | 100990.1252
C | Xist Rating 4396 | -27.07 | 1671.41 | 150.289 | 35.6 | 2040.63 | 8418.14 | 10537.6 | 0.25 | 1.25 | 17.263 | 12.094 | 1 | 1 | 2740 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3410729.3883 | 267758.5037 | 7311.9847 | 23777.9783 | 243980.5254 | 13089.6583 | 0.1044 | -101074.8718 | 101074.8718
C | Xist Rating 4397 | -27.05 | 1672.95 | 150.289 | 35.6 | 2039.89 | 8405.46 | 10537.6 | 0.25 | 1.25 | 17.261 | 12.104 | 1 | 1 | 2750 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3412633.9755 | 269629.4141 | 7365.4543 | 23864.7592 | 245764.6549 | 13101.9162 | 0.10478 | -101169.5238 | 101169.5238
C | Xist Rating 4398 | -27.02 | 1674.38 | 150.289 | 35.6 | 2039.62 | 8400.95 | 10537.6 | 0.24 | 1.25 | 17.262 | 12.114 | 1 | 1 | 2760 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3415098.9356 | 271506.8242 | 7419.1186 | 23951.5402 | 247555.284 | 13092.9105 | 0.10516 | -101099.9846 | 101099.9846
C | Xist Rating 4399 | -27.03 | 1675.61 | 150.289 | 35.6 | 2038.55 | 8382.72 | 10537.6 | 0.24 | 1.25 | 17.256 | 12.123 | 1 | 1 | 2770 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3415814.7655 | 273390.7338 | 7472.9777 | 24038.3211 | 249352.4126 | 13103.9353 | 0.10554 | -101185.1145 | 101185.1145
C | Xist Rating 4400 | -27 | 1677.16 | 150.289 | 35.6 | 2038.26 | 8377.88 | 10537.6 | 0.24 | 1.25 | 17.297 | 12.134 | 1 | 1 | 2780 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3418488.1416 | 275281.1429 | 7527.0316 | 24125.1021 | 251156.0408 | 13118.4413 | 0.10592 | -101297.1265 | 101297.1265
C | Xist Rating 4401 | -27 | 1678.57 | 150.289 | 35.6 | 2037.32 | 8362.01 | 10537.6 | 0.23 | 1.25 | 17.291 | 12.143 | 1 | 1 | 2790 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3419784.2324 | 277178.0516 | 7581.2803 | 24211.883 | 252966.1686 | 13107.8442 | 0.1063 | -101215.2987 | 101215.2987
C | Xist Rating 4402 | -26.9 | 1679.55 | 150.289 | 35.6 | 2039.48 | 8398.46 | 10537.7 | 0.23 | 1.25 | 17.298 | 12.151 | 1 | 1 | 2800 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3425408.634 | 279081.4599 | 7635.7238 | 24298.664 | 254782.796 | 13118.1369 | 0.10668 | -101294.7763 | 101294.7763
C | Xist Rating 4403 | -26.86 | 1681.29 | 150.289 | 35.6 | 2039.26 | 8394.76 | 10537.7 | 0.23 | 1.25 | 17.304 | 12.162 | 1 | 1 | 2810 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3428587.4454 | 280991.3678 | 7690.3621 | 24385.4449 | 256605.9228 | 13131.5176 | 0.10706 | -101398.0982 | 101398.0982
C | Xist Rating 4404 | -26.87 | 1682.77 | 150.289 | 35.6 | 2037.84 | 8370.76 | 10537.7 | 0.23 | 1.25 | 17.3 | 12.172 | 1 | 1 | 2820 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3429216.0168 | 282907.7752 | 7745.1952 | 24472.2258 | 258435.5493 | 13143.5703 | 0.10744 | -101491.1658 | 101491.1658
C | Xist Rating 4405 | -26.65 | 1684.14 | 150.289 | 35.6 | 2043.13 | 8460.66 | 10537.8 | 0.22 | 1.25 | 17.374 | 12.182 | 1 | 1 | 2830 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3440916.9582 | 284830.6821 | 7800.223 | 24559.0068 | 260271.6753 | 13135.8583 | 0.10783 | -101431.6161 | 101431.6161
C | Xist Rating 4406 | -26.16 | 1685.45 | 150.289 | 35.6 | 2055.95 | 8684.67 | 10538.1 | 0.22 | 1.25 | 17.451 | 12.192 | 1 | 1 | 2840 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3465200.9275 | 286760.0886 | 7855.4457 | 24645.7877 | 262114.3009 | 13150.1131 | 0.10821 | -101541.6879 | 101541.6879
C | Xist Rating 4407 | -26.56 | 1686.9 | 150.289 | 35.6 | 2043.51 | 8466.98 | 10537.9 | 0.22 | 1.25 | 17.378 | 12.201 | 1 | 1 | 2850 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3447197.019 | 288695.9947 | 7910.8631 | 24732.5687 | 263963.426 | 13159.1289 | 0.10859 | -101611.305 | 101611.305
C | Xist Rating 4408 | -26.02 | 1688.3 | 150.289 | 35.6 | 2057.94 | 8720.21 | 10538.1 | 0.21 | 1.25 | 17.467 | 12.211 | 1 | 1 | 2860 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3474420.102 | 290638.4004 | 7966.4753 | 24819.3496 | 265819.0507 | 13151.3453 | 0.10897 | -101551.2021 | 101551.2021
C | Xist Rating 4409 | -25.53 | 1689.49 | 150.289 | 35.6 | 2071.14 | 8962.16 | 10538.2 | 0.21 | 1.25 | 17.528 | 12.221 | 1 | 1 | 2870 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3499170.3186 | 292587.3056 | 8022.2824 | 24906.1306 | 267681.175 | 13165.0224 | 0.10935 | -101656.8134 | 101656.8134
C | Xist Rating 4410 | -25.3 | 1691 | 150.289 | 35.6 | 2076.55 | 9064.56 | 10538.1 | 0.21 | 1.25 | 17.59 | 12.231 | 1 | 1 | 2880 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3511446.05 | 294542.7103 | 8078.2842 | 24992.9115 | 269549.7988 | 13178.7382 | 0.10973 | -101762.7227 | 101762.7227
C | Xist Rating 4411 | -25.1 | 1692.35 | 150.289 | 35.6 | 2081.21 | 9153.87 | 10538.1 | 0.2 | 1.25 | 17.606 | 12.24 | 1 | 1 | 2890 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3522135.7435 | 296504.6147 | 8134.4807 | 25079.6924 | 271424.9222 | 13167.3683 | 0.11011 | -101674.9277 | 101674.9277
C | Xist Rating 4412 | -24.96 | 1693.73 | 150.289 | 35.6 | 2084.07 | 9209.56 | 10538.1 | 0.2 | 1.25 | 17.615 | 12.25 | 1 | 1 | 2900 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3529851.8811 | 298473.0185 | 8190.8721 | 25166.4734 | 273306.5451 | 13179.5656 | 0.11049 | -101769.1123 | 101769.1123
C | Xist Rating 4413 | -24.85 | 1695.27 | 150.289 | 35.6 | 2086.13 | 9249.97 | 10538.1 | 0.2 | 1.25 | 17.624 | 12.26 | 1 | 1 | 2910 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3536553.6051 | 300447.922 | 8247.4583 | 25253.2543 | 275194.6677 | 13191.7646 | 0.11087 | -101863.3093 | 101863.3093
C | Xist Rating 4414 | -24.68 | 1696.66 | 150.289 | 35.6 | 2089.79 | 9322.3 | 10538.1 | 0.2 | 1.25 | 17.636 | 12.269 | 1 | 1 | 2920 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3545663.1014 | 302429.325 | 8304.2393 | 25340.0353 | 277089.2897 | 13203.0052 | 0.11125 | -101950.1063 | 101950.1063
C | Xist Rating 4415 | -24.55 | 1698.05 | 150.289 | 35.6 | 2092.43 | 9375.09 | 10538.1 | 0.19 | 1.25 | 17.685 | 12.279 | 1 | 1 | 2930 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3553050.7615 | 304417.2276 | 8361.215 | 25426.8162 | 278990.4113 | 13193.0315 | 0.11164 | -101873.0922 | 101873.0922
C | Xist Rating 4416 | -24.31 | 1699.41 | 150.289 | 35.5 | 2098.35 | 9495.12 | 10538 | 0.19 | 1.25 | 17.703 | 12.288 | 1 | 1 | 2940 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3565956.9735 | 306411.6297 | 8418.3855 | 25513.5972 | 280898.0325 | 13204.3349 | 0.11202 | -101960.3737 | 101960.3737
C | Xist Rating 4417 | -24.14 | 1700.82 | 150.289 | 35.5 | 2102.26 | 9575.96 | 10537.9 | 0.19 | 1.25 | 17.704 | 12.298 | 1 | 1 | 2950 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3575565.8532 | 308412.5314 | 8475.7509 | 25600.3781 | 282812.1533 | 13216.2527 | 0.1124 | -102052.4 | 102052.4
C | Xist Rating 4418 | -24.13 | 1702.19 | 150.289 | 35.5 | 2101.58 | 9561.77 | 10537.9 | 0.19 | 1.25 | 17.7 | 12.307 | 1 | 1 | 2960 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3577288.4602 | 310419.9326 | 8533.311 | 25687.159 | 284732.7736 | 13227.0061 | 0.11278 | -102135.4352 | 102135.4352
C | Xist Rating 4419 | -24.12 | 1703.58 | 150.289 | 35.5 | 2100.88 | 9547.26 | 10537.9 | 0.18 | 1.25 | 17.697 | 12.316 | 1 | 1 | 2970 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3579017.1504 | 312433.8335 | 8591.0659 | 25773.94 | 286659.8935 | 13214.2243 | 0.11316 | -102036.7374 | 102036.7374
C | Xist Rating 4420 | -24.11 | 1704.8 | 150.289 | 35.5 | 2100.27 | 9534.7 | 10537.9 | 0.18 | 1.25 | 17.734 | 12.324 | 1 | 1 | 2980 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3580540.296 | 314454.2338 | 8649.0156 | 25860.7209 | 288593.5129 | 13224.8498 | 0.11354 | -102118.7845 | 102118.7845
C | Xist Rating 4421 | -24.08 | 1706.36 | 150.289 | 35.5 | 2099.67 | 9522.41 | 10537.9 | 0.18 | 1.25 | 17.729 | 12.334 | 1 | 1 | 2990 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3582792.9012 | 316481.1338 | 8707.16 | 25947.5019 | 290533.6319 | 13236.545 | 0.11392 | -102209.0919 | 102209.0919
C | Xist Rating 4422 | -24.07 | 1707.79 | 150.289 | 35.5 | 2099.02 | 9508.95 | 10537.9 | 0.18 | 1.25 | 17.725 | 12.343 | 1 | 1 | 3000 | 152.4 | 2 | 3.1 | 19.05 | 1.3333 | 17 | E | Rod | 3584685.3658 | 318514.5333 | 8765.4993 | 26034.2828 | 292480.2505 | 13247.2251 | 0.1143 | -102291.5609 | 102291.5609
C | Xist Rating 4423 | -90.8 | 167.973 | 150.293 | 35.8 | 2388.45 | 7298.75 | 58745.9 | 2.45 | 10.95 | 18.999 | 457.655 | 1 | 1 | 1000 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 20 | E | Rod | 401195.1118 | 42504.1547 | 973.9444 | 8958.0328 | 33546.1219 | 477360.4715 | 0.038101 | -3686051.0269 | 3686051.0269
C | Xist Rating 4424 | -90.72 | 169.728 | 150.293 | 35.8 | 2385.82 | 7282.47 | 58283.6 | 2.44 | 10.85 | 19.043 | 449.071 | 1 | 1 | 1010 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 20 | E | Rod | 404940.457 | 43268.0121 | 993.5206 | 9047.6131 | 34220.399 | 468463.125 | 0.038482 | -3617348.0753 | 3617348.0753
C | Xist Rating 4425 | -90.03 | 182.955 | 150.293 | 35.8 | 2379.11 | 7282.85 | 54967.7 | 2.45 | 10.07 | 19.097 | 389.171 | 1 | 1 | 1020 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 20 | E | Rod | 435270.0701 | 44038.5787 | 1013.2917 | 9137.1935 | 34901.3852 | 406292.653 | 0.038863 | -3137284.1703 | 3137284.1703
C | Xist Rating 4426 | -89.92 | 186.611 | 150.292 | 35.8 | 2359.84 | 7120.69 | 54178.5 | 2.36 | 9.89 | 18.684 | 376.162 | 1 | 1 | 1030 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 20 | E | Rod | 440372.1022 | 44815.8545 | 1033.2576 | 9226.7738 | 35589.0807 | 392679.4464 | 0.039244 | -3032166.5972 | 3032166.5972
C | Xist Rating 4427 | -89.85 | 188.441 | 150.292 | 35.8 | 2353.85 | 7074.04 | 53793.7 | 2.32 | 9.8 | 18.584 | 369.939 | 1 | 1 | 1040 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 20 | E | Rod | 443561.8478 | 45599.8396 | 1053.4182 | 9316.3541 | 36283.4855 | 386190.9804 | 0.039625 | -2982064.3825 | 2982064.3825
C | Xist Rating 4428 | -89.67 | 191.975 | 150.292 | 35.8 | 2353.38 | 7084.96 | 53043.5 | 2.28 | 9.63 | 18.528 | 357.709 | 1 | 1 | 1050 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 20 | E | Rod | 451790.1255 | 46390.5338 | 1073.7737 | 9405.9344 | 36984.5994 | 373468.4745 | 0.040006 | -2883824.5648 | 2883824.5648
C | Xist Rating 4429 | -89.51 | 193.786 | 150.292 | 35.8 | 2367.65 | 7223.73 | 52676.8 | 2.23 | 9.54 | 18.522 | 351.931 | 1 | 1 | 1060 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 20 | E | Rod | 458817.4229 | 47187.9373 | 1094.3239 | 9495.5148 | 37692.4226 | 367442.3135 | 0.040387 | -2837292.1466 | 2837292.1466
C | Xist Rating 4430 | -88.83 | 208.045 | 150.291 | 35.8 | 2348.49 | 7110.16 | 49857.3 | 2.21 | 8.9 | 18.269 | 307.952 | 1 | 1 | 1070 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 488591.602 | 47992.0501 | 1115.0689 | 9585.0951 | 38406.955 | 321744.1216 | 0.040768 | -2484422.8216 | 2484422.8216
C | Xist Rating 4431 | -88.66 | 210.764 | 150.291 | 35.8 | 2355.57 | 7186.93 | 49380.8 | 2.16 | 8.79 | 18.191 | 301.076 | 1 | 1 | 1080 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 496469.3555 | 48802.872 | 1136.0087 | 9674.6754 | 39128.1966 | 314569.1272 | 0.041149 | -2429019.4175 | 2429019.4175
C | Xist Rating 4432 | -88.46 | 214.379 | 150.291 | 35.8 | 2358.07 | 7225.69 | 48761.1 | 2.1 | 8.65 | 18.066 | 292.233 | 1 | 1 | 1090 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 505520.6885 | 49620.4032 | 1157.1433 | 9764.2557 | 39856.1474 | 305337.1455 | 0.04153 | -2357732.5018 | 2357732.5018
C | Xist Rating 4433 | -88.28 | 217.066 | 150.291 | 35.8 | 2365.17 | 7304.55 | 48308.1 | 2.06 | 8.55 | 18.063 | 285.849 | 1 | 1 | 1100 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 513397.9912 | 50444.6436 | 1178.4727 | 9853.8361 | 40590.8075 | 298688.4414 | 0.041911 | -2306392.9713 | 2306392.9713
C | Xist Rating 4434 | -88.2 | 219.064 | 150.29 | 35.8 | 2360.17 | 7264.83 | 48011.4 | 1.98 | 8.49 | 17.817 | 281.972 | 1 | 1 | 1110 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 517028.2809 | 51275.5932 | 1199.9969 | 9943.4164 | 41332.1768 | 294582.7289 | 0.042292 | -2274689.7473 | 2274689.7473
C | Xist Rating 4435 | -87.37 | 234.903 | 150.291 | 35.8 | 2357.26 | 7308.79 | 45448.3 | 2.02 | 7.92 | 18.037 | 246.724 | 1 | 1 | 1120 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 553727.4458 | 52113.2521 | 1221.7158 | 10032.9967 | 42080.2553 | 258051.6393 | 0.042673 | -1992606.3568 | 1992606.3568
C | Xist Rating 4436 | -87.27 | 236.855 | 150.29 | 35.8 | 2357.96 | 7323.38 | 45189.1 | 1.96 | 7.86 | 17.876 | 243.587 | 1 | 1 | 1130 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 558494.6158 | 52957.6201 | 1243.6296 | 10122.5771 | 42835.0431 | 254739.4014 | 0.043054 | -1967030.1334 | 1967030.1334
C | Xist Rating 4437 | -87.1 | 240.54 | 150.29 | 35.8 | 2353.9 | 7299.66 | 44681.9 | 1.91 | 7.75 | 17.733 | 237.262 | 1 | 1 | 1140 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 566207.106 | 53808.6974 | 1265.7381 | 10212.1574 | 43596.54 | 248126.9738 | 0.043435 | -1915970.7206 | 1915970.7206
C | Xist Rating 4438 | -86.92 | 244.163 | 150.29 | 35.8 | 2353.45 | 7310.75 | 44186.8 | 1.87 | 7.64 | 17.585 | 231.128 | 1 | 1 | 1150 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 574625.4123 | 54666.484 | 1288.0414 | 10301.7377 | 44364.7462 | 241721.1758 | 0.043816 | -1866506.8467 | 1866506.8467
C | Xist Rating 4439 | -86.72 | 247.864 | 150.289 | 35.8 | 2354 | 7331.51 | 43704.1 | 1.82 | 7.53 | 17.468 | 225.305 | 1 | 1 | 1160 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 583471.856 | 55530.9797 | 1310.5395 | 10391.318 | 45139.6617 | 235631.9495 | 0.044197 | -1819487.455 | 1819487.455
C | Xist Rating 4440 | -85.97 | 262.11 | 150.29 | 35.8 | 2353.39 | 7389.34 | 41832.9 | 1.83 | 7.13 | 17.597 | 202.68 | 1 | 1 | 1170 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 616847.0529 | 56402.1847 | 1333.2324 | 10480.8984 | 45921.2863 | 212171.715 | 0.044578 | -1638333.7431 | 1638333.7431
C | Xist Rating 4441 | -85.87 | 263.178 | 150.289 | 35.8 | 2361.65 | 7475.25 | 41725.3 | 1.78 | 7.11 | 17.532 | 201.607 | 1 | 1 | 1180 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 621534.3237 | 57280.0989 | 1356.1201 | 10570.4787 | 46709.6202 | 211019.1832 | 0.044959 | -1629434.1976 | 1629434.1976
C | Xist Rating 4442 | -85.55 | 270.409 | 150.289 | 35.8 | 2351.96 | 7410.03 | 40886.3 | 1.73 | 6.93 | 17.398 | 192.185 | 1 | 1 | 1190 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 635991.1516 | 58164.7223 | 1379.2026 | 10660.059 | 47504.6632 | 201189.3149 | 0.04534 | -1553530.5602 | 1553530.5602
C | Xist Rating 4443 | -85.38 | 272.252 | 150.289 | 35.8 | 2364.12 | 7540.1 | 40682.7 | 1.7 | 6.88 | 17.426 | 189.992 | 1 | 1 | 1200 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 643636.3982 | 59056.0549 | 1402.4799 | 10749.6394 | 48306.4156 | 198899.8649 | 0.045721 | -1535852.0341 | 1535852.0341
C | Xist Rating 4444 | -85.21 | 276.023 | 150.289 | 35.8 | 2360.09 | 7515.11 | 40281.9 | 1.65 | 6.8 | 17.312 | 185.733 | 1 | 1 | 1210 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 651439.1221 | 59954.0968 | 1425.9519 | 10839.2197 | 49114.8771 | 194432.7195 | 0.046102 | -1501357.9216 | 1501357.9216
C | Xist Rating 4445 | -84.43 | 292.216 | 150.289 | 35.8 | 2347.79 | 7463 | 38538.1 | 1.65 | 6.43 | 17.325 | 167.043 | 1 | 1 | 1220 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 686061.8026 | 60858.8479 | 1449.6188 | 10928.8 | 49930.0479 | 175037.1611 | 0.046483 | -1351590.5611 | 1351590.5611
C | Xist Rating 4446 | -84.2 | 295.837 | 150.289 | 35.8 | 2354.16 | 7543.55 | 38183.3 | 1.63 | 6.35 | 17.331 | 163.475 | 1 | 1 | 1230 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 696447.6319 | 61770.3082 | 1473.4804 | 11018.3803 | 50751.9278 | 171326.0476 | 0.046864 | -1322934.3264 | 1322934.3264
C | Xist Rating 4447 | -84.01 | 299.597 | 150.289 | 35.8 | 2353.46 | 7552.07 | 37835.8 | 1.59 | 6.28 | 17.251 | 160.092 | 1 | 1 | 1240 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 705089.5556 | 62688.4777 | 1497.5369 | 11107.9607 | 51580.5171 | 167779.8681 | 0.047245 | -1295551.6678 | 1295551.6678
C | Xist Rating 4448 | -83.89 | 301.585 | 150.289 | 35.8 | 2356.6 | 7592.51 | 37664.5 | 1.55 | 6.24 | 17.195 | 158.511 | 1 | 1 | 1250 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 710715.211 | 63613.3565 | 1521.7881 | 11197.541 | 52415.8155 | 166106.7701 | 0.047626 | -1282632.4487 | 1282632.4487
C | Xist Rating 4449 | -83.62 | 307.039 | 150.289 | 35.8 | 2355.15 | 7601.32 | 37161.5 | 1.52 | 6.14 | 17.159 | 153.61 | 1 | 1 | 1260 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 723122.9008 | 64544.9445 | 1546.2341 | 11287.1213 | 53257.8232 | 160996.8109 | 0.048007 | -1243174.698 | 1243174.698
C | Xist Rating 4450 | -82.86 | 322.38 | 150.289 | 35.8 | 2348.07 | 7596.44 | 35778 | 1.53 | 5.85 | 17.218 | 140.308 | 1 | 1 | 1270 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 756970.8066 | 65483.2417 | 1570.8749 | 11376.7017 | 54106.54 | 147209.3029 | 0.048388 | -1136711.2162 | 1136711.2162
C | Xist Rating 4451 | -82.69 | 326.209 | 150.288 | 35.8 | 2344.51 | 7574.9 | 35477.6 | 1.49 | 5.79 | 17.133 | 137.668 | 1 | 1 | 1280 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 764800.2626 | 66428.2481 | 1595.7105 | 11466.282 | 54961.9661 | 144432.6932 | 0.048769 | -1115270.9718 | 1115270.9718
C | Xist Rating 4452 | -82.5 | 329.986 | 150.288 | 35.8 | 2344.15 | 7586.74 | 35183 | 1.45 | 5.73 | 17.106 | 135.085 | 1 | 1 | 1290 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 773536.6819 | 67379.9638 | 1620.7408 | 11555.8623 | 55824.1015 | 141719.8031 | 0.04915 | -1094322.7535 | 1094322.7535
C | Xist Rating 4453 | -82.17 | 335.418 | 150.288 | 35.8 | 2350.41 | 7676.56 | 34751.5 | 1.43 | 5.64 | 17.136 | 131.255 | 1 | 1 | 1300 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 788369.8214 | 68338.3887 | 1645.966 | 11645.4426 | 56692.946 | 137736.0361 | 0.049531 | -1063561.1612 | 1063561.1612
C | Xist Rating 4454 | -81.99 | 338.33 | 150.288 | 35.8 | 2355.58 | 7744.08 | 34540.2 | 1.39 | 5.59 | 17.097 | 129.487 | 1 | 1 | 1310 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 796963.3814 | 69303.5228 | 1671.3859 | 11735.023 | 57568.4998 | 135867.5225 | 0.049912 | -1049132.9943 | 1049132.9943
C | Xist Rating 4455 | -81.22 | 353.769 | 150.288 | 35.8 | 2350.38 | 7758.23 | 33363.4 | 1.39 | 5.35 | 17.146 | 119.271 | 1 | 1 | 1320 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 831491.5822 | 70275.3661 | 1697.0007 | 11824.6033 | 58450.7628 | 125272.9051 | 0.050293 | -967324.1673 | 967324.1673
C | Xist Rating 4456 | -80.95 | 359.418 | 150.288 | 35.8 | 2347.23 | 7748.01 | 32980.2 | 1.36 | 5.28 | 17.028 | 116.18 | 1 | 1 | 1330 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 843636.7121 | 71253.9187 | 1722.8102 | 11914.1836 | 59339.7351 | 122033.3566 | 0.050674 | -942309.232 | 942309.232
C | Xist Rating 4457 | -80.65 | 364.966 | 150.288 | 35.8 | 2349.41 | 7796 | 32607.5 | 1.33 | 5.2 | 17.001 | 113.188 | 1 | 1 | 1340 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 857454.7701 | 72239.1805 | 1748.8145 | 12003.7639 | 60235.4165 | 118903.7093 | 0.051055 | -918142.9251 | 918142.9251
C | Xist Rating 4458 | -80.47 | 367.894 | 150.288 | 35.7 | 2353.64 | 7854.98 | 32424.4 | 1.3 | 5.16 | 16.97 | 111.793 | 1 | 1 | 1350 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 865890.0342 | 73231.1515 | 1775.0136 | 12093.3443 | 61137.8072 | 117431.8372 | 0.051436 | -906777.5188 | 906777.5188
C | Xist Rating 4459 | -80.26 | 369.685 | 150.288 | 35.7 | 2368.75 | 8034.46 | 32303.8 | 1.29 | 5.14 | 17.029 | 110.842 | 1 | 1 | 1360 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 875691.3438 | 74229.8317 | 1801.4075 | 12182.9246 | 62046.9071 | 116448.4085 | 0.051817 | -899183.7437 | 899183.7437
C | Xist Rating 4460 | -79.31 | 391.671 | 150.288 | 35.7 | 2343.22 | 7846.27 | 30902.9 | 1.28 | 4.86 | 16.983 | 99.918 | 1 | 1 | 1370 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 917771.3206 | 75235.2212 | 1827.9962 | 12272.5049 | 62962.7162 | 105099.6254 | 0.052198 | -811551.4481 | 811551.4481
C | Xist Rating 4461 | -79.22 | 393.723 | 150.288 | 35.7 | 2342.85 | 7850.11 | 30794.4 | 1.25 | 4.84 | 16.951 | 99.182 | 1 | 1 | 1380 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 922433.9306 | 76247.3198 | 1854.7797 | 12362.0853 | 63885.2346 | 104311.0442 | 0.052579 | -805462.2338 | 805462.2338
C | Xist Rating 4462 | -78.98 | 398.465 | 150.288 | 35.7 | 2343.11 | 7873.24 | 30527.3 | 1.23 | 4.78 | 16.919 | 97.261 | 1 | 1 | 1390 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 933647.3261 | 77266.1277 | 1881.7579 | 12451.6656 | 64814.4622 | 102302.0111 | 0.05296 | -789949.0126 | 789949.0126
C | Xist Rating 4463 | -78.73 | 403.203 | 150.288 | 35.7 | 2343.82 | 7901.6 | 30265.5 | 1.2 | 4.73 | 16.893 | 95.397 | 1 | 1 | 1400 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 945035.2555 | 78291.6449 | 1908.931 | 12541.2459 | 65750.399 | 100341.768 | 0.053341 | -774812.5348 | 774812.5348
C | Xist Rating 4464 | -78.44 | 408.811 | 150.288 | 35.7 | 2344.39 | 7932.53 | 29957.8 | 1.18 | 4.67 | 16.875 | 93.215 | 1 | 1 | 1410 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 958412.4203 | 79323.8712 | 1936.2988 | 12630.8262 | 66693.045 | 98062.155 | 0.053722 | -757209.9676 | 757209.9676
C | Xist Rating 4465 | -77.62 | 425.248 | 150.288 | 35.7 | 2340.46 | 7962.93 | 29052.1 | 1.19 | 4.49 | 16.939 | 86.76 | 1 | 1 | 1420 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 995275.9341 | 80362.8068 | 1963.8614 | 12720.4066 | 67642.4002 | 91383.1622 | 0.054103 | -705636.5554 | 705636.5554
C | Xist Rating 4466 | -77.5 | 428.417 | 150.288 | 35.7 | 2337.2 | 7937.45 | 28910.9 | 1.15 | 4.47 | 16.871 | 85.891 | 1 | 1 | 1430 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1001296.2124 | 81408.4516 | 1991.6188 | 12809.9869 | 68598.4647 | 90441.2989 | 0.054484 | -698363.7368 | 698363.7368
C | Xist Rating 4467 | -77.14 | 435.816 | 150.288 | 35.7 | 2335.15 | 7946.2 | 28542.4 | 1.14 | 4.39 | 16.857 | 83.421 | 1 | 1 | 1440 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1017695.7324 | 82460.8056 | 2019.571 | 12899.5672 | 69561.2384 | 87872.9845 | 0.054865 | -678531.8941 | 678531.8941
C | Xist Rating 4468 | -76.89 | 440.592 | 150.288 | 35.7 | 2335.69 | 7972.78 | 28317.1 | 1.12 | 4.35 | 16.835 | 81.969 | 1 | 1 | 1450 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1029086.3285 | 83519.8689 | 2047.718 | 12989.1476 | 70530.7213 | 86350.1846 | 0.055246 | -666773.2368 | 666773.2368
C | Xist Rating 4469 | -76.69 | 443.402 | 150.288 | 35.7 | 2342.76 | 8068.23 | 28183.8 | 1.1 | 4.32 | 16.853 | 81.116 | 1 | 1 | 1460 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1038784.4695 | 84585.6414 | 2076.0598 | 13078.7279 | 71506.9135 | 85452.0581 | 0.055627 | -659838.1414 | 659838.1414
C | Xist Rating 4470 | -75.88 | 462.057 | 150.288 | 35.7 | 2326.99 | 7966.23 | 27310.5 | 1.09 | 4.16 | 16.844 | 75.458 | 1 | 1 | 1470 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1075202.0184 | 85658.1231 | 2104.5964 | 13168.3082 | 72489.8148 | 79572.7925 | 0.056008 | -614440.0113 | 614440.0113
C | Xist Rating 4471 | -75.59 | 467.71 | 150.288 | 35.7 | 2327.21 | 7993.07 | 27066.2 | 1.08 | 4.11 | 16.831 | 73.963 | 1 | 1 | 1480 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1088459.3891 | 86737.314 | 2133.3277 | 13257.8885 | 73479.4254 | 78016.3613 | 0.056389 | -602421.6624 | 602421.6624
C | Xist Rating 4472 | -75.33 | 472.487 | 150.288 | 35.7 | 2328.74 | 8031.44 | 26866.9 | 1.06 | 4.07 | 16.823 | 72.767 | 1 | 1 | 1490 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1100299.3764 | 87823.2141 | 2162.2539 | 13347.4689 | 74475.7453 | 76759.4164 | 0.05677 | -592715.867 | 592715.867
C | Xist Rating 4473 | -75.06 | 477.357 | 150.288 | 35.7 | 2331.43 | 8084.06 | 26670.5 | 1.04 | 4.03 | 16.806 | 71.615 | 1 | 1 | 1500 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1112924.4305 | 88915.8235 | 2191.3748 | 13437.0492 | 75478.7743 | 75547.2483 | 0.057151 | -583355.8257 | 583355.8257
C | Xist Rating 4474 | -74.72 | 483.037 | 150.288 | 35.7 | 2336.75 | 8173.55 | 26439 | 1.02 | 3.99 | 16.807 | 70.245 | 1 | 1 | 1510 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1128736.7097 | 90015.1421 | 2220.6906 | 13526.6295 | 76488.5126 | 74109.6587 | 0.057532 | -572255.1399 | 572255.1399
C | Xist Rating 4475 | -73.8 | 501.375 | 150.288 | 35.7 | 2334.32 | 8229.92 | 25681.2 | 1.03 | 3.85 | 16.881 | 65.7 | 1 | 1 | 1520 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1170369.69 | 91121.1699 | 2250.2011 | 13616.2099 | 77504.9601 | 69414.012 | 0.057913 | -535996.6013 | 535996.6013
C | Xist Rating 4476 | -73.56 | 507.398 | 150.288 | 35.7 | 2328.12 | 8178.27 | 25468.5 | 1 | 3.8 | 16.823 | 64.548 | 1 | 1 | 1530 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1181283.4318 | 92233.907 | 2279.9064 | 13705.7902 | 78528.1168 | 68186.7461 | 0.058294 | -526519.9793 | 526519.9793
C | Xist Rating 4477 | -73.35 | 510.483 | 150.288 | 35.7 | 2333.5 | 8257.72 | 25363.7 | 0.98 | 3.78 | 16.814 | 64.001 | 1 | 1 | 1540 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1191212.0805 | 93353.3532 | 2309.8065 | 13795.3705 | 79557.9827 | 67602.3937 | 0.058675 | -522007.7646 | 522007.7646
C | Xist Rating 4478 | -72.9 | 519.798 | 150.288 | 35.7 | 2332.02 | 8281.68 | 25021.2 | 0.96 | 3.72 | 16.809 | 62.088 | 1 | 1 | 1550 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1212179.332 | 94479.5087 | 2339.9013 | 13884.9508 | 80594.5579 | 65599.4347 | 0.059056 | -506541.4459 | 506541.4459
C | Xist Rating 4479 | -72.62 | 522.658 | 150.288 | 35.7 | 2343.84 | 8445.8 | 24920.6 | 0.95 | 3.7 | 16.837 | 61.552 | 1 | 1 | 1560 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1225026.7267 | 95612.3735 | 2370.191 | 13974.5312 | 81637.8423 | 65040.1388 | 0.059437 | -502222.7116 | 502222.7116
C | Xist Rating 4480 | -71.75 | 544.306 | 150.288 | 35.7 | 2323.32 | 8283.65 | 24162.1 | 0.94 | 3.56 | 16.822 | 57.42 | 1 | 1 | 1570 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1264597.0159 | 96751.9474 | 2400.6755 | 14064.1115 | 82687.8359 | 60743.3918 | 0.059818 | -469044.3704 | 469044.3704
C | Xist Rating 4481 | -71.46 | 549.204 | 150.288 | 35.7 | 2327 | 8351.95 | 24007.6 | 0.93 | 3.53 | 16.816 | 56.639 | 1 | 1 | 1580 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1277997.708 | 97898.2306 | 2431.3547 | 14153.6918 | 83744.5388 | 59927.1035 | 0.0602 | -462741.2084 | 462741.2084
C | Xist Rating 4482 | -71.19 | 554.138 | 150.288 | 35.7 | 2329.06 | 8400.05 | 23855.2 | 0.91 | 3.5 | 16.803 | 55.88 | 1 | 1 | 1590 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1290620.6503 | 99051.223 | 2462.2288 | 14243.2721 | 84807.9508 | 59121.0802 | 0.060581 | -456517.3102 | 456517.3102
C | Xist Rating 4483 | -70.79 | 560.719 | 150.288 | 35.7 | 2334.62 | 8503.67 | 23645.5 | 0.9 | 3.46 | 16.817 | 54.809 | 1 | 1 | 1600 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1309065.7918 | 100210.9246 | 2493.2976 | 14332.8525 | 85878.0721 | 58004.5551 | 0.060962 | -447895.799 | 447895.799
C | Xist Rating 4484 | -70.61 | 563.999 | 150.288 | 35.7 | 2335.79 | 8532.42 | 23556.9 | 0.88 | 3.45 | 16.792 | 54.409 | 1 | 1 | 1610 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1317383.2242 | 101377.3354 | 2524.5612 | 14422.4328 | 86954.9026 | 57570.0795 | 0.061343 | -444540.8937 | 444540.8937
C | Xist Rating 4485 | -69.55 | 588.17 | 150.288 | 35.7 | 2321.82 | 8462.7 | 22805.2 | 0.88 | 3.31 | 16.807 | 50.594 | 1 | 1 | 1620 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1365624.8694 | 102550.4555 | 2556.0196 | 14512.0131 | 88038.4424 | 53615.7903 | 0.061724 | -414006.9205 | 414006.9205
C | Xist Rating 4486 | -69.29 | 591.105 | 150.288 | 35.7 | 2330.76 | 8596.07 | 22723.6 | 0.87 | 3.29 | 16.823 | 50.219 | 1 | 1 | 1630 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1377723.8898 | 103730.2848 | 2587.6728 | 14601.5935 | 89128.6913 | 53221.7202 | 0.062105 | -410964.0156 | 410964.0156
C | Xist Rating 4487 | -69.04 | 596.187 | 150.288 | 35.7 | 2330.52 | 8615.07 | 22589 | 0.85 | 3.27 | 16.799 | 49.607 | 1 | 1 | 1640 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1389425.7272 | 104916.8233 | 2619.5208 | 14691.1738 | 90225.6495 | 52566.486 | 0.062486 | -405904.4712 | 405904.4712
C | Xist Rating 4488 | -68.74 | 603.125 | 150.288 | 35.7 | 2327.49 | 8605.02 | 22403.2 | 0.84 | 3.23 | 16.777 | 48.753 | 1 | 1 | 1650 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1403767.4062 | 106110.071 | 2651.5635 | 14780.7541 | 91329.3169 | 51672.2175 | 0.062867 | -398999.1668 | 398999.1668
C | Xist Rating 4489 | -68.4 | 609.819 | 150.288 | 35.7 | 2327.64 | 8638.37 | 22221.1 | 0.83 | 3.2 | 16.777 | 47.907 | 1 | 1 | 1660 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1419439.0972 | 107310.028 | 2683.8011 | 14870.3344 | 92439.6936 | 50787.4813 | 0.063248 | -392167.468 | 392167.468
C | Xist Rating 4490 | -67.45 | 631.511 | 150.288 | 35.7 | 2316.47 | 8589.04 | 21633.4 | 0.82 | 3.1 | 16.8 | 45.157 | 1 | 1 | 1670 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1462876.2862 | 108516.6942 | 2716.2334 | 14959.9148 | 93556.7794 | 47926.7054 | 0.063629 | -370077.3152 | 370077.3152
C | Xist Rating 4491 | -67.24 | 634.558 | 150.288 | 35.7 | 2321.21 | 8667.98 | 21560.6 | 0.81 | 3.08 | 16.805 | 44.855 | 1 | 1 | 1680 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1472942.3752 | 109730.0696 | 2748.8606 | 15049.4951 | 94680.5745 | 47606.9076 | 0.06401 | -367607.9214 | 367607.9214
C | Xist Rating 4492 | -66.87 | 643.402 | 150.288 | 35.7 | 2316.49 | 8642.34 | 21346.2 | 0.8 | 3.04 | 16.783 | 43.922 | 1 | 1 | 1690 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1490434.299 | 110950.1542 | 2781.6825 | 15139.0754 | 95811.0788 | 46630.0265 | 0.064391 | -360064.7042 | 360064.7042
C | Xist Rating 4493 | -66.54 | 649.238 | 150.288 | 35.7 | 2319.05 | 8705.02 | 21206.1 | 0.79 | 3.02 | 16.782 | 43.32 | 1 | 1 | 1700 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1505615.3839 | 112176.9481 | 2814.6992 | 15228.6558 | 96948.2923 | 45998.0196 | 0.064772 | -355184.5146 | 355184.5146
C | Xist Rating 4494 | -66.21 | 656.125 | 150.288 | 35.7 | 2318.02 | 8721.93 | 21045 | 0.78 | 2.99 | 16.772 | 42.637 | 1 | 1 | 1710 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1520910.8725 | 113410.4512 | 2847.9107 | 15318.2361 | 98092.2151 | 45281.2066 | 0.065153 | -349649.4749 | 349649.4749
C | Xist Rating 4495 | -65.34 | 676.114 | 150.288 | 35.7 | 2308.52 | 8683.68 | 20567.5 | 0.77 | 2.9 | 16.804 | 40.563 | 1 | 1 | 1720 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1560822.6913 | 114650.6635 | 2881.317 | 15407.8164 | 99242.8471 | 43122.1937 | 0.065534 | -332978.1494 | 332978.1494
C | Xist Rating 4496 | -64.95 | 684.829 | 150.288 | 35.6 | 2306.17 | 8690.34 | 20374.3 | 0.76 | 2.87 | 16.793 | 39.769 | 1 | 1 | 1730 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1579332.0949 | 115897.585 | 2914.9181 | 15497.3967 | 100400.1883 | 42289.7466 | 0.065915 | -326550.2137 | 326550.2137
C | Xist Rating 4497 | -64.69 | 688.899 | 150.288 | 35.7 | 2310.17 | 8765.33 | 20290.1 | 0.75 | 2.85 | 16.793 | 39.443 | 1 | 1 | 1740 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1591473.8028 | 117151.2158 | 2948.714 | 15586.9771 | 101564.2387 | 41943.8193 | 0.066296 | -323879.0545 | 323879.0545
C | Xist Rating 4498 | -64.35 | 696.87 | 150.288 | 35.6 | 2307.31 | 8760.31 | 20123.3 | 0.74 | 2.82 | 16.777 | 38.781 | 1 | 1 | 1750 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1607895.1197 | 118411.5558 | 2982.7046 | 15676.5574 | 102734.9984 | 41247.8772 | 0.066677 | -318505.1739 | 318505.1739
C | Xist Rating 4499 | -64.08 | 702.822 | 150.288 | 35.7 | 2305.37 | 8759.06 | 20001.2 | 0.73 | 2.8 | 16.773 | 38.301 | 1 | 1 | 1760 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1620264.7541 | 119678.605 | 3016.8901 | 15766.1377 | 103912.4672 | 40741.4969 | 0.067058 | -314595.0399 | 314595.0399
C | Xist Rating 4500 | -63.05 | 726.508 | 150.288 | 35.7 | 2294.47 | 8715.07 | 19497.8 | 0.73 | 2.71 | 16.81 | 36.259 | 1 | 1 | 1770 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1666950.8108 | 120952.3634 | 3051.2703 | 15855.7181 | 105096.6454 | 38628.5146 | 0.067439 | -298279.1503 | 298279.1503
C | Xist Rating 4501 | -62.95 | 732.571 | 150.288 | 35.6 | 2284.38 | 8596.8 | 19383.8 | 0.72 | 2.69 | 16.985 | 35.826 | 1 | 1 | 1780 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1673470.541 | 122232.8311 | 3085.8453 | 15945.2984 | 106287.5327 | 38180.9863 | 0.06782 | -294823.4552 | 294823.4552
C | Xist Rating 4502 | -62.79 | 735.877 | 150.288 | 35.6 | 2284.78 | 8615.4 | 19327.2 | 0.7 | 2.68 | 16.974 | 35.634 | 1 | 1 | 1790 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1681317.0521 | 123520.0079 | 3120.6151 | 16034.8787 | 107485.1292 | 37959.2022 | 0.068201 | -293110.8978 | 293110.8978
C | Xist Rating 4503 | -62.34 | 746.536 | 150.288 | 35.6 | 2282.43 | 8629.42 | 19121.9 | 0.7 | 2.65 | 16.962 | 34.857 | 1 | 1 | 1800 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1703916.1625 | 124813.894 | 3155.5797 | 16124.459 | 108689.435 | 37156.9372 | 0.068582 | -286916.0197 | 286916.0197
C | Xist Rating 4504 | -62.06 | 752.471 | 150.288 | 35.6 | 2281.92 | 8647.94 | 19012.5 | 0.69 | 2.63 | 16.959 | 34.456 | 1 | 1 | 1810 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1717078.6243 | 126114.4894 | 3190.7391 | 16214.0394 | 109900.45 | 36731.8919 | 0.068963 | -283633.9325 | 283633.9325
C | Xist Rating 4505 | -61.05 | 776.415 | 150.288 | 35.6 | 2270.98 | 8599.86 | 18562.8 | 0.69 | 2.55 | 16.993 | 32.76 | 1 | 1 | 1820 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1763222.9367 | 127421.7939 | 3226.0933 | 16303.6197 | 111118.1742 | 34977.7577 | 0.069344 | -270088.9733 | 270088.9733
C | Xist Rating 4506 | -61.02 | 772.6 | 150.288 | 35.6 | 2285.13 | 8788.87 | 18631.3 | 0.68 | 2.56 | 17.019 | 33.027 | 1 | 1 | 1830 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1765491.438 | 128735.8077 | 3261.6423 | 16393.2 | 112342.6077 | 35247.8036 | 0.069725 | -272174.1963 | 272174.1963
C | Xist Rating 4507 | -60.65 | 777.46 | 150.288 | 35.6 | 2292.34 | 8919.2 | 18545.3 | 0.67 | 2.55 | 17.039 | 32.722 | 1 | 1 | 1840 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1782202.6564 | 130056.5307 | 3297.386 | 16482.7803 | 113573.7504 | 34923.3175 | 0.070106 | -269668.6004 | 269668.6004
C | Xist Rating 4508 | -60.29 | 785.548 | 150.288 | 35.6 | 2290.29 | 8924.49 | 18409.3 | 0.66 | 2.52 | 17.025 | 32.248 | 1 | 1 | 1850 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1799132.7289 | 131383.9629 | 3333.3246 | 16572.3607 | 114811.6023 | 34421.2905 | 0.070487 | -265792.0815 | 265792.0815
C | Xist Rating 4509 | -59.9 | 794.605 | 150.288 | 35.6 | 2286.89 | 8913.72 | 18259.3 | 0.65 | 2.5 | 17.017 | 31.727 | 1 | 1 | 1860 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1817174.2285 | 132718.1044 | 3369.4579 | 16661.941 | 116056.1634 | 33870.6416 | 0.070868 | -261540.1167 | 261540.1167
C | Xist Rating 4510 | -58.91 | 816.575 | 150.288 | 35.6 | 2280.92 | 8929.14 | 17879.8 | 0.65 | 2.43 | 17.065 | 30.366 | 1 | 1 | 1870 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1862542.249 | 134058.9551 | 3405.7861 | 16751.5213 | 117307.4337 | 32464.8186 | 0.071249 | -250684.724 | 250684.724
C | Xist Rating 4511 | -58.52 | 825.618 | 150.288 | 35.6 | 2277.96 | 8924.38 | 17739 | 0.64 | 2.41 | 17.051 | 29.897 | 1 | 1 | 1880 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1880724.7793 | 135406.515 | 3442.309 | 16841.1017 | 118565.4133 | 31967.5991 | 0.07163 | -246845.3268 | 246845.3268
C | Xist Rating 4512 | -58.16 | 831.601 | 150.288 | 35.6 | 2281.76 | 9010.45 | 17646.8 | 0.63 | 2.39 | 17.064 | 29.593 | 1 | 1 | 1890 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1897513.8978 | 136760.7841 | 3479.0267 | 16930.682 | 119830.1021 | 31643.0356 | 0.072011 | -244339.1336 | 244339.1336
C | Xist Rating 4513 | -57.92 | 838.041 | 150.288 | 35.6 | 2277.68 | 8974.36 | 17555.3 | 0.62 | 2.38 | 17.053 | 29.309 | 1 | 1 | 1900 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1908789.2249 | 138121.7624 | 3515.9392 | 17020.2623 | 121101.5001 | 31337.8072 | 0.072392 | -241982.2403 | 241982.2403
C | Xist Rating 4514 | -57.65 | 844.203 | 150.288 | 35.6 | 2276.27 | 8979.73 | 17465.1 | 0.61 | 2.36 | 17.054 | 29.021 | 1 | 1 | 1910 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1921633.9628 | 139489.45 | 3553.0464 | 17109.8426 | 122379.6074 | 31028.9112 | 0.072773 | -239597.0272 | 239597.0272
C | Xist Rating 4515 | -56.49 | 870.893 | 150.288 | 35.6 | 2267.5 | 8971.91 | 17050.3 | 0.61 | 2.29 | 17.101 | 27.62 | 1 | 1 | 1920 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1974749.8775 | 140863.8468 | 3590.3485 | 17199.423 | 123664.4238 | 29581.1054 | 0.073154 | -228417.4548 | 228417.4548
C | Xist Rating 4516 | -56.11 | 880.012 | 150.288 | 35.6 | 2264.09 | 8959 | 16924.2 | 0.6 | 2.27 | 17.096 | 27.226 | 1 | 1 | 1930 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 1992426.3691 | 142244.9528 | 3627.8454 | 17289.0033 | 124955.9495 | 29161.5591 | 0.073535 | -225177.8293 | 225177.8293
C | Xist Rating 4517 | -55.8 | 882.957 | 150.288 | 35.6 | 2273.53 | 9122.68 | 16882.1 | 0.6 | 2.26 | 17.112 | 27.102 | 1 | 1 | 1940 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2007429.2282 | 143632.7681 | 3665.537 | 17378.5836 | 126254.1844 | 29038.218 | 0.073916 | -224225.4224 | 224225.4224
C | Xist Rating 4518 | -55.54 | 891.615 | 150.288 | 35.6 | 2265.08 | 9024.39 | 16772.1 | 0.58 | 2.24 | 17.091 | 26.778 | 1 | 1 | 1950 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2019579.3042 | 145027.2925 | 3703.4235 | 17468.164 | 127559.1286 | 28675.3676 | 0.074297 | -221423.5876 | 221423.5876
C | Xist Rating 4519 | -55.11 | 901.584 | 150.288 | 35.6 | 2262.38 | 9026.74 | 16637.1 | 0.58 | 2.22 | 17.109 | 26.36 | 1 | 1 | 1960 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2039725.6099 | 146428.5262 | 3741.5047 | 17557.7443 | 128870.782 | 28246.6359 | 0.074678 | -218113.0347 | 218113.0347
C | Xist Rating 4520 | -54.08 | 925.657 | 150.289 | 35.6 | 2254.99 | 9024.09 | 16303.2 | 0.58 | 2.16 | 17.166 | 25.304 | 1 | 1 | 1970 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2087347.2784 | 147836.4692 | 3779.7807 | 17647.3246 | 130189.1445 | 27157.3489 | 0.075059 | -209701.8498 | 209701.8498
C | Xist Rating 4521 | -53.74 | 932.769 | 150.289 | 35.6 | 2254.95 | 9055.06 | 16214.4 | 0.57 | 2.15 | 17.195 | 25.046 | 1 | 1 | 1980 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2103347.4565 | 149251.1213 | 3818.2515 | 17736.9049 | 131514.2164 | 26880.111 | 0.07544 | -207561.0918 | 207561.0918
C | Xist Rating 4522 | -53.37 | 942.083 | 150.289 | 35.6 | 2250.75 | 9028.16 | 16101.5 | 0.56 | 2.13 | 17.192 | 24.721 | 1 | 1 | 1990 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2120393.3122 | 150672.4827 | 3856.9171 | 17826.4853 | 132845.9974 | 26531.5043 | 0.075821 | -204869.2438 | 204869.2438
C | Xist Rating 4523 | -53.05 | 949.32 | 150.289 | 35.6 | 2249.58 | 9040.62 | 16015.1 | 0.55 | 2.12 | 17.194 | 24.476 | 1 | 1 | 2000 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2135571.2856 | 152100.5533 | 3895.7775 | 17916.0656 | 134184.4877 | 26266.0738 | 0.076202 | -202819.6598 | 202819.6598
C | Xist Rating 4524 | -52.8 | 954.652 | 150.289 | 35.6 | 2249.63 | 9064.07 | 15953.9 | 0.54 | 2.11 | 17.197 | 24.309 | 1 | 1 | 2010 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2147613.7788 | 153535.3331 | 3934.8326 | 18005.6459 | 135529.6872 | 26081.5381 | 0.076583 | -201394.7239 | 201394.7239
C | Xist Rating 4525 | -51.69 | 981.79 | 150.289 | 35.6 | 2239.64 | 9029.89 | 15615 | 0.54 | 2.05 | 17.234 | 23.299 | 1 | 1 | 2020 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2198856.1556 | 154976.8221 | 3974.0826 | 18095.2262 | 136881.5959 | 25038.6264 | 0.076964 | -193341.6361 | 193341.6361
C | Xist Rating 4526 | -51.24 | 991.703 | 150.289 | 35.6 | 2238.6 | 9057.74 | 15499.9 | 0.54 | 2.03 | 17.237 | 22.975 | 1 | 1 | 2030 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2220026.3358 | 156425.0204 | 4013.5273 | 18184.8066 | 138240.2138 | 24706.4719 | 0.077345 | -190776.8269 | 190776.8269
C | Xist Rating 4527 | -50.98 | 998.342 | 150.289 | 35.6 | 2236.07 | 9043.02 | 15431.8 | 0.53 | 2.02 | 17.232 | 22.801 | 1 | 1 | 2040 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2232362.5959 | 157879.9279 | 4053.1669 | 18274.3869 | 139605.541 | 24513.9412 | 0.077726 | -189290.1559 | 189290.1559
C | Xist Rating 4528 | -50.64 | 1004.17 | 150.289 | 35.7 | 2239.56 | 9127.72 | 15364.3 | 0.52 | 2.01 | 17.245 | 22.614 | 1 | 1 | 2050 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2248898.9652 | 159341.5446 | 4093.0012 | 18363.9672 | 140977.5774 | 24308.6224 | 0.078107 | -187704.7387 | 187704.7387
C | Xist Rating 4529 | -50.31 | 1013.88 | 150.289 | 35.7 | 2233.4 | 9066.27 | 15264.3 | 0.51 | 1.99 | 17.23 | 22.353 | 1 | 1 | 2060 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2264399.592 | 160809.8705 | 4133.0303 | 18453.5476 | 142356.323 | 24024.9637 | 0.078488 | -185514.4015 | 185514.4015
C | Xist Rating 4530 | -49.14 | 1043.02 | 150.289 | 35.7 | 2223.05 | 9031.12 | 14936.2 | 0.51 | 1.94 | 17.268 | 21.431 | 1 | 1 | 2070 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2318685.611 | 162284.9057 | 4173.2542 | 18543.1279 | 143741.7778 | 23073.2053 | 0.078869 | -178165.175 | 178165.175
C | Xist Rating 4531 | -48.87 | 1049.46 | 150.289 | 35.7 | 2221.84 | 9037.61 | 14873.5 | 0.51 | 1.93 | 17.265 | 21.276 | 1 | 1 | 2080 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2331732.2064 | 163766.6501 | 4213.6729 | 18632.7082 | 145133.9419 | 22916.0429 | 0.07925 | -176951.609 | 176951.609
C | Xist Rating 4532 | -48.52 | 1057.75 | 150.289 | 35.7 | 2219.98 | 9042.08 | 14790.8 | 0.5 | 1.91 | 17.262 | 21.065 | 1 | 1 | 2090 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2348183.845 | 165255.1037 | 4254.2864 | 18722.2885 | 146532.8151 | 22684.5516 | 0.079631 | -175164.0948 | 175164.0948
C | Xist Rating 4533 | -48.18 | 1066.05 | 150.289 | 35.7 | 2218.03 | 9045.09 | 14709.3 | 0.49 | 1.9 | 17.264 | 20.858 | 1 | 1 | 2100 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2364530.8815 | 166750.2665 | 4295.0947 | 18811.8689 | 147938.3977 | 22457.2945 | 0.080012 | -173409.2754 | 173409.2754
C | Xist Rating 4534 | -47.87 | 1073.38 | 150.289 | 35.7 | 2216.73 | 9054.35 | 14638.7 | 0.49 | 1.89 | 17.264 | 20.682 | 1 | 1 | 2110 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2379393.6474 | 168252.1386 | 4336.0977 | 18901.4492 | 149350.6894 | 22278.3107 | 0.080393 | -172027.2096 | 172027.2096
C | Xist Rating 4535 | -46.79 | 1100.95 | 150.289 | 35.7 | 2206.69 | 9011.78 | 14359 | 0.48 | 1.84 | 17.299 | 19.942 | 1 | 1 | 2120 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 19 | E | Rod | 2429455.3555 | 169760.7199 | 4377.2956 | 18991.0295 | 150769.6903 | 21498.8045 | 0.080774 | -166008.0697 | 166008.0697
C | Xist Rating 4536 | -46.36 | 1111.21 | 150.289 | 35.6 | 2205.19 | 9030.25 | 14263.6 | 0.48 | 1.83 | 17.288 | 19.707 | 1 | 1 | 2130 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2450429.1799 | 171276.0104 | 4418.6882 | 19080.6099 | 152195.4005 | 21257.9753 | 0.081155 | -164148.4503 | 164148.4503
C | Xist Rating 4537 | -45.98 | 1121.49 | 150.289 | 35.6 | 2201.17 | 9006.27 | 14169.8 | 0.47 | 1.81 | 17.281 | 19.477 | 1 | 1 | 2140 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2468590.1433 | 172798.0101 | 4460.2756 | 19170.1902 | 153627.8199 | 21005.9412 | 0.081536 | -162202.3103 | 162202.3103
C | Xist Rating 4538 | -45.73 | 1126.97 | 150.289 | 35.7 | 2201.02 | 9025.44 | 14123.4 | 0.47 | 1.8 | 17.28 | 19.372 | 1 | 1 | 2150 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2480483.5094 | 174326.7191 | 4502.0578 | 19259.7705 | 155066.9486 | 20900.4943 | 0.081917 | -161388.0769 | 161388.0769
C | Xist Rating 4539 | -45.41 | 1134.25 | 150.289 | 35.7 | 2200.56 | 9048.1 | 14059.2 | 0.46 | 1.79 | 17.282 | 19.22 | 1 | 1 | 2160 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2495985.18 | 175862.1373 | 4544.0348 | 19349.3508 | 156512.7864 | 20729.6414 | 0.082298 | -160068.796 | 160068.796
C | Xist Rating 4540 | -44.3 | 1164.05 | 150.289 | 35.7 | 2188.42 | 8974.98 | 13786.1 | 0.46 | 1.75 | 17.316 | 18.537 | 1 | 1 | 2170 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2547430.301 | 177404.2647 | 4586.2066 | 19438.9312 | 157965.3335 | 20025.4317 | 0.082679 | -154631.0754 | 154631.0754
C | Xist Rating 4541 | -43.87 | 1174.08 | 150.289 | 35.7 | 2187.07 | 8994.89 | 13699.3 | 0.46 | 1.74 | 17.318 | 18.331 | 1 | 1 | 2180 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2567795.1456 | 178953.1013 | 4628.5732 | 19528.5115 | 159424.5898 | 19815.1614 | 0.08306 | -153007.4237 | 153007.4237
C | Xist Rating 4542 | -43.56 | 1181.59 | 150.289 | 35.7 | 2186.09 | 9008.43 | 13639 | 0.45 | 1.73 | 17.316 | 18.197 | 1 | 1 | 2190 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2583062.0831 | 180508.6471 | 4671.1346 | 19618.0918 | 160890.5553 | 19662.4847 | 0.083441 | -151828.4949 | 151828.4949
C | Xist Rating 4543 | -43.3 | 1189.51 | 150.289 | 35.6 | 2182.52 | 8977.81 | 13579.4 | 0.44 | 1.72 | 17.308 | 18.07 | 1 | 1 | 2200 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2596129.3652 | 182070.9022 | 4713.8907 | 19707.6722 | 162363.2301 | 19516.6651 | 0.083822 | -150702.5144 | 150702.5144
C | Xist Rating 4544 | -42.9 | 1199.79 | 150.289 | 35.6 | 2179.61 | 8971.03 | 13495.4 | 0.44 | 1.7 | 17.311 | 17.878 | 1 | 1 | 2210 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2615074.2819 | 183639.8665 | 4756.8417 | 19797.2525 | 163842.6141 | 19320.8178 | 0.084203 | -149190.2334 | 149190.2334
C | Xist Rating 4545 | -41.76 | 1229.46 | 150.289 | 35.6 | 2170.46 | 8944.39 | 13246.2 | 0.44 | 1.66 | 17.349 | 17.285 | 1 | 1 | 2220 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2668493.7516 | 185215.5401 | 4799.9874 | 19886.8328 | 165328.7073 | 18710.0662 | 0.084584 | -144474.1721 | 144474.1721
C | Xist Rating 4546 | -41.42 | 1237.71 | 150.289 | 35.6 | 2169.22 | 8956.96 | 13182.5 | 0.43 | 1.65 | 17.347 | 17.145 | 1 | 1 | 2230 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2684865.2862 | 186797.9228 | 4843.3279 | 19976.4131 | 166821.5097 | 18550.6703 | 0.084965 | -143243.3591 | 143243.3591
C | Xist Rating 4547 | -41.08 | 1247.39 | 150.289 | 35.6 | 2165.68 | 8934.27 | 13111.7 | 0.43 | 1.64 | 17.341 | 16.994 | 1 | 1 | 2240 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2701447.5752 | 188387.0148 | 4886.8633 | 20065.9935 | 168321.0213 | 18396.9416 | 0.085346 | -142056.3065 | 142056.3065
C | Xist Rating 4548 | -40.7 | 1257.99 | 150.289 | 35.6 | 2162.06 | 8914.41 | 13034 | 0.42 | 1.63 | 17.336 | 16.827 | 1 | 1 | 2250 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2719849.8594 | 189982.816 | 4930.5934 | 20155.5738 | 169827.2422 | 18209.1536 | 0.085727 | -140606.2575 | 140606.2575
C | Xist Rating 4549 | -40.45 | 1263.43 | 150.289 | 35.6 | 2162.5 | 8942.71 | 12995.5 | 0.42 | 1.62 | 17.338 | 16.75 | 1 | 1 | 2260 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2732167.375 | 191585.3264 | 4974.5182 | 20245.1541 | 171340.1723 | 18132.5381 | 0.086108 | -140014.6526 | 140014.6526
C | Xist Rating 4550 | -39.26 | 1295.41 | 150.289 | 35.6 | 2151.81 | 8894.67 | 12751.8 | 0.42 | 1.59 | 17.374 | 16.201 | 1 | 1 | 2270 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2787476.1921 | 193194.5461 | 5018.6379 | 20334.7344 | 172859.8116 | 17567.205 | 0.086489 | -135649.3008 | 135649.3008
C | Xist Rating 4551 | -38.91 | 1305.04 | 150.289 | 35.6 | 2149.18 | 8886.68 | 12686.1 | 0.41 | 1.58 | 17.37 | 16.066 | 1 | 1 | 2280 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2804765.8672 | 194810.4749 | 5062.9524 | 20424.3148 | 174386.1602 | 17412.3548 | 0.08687 | -134453.5881 | 134453.5881
C | Xist Rating 4552 | -38.47 | 1316.34 | 150.289 | 35.6 | 2146.72 | 8889.53 | 12606.8 | 0.41 | 1.56 | 17.369 | 15.9 | 1 | 1 | 2290 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2825813.4048 | 196433.113 | 5107.4617 | 20513.8951 | 175919.2179 | 17243.1142 | 0.087251 | -133146.7574 | 133146.7574
C | Xist Rating 4553 | -38.16 | 1324.02 | 150.289 | 35.6 | 2145.71 | 8900.81 | 12556.9 | 0.4 | 1.56 | 17.367 | 15.802 | 1 | 1 | 2300 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2840962.9542 | 198062.4604 | 5152.1657 | 20603.4754 | 177458.9849 | 17126.5441 | 0.087632 | -132246.6341 | 132246.6341
| Xist Rating 4554 | -37.9 | 1331.96 | 150.289 | 35.6 | 2142.7 | 8877.75 | 12507.5 | 0.4 | 1.55 | 17.362 | 15.708 | 1 | 1 | 2310 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2853990.692 | 199698.5169 | 5197.0645 | 20693.0558 | 179005.4612 | 17031.8321 | 0.088013 | -131515.2926 | 131515.2926
| Xist Rating 4555 | -36.67 | 1364.74 | 150.289 | 35.6 | 2133.3 | 8851.86 | 12277 | 0.4 | 1.51 | 17.399 | 15.211 | 1 | 1 | 2320 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2911399.842 | 201341.2827 | 5242.1582 | 20782.6361 | 180558.6466 | 16520.3504 | 0.088394 | -127565.767 | 127565.767
| Xist Rating 4556 | -36.35 | 1374.39 | 150.289 | 35.6 | 2129.46 | 8821.94 | 12216.8 | 0.39 | 1.5 | 17.4 | 15.094 | 1 | 1 | 2330 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2926708.5294 | 202990.7577 | 5287.4466 | 20872.2164 | 182118.5413 | 16383.8347 | 0.088775 | -126511.6288 | 126511.6288
| Xist Rating 4557 | -36 | 1384.02 | 150.289 | 35.6 | 2127.02 | 8815.91 | 12157.1 | 0.39 | 1.49 | 17.39 | 14.979 | 1 | 1 | 2340 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2943838.2204 | 204646.9419 | 5332.9298 | 20961.7967 | 183685.1452 | 16267.0401 | 0.089156 | -125609.7719 | 125609.7719
| Xist Rating 4558 | -35.69 | 1392.78 | 150.289 | 35.6 | 2124.78 | 8809.17 | 12104.7 | 0.38 | 1.49 | 17.391 | 14.88 | 1 | 1 | 2350 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2959351.0884 | 206309.8354 | 5378.6078 | 21051.3771 | 185258.4583 | 16148.9906 | 0.089537 | -124698.2247 | 124698.2247
| Xist Rating 4559 | -35.31 | 1403.43 | 150.289 | 35.6 | 2121.74 | 8796.65 | 12039.9 | 0.38 | 1.48 | 17.386 | 14.755 | 1 | 1 | 2360 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 2977713.5682 | 207979.438 | 5424.4805 | 21140.9574 | 186838.4806 | 16021.9396 | 0.089918 | -123717.1704 | 123717.1704
| Xist Rating 4560 | -34.2 | 1433.52 | 150.289 | 35.6 | 2113.65 | 8777.56 | 11846.8 | 0.38 | 1.45 | 17.416 | 14.36 | 1 | 1 | 2370 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3029959.548 | 209655.7499 | 5470.5481 | 21230.5377 | 188425.2122 | 15615.9052 | 0.090299 | -120581.8806 | 120581.8806
| Xist Rating 4561 | -33.86 | 1443.39 | 150.289 | 35.6 | 2110.5 | 8758.43 | 11791.2 | 0.37 | 1.44 | 17.41 | 14.259 | 1 | 1 | 2380 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3046274.595 | 211338.771 | 5516.8105 | 21320.1181 | 190018.653 | 15495.1667 | 0.09068 | -119649.5699 | 119649.5699
| Xist Rating 4562 | -33.49 | 1453.59 | 150.289 | 35.6 | 2108.19 | 8757.63 | 11730 | 0.37 | 1.43 | 17.404 | 14.142 | 1 | 1 | 2390 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3064443.9021 | 213028.5014 | 5563.2676 | 21409.6984 | 191618.803 | 15376.312 | 0.091061 | -118731.8056 | 118731.8056
C | Xist Rating 4566 | -25.77 | 1670.38 | 150.289 | 35.6 | 2049.95 | 8578.75 | 10537.9 | 0.39 | 1.25 | 17.434 | 11.906 | 1 | 1 | 2430 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3424195.481 | 219854.515 | 5751.0441 | 21768.0197 | 198086.4953 | 13104.9641 | 0.092585 | -101193.059 | 101193.059
C | Xist Rating 4567 | -25.74 | 1671.75 | 150.289 | 35.6 | 2049.7 | 8574.22 | 10538 | 0.38 | 1.25 | 17.428 | 11.917 | 1 | 1 | 2440 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3426585.975 | 221577.7915 | 5798.4752 | 21857.6 | 199720.1914 | 13100.118 | 0.092966 | -101155.6388 | 101155.6388
C | Xist Rating 4568 | -25.72 | 1673.08 | 150.289 | 35.6 | 2049.47 | 8570.29 | 10537.9 | 0.38 | 1.25 | 17.422 | 11.928 | 1 | 1 | 2450 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3428927.2676 | 223307.7772 | 5846.1011 | 21947.1804 | 201360.5968 | 13114.2597 | 0.093347 | -101264.837 | 101264.837
C | Xist Rating 4569 | -25.69 | 1674.55 | 150.289 | 35.6 | 2049.11 | 8563.98 | 10537.9 | 0.37 | 1.25 | 17.416 | 11.939 | 1 | 1 | 2460 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3431337.1505 | 225044.4721 | 5893.9217 | 22036.7607 | 203007.7114 | 13109.1949 | 0.093728 | -101225.7282 | 101225.7282
C | Xist Rating 4570 | -25.66 | 1675.9 | 150.289 | 35.6 | 2049.07 | 8563.26 | 10537.9 | 0.36 | 1.25 | 17.451 | 11.95 | 1 | 1 | 2470 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3434036.413 | 226787.8762 | 5941.9372 | 22126.341 | 204661.5352 | 13105.6194 | 0.094109 | -101198.1194 | 101198.1194
C | Xist Rating 4571 | -25.63 | 1677.25 | 150.289 | 35.6 | 2048.88 | 8560.04 | 10537.9 | 0.36 | 1.25 | 17.443 | 11.96 | 1 | 1 | 2480 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3436483.98 | 228537.9896 | 5990.1474 | 22215.9213 | 206322.0682 | 13118.5003 | 0.09449 | -101297.5821 | 101297.5821
C | Xist Rating 4572 | -25.61 | 1678.65 | 150.289 | 35.6 | 2048.56 | 8554.37 | 10537.9 | 0.35 | 1.25 | 17.439 | 11.971 | 1 | 1 | 2490 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3438815.244 | 230294.8122 | 6038.5525 | 22305.5017 | 207989.3105 | 13113.1136 | 0.094871 | -101255.9871 | 101255.9871
C | Xist Rating 4573 | -25.58 | 1679.63 | 150.289 | 35.6 | 2049 | 8562.13 | 10537.9 | 0.35 | 1.25 | 17.434 | 11.98 | 1 | 1 | 2500 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3441561.87 | 232058.344 | 6087.1523 | 22395.082 | 209663.262 | 13124.9999 | 0.095252 | -101347.7701 | 101347.7701
C | Xist Rating 4574 | -25.56 | 1681.48 | 150.289 | 35.6 | 2048.06 | 8545.68 | 10537.9 | 0.34 | 1.25 | 17.427 | 11.992 | 1 | 1 | 2510 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3443771.9288 | 233828.585 | 6135.9469 | 22484.6623 | 211343.9227 | 13120.3143 | 0.095633 | -101311.5891 | 101311.5891
C | Xist Rating 4575 | -25.56 | 1682.93 | 150.289 | 35.6 | 2047.27 | 8532 | 10537.7 | 0.34 | 1.25 | 17.463 | 12.003 | 1 | 1 | 2520 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3445412.1011 | 235605.5353 | 6184.9363 | 22574.2426 | 213031.2926 | 13135.7763 | 0.096014 | -101430.9828 | 101430.9828
C | Xist Rating 4576 | -25.54 | 1684.27 | 150.289 | 35.6 | 2046.77 | 8523.48 | 10537.8 | 0.33 | 1.25 | 17.458 | 12.013 | 1 | 1 | 2530 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3447313.3079 | 237389.1947 | 6234.1205 | 22663.823 | 214725.3718 | 13128.8314 | 0.096395 | -101377.3564 | 101377.3564
C | Xist Rating 4577 | -25.51 | 1685.42 | 150.289 | 35.6 | 2046.77 | 8523.35 | 10537.7 | 0.33 | 1.25 | 17.452 | 12.023 | 1 | 1 | 2540 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3449667.0934 | 239179.5635 | 6283.4995 | 22753.4033 | 216426.1602 | 13141.5734 | 0.096776 | -101475.7464 | 101475.7464
C | Xist Rating 4578 | -25.5 | 1686.97 | 150.289 | 35.6 | 2046.08 | 8511.44 | 10537.7 | 0.32 | 1.25 | 17.446 | 12.034 | 1 | 1 | 2550 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3451675.5776 | 240976.6414 | 6333.0732 | 22842.9836 | 218133.6578 | 13135.4108 | 0.097157 | -101428.1606 | 101428.1606
C | Xist Rating 4579 | -25.48 | 1688.42 | 150.289 | 35.6 | 2045.55 | 8502.41 | 10537.6 | 0.32 | 1.25 | 17.442 | 12.044 | 1 | 1 | 2560 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3453747.531 | 242780.4286 | 6382.8418 | 22932.564 | 219847.8646 | 13148.1514 | 0.097538 | -101526.5396 | 101526.5396
C | Xist Rating 4580 | -25.48 | 1689.81 | 150.289 | 35.6 | 2044.75 | 8488.58 | 10537.7 | 0.31 | 1.25 | 17.458 | 12.055 | 1 | 1 | 2570 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3455238.9975 | 244590.9249 | 6432.8051 | 23022.1443 | 221568.7806 | 13142.555 | 0.097919 | -101483.3262 | 101483.3262
C | Xist Rating 4581 | -25.46 | 1691.17 | 150.289 | 35.6 | 2044.16 | 8478.29 | 10537.7 | 0.31 | 1.25 | 17.494 | 12.065 | 1 | 1 | 2580 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3457022.0672 | 246408.1305 | 6482.9633 | 23111.7246 | 223296.4059 | 13156.6565 | 0.0983 | -101592.2143 | 101592.2143
C | Xist Rating 4582 | -25.44 | 1692.53 | 150.289 | 35.6 | 2043.8 | 8472.2 | 10537.7 | 0.3 | 1.25 | 17.491 | 12.075 | 1 | 1 | 2590 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3459192.814 | 248232.0454 | 6533.3162 | 23201.3049 | 225030.7404 | 13149.0581 | 0.098681 | -101533.5414 | 101533.5414
C | Xist Rating 4583 | -25.42 | 1693.71 | 150.289 | 35.6 | 2043.62 | 8469.07 | 10537.7 | 0.3 | 1.25 | 17.488 | 12.084 | 1 | 1 | 2600 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3461299.6302 | 250062.6694 | 6583.8639 | 23290.8853 | 226771.7842 | 13160.6518 | 0.099062 | -101623.0648 | 101623.0648
C | Xist Rating 4584 | -25.39 | 1695.4 | 150.289 | 35.6 | 2043 | 8458.49 | 10537.7 | 0.29 | 1.25 | 17.484 | 12.096 | 1 | 1 | 2610 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3463702.2 | 251900.0027 | 6634.6064 | 23380.4656 | 228519.5371 | 13154.8701 | 0.099443 | -101578.4202 | 101578.4202
C | Xist Rating 4585 | -25.36 | 1696.8 | 150.289 | 35.6 | 2042.91 | 8457 | 10537.6 | 0.29 | 1.25 | 17.484 | 12.106 | 1 | 1 | 2620 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3466409.688 | 253744.0452 | 6685.5437 | 23470.0459 | 230273.9993 | 13167.5279 | 0.099824 | -101676.1601 | 101676.1601
C | Xist Rating 4586 | -25.33 | 1698.22 | 150.29 | 35.6 | 2042.64 | 8452.26 | 10537.6 | 0.29 | 1.25 | 17.523 | 12.116 | 1 | 1 | 2630 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3468852.1008 | 255594.7969 | 6736.6758 | 23559.6263 | 232035.1707 | 13181.519 | 0.10021 | -101784.1955 | 101784.1955
C | Xist Rating 4587 | -25.29 | 1699.47 | 150.29 | 35.6 | 2042.87 | 8456.27 | 10537.6 | 0.28 | 1.25 | 17.521 | 12.126 | 1 | 1 | 2640 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3471796.2789 | 257452.2579 | 6788.0027 | 23649.2066 | 233803.0513 | 13173.3793 | 0.10059 | -101721.3432 | 101721.3432
C | Xist Rating 4588 | -25.25 | 1700.97 | 150.29 | 35.6 | 2043.21 | 8462.13 | 10537.6 | 0.28 | 1.25 | 17.518 | 12.136 | 1 | 1 | 2650 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3475438.9137 | 259316.4281 | 6839.5243 | 23738.7869 | 235577.6412 | 13185.8636 | 0.10097 | -101817.7433 | 101817.7433
C | Xist Rating 4589 | -25.24 | 1702.31 | 150.29 | 35.6 | 2042.45 | 8449.09 | 10537.7 | 0.28 | 1.25 | 17.514 | 12.146 | 1 | 1 | 2660 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3476883.0595 | 261187.3075 | 6891.2408 | 23828.3672 | 237358.9402 | 13198.3137 | 0.10135 | -101913.8798 | 101913.8798
C | Xist Rating 4590 | -25.19 | 1703.7 | 150.29 | 35.6 | 2042.95 | 8457.69 | 10537.6 | 0.27 | 1.25 | 17.514 | 12.156 | 1 | 1 | 2670 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3480573.915 | 263064.8961 | 6943.152 | 23917.9476 | 239146.9485 | 13189.9358 | 0.10173 | -101849.1876 | 101849.1876
C | Xist Rating 4591 | -25.18 | 1705.12 | 150.29 | 35.6 | 2042.01 | 8441.57 | 10537.7 | 0.27 | 1.25 | 17.55 | 12.166 | 1 | 1 | 2680 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3481872.0912 | 264949.1939 | 6995.258 | 24007.5279 | 240941.6661 | 13203.6081 | 0.10211 | -101954.7616 | 101954.7616
C | Xist Rating 4592 | -25.13 | 1706.49 | 150.29 | 35.6 | 2042.55 | 8450.84 | 10537.6 | 0.26 | 1.25 | 17.546 | 12.176 | 1 | 1 | 2690 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3485591.1495 | 266840.201 | 7047.5588 | 24097.1082 | 242743.0928 | 13194.8302 | 0.10249 | -101886.981 | 101886.981
C | Xist Rating 4593 | -25.1 | 1707.69 | 150.29 | 35.6 | 2042.82 | 8455.56 | 10537.5 | 0.26 | 1.25 | 17.539 | 12.185 | 1 | 1 | 2700 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3488503.2858 | 268737.9173 | 7100.0544 | 24186.6886 | 244551.2288 | 13206.0013 | 0.10287 | -101973.2413 | 101973.2413
C | Xist Rating 4594 | -25.06 | 1709.35 | 150.29 | 35.6 | 2042.45 | 8449.14 | 10537.5 | 0.26 | 1.25 | 17.535 | 12.196 | 1 | 1 | 2710 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3491261.9075 | 270642.3428 | 7152.7448 | 24276.2689 | 246366.074 | 13219.3425 | 0.10325 | -102076.2586 | 102076.2586
C | Xist Rating 4595 | -25.06 | 1710.69 | 150.29 | 35.6 | 2041.54 | 8433.61 | 10537.5 | 0.26 | 1.25 | 17.529 | 12.206 | 1 | 1 | 2720 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3492442.0626 | 272553.4776 | 7205.63 | 24365.8492 | 248187.6284 | 13231.5809 | 0.10363 | -102170.7602 | 102170.7602
C | Xist Rating 4596 | -25.05 | 1712.02 | 150.29 | 35.6 | 2040.98 | 8423.95 | 10537.6 | 0.25 | 1.25 | 17.566 | 12.215 | 1 | 1 | 2730 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3494198.5796 | 274471.3216 | 7258.71 | 24455.4295 | 250015.892 | 13222.6517 | 0.10402 | -102101.8117 | 102101.8117
C | Xist Rating 4597 | -25.04 | 1713.3 | 150.29 | 35.6 | 2040.59 | 8417.52 | 10537.5 | 0.25 | 1.25 | 17.557 | 12.224 | 1 | 1 | 2740 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3496142.847 | 276395.8748 | 7311.9847 | 24545.0099 | 251850.8649 | 13233.6903 | 0.1044 | -102187.049 | 102187.049
C | Xist Rating 4598 | -25.05 | 1714.85 | 150.29 | 35.6 | 2039.06 | 8391.48 | 10537.5 | 0.25 | 1.25 | 17.556 | 12.235 | 1 | 1 | 2750 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3496682.041 | 278327.1372 | 7365.4543 | 24634.5902 | 253692.547 | 13247.0505 | 0.10478 | -102290.2124 | 102290.2124
C | Xist Rating 4599 | -25.03 | 1716.27 | 150.29 | 35.6 | 2038.55 | 8382.84 | 10537.6 | 0.24 | 1.25 | 17.555 | 12.245 | 1 | 1 | 2760 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3498702.2085 | 280265.1088 | 7419.1186 | 24724.1705 | 255540.9383 | 13237.6535 | 0.10516 | -102217.6517 | 102217.6517
C | Xist Rating 4600 | -25.04 | 1717.51 | 150.29 | 35.6 | 2037.56 | 8366.06 | 10537.5 | 0.24 | 1.25 | 17.549 | 12.253 | 1 | 1 | 2770 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3499529.6756 | 282209.7897 | 7472.9777 | 24813.7508 | 257396.0389 | 13247.6713 | 0.10554 | -102295.006 | 102295.006
C | Xist Rating 4601 | -25 | 1719.05 | 150.29 | 35.6 | 2037.49 | 8364.88 | 10537.6 | 0.24 | 1.25 | 17.591 | 12.264 | 1 | 1 | 2780 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3502547.1845 | 284161.1798 | 7527.0316 | 24903.3312 | 259257.8486 | 13262.2388 | 0.10592 | -102407.4923 | 102407.4923
C | Xist Rating 4602 | -24.96 | 1720.46 | 150.29 | 35.6 | 2037.54 | 8365.61 | 10537.6 | 0.23 | 1.25 | 17.591 | 12.274 | 1 | 1 | 2790 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3505506.0684 | 286119.2791 | 7581.2803 | 24992.9115 | 261126.3676 | 13252.5167 | 0.1063 | -102332.4213 | 102332.4213
C | Xist Rating 4603 | -24.93 | 1721.44 | 150.29 | 35.6 | 2037.93 | 8372.21 | 10537.7 | 0.23 | 1.25 | 17.588 | 12.281 | 1 | 1 | 2800 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3508174.2192 | 288084.0877 | 7635.7238 | 25082.4918 | 263001.5958 | 13261.5132 | 0.10668 | -102401.8896 | 102401.8896
C | Xist Rating 4604 | -24.89 | 1723.18 | 150.29 | 35.6 | 2037.48 | 8364.6 | 10537.7 | 0.23 | 1.25 | 17.592 | 12.292 | 1 | 1 | 2810 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3510944.7864 | 290055.6054 | 7690.3621 | 25172.0722 | 264883.5333 | 13274.8658 | 0.10706 | -102504.9951 | 102504.9951
C | Xist Rating 4605 | -24.79 | 1724.66 | 150.29 | 35.6 | 2039.27 | 8394.83 | 10537.8 | 0.23 | 1.25 | 17.61 | 12.302 | 1 | 1 | 2820 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3517047.3982 | 292033.8324 | 7745.1952 | 25261.6525 | 266772.1799 | 13287.5878 | 0.10744 | -102603.2308 | 102603.2308
C | Xist Rating 4606 | -24.75 | 1726.03 | 150.29 | 35.6 | 2039.33 | 8395.87 | 10537.8 | 0.22 | 1.25 | 17.653 | 12.312 | 1 | 1 | 2830 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3519944.7599 | 294018.7686 | 7800.223 | 25351.2328 | 268667.5358 | 13278.6494 | 0.10783 | -102534.2109 | 102534.2109
C | Xist Rating 4607 | -24.35 | 1727.35 | 150.29 | 35.6 | 2049.48 | 8570.43 | 10538 | 0.22 | 1.25 | 17.716 | 12.322 | 1 | 1 | 2840 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3540169.278 | 296010.4141 | 7855.4457 | 25440.8131 | 270569.6009 | 13292.5396 | 0.10821 | -102641.4676 | 102641.4676
C | Xist Rating 4608 | -24.72 | 1728.79 | 150.29 | 35.6 | 2038.43 | 8380.55 | 10537.8 | 0.22 | 1.25 | 17.65 | 12.331 | 1 | 1 | 2850 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3524017.3997 | 298008.7687 | 7910.8631 | 25530.3935 | 272478.3753 | 13301.7782 | 0.10859 | -102712.8056 | 102712.8056
C | Xist Rating 4609 | -24.31 | 1730.19 | 150.29 | 35.6 | 2048.75 | 8557.62 | 10538 | 0.21 | 1.25 | 17.715 | 12.341 | 1 | 1 | 2860 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3544726.7625 | 300013.8326 | 7966.4753 | 25619.9738 | 274393.8588 | 13293.0266 | 0.10897 | -102645.2281 | 102645.2281
C | Xist Rating 4610 | -23.65 | 1731.39 | 150.29 | 35.6 | 2066.25 | 8871.44 | 10538.1 | 0.21 | 1.25 | 17.809 | 12.351 | 1 | 1 | 2870 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3577484.5875 | 302025.6057 | 8022.2824 | 25709.5541 | 276316.0516 | 13307.6186 | 0.10935 | -102757.9037 | 102757.9037
C | Xist Rating 4611 | -23.32 | 1732.89 | 150.29 | 35.6 | 2074.09 | 9017.71 | 10538.1 | 0.21 | 1.25 | 17.883 | 12.361 | 1 | 1 | 2880 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3594169.8201 | 304044.0881 | 8078.2842 | 25799.1345 | 278244.9536 | 13321.6862 | 0.10973 | -102866.5294 | 102866.5294
C | Xist Rating 4612 | -23.12 | 1734.24 | 150.29 | 35.6 | 2078.84 | 9108.28 | 10538.1 | 0.2 | 1.25 | 17.899 | 12.37 | 1 | 1 | 2890 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3605207.4816 | 306069.2796 | 8134.4807 | 25888.7148 | 280180.5649 | 13309.9643 | 0.11011 | -102776.0165 | 102776.0165
C | Xist Rating 4613 | -22.97 | 1735.62 | 150.29 | 35.6 | 2081.82 | 9165.82 | 10538.1 | 0.2 | 1.25 | 17.91 | 12.38 | 1 | 1 | 2900 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3613248.4284 | 308101.1804 | 8190.8721 | 25978.2951 | 282122.8853 | 13322.2399 | 0.11049 | -102870.8054 | 102870.8054
C | Xist Rating 4614 | -22.85 | 1737.16 | 150.29 | 35.6 | 2084.11 | 9210.4 | 10538.1 | 0.2 | 1.25 | 17.92 | 12.39 | 1 | 1 | 2910 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3620432.5276 | 310139.7904 | 8247.4583 | 26067.8754 | 284071.915 | 13334.4914 | 0.11087 | -102965.4081 | 102965.4081
C | Xist Rating 4615 | -22.68 | 1738.55 | 150.29 | 35.6 | 2087.6 | 9278.93 | 10538.1 | 0.2 | 1.25 | 17.932 | 12.4 | 1 | 1 | 2920 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3629396.98 | 312185.1097 | 8304.2393 | 26157.4558 | 286027.6539 | 13346.797 | 0.11125 | -103060.4289 | 103060.4289
C | Xist Rating 4616 | -22.53 | 1739.94 | 150.29 | 35.6 | 2091.12 | 9348.98 | 10538 | 0.19 | 1.25 | 17.983 | 12.409 | 1 | 1 | 2930 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3638423.3328 | 314237.1381 | 8361.215 | 26247.0361 | 287990.102 | 13335.4726 | 0.11164 | -102972.9842 | 102972.9842
C | Xist Rating 4617 | -22.32 | 1741.31 | 150.29 | 35.6 | 2095.64 | 9439.93 | 10538 | 0.19 | 1.25 | 18.002 | 12.418 | 1 | 1 | 2940 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3649158.8884 | 316295.8758 | 8418.3855 | 26336.6164 | 289959.2594 | 13346.8263 | 0.11202 | -103060.6551 | 103060.6551
C | Xist Rating 4618 | -22.06 | 1742.71 | 150.29 | 35.5 | 2101.71 | 9564.43 | 10538 | 0.19 | 1.25 | 18.009 | 12.428 | 1 | 1 | 2950 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3662671.0341 | 318361.3227 | 8475.7509 | 26426.1968 | 291935.126 | 13358.9204 | 0.1124 | -103154.042 | 103154.042
C | Xist Rating 4619 | -22.05 | 1744.09 | 150.29 | 35.5 | 2101.04 | 9550.59 | 10538 | 0.19 | 1.25 | 18.005 | 12.437 | 1 | 1 | 2960 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3664402.8536 | 320433.4789 | 8533.311 | 26515.7771 | 293917.7018 | 13369.6998 | 0.11278 | -103237.2778 | 103237.2778
C | Xist Rating 4620 | -22.04 | 1745.47 | 150.29 | 35.5 | 2100.39 | 9537.04 | 10538 | 0.18 | 1.25 | 18.002 | 12.446 | 1 | 1 | 2970 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3666167.7333 | 322512.3442 | 8591.0659 | 26605.3574 | 295906.9868 | 13356.5379 | 0.11316 | -103135.6452 | 103135.6452
C | Xist Rating 4621 | -22.03 | 1746.69 | 150.29 | 35.5 | 2099.79 | 9524.81 | 10538 | 0.18 | 1.25 | 18.038 | 12.454 | 1 | 1 | 2980 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3667682.1951 | 324597.9188 | 8649.0156 | 26694.9377 | 297902.9811 | 13367.1639 | 0.11354 | -103217.6967 | 103217.6967
C | Xist Rating 4622 | -22.05 | 1748.25 | 150.29 | 35.5 | 2098.36 | 9495.53 | 10537.9 | 0.18 | 1.25 | 18.033 | 12.464 | 1 | 1 | 2990 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3668457.87 | 326690.2026 | 8707.16 | 26784.5181 | 299905.6845 | 13378.8837 | 0.11392 | -103308.1935 | 103308.1935
C | Xist Rating 4623 | -22.03 | 1749.68 | 150.29 | 35.5 | 2097.71 | 9482.26 | 10537.9 | 0.18 | 1.25 | 18.029 | 12.473 | 1 | 1 | 3000 | 152.4 | 2 | 3.2 | 19.05 | 1.3333 | 18 | E | Rod | 3670321.2328 | 328789.1956 | 8765.4993 | 26874.0984 | 301915.0972 | 13389.5883 | 0.1143 | -103390.8519 | 103390.8519
C | Xist Rating 4624 | -90.54 | 172.748 | 150.293 | 35.9 | 2386.35 | 7279.14 | 58745.9 | 2.46 | 10.95 | 19.264 | 465.723 | 1 | 1 | 1000 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 412237.1898 | 43832.4095 | 973.9444 | 9237.9713 | 34594.4382 | 485776.8142 | 0.038101 | -3751039.7941 | 3751039.7941
C | Xist Rating 4625 | -90.45 | 174.552 | 150.293 | 35.9 | 2383.82 | 7263.86 | 58284.3 | 2.44 | 10.85 | 19.31 | 456.994 | 1 | 1 | 1010 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 416100.5486 | 44620.1375 | 993.5206 | 9330.351 | 35289.7864 | 476720.6424 | 0.038482 | -3681110.4355 | 3681110.4355
C | Xist Rating 4626 | -89.74 | 188.149 | 150.294 | 35.8 | 2377.42 | 7267.04 | 54967 | 2.45 | 10.07 | 19.36 | 396.023 | 1 | 1 | 1020 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 447309.1956 | 45414.7843 | 1013.2917 | 9422.7307 | 35992.0535 | 413437.9046 | 0.038863 | -3192457.9091 | 3192457.9091
C | Xist Rating 4627 | -89.63 | 191.901 | 150.293 | 35.8 | 2357.9 | 7103.03 | 54179.2 | 2.36 | 9.89 | 18.951 | 382.791 | 1 | 1 | 1030 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 452483.3679 | 46216.35 | 1033.2576 | 9515.1105 | 36701.2395 | 399592.7447 | 0.039244 | -3085549.254 | 3085549.254
C | Xist Rating 4628 | -89.56 | 193.779 | 150.292 | 35.8 | 2351.96 | 7057.02 | 53793.6 | 2.32 | 9.8 | 18.846 | 376.447 | 1 | 1 | 1040 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 455760.4568 | 47024.8346 | 1053.4182 | 9607.4902 | 37417.3444 | 392977.8641 | 0.039625 | -3034470.9 | 3034470.9
C | Xist Rating 4629 | -89.38 | 197.409 | 150.292 | 35.8 | 2349.9 | 7053.48 | 53043.4 | 2.28 | 9.63 | 18.788 | 363.997 | 1 | 1 | 1050 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 463891.4091 | 47840.238 | 1073.7737 | 9699.8699 | 38140.3681 | 380026.4533 | 0.040006 | -2934463.5381 | 2934463.5381
C | Xist Rating 4630 | -89.22 | 199.268 | 150.292 | 35.8 | 2364.09 | 7190.67 | 52676.8 | 2.23 | 9.54 | 18.783 | 358.112 | 1 | 1 | 1060 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 471087.4861 | 48662.5604 | 1094.3239 | 9792.2496 | 38870.3108 | 373888.9269 | 0.040387 | -2887071.1863 | 2887071.1863
C | Xist Rating 4631 | -88.52 | 213.922 | 150.292 | 35.8 | 2345.24 | 7080.47 | 49857.3 | 2.21 | 8.9 | 18.636 | 313.358 | 1 | 1 | 1070 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 501698.4313 | 49491.8016 | 1115.0689 | 9884.6293 | 39607.1723 | 327397.1448 | 0.040768 | -2528073.9691 | 2528073.9691
C | Xist Rating 4632 | -88.34 | 216.713 | 150.292 | 35.8 | 2352.28 | 7156.42 | 49380.7 | 2.16 | 8.79 | 18.555 | 306.357 | 1 | 1 | 1080 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 509769.6556 | 50327.9618 | 1136.0087 | 9977.009 | 40350.9527 | 320091.4998 | 0.041149 | -2471661.7142 | 2471661.7142
C | Xist Rating 4633 | -88.13 | 220.423 | 150.292 | 35.8 | 2354.74 | 7194.53 | 48761.1 | 2.1 | 8.65 | 18.425 | 297.354 | 1 | 1 | 1090 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 519038.855 | 51171.0408 | 1157.1433 | 10069.3887 | 41101.6521 | 310692.1306 | 0.04153 | -2399082.2773 | 2399082.2773
C | Xist Rating 4634 | -87.95 | 223.182 | 150.292 | 35.8 | 2362.03 | 7274.69 | 48308.2 | 2.06 | 8.55 | 18.423 | 290.857 | 1 | 1 | 1100 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 527162.5795 | 52021.0387 | 1178.4727 | 10161.7685 | 41859.2703 | 303925.8077 | 0.041911 | -2346834.5251 | 2346834.5251
C | Xist Rating 4635 | -87.87 | 225.228 | 150.291 | 35.8 | 2357.57 | 7240.25 | 48010.6 | 1.98 | 8.49 | 18.162 | 286.895 | 1 | 1 | 1110 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 530990.776 | 52877.9555 | 1199.9969 | 10254.1482 | 42623.8073 | 299729.2445 | 0.042292 | -2314429.7766 | 2314429.7766
C | Xist Rating 4636 | -87.01 | 241.51 | 150.291 | 35.8 | 2354.51 | 7282.42 | 45448.2 | 2.03 | 7.92 | 18.394 | 251.039 | 1 | 1 | 1120 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 568637.7101 | 53741.7912 | 1221.7158 | 10346.5279 | 43395.2633 | 262578.1983 | 0.042673 | -2027559.2452 | 2027559.2452
C | Xist Rating 4637 | -86.92 | 243.51 | 150.291 | 35.8 | 2353.9 | 7284.29 | 45188.9 | 1.97 | 7.86 | 18.225 | 247.839 | 1 | 1 | 1130 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 573198.189 | 54612.5458 | 1243.6296 | 10438.9076 | 44173.6382 | 259198.9758 | 0.043054 | -2001465.7854 | 2001465.7854
C | Xist Rating 4638 | -86.74 | 247.291 | 150.291 | 35.8 | 2351.15 | 7273.3 | 44681.9 | 1.91 | 7.75 | 18.078 | 241.402 | 1 | 1 | 1140 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 581418.2346 | 55490.2192 | 1265.7381 | 10531.2873 | 44958.9319 | 252460.0297 | 0.043435 | -1949429.4295 | 1949429.4295
C | Xist Rating 4639 | -86.54 | 251.009 | 150.29 | 35.8 | 2351.27 | 7289.7 | 44186.8 | 1.87 | 7.64 | 17.923 | 235.158 | 1 | 1 | 1150 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 590189.9314 | 56374.8116 | 1288.0414 | 10623.667 | 45751.1446 | 245938.9061 | 0.043816 | -1899075.0419 | 1899075.0419
C | Xist Rating 4640 | -86.35 | 254.806 | 150.29 | 35.8 | 2351.16 | 7304.04 | 43703.9 | 1.82 | 7.53 | 17.8 | 229.228 | 1 | 1 | 1160 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 599089.675 | 57266.3228 | 1310.5395 | 10716.0467 | 46550.2761 | 239737.3972 | 0.044197 | -1851188.634 | 1851188.634
C | Xist Rating 4641 | -85.57 | 269.447 | 150.29 | 35.8 | 2350.51 | 7360.92 | 41832.9 | 1.84 | 7.13 | 17.933 | 206.207 | 1 | 1 | 1170 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 633337.868 | 58164.7529 | 1333.2324 | 10808.4264 | 47356.3265 | 215876.1512 | 0.044578 | -1666938.417 | 1666938.417
C | Xist Rating 4642 | -85.47 | 270.54 | 150.29 | 35.8 | 2358.94 | 7448.17 | 41725.3 | 1.78 | 7.11 | 17.865 | 205.112 | 1 | 1 | 1180 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 638187.6276 | 59070.1019 | 1356.1201 | 10900.8062 | 48169.2958 | 214690.472 | 0.044959 | -1657782.9166 | 1657782.9166
C | Xist Rating 4643 | -85.14 | 277.961 | 150.29 | 35.8 | 2349.44 | 7385.03 | 40886.2 | 1.74 | 6.93 | 17.725 | 195.522 | 1 | 1 | 1190 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 653052.6918 | 59982.3698 | 1379.2026 | 10993.1859 | 48989.184 | 204694.4146 | 0.04534 | -1580596.011 | 1580596.011
C | Xist Rating 4644 | -84.97 | 279.853 | 150.29 | 35.8 | 2361.29 | 7511.36 | 40682.6 | 1.71 | 6.88 | 17.754 | 193.288 | 1 | 1 | 1200 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 660814.0904 | 60901.5566 | 1402.4799 | 11085.5656 | 49815.991 | 202362.2985 | 0.045721 | -1562588.029 | 1562588.029
C | Xist Rating 4645 | -84.79 | 283.719 | 150.29 | 35.8 | 2357.09 | 7484.7 | 40282 | 1.65 | 6.8 | 17.636 | 188.951 | 1 | 1 | 1210 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 668751.2177 | 61827.6623 | 1425.9519 | 11177.9453 | 50649.717 | 197803.603 | 0.046102 | -1527386.9901 | 1527386.9901
C | Xist Rating 4646 | -83.99 | 300.356 | 150.29 | 35.8 | 2344.65 | 7431.37 | 38538.1 | 1.66 | 6.43 | 17.647 | 169.932 | 1 | 1 | 1220 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 704229.6954 | 62760.6869 | 1449.6188 | 11270.325 | 51490.3619 | 178076.0882 | 0.046483 | -1375056.3506 | 1375056.3506
C | Xist Rating 4647 | -83.76 | 304.072 | 150.29 | 35.8 | 2351.28 | 7514.05 | 38183.4 | 1.63 | 6.35 | 17.655 | 166.301 | 1 | 1 | 1230 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 714958.4122 | 63700.6303 | 1473.4804 | 11362.7047 | 52337.9256 | 174289.9617 | 0.046864 | -1345820.8852 | 1345820.8852
C | Xist Rating 4648 | -83.56 | 307.928 | 150.289 | 35.8 | 2350.76 | 7524.37 | 37835.8 | 1.59 | 6.28 | 17.571 | 162.857 | 1 | 1 | 1240 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 723864.8253 | 64647.4927 | 1497.5369 | 11455.0844 | 53192.4082 | 170679.5966 | 0.047245 | -1317942.6029 | 1317942.6029
C | Xist Rating 4649 | -83.44 | 309.964 | 150.289 | 35.8 | 2354.05 | 7566.08 | 37664.5 | 1.55 | 6.24 | 17.513 | 161.245 | 1 | 1 | 1250 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 729670.7542 | 65601.2739 | 1521.7881 | 11547.4642 | 54053.8097 | 168973.6424 | 0.047626 | -1304769.6764 | 1304769.6764
C | Xist Rating 4650 | -83.16 | 315.561 | 150.289 | 35.8 | 2352.59 | 7574.66 | 37161.6 | 1.52 | 6.14 | 17.476 | 156.257 | 1 | 1 | 1260 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 742385.653 | 66561.974 | 1546.2341 | 11639.8439 | 54922.1301 | 163772.9301 | 0.048007 | -1264611.1545 | 1264611.1545
C | Xist Rating 4651 | -82.38 | 331.321 | 150.289 | 35.8 | 2345.53 | 7569.93 | 35777.7 | 1.53 | 5.85 | 17.536 | 142.723 | 1 | 1 | 1270 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 777123.3451 | 67529.593 | 1570.8749 | 11732.2236 | 55797.3694 | 149744.974 | 0.048388 | -1156290.9962 | 1156290.9962
C | Xist Rating 4652 | -82.2 | 335.246 | 150.289 | 35.8 | 2342.28 | 7551.65 | 35477.6 | 1.49 | 5.79 | 17.449 | 140.033 | 1 | 1 | 1280 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 785240.0009 | 68504.1309 | 1595.7105 | 11824.6033 | 56679.5276 | 146915.7566 | 0.048769 | -1134444.5297 | 1134444.5297
C | Xist Rating 4653 | -82.01 | 339.119 | 150.289 | 35.8 | 2341.35 | 7557.52 | 35183 | 1.45 | 5.73 | 17.417 | 137.403 | 1 | 1 | 1290 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 793996.2707 | 69485.5877 | 1620.7408 | 11916.983 | 57568.6047 | 144153.118 | 0.04915 | -1113112.1668 | 1113112.1668
C | Xist Rating 4654 | -81.68 | 344.694 | 150.289 | 35.8 | 2347.34 | 7643.96 | 34751.3 | 1.43 | 5.64 | 17.448 | 133.505 | 1 | 1 | 1300 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 809114.014 | 70473.9633 | 1645.966 | 12009.3627 | 58464.6006 | 140098.6562 | 0.049531 | -1081804.6874 | 1081804.6874
C | Xist Rating 4655 | -81.48 | 347.678 | 150.289 | 35.8 | 2353.33 | 7719.85 | 34540.3 | 1.39 | 5.59 | 17.408 | 131.704 | 1 | 1 | 1310 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 818201.0677 | 71469.2579 | 1671.3859 | 12101.7424 | 59367.5154 | 138195.2577 | 0.049912 | -1067107.1485 | 1067107.1485
C | Xist Rating 4656 | -80.69 | 363.536 | 150.289 | 35.8 | 2347.52 | 7727.22 | 33363 | 1.4 | 5.35 | 17.457 | 121.31 | 1 | 1 | 1320 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 853408.0307 | 72471.4713 | 1697.0007 | 12194.1221 | 60277.3492 | 127426.3104 | 0.050293 | -983952.1922 | 983952.1922
C | Xist Rating 4657 | -80.42 | 369.329 | 150.289 | 35.8 | 2344.01 | 7713.05 | 32980.3 | 1.36 | 5.28 | 17.335 | 118.163 | 1 | 1 | 1330 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 865710.8693 | 73480.6036 | 1722.8102 | 12286.5019 | 61194.1018 | 124117.5901 | 0.050674 | -958403.1311 | 958403.1311
C | Xist Rating 4658 | -80.12 | 375.02 | 150.289 | 35.8 | 2345.81 | 7756.46 | 32607.3 | 1.33 | 5.2 | 17.305 | 115.115 | 1 | 1 | 1340 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 879725.6662 | 74496.6548 | 1748.8145 | 12378.8816 | 62117.7733 | 120929.1812 | 0.051055 | -933783.0826 | 933783.0826
C | Xist Rating 4659 | -79.92 | 378.02 | 150.289 | 35.8 | 2351.22 | 7828.16 | 32424.5 | 1.3 | 5.16 | 17.276 | 113.695 | 1 | 1 | 1350 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 888808.1844 | 75519.625 | 1775.0136 | 12471.2613 | 63048.3637 | 119431.1333 | 0.051436 | -922215.5539 | 922215.5539
C | Xist Rating 4660 | -79.7 | 379.859 | 150.289 | 35.7 | 2366.37 | 8007.06 | 32303.8 | 1.29 | 5.14 | 17.337 | 112.728 | 1 | 1 | 1360 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 898886.9418 | 76549.5139 | 1801.4075 | 12563.641 | 63985.8729 | 118431.2378 | 0.051817 | -914494.6256 | 914494.6256
C | Xist Rating 4661 | -78.73 | 402.432 | 150.289 | 35.7 | 2340.68 | 7817.83 | 30902.9 | 1.28 | 4.86 | 17.287 | 101.612 | 1 | 1 | 1370 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 941964.5338 | 77586.3218 | 1827.9962 | 12656.0207 | 64930.3011 | 106882.7374 | 0.052198 | -825320.167 | 825320.167
C | Xist Rating 4662 | -78.64 | 404.532 | 150.289 | 35.7 | 2340.01 | 7818.28 | 30794.8 | 1.25 | 4.84 | 17.256 | 100.863 | 1 | 1 | 1380 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 946608.9253 | 78630.0486 | 1854.7797 | 12748.4004 | 65881.6482 | 106080.3435 | 0.052579 | -819124.2933 | 819124.2933
C | Xist Rating 4663 | -78.39 | 409.393 | 150.289 | 35.7 | 2340.75 | 7846.7 | 30527.6 | 1.23 | 4.78 | 17.224 | 98.907 | 1 | 1 | 1390 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 958286.6647 | 79680.6942 | 1881.7579 | 12840.7801 | 66839.9141 | 104034.7537 | 0.05296 | -803328.7916 | 803328.7916
C | Xist Rating 4664 | -78.13 | 414.25 | 150.289 | 35.7 | 2341.75 | 7878.14 | 30265.5 | 1.2 | 4.73 | 17.195 | 97.009 | 1 | 1 | 1400 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 970069.9375 | 80738.2588 | 1908.931 | 12933.1599 | 67805.0989 | 102038.5697 | 0.053341 | -787914.7876 | 787914.7876
C | Xist Rating 4665 | -77.84 | 420.003 | 150.289 | 35.7 | 2342.04 | 7905.78 | 29957.8 | 1.18 | 4.67 | 17.174 | 94.787 | 1 | 1 | 1410 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 983663.8261 | 81802.7422 | 1936.2988 | 13025.5396 | 68777.2026 | 99716.9737 | 0.053722 | -769988.039 | 769988.039
C | Xist Rating 4666 | -76.99 | 436.882 | 150.289 | 35.7 | 2338.31 | 7938.11 | 29052.1 | 1.19 | 4.49 | 17.24 | 88.22 | 1 | 1 | 1420 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1021565.5494 | 82874.1445 | 1963.8614 | 13117.9193 | 69756.2252 | 92922.169 | 0.054103 | -717520.3583 | 717520.3583
C | Xist Rating 4667 | -76.86 | 440.123 | 150.289 | 35.7 | 2335.1 | 7913.37 | 28910.9 | 1.15 | 4.47 | 17.169 | 87.333 | 1 | 1 | 1430 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1027731.2173 | 83952.4657 | 1991.6188 | 13210.299 | 70742.1667 | 91960.7804 | 0.054484 | -710096.7704 | 710096.7704
C | Xist Rating 4668 | -76.49 | 447.713 | 150.288 | 35.7 | 2333.16 | 7923.23 | 28542.3 | 1.14 | 4.39 | 17.153 | 84.819 | 1 | 1 | 1440 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1044586.0631 | 85037.7058 | 2019.571 | 13302.6787 | 71735.0271 | 89346.5862 | 0.054865 | -689910.6558 | 689910.6558
C | Xist Rating 4669 | -76.25 | 452.609 | 150.288 | 35.7 | 2332.86 | 7939.95 | 28317.1 | 1.12 | 4.35 | 17.131 | 83.34 | 1 | 1 | 1450 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1055873.4317 | 86129.8648 | 2047.718 | 13395.0584 | 72734.8064 | 87795.5133 | 0.055246 | -677933.682 | 677933.682
C | Xist Rating 4670 | -76.04 | 455.491 | 150.288 | 35.7 | 2340.15 | 8037.39 | 28183.9 | 1.11 | 4.32 | 17.15 | 82.472 | 1 | 1 | 1460 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1065917.2637 | 87228.9427 | 2076.0598 | 13487.4381 | 73741.5045 | 86892.8661 | 0.055627 | -670963.6793 | 670963.6793
C | Xist Rating 4671 | -75.21 | 474.637 | 150.288 | 35.7 | 2324.38 | 7935.7 | 27310.5 | 1.09 | 4.16 | 17.14 | 76.715 | 1 | 1 | 1470 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1103236.7501 | 88334.9394 | 2104.5964 | 13579.8178 | 74755.1216 | 80899.4445 | 0.056008 | -624684.0662 | 624684.0662
C | Xist Rating 4672 | -74.91 | 480.433 | 150.288 | 35.7 | 2325.02 | 7967.22 | 27066.2 | 1.08 | 4.11 | 17.126 | 75.194 | 1 | 1 | 1480 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1117016.3337 | 89447.855 | 2133.3277 | 13672.1976 | 75775.6575 | 79315.889 | 0.056389 | -612456.2703 | 612456.2703
C | Xist Rating 4673 | -74.65 | 485.33 | 150.288 | 35.7 | 2326.59 | 8005.9 | 26866.6 | 1.06 | 4.07 | 17.116 | 73.975 | 1 | 1 | 1490 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1129163.9247 | 90567.6896 | 2162.2539 | 13764.5773 | 76803.1123 | 78034.6658 | 0.05677 | -602563.0044 | 602563.0044
C | Xist Rating 4674 | -74.37 | 490.32 | 150.288 | 35.7 | 2328.84 | 8052.98 | 26670.5 | 1.04 | 4.03 | 17.099 | 72.802 | 1 | 1 | 1500 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1141876.8288 | 91694.443 | 2191.3748 | 13856.957 | 77837.486 | 76800.4343 | 0.057151 | -593032.5964 | 593032.5964
C | Xist Rating 4675 | -74.02 | 496.143 | 150.288 | 35.7 | 2334.24 | 8142.87 | 26439 | 1.02 | 3.99 | 17.101 | 71.408 | 1 | 1 | 1510 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1158116.8363 | 92828.1153 | 2220.6906 | 13949.3367 | 78878.7786 | 75337.7298 | 0.057532 | -581737.9795 | 581737.9795
C | Xist Rating 4676 | -73.07 | 514.972 | 150.289 | 35.7 | 2331.9 | 8199.82 | 25681.2 | 1.03 | 3.85 | 17.176 | 66.785 | 1 | 1 | 1520 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1200863.2068 | 93968.7065 | 2250.2011 | 14041.7164 | 79926.9901 | 70561.4852 | 0.057913 | -544857.0847 | 544857.0847
C | Xist Rating 4677 | -72.83 | 521.139 | 150.288 | 35.7 | 2325.68 | 8148.22 | 25468.5 | 1 | 3.8 | 17.115 | 65.61 | 1 | 1 | 1530 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1212002.5495 | 95116.2166 | 2279.9064 | 14134.0961 | 80982.1204 | 69309.6573 | 0.058294 | -535190.8018 | 535190.8018
C | Xist Rating 4678 | -72.61 | 524.295 | 150.288 | 35.7 | 2330.9 | 8225.3 | 25363.7 | 0.98 | 3.78 | 17.106 | 65.054 | 1 | 1 | 1540 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1222079.2155 | 96270.6455 | 2309.8065 | 14226.4758 | 82044.1697 | 68715.6861 | 0.058675 | -530604.3137 | 530604.3137
C | Xist Rating 4679 | -72.14 | 533.85 | 150.288 | 35.7 | 2329.5 | 8249.96 | 25021.2 | 0.97 | 3.72 | 17.1 | 63.107 | 1 | 1 | 1550 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1243603.575 | 97431.9934 | 2339.9013 | 14318.8555 | 83113.1378 | 66688.9548 | 0.059056 | -514954.4313 | 514954.4313
C | Xist Rating 4680 | -71.87 | 536.782 | 150.288 | 35.7 | 2340.88 | 8407.5 | 24920.6 | 0.95 | 3.7 | 17.129 | 62.561 | 1 | 1 | 1560 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1256542.2482 | 98600.2601 | 2370.191 | 14411.2353 | 84189.0249 | 66107.3813 | 0.059437 | -510463.6753 | 510463.6753
C | Xist Rating 4681 | -70.96 | 558.992 | 150.288 | 35.7 | 2321.12 | 8255.7 | 24162.1 | 0.95 | 3.56 | 17.114 | 58.356 | 1 | 1 | 1570 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1297487.511 | 99775.4458 | 2400.6755 | 14503.615 | 85271.8308 | 61746.7867 | 0.059818 | -476792.3198 | 476792.3198
C | Xist Rating 4682 | -70.67 | 564.01 | 150.288 | 35.7 | 2324.26 | 8316.64 | 24007.5 | 0.93 | 3.53 | 17.106 | 57.561 | 1 | 1 | 1580 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1310905.8826 | 100957.5503 | 2431.3547 | 14595.9947 | 86361.5556 | 60903.7 | 0.0602 | -470282.2277 | 470282.2277
C | Xist Rating 4683 | -70.39 | 569.063 | 150.288 | 35.7 | 2327.09 | 8374.46 | 23855.1 | 0.91 | 3.5 | 17.096 | 56.787 | 1 | 1 | 1590 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1324260.8167 | 102146.5737 | 2462.2288 | 14688.3744 | 87458.1993 | 60082.0013 | 0.060581 | -463937.2883 | 463937.2883
C | Xist Rating 4684 | -70 | 575.812 | 150.288 | 35.7 | 2330.66 | 8451.33 | 23645.4 | 0.9 | 3.46 | 17.105 | 55.697 | 1 | 1 | 1600 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1342021.9959 | 103342.516 | 2493.2976 | 14780.7541 | 88561.7619 | 58945.3314 | 0.060962 | -455160.2241 | 455160.2241
C | Xist Rating 4685 | -69.8 | 579.164 | 150.288 | 35.7 | 2333.8 | 8505.97 | 23556.7 | 0.88 | 3.45 | 17.084 | 55.29 | 1 | 1 | 1610 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1351652.9432 | 104545.3772 | 2524.5612 | 14873.1338 | 89672.2433 | 58503.5408 | 0.061343 | -451748.8345 | 451748.8345
C | Xist Rating 4686 | -68.72 | 603.97 | 150.288 | 35.7 | 2318.44 | 8418 | 22805 | 0.88 | 3.31 | 17.093 | 51.409 | 1 | 1 | 1620 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1400268.2068 | 105755.1572 | 2556.0196 | 14965.5135 | 90789.6437 | 54480.4425 | 0.061724 | -420683.5355 | 420683.5355
C | Xist Rating 4687 | -68.44 | 606.977 | 150.289 | 35.7 | 2328.4 | 8564 | 22723.6 | 0.87 | 3.29 | 17.111 | 51.027 | 1 | 1 | 1630 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1413285.2468 | 106971.8562 | 2587.6728 | 15057.8933 | 91913.9629 | 54079.1338 | 0.062105 | -417584.7368 | 417584.7368
C | Xist Rating 4688 | -68.18 | 612.178 | 150.289 | 35.7 | 2328.36 | 8585.63 | 22589 | 0.85 | 3.27 | 17.088 | 50.404 | 1 | 1 | 1640 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1425370.7681 | 108195.474 | 2619.5208 | 15150.273 | 93045.2011 | 53412.2276 | 0.062486 | -412435.0634 | 412435.0634
C | Xist Rating 4689 | -67.87 | 619.283 | 150.288 | 35.7 | 2325.27 | 8574.69 | 22403.3 | 0.84 | 3.24 | 17.063 | 49.535 | 1 | 1 | 1650 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1440000.1814 | 109426.0108 | 2651.5635 | 15242.6527 | 94183.3581 | 52502.0916 | 0.062867 | -405407.2344 | 405407.2344
C | Xist Rating 4690 | -67.51 | 626.145 | 150.289 | 35.7 | 2326.49 | 8622.48 | 22221.2 | 0.83 | 3.2 | 17.063 | 48.673 | 1 | 1 | 1660 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1456720.081 | 110663.4664 | 2683.8011 | 15335.0324 | 95328.434 | 51600.6342 | 0.063248 | -398446.4197 | 398446.4197
C | Xist Rating 4691 | -66.54 | 648.399 | 150.289 | 35.7 | 2315.05 | 8569.52 | 21633.2 | 0.82 | 3.1 | 17.09 | 45.875 | 1 | 1 | 1670 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1501076.105 | 111907.8409 | 2716.2334 | 15427.4121 | 96480.4288 | 48690.1483 | 0.063629 | -375972.4189 | 375972.4189
C | Xist Rating 4692 | -66.32 | 651.518 | 150.289 | 35.7 | 2320.1 | 8652.48 | 21560.6 | 0.81 | 3.08 | 17.093 | 45.567 | 1 | 1 | 1680 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1511586.9118 | 113159.1343 | 2748.8606 | 15519.7918 | 97639.3424 | 48363.8857 | 0.06401 | -373453.1058 | 373453.1058
C | Xist Rating 4693 | -65.94 | 660.578 | 150.289 | 35.7 | 2314.98 | 8621.39 | 21346.3 | 0.8 | 3.04 | 17.068 | 44.618 | 1 | 1 | 1690 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1529224.8584 | 114417.3466 | 2781.6825 | 15612.1715 | 98805.175 | 47370.0932 | 0.064391 | -365779.3033 | 365779.3033
C | Xist Rating 4694 | -65.63 | 666.558 | 150.289 | 35.7 | 2316.21 | 8665.09 | 21206 | 0.79 | 3.02 | 17.069 | 44.005 | 1 | 1 | 1700 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1543888.3052 | 115682.4777 | 2814.6992 | 15704.5512 | 99977.9265 | 46726.6683 | 0.064772 | -360810.9465 | 360810.9465
C | Xist Rating 4695 | -65.27 | 673.613 | 150.289 | 35.7 | 2316.14 | 8695.46 | 21045.2 | 0.78 | 2.99 | 17.06 | 43.31 | 1 | 1 | 1710 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1560182.0138 | 116954.5278 | 2847.9107 | 15796.931 | 101157.5968 | 45997.3348 | 0.065153 | -355179.2265 | 355179.2265
C | Xist Rating 4696 | -64.39 | 694.116 | 150.289 | 35.7 | 2305.91 | 8646.72 | 20567.5 | 0.77 | 2.9 | 17.092 | 41.2 | 1 | 1 | 1720 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1600569.0256 | 118233.4967 | 2881.317 | 15889.3107 | 102344.186 | 43800.8145 | 0.065534 | -338218.2796 | 338218.2796
C | Xist Rating 4697 | -63.97 | 703.046 | 150.289 | 35.7 | 2304.16 | 8661.81 | 20374.8 | 0.76 | 2.87 | 17.082 | 40.393 | 1 | 1 | 1730 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1619930.4714 | 119519.3846 | 2914.9181 | 15981.6904 | 103537.6942 | 42954.802 | 0.065915 | -331685.5949 | 331685.5949
C | Xist Rating 4698 | -63.71 | 707.212 | 150.289 | 35.7 | 2308.7 | 8744.2 | 20290.1 | 0.75 | 2.85 | 17.083 | 40.059 | 1 | 1 | 1740 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1632740.3444 | 120812.1913 | 2948.714 | 16074.0701 | 104738.1212 | 42600.4982 | 0.066296 | -328949.755 | 328949.755
C | Xist Rating 4699 | -63.37 | 715.374 | 150.289 | 35.6 | 2305.17 | 8729.4 | 20123.5 | 0.74 | 2.82 | 17.062 | 39.385 | 1 | 1 | 1750 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1649058.6836 | 122111.9169 | 2982.7046 | 16166.4498 | 105945.4671 | 41891.6739 | 0.066677 | -323476.4014 | 323476.4014
C | Xist Rating 4700 | -63.08 | 721.471 | 150.289 | 35.7 | 2303.62 | 8733.81 | 20001.2 | 0.73 | 2.8 | 17.059 | 38.896 | 1 | 1 | 1760 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 20 | E | Rod | 1661995.025 | 123418.5614 | 3016.8901 | 16258.8295 | 107159.7318 | 41375.8744 | 0.067058 | -319493.5348 | 319493.5348
C | Xist Rating 4701 | -62.04 | 745.767 | 150.289 | 35.7 | 2292.39 | 8685.14 | 19497.8 | 0.73 | 2.71 | 17.083 | 36.819 | 1 | 1 | 1770 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1709588.8131 | 124732.1248 | 3051.2703 | 16351.2092 | 108380.9155 | 39225.8853 | 0.067439 | -302891.8886 | 302891.8886
C | Xist Rating 4702 | -61.91 | 751.973 | 150.289 | 35.6 | 2284.49 | 8598.44 | 19383.4 | 0.72 | 2.69 | 17.265 | 36.377 | 1 | 1 | 1780 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1717874.7988 | 126052.607 | 3085.8453 | 16443.589 | 109609.0181 | 38769.2841 | 0.06782 | -299366.1354 | 299366.1354
C | Xist Rating 4703 | -61.76 | 755.351 | 150.289 | 35.6 | 2283.09 | 8591.42 | 19327.2 | 0.7 | 2.68 | 17.253 | 36.183 | 1 | 1 | 1790 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1724534.3146 | 127380.0082 | 3120.6151 | 16535.9687 | 110844.0395 | 38545.008 | 0.068201 | -297634.3345 | 297634.3345
C | Xist Rating 4704 | -61.3 | 766.273 | 150.289 | 35.6 | 2280.47 | 8601.51 | 19121.9 | 0.7 | 2.65 | 17.239 | 35.392 | 1 | 1 | 1800 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1747462.5883 | 128714.3282 | 3155.5797 | 16628.3484 | 112085.9799 | 37728.1785 | 0.068582 | -291326.9941 | 291326.9941
C | Xist Rating 4705 | -61 | 772.351 | 150.289 | 35.6 | 2280.59 | 8628.91 | 19012.5 | 0.69 | 2.63 | 17.239 | 34.984 | 1 | 1 | 1810 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1761415.9671 | 130055.5672 | 3190.7391 | 16720.7281 | 113334.8391 | 37295.8939 | 0.068963 | -287989.0063 | 287989.0063
C | Xist Rating 4706 | -59.97 | 796.907 | 150.289 | 35.6 | 2269.41 | 8577.41 | 18562.8 | 0.69 | 2.55 | 17.272 | 33.258 | 1 | 1 | 1820 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1808508.7149 | 131403.725 | 3226.0933 | 16813.1078 | 114590.6172 | 35510.635 | 0.069344 | -274203.7109 | 274203.7109
C | Xist Rating 4707 | -59.94 | 792.996 | 150.289 | 35.6 | 2283.09 | 8758.64 | 18631.2 | 0.68 | 2.56 | 17.297 | 33.529 | 1 | 1 | 1830 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1810481.2376 | 132758.8017 | 3261.6423 | 16905.4875 | 115853.3142 | 35784.6366 | 0.069725 | -276319.4783 | 276319.4783
C | Xist Rating 4708 | -59.56 | 797.975 | 150.289 | 35.6 | 2291.11 | 8900.54 | 18545.3 | 0.68 | 2.55 | 17.317 | 33.219 | 1 | 1 | 1840 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1828248.5023 | 134120.7973 | 3297.386 | 16997.8672 | 117122.9301 | 35469.096 | 0.070106 | -273882.9577 | 273882.9577
C | Xist Rating 4709 | -59.19 | 806.255 | 150.289 | 35.6 | 2288.68 | 8900.17 | 18409.4 | 0.66 | 2.52 | 17.306 | 32.737 | 1 | 1 | 1850 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1845259.6934 | 135489.7118 | 3333.3246 | 17090.2469 | 118399.4648 | 34944.4957 | 0.070487 | -269832.1327 | 269832.1327
C | Xist Rating 4710 | -58.8 | 815.527 | 150.289 | 35.6 | 2284.6 | 8879.03 | 18259.3 | 0.65 | 2.5 | 17.297 | 32.206 | 1 | 1 | 1860 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1863152.9842 | 136865.5451 | 3369.4579 | 17182.6267 | 119682.9185 | 34383.2564 | 0.070868 | -265498.3922 | 265498.3922
C | Xist Rating 4711 | -57.78 | 838.06 | 150.289 | 35.6 | 2279.07 | 8900.77 | 17879.7 | 0.65 | 2.43 | 17.343 | 30.821 | 1 | 1 | 1870 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1909997.4042 | 138248.2974 | 3405.7861 | 17275.0064 | 120973.291 | 32952.4821 | 0.071249 | -254450.3317 | 254450.3317
C | Xist Rating 4712 | -57.37 | 847.318 | 150.289 | 35.6 | 2276.3 | 8898.85 | 17739.1 | 0.64 | 2.41 | 17.335 | 30.344 | 1 | 1 | 1880 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1928749.9634 | 139637.9686 | 3442.309 | 17367.3861 | 122270.5825 | 32447.1249 | 0.07163 | -250548.0977 | 250548.0977
C | Xist Rating 4713 | -57.01 | 853.444 | 150.289 | 35.6 | 2279.72 | 8978.67 | 17646.7 | 0.63 | 2.39 | 17.345 | 30.035 | 1 | 1 | 1890 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1945613.3557 | 141034.5586 | 3479.0267 | 17459.7658 | 123574.7928 | 32117.0497 | 0.072011 | -247999.3443 | 247999.3443
C | Xist Rating 4714 | -56.77 | 860.029 | 150.289 | 35.6 | 2275.68 | 8943.38 | 17555.2 | 0.62 | 2.38 | 17.333 | 29.745 | 1 | 1 | 1900 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1957150.7947 | 142438.0675 | 3515.9392 | 17552.1455 | 124885.922 | 31805.3775 | 0.072392 | -245592.694 | 245592.694
C | Xist Rating 4715 | -56.48 | 866.334 | 150.289 | 35.6 | 2274.53 | 8952.63 | 17465.2 | 0.61 | 2.36 | 17.34 | 29.452 | 1 | 1 | 1910 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 1970502.673 | 143848.4953 | 3553.0464 | 17644.5252 | 126203.9701 | 31491.4404 | 0.072773 | -243168.5553 | 243168.5553
C | Xist Rating 4716 | -55.3 | 893.706 | 150.289 | 35.6 | 2265.73 | 8944.25 | 17050.3 | 0.61 | 2.29 | 17.383 | 28.026 | 1 | 1 | 1920 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2024896.4954 | 145265.842 | 3590.3485 | 17736.9049 | 127528.9371 | 30017.5404 | 0.073154 | -231787.49 | 231787.49
C | Xist Rating 4717 | -54.9 | 903.041 | 150.289 | 35.6 | 2262.44 | 8933.18 | 16924.2 | 0.6 | 2.27 | 17.378 | 27.626 | 1 | 1 | 1930 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2043076.08 | 146690.1076 | 3627.8454 | 17829.2847 | 128860.8229 | 29591.5962 | 0.073535 | -228498.462 | 228498.462
C | Xist Rating 4718 | -54.59 | 906.057 | 150.289 | 35.6 | 2271.37 | 9088.07 | 16882.1 | 0.6 | 2.26 | 17.393 | 27.499 | 1 | 1 | 1940 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2057990.6881 | 148121.2921 | 3665.537 | 17921.6644 | 130199.6277 | 29465.1633 | 0.073916 | -227522.1808 | 227522.1808
C | Xist Rating 4719 | -54.31 | 914.907 | 150.289 | 35.6 | 2264.05 | 9007.93 | 16772.2 | 0.58 | 2.24 | 17.377 | 27.169 | 1 | 1 | 1950 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2071395.1934 | 149559.3954 | 3703.4235 | 18014.0441 | 131545.3514 | 29095.9197 | 0.074297 | -224670.9797 | 224670.9797
C | Xist Rating 4720 | -53.88 | 925.115 | 150.289 | 35.6 | 2260.5 | 8996.95 | 16637.1 | 0.58 | 2.22 | 17.389 | 26.744 | 1 | 1 | 1960 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2091222.4575 | 151004.4177 | 3741.5047 | 18106.4238 | 132897.9939 | 28659.6871 | 0.074678 | -221302.507 | 221302.507
C | Xist Rating 4721 | -52.82 | 949.799 | 150.289 | 35.6 | 2252.94 | 8991.4 | 16303.2 | 0.58 | 2.16 | 17.451 | 25.67 | 1 | 1 | 1970 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2139840.1591 | 152456.3588 | 3779.7807 | 18198.8035 | 134257.5553 | 27552.0361 | 0.075059 | -212749.5194 | 212749.5194
C | Xist Rating 4722 | -52.47 | 957.078 | 150.289 | 35.6 | 2253.03 | 9024.26 | 16214.4 | 0.57 | 2.15 | 17.479 | 25.406 | 1 | 1 | 1980 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2156325.4463 | 153915.2188 | 3818.2515 | 18291.1832 | 135624.0356 | 27268.3377 | 0.07544 | -210558.8758 | 210558.8758
C | Xist Rating 4723 | -52.1 | 966.608 | 150.289 | 35.6 | 2248.84 | 8997.4 | 16101.5 | 0.56 | 2.13 | 17.477 | 25.076 | 1 | 1 | 1990 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2173746.7347 | 155380.9977 | 3856.9171 | 18383.5629 | 136997.4348 | 26914.4078 | 0.075821 | -207825.9226 | 207825.9226
C | Xist Rating 4724 | -51.78 | 974.012 | 150.289 | 35.6 | 2247.17 | 9001.95 | 16015 | 0.55 | 2.12 | 17.479 | 24.826 | 1 | 1 | 2000 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2188770.546 | 156853.6955 | 3895.7775 | 18475.9426 | 138377.7529 | 26643.6008 | 0.076202 | -205734.823 | 205734.823
C | Xist Rating 4725 | -51.51 | 979.464 | 150.289 | 35.6 | 2247.69 | 9032.74 | 15953.9 | 0.54 | 2.11 | 17.482 | 24.656 | 1 | 1 | 2010 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2201531.4382 | 158333.3122 | 3934.8326 | 18568.3224 | 139764.9899 | 26455.7631 | 0.076583 | -204284.3899 | 204284.3899
C | Xist Rating 4726 | -50.38 | 1007.28 | 150.289 | 35.6 | 2237.73 | 8998.94 | 15614.9 | 0.54 | 2.05 | 17.519 | 23.629 | 1 | 1 | 2020 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2254020.6744 | 159819.8478 | 3974.0826 | 18660.7021 | 141159.1457 | 25395.2659 | 0.076964 | -196095.5116 | 196095.5116
C | Xist Rating 4727 | -49.91 | 1017.44 | 150.289 | 35.6 | 2236.7 | 9026.61 | 15499.8 | 0.54 | 2.03 | 17.522 | 23.299 | 1 | 1 | 2030 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2275708.048 | 161313.3023 | 4013.5273 | 18753.0818 | 142560.2205 | 25056.9493 | 0.077345 | -193483.121 | 193483.121
C | Xist Rating 4728 | -49.65 | 1024.22 | 150.289 | 35.7 | 2234.02 | 9009.62 | 15431.8 | 0.53 | 2.02 | 17.517 | 23.122 | 1 | 1 | 2040 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2288127.9644 | 162813.6756 | 4053.1669 | 18845.4615 | 143968.2141 | 24861.1115 | 0.077726 | -191970.9134 | 191970.9134
C | Xist Rating 4729 | -49.29 | 1030.19 | 150.289 | 35.7 | 2237.76 | 9097.88 | 15364.3 | 0.52 | 2.01 | 17.531 | 22.932 | 1 | 1 | 2050 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2305317.9744 | 164320.9679 | 4093.0012 | 18937.8412 | 145383.1266 | 24652.5309 | 0.078107 | -190360.3087 | 190360.3087
C | Xist Rating 4730 | -48.96 | 1040.11 | 150.289 | 35.7 | 2231.58 | 9036.38 | 15264.3 | 0.51 | 1.99 | 17.517 | 22.666 | 1 | 1 | 2060 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2321088.6738 | 165835.179 | 4133.0303 | 19030.2209 | 146804.9581 | 24363.5293 | 0.078488 | -188128.7155 | 188128.7155
C | Xist Rating 4731 | -47.75 | 1069.99 | 150.289 | 35.7 | 2221.25 | 9001.53 | 14936.2 | 0.51 | 1.94 | 17.554 | 21.728 | 1 | 1 | 2070 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2376715.2875 | 167356.309 | 4173.2542 | 19122.6006 | 148233.7084 | 23395.1732 | 0.078869 | -180651.3261 | 180651.3261
C | Xist Rating 4732 | -47.47 | 1076.57 | 150.289 | 35.7 | 2220.04 | 9007.86 | 14873.5 | 0.51 | 1.93 | 17.551 | 21.57 | 1 | 1 | 2080 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2390028.4628 | 168884.3579 | 4213.6729 | 19214.9803 | 149669.3775 | 23234.9607 | 0.07925 | -179414.208 | 179414.208
C | Xist Rating 4733 | -47.13 | 1085.05 | 150.289 | 35.7 | 2218.03 | 9009.83 | 14790.9 | 0.5 | 1.91 | 17.552 | 21.355 | 1 | 1 | 2090 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2406673.4515 | 170419.3257 | 4254.2864 | 19307.3601 | 151111.9656 | 22999.3003 | 0.079631 | -177594.5004 | 177594.5004
C | Xist Rating 4734 | -46.78 | 1093.54 | 150.289 | 35.7 | 2216.15 | 9013.88 | 14709.3 | 0.49 | 1.9 | 17.55 | 21.144 | 1 | 1 | 2100 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2423448.671 | 171961.2124 | 4295.0947 | 19399.7398 | 152561.4726 | 22767.4967 | 0.080012 | -175804.5744 | 175804.5744
C | Xist Rating 4735 | -46.43 | 1101.04 | 150.289 | 35.7 | 2216.26 | 9046.57 | 14638.6 | 0.49 | 1.89 | 17.553 | 20.965 | 1 | 1 | 2110 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2440190.9104 | 173510.0179 | 4336.0977 | 19492.1195 | 154017.8984 | 22585.5992 | 0.080393 | -174400.0102 | 174400.0102
C | Xist Rating 4736 | -45.32 | 1129.3 | 150.289 | 35.7 | 2206.2 | 9003.61 | 14358.9 | 0.48 | 1.84 | 17.588 | 20.212 | 1 | 1 | 2120 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2491461.66 | 175065.7424 | 4377.2956 | 19584.4992 | 155481.2432 | 21792.3814 | 0.080774 | -168274.9927 | 168274.9927
C | Xist Rating 4737 | -44.89 | 1139.79 | 150.289 | 35.7 | 2203.67 | 9004.73 | 14263.6 | 0.48 | 1.83 | 17.581 | 19.973 | 1 | 1 | 2130 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2511721.0293 | 176628.3857 | 4418.6882 | 19676.8789 | 156951.5068 | 21547.6437 | 0.081155 | -166385.1929 | 166385.1929
C | Xist Rating 4738 | -44.51 | 1150.31 | 150.289 | 35.7 | 2199.39 | 8976.49 | 14169.9 | 0.47 | 1.81 | 17.575 | 19.739 | 1 | 1 | 2140 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2529980.3109 | 178197.9479 | 4460.2756 | 19769.2586 | 158428.6893 | 21291.2827 | 0.081536 | -164405.6414 | 164405.6414
C | Xist Rating 4739 | -44.28 | 1155.92 | 150.289 | 35.7 | 2198.7 | 8986.66 | 14123.3 | 0.47 | 1.8 | 17.575 | 19.633 | 1 | 1 | 2150 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2541521.304 | 179774.429 | 4502.0578 | 19861.6383 | 159912.7907 | 21184.9045 | 0.081917 | -163584.2171 | 163584.2171
C | Xist Rating 4740 | -43.94 | 1163.36 | 150.289 | 35.7 | 2198.2 | 9008.22 | 14059.2 | 0.46 | 1.79 | 17.575 | 19.477 | 1 | 1 | 2160 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2557297.952 | 181357.829 | 4544.0348 | 19954.0181 | 161403.811 | 21009.5851 | 0.082298 | -162230.4467 | 162230.4467
C | Xist Rating 4741 | -42.81 | 1193.89 | 150.29 | 35.7 | 2186.08 | 8935.76 | 13786 | 0.46 | 1.75 | 17.61 | 18.783 | 1 | 1 | 2170 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2609939.0512 | 182948.1479 | 4586.2066 | 20046.3978 | 162901.7502 | 20294.057 | 0.082679 | -156705.3291 | 156705.3291
C | Xist Rating 4742 | -42.38 | 1204.16 | 150.29 | 35.7 | 2184.44 | 8950.75 | 13699 | 0.46 | 1.74 | 17.61 | 18.573 | 1 | 1 | 2180 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2630415.2704 | 184545.3857 | 4628.5732 | 20138.7775 | 164406.6082 | 20079.6034 | 0.08306 | -155049.3752 | 155049.3752
C | Xist Rating 4743 | -42.04 | 1211.84 | 150.289 | 35.7 | 2184.14 | 8975.24 | 13639.1 | 0.45 | 1.73 | 17.609 | 18.437 | 1 | 1 | 2190 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2646828.2176 | 186149.5424 | 4671.1346 | 20231.1572 | 165918.3852 | 19924.6675 | 0.083441 | -153853.0011 | 153853.0011
C | Xist Rating 4744 | -41.77 | 1219.92 | 150.29 | 35.6 | 2180.73 | 8947.5 | 13579.5 | 0.44 | 1.72 | 17.605 | 18.307 | 1 | 1 | 2200 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2660316.1416 | 187760.6179 | 4713.8907 | 20323.5369 | 167437.081 | 19775.6761 | 0.083822 | -152702.5289 | 152702.5289
C | Xist Rating 4745 | -41.35 | 1230.45 | 150.289 | 35.6 | 2178.41 | 8950.7 | 13495.4 | 0.44 | 1.7 | 17.605 | 18.111 | 1 | 1 | 2210 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2680424.5845 | 189378.6124 | 4756.8417 | 20415.9166 | 168962.6957 | 19575.6026 | 0.084203 | -151157.6145 | 151157.6145
C | Xist Rating 4746 | -40.18 | 1260.84 | 150.29 | 35.6 | 2168.92 | 8918.45 | 13246.1 | 0.44 | 1.66 | 17.643 | 17.508 | 1 | 1 | 2220 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2734661.0928 | 191003.5257 | 4799.9874 | 20508.2963 | 170495.2294 | 18954.5241 | 0.084584 | -146361.8108 | 146361.8108
C | Xist Rating 4747 | -39.82 | 1269.29 | 150.29 | 35.6 | 2167.95 | 8935.44 | 13182.4 | 0.43 | 1.65 | 17.642 | 17.366 | 1 | 1 | 2230 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2751757.2555 | 192635.3579 | 4843.3279 | 20600.676 | 172034.6819 | 18792.8583 | 0.084965 | -145113.4702 | 145113.4702
C | Xist Rating 4748 | -39.47 | 1279.18 | 150.29 | 35.6 | 2164.41 | 8912.79 | 13111.6 | 0.43 | 1.64 | 17.636 | 17.212 | 1 | 1 | 2240 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2768669.9838 | 194274.109 | 4886.8633 | 20693.0558 | 173581.0532 | 18636.0709 | 0.085346 | -143902.7996 | 143902.7996
C | Xist Rating 4749 | -39.08 | 1290.02 | 150.29 | 35.6 | 2160.84 | 8893.66 | 13034 | 0.42 | 1.63 | 17.631 | 17.043 | 1 | 1 | 2250 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2787526.8168 | 195919.779 | 4930.5934 | 20785.4355 | 175134.3435 | 18445.9653 | 0.085727 | -142434.8543 | 142434.8543
C | Xist Rating 4750 | -38.83 | 1295.58 | 150.29 | 35.6 | 2161.12 | 8919.14 | 12995.5 | 0.42 | 1.62 | 17.633 | 16.963 | 1 | 1 | 2260 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2799903.8496 | 197572.3679 | 4974.5182 | 20877.8152 | 176694.5527 | 18366.2898 | 0.086108 | -141819.6212 | 141819.6212
C | Xist Rating 4751 | -37.63 | 1328.34 | 150.29 | 35.6 | 2149.97 | 8863.29 | 12751.8 | 0.42 | 1.59 | 17.668 | 16.405 | 1 | 1 | 2270 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2855891.1498 | 199231.8756 | 5018.6379 | 20970.1949 | 178261.6807 | 17791.6231 | 0.086489 | -137382.1972 | 137382.1972
C | Xist Rating 4752 | -37.25 | 1338.18 | 150.29 | 35.6 | 2147.78 | 8862.65 | 12686.1 | 0.41 | 1.58 | 17.665 | 16.268 | 1 | 1 | 2280 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2874116.2404 | 200898.3023 | 5062.9524 | 21062.5746 | 179835.7277 | 17634.4926 | 0.08687 | -136168.8773 | 136168.8773
C | Xist Rating 4753 | -36.81 | 1349.75 | 150.29 | 35.6 | 2145.17 | 8863.1 | 12606.8 | 0.41 | 1.56 | 17.665 | 16.099 | 1 | 1 | 2290 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2895443.2075 | 202571.6478 | 5107.4617 | 21154.9543 | 181416.6935 | 17462.2328 | 0.087251 | -134838.7332 | 134838.7332
C | Xist Rating 4754 | -36.51 | 1357.59 | 150.29 | 35.6 | 2143.41 | 8861.34 | 12557 | 0.4 | 1.56 | 17.665 | 15.999 | 1 | 1 | 2300 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2909871.9819 | 204251.9123 | 5152.1657 | 21247.334 | 183004.5782 | 17343.4175 | 0.087632 | -133921.2723 | 133921.2723
| Xist Rating 4755 | -36.23 | 1365.7 | 150.29 | 35.6 | 2140.68 | 8843.17 | 12507.5 | 0.4 | 1.55 | 17.661 | 15.903 | 1 | 1 | 2310 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2923526.676 | 205939.0956 | 5197.0645 | 21339.7138 | 184599.3818 | 17246.7232 | 0.088013 | -133174.6253 | 133174.6253
| Xist Rating 4756 | -34.97 | 1399.28 | 150.29 | 35.6 | 2131.35 | 8818.38 | 12277.1 | 0.4 | 1.51 | 17.697 | 15.398 | 1 | 1 | 2320 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2982355.428 | 207633.1978 | 5242.1582 | 21432.0935 | 186201.1043 | 16726.9456 | 0.088394 | -129161.0404 | 129161.0404
| Xist Rating 4757 | -34.62 | 1409.15 | 150.29 | 35.6 | 2128.56 | 8806.4 | 12216.8 | 0.39 | 1.5 | 17.69 | 15.279 | 1 | 1 | 2330 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 2999460.324 | 209334.2189 | 5287.4466 | 21524.4732 | 187809.7457 | 16587.7692 | 0.088775 | -128086.3572 | 128086.3572
| Xist Rating 4758 | -34.25 | 1419 | 150.29 | 35.6 | 2126.55 | 8807.84 | 12157.2 | 0.39 | 1.49 | 17.685 | 15.161 | 1 | 1 | 2340 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3017574.45 | 211042.1588 | 5332.9298 | 21616.8529 | 189425.306 | 16468.1144 | 0.089156 | -127162.4141 | 127162.4141
| Xist Rating 4759 | -33.93 | 1427.95 | 150.29 | 35.6 | 2123.95 | 8795.08 | 12104.7 | 0.38 | 1.49 | 17.681 | 15.06 | 1 | 1 | 2350 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3032894.4025 | 212757.0177 | 5378.6078 | 21709.2326 | 191047.7851 | 16347.5285 | 0.089537 | -126231.2822 | 126231.2822
| Xist Rating 4760 | -33.55 | 1438.83 | 150.29 | 35.6 | 2120.92 | 8782.67 | 12039.8 | 0.38 | 1.48 | 17.675 | 14.933 | 1 | 1 | 2360 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3051643.3236 | 214478.7955 | 5424.4805 | 21801.6123 | 192677.1831 | 16218.4097 | 0.089918 | -125234.2609 | 125234.2609
| Xist Rating 4761 | -32.41 | 1469.66 | 150.29 | 35.6 | 2112.72 | 8761.57 | 11846.7 | 0.38 | 1.45 | 17.709 | 14.532 | 1 | 1 | 2370 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3104980.0752 | 216207.4921 | 5470.5481 | 21893.992 | 194313.5001 | 15806.3551 | 0.090299 | -122052.484 | 122052.484
| Xist Rating 4762 | -32.09 | 1479.74 | 150.29 | 35.6 | 2108.85 | 8730.18 | 11791.2 | 0.37 | 1.44 | 17.706 | 14.429 | 1 | 1 | 2380 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3120549.699 | 217943.1076 | 5516.8105 | 21986.3717 | 195956.7359 | 15683.3953 | 0.09068 | -121103.0214 | 121103.0214
| Xist Rating 4763 | -31.71 | 1490.18 | 150.29 | 35.6 | 2106.61 | 8730.49 | 11730.1 | 0.37 | 1.43 | 17.7 | 14.31 | 1 | 1 | 2390 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3139228.0898 | 219685.6421 | 5563.2676 | 22078.7515 | 197606.8906 | 15562.5127 | 0.091061 | -120169.5981 | 120169.5981
C | Xist Rating 4767 | -23.73 | 1712.27 | 150.29 | 35.6 | 2049.7 | 8574.38 | 10537.9 | 0.39 | 1.25 | 17.728 | 12.037 | 1 | 1 | 2430 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3509639.819 | 226724.9686 | 5751.0441 | 22448.2703 | 204276.6983 | 13253.4966 | 0.092585 | -102339.9876 | 102339.9876
C | Xist Rating 4768 | -23.71 | 1713.64 | 150.29 | 35.6 | 2049.4 | 8569.06 | 10538 | 0.38 | 1.25 | 17.721 | 12.047 | 1 | 1 | 2440 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3511933.816 | 228502.0974 | 5798.4752 | 22540.65 | 205961.4474 | 13247.3003 | 0.092966 | -102292.1414 | 102292.1414
C | Xist Rating 4769 | -23.68 | 1714.97 | 150.29 | 35.6 | 2049.29 | 8567.19 | 10538 | 0.38 | 1.25 | 17.714 | 12.058 | 1 | 1 | 2450 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3514470.8713 | 230286.1452 | 5846.1011 | 22633.0297 | 207653.1155 | 13261.4501 | 0.093347 | -102401.4028 | 102401.4028
C | Xist Rating 4770 | -23.66 | 1716.44 | 150.29 | 35.6 | 2048.97 | 8561.57 | 10537.9 | 0.37 | 1.25 | 17.707 | 12.069 | 1 | 1 | 2460 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3516934.0668 | 232077.1118 | 5893.9217 | 22725.4095 | 209351.7024 | 13256.0723 | 0.093728 | -102359.8767 | 102359.8767
C | Xist Rating 4771 | -23.62 | 1717.79 | 150.29 | 35.6 | 2048.96 | 8561.37 | 10537.9 | 0.36 | 1.25 | 17.741 | 12.08 | 1 | 1 | 2470 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3519682.9984 | 233874.9973 | 5941.9372 | 22817.7892 | 211057.2082 | 13252.1831 | 0.094109 | -102329.8449 | 102329.8449
C | Xist Rating 4772 | -23.6 | 1719.14 | 150.29 | 35.6 | 2048.81 | 8558.83 | 10537.9 | 0.36 | 1.25 | 17.733 | 12.09 | 1 | 1 | 2480 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3522191.2234 | 235679.8017 | 5990.1474 | 22910.1689 | 212769.6329 | 13265.1107 | 0.09449 | -102429.669 | 102429.669
C | Xist Rating 4773 | -23.61 | 1720.54 | 150.29 | 35.6 | 2047.68 | 8539.14 | 10537.9 | 0.35 | 1.25 | 17.732 | 12.101 | 1 | 1 | 2490 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3523115.3472 | 237491.525 | 6038.5525 | 23002.5486 | 214488.9764 | 13259.5643 | 0.094871 | -102386.8409 | 102386.8409
C | Xist Rating 4774 | -23.58 | 1721.52 | 150.29 | 35.6 | 2048.01 | 8544.94 | 10537.8 | 0.35 | 1.25 | 17.727 | 12.11 | 1 | 1 | 2500 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3525690.1752 | 239310.1672 | 6087.1523 | 23094.9283 | 216215.2389 | 13271.4966 | 0.095252 | -102478.9789 | 102478.9789
C | Xist Rating 4775 | -23.57 | 1723.37 | 150.29 | 35.6 | 2046.77 | 8523.38 | 10537.8 | 0.34 | 1.25 | 17.721 | 12.122 | 1 | 1 | 2510 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3527342.0149 | 241135.7283 | 6135.9469 | 23187.308 | 217948.4203 | 13266.5656 | 0.095633 | -102440.9027 | 102440.9027
C | Xist Rating 4776 | -23.55 | 1724.83 | 150.29 | 35.6 | 2046.33 | 8515.83 | 10537.8 | 0.34 | 1.25 | 17.757 | 12.133 | 1 | 1 | 2520 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3529571.3739 | 242968.2082 | 6184.9363 | 23279.6877 | 219688.5205 | 13282.0724 | 0.096014 | -102560.6424 | 102560.6424
C | Xist Rating 4777 | -23.53 | 1726.17 | 150.29 | 35.6 | 2046.02 | 8510.44 | 10537.7 | 0.33 | 1.25 | 17.75 | 12.144 | 1 | 1 | 2530 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3531778.3434 | 244807.6071 | 6234.1205 | 23372.0674 | 221435.5396 | 13275.8026 | 0.096395 | -102512.2285 | 102512.2285
C | Xist Rating 4778 | -23.5 | 1727.32 | 150.29 | 35.6 | 2046.02 | 8510.4 | 10537.7 | 0.33 | 1.25 | 17.744 | 12.153 | 1 | 1 | 2540 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3534131.2664 | 246653.9248 | 6283.4995 | 23464.4472 | 223189.4777 | 13287.5492 | 0.096776 | -102602.9331 | 102602.9331
C | Xist Rating 4779 | -23.52 | 1728.86 | 150.29 | 35.6 | 2044.31 | 8480.84 | 10537.8 | 0.32 | 1.25 | 17.744 | 12.164 | 1 | 1 | 2550 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3534325.7866 | 248507.1614 | 6333.0732 | 23556.8269 | 224950.3346 | 13281.3155 | 0.097157 | -102554.7981 | 102554.7981
C | Xist Rating 4780 | -23.5 | 1730.31 | 150.29 | 35.6 | 2043.66 | 8469.71 | 10537.7 | 0.32 | 1.25 | 17.74 | 12.175 | 1 | 1 | 2560 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3536165.3346 | 250367.3169 | 6382.8418 | 23649.2066 | 226718.1104 | 13295.1373 | 0.097538 | -102661.5262 | 102661.5262
C | Xist Rating 4781 | -23.47 | 1731.7 | 150.29 | 35.6 | 2043.78 | 8471.85 | 10537.8 | 0.31 | 1.25 | 17.753 | 12.185 | 1 | 1 | 2570 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3539213.826 | 252234.3913 | 6432.8051 | 23741.5863 | 228492.805 | 13288.0948 | 0.097919 | -102607.1457 | 102607.1457
C | Xist Rating 4782 | -23.44 | 1733.07 | 150.29 | 35.6 | 2043.56 | 8468.01 | 10537.8 | 0.31 | 1.25 | 17.789 | 12.195 | 1 | 1 | 2580 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3541632.5292 | 254108.3846 | 6482.9633 | 23833.966 | 230274.4186 | 13302.2373 | 0.0983 | -102716.3504 | 102716.3504
C | Xist Rating 4783 | -23.43 | 1734.43 | 150.29 | 35.6 | 2043.13 | 8460.74 | 10537.7 | 0.3 | 1.25 | 17.784 | 12.205 | 1 | 1 | 2590 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3543665.9659 | 255989.2968 | 6533.3162 | 23926.3457 | 232062.9511 | 13294.2677 | 0.098681 | -102654.8116 | 102654.8116
C | Xist Rating 4784 | -23.4 | 1735.6 | 150.29 | 35.6 | 2043.2 | 8461.83 | 10537.7 | 0.3 | 1.25 | 17.782 | 12.215 | 1 | 1 | 2600 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3546177.92 | 257877.1278 | 6583.8639 | 24018.7254 | 233858.4024 | 13306.9743 | 0.099062 | -102752.9282 | 102752.9282
C | Xist Rating 4785 | -23.39 | 1737.29 | 150.29 | 35.6 | 2042.3 | 8446.56 | 10537.6 | 0.29 | 1.25 | 17.779 | 12.226 | 1 | 1 | 2610 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3548067.367 | 259771.8778 | 6634.6064 | 24111.1051 | 235660.7726 | 13299.8836 | 0.099443 | -102698.176 | 102698.176
C | Xist Rating 4786 | -23.35 | 1738.69 | 150.29 | 35.6 | 2042.15 | 8443.84 | 10537.6 | 0.29 | 1.25 | 17.78 | 12.236 | 1 | 1 | 2620 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3550665.7835 | 261673.5466 | 6685.5437 | 24203.4849 | 237470.0618 | 13312.6138 | 0.099824 | -102796.4749 | 102796.4749
C | Xist Rating 4787 | -23.32 | 1740.11 | 150.29 | 35.6 | 2041.91 | 8439.86 | 10537.6 | 0.29 | 1.25 | 17.819 | 12.247 | 1 | 1 | 2630 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3553148.0101 | 263582.1343 | 6736.6758 | 24295.8646 | 239286.2698 | 13327.6818 | 0.10021 | -102912.8264 | 102912.8264
C | Xist Rating 4788 | -23.29 | 1741.36 | 150.29 | 35.6 | 2042.11 | 8443.28 | 10537.6 | 0.28 | 1.25 | 17.815 | 12.256 | 1 | 1 | 2640 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3556048.6696 | 265497.641 | 6788.0027 | 24388.2443 | 241109.3967 | 13318.1256 | 0.10059 | -102839.0358 | 102839.0358
C | Xist Rating 4789 | -23.27 | 1742.86 | 150.29 | 35.6 | 2041.58 | 8434.28 | 10537.6 | 0.28 | 1.25 | 17.81 | 12.267 | 1 | 1 | 2650 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3558188.1188 | 267420.0664 | 6839.5243 | 24480.624 | 242939.4424 | 13331.6188 | 0.10097 | -102943.2262 | 102943.2262
C | Xist Rating 4790 | -23.22 | 1744.2 | 150.29 | 35.6 | 2041.95 | 8440.43 | 10537.7 | 0.28 | 1.25 | 17.81 | 12.276 | 1 | 1 | 2660 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3561569.19 | 269349.4108 | 6891.2408 | 24573.0037 | 244776.4071 | 13343.2006 | 0.10135 | -103032.6578 | 103032.6578
C | Xist Rating 4791 | -23.19 | 1745.59 | 150.29 | 35.6 | 2042.04 | 8442.06 | 10537.7 | 0.27 | 1.25 | 17.808 | 12.286 | 1 | 1 | 2670 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3564564.6036 | 271285.6741 | 6943.152 | 24665.3834 | 246620.2907 | 13334.4409 | 0.10173 | -102965.018 | 102965.018
C | Xist Rating 4792 | -23.17 | 1747.01 | 150.29 | 35.6 | 2041.5 | 8432.94 | 10537.6 | 0.27 | 1.25 | 17.844 | 12.296 | 1 | 1 | 2680 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3566520.915 | 273228.8563 | 6995.258 | 24757.7631 | 248471.0931 | 13348.1488 | 0.10211 | -103070.8667 | 103070.8667
C | Xist Rating 4793 | -23.15 | 1748.38 | 150.29 | 35.6 | 2041.24 | 8428.5 | 10537.6 | 0.26 | 1.25 | 17.839 | 12.306 | 1 | 1 | 2690 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3568863.1912 | 275178.9573 | 7047.5588 | 24850.1429 | 250328.8144 | 13339.0206 | 0.10249 | -103000.3814 | 103000.3814
C | Xist Rating 4794 | -23.08 | 1749.59 | 150.29 | 35.6 | 2042.44 | 8448.94 | 10537.5 | 0.26 | 1.25 | 17.835 | 12.315 | 1 | 1 | 2700 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3573432.5996 | 277135.9772 | 7100.0544 | 24942.5226 | 252193.4547 | 13350.3203 | 0.10287 | -103087.6343 | 103087.6343
C | Xist Rating 4795 | -23.04 | 1751.24 | 150.29 | 35.6 | 2042.51 | 8450.2 | 10537.5 | 0.26 | 1.25 | 17.83 | 12.326 | 1 | 1 | 2710 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3576925.2124 | 279099.9161 | 7152.7448 | 25034.9023 | 254065.0138 | 13363.6644 | 0.10325 | -103190.6742 | 103190.6742
C | Xist Rating 4796 | -23.04 | 1752.59 | 150.29 | 35.6 | 2041.48 | 8432.62 | 10537.5 | 0.25 | 1.25 | 17.823 | 12.336 | 1 | 1 | 2720 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3577877.4332 | 281070.7738 | 7205.63 | 25127.282 | 255943.4918 | 13354.1751 | 0.10363 | -103117.4005 | 103117.4005
C | Xist Rating 4797 | -23.02 | 1753.91 | 150.29 | 35.6 | 2041.07 | 8425.66 | 10537.5 | 0.25 | 1.25 | 17.86 | 12.345 | 1 | 1 | 2730 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3579853.0837 | 283048.5504 | 7258.71 | 25219.6617 | 257828.8887 | 13366.6508 | 0.10402 | -103213.7345 | 103213.7345
C | Xist Rating 4798 | -23.03 | 1755.19 | 150.29 | 35.6 | 2040.14 | 8409.71 | 10537.5 | 0.25 | 1.25 | 17.853 | 12.354 | 1 | 1 | 2740 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3580833.3266 | 285033.2458 | 7311.9847 | 25312.0414 | 259721.2044 | 13377.7838 | 0.1044 | -103299.7003 | 103299.7003
C | Xist Rating 4799 | -23.02 | 1756.74 | 150.29 | 35.6 | 2039.04 | 8391.22 | 10537.5 | 0.25 | 1.25 | 17.85 | 12.365 | 1 | 1 | 2750 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3582063.1296 | 287024.8602 | 7365.4543 | 25404.4211 | 261620.4391 | 13391.1155 | 0.10478 | -103402.6439 | 103402.6439
C | Xist Rating 4800 | -23.02 | 1758.16 | 150.29 | 35.6 | 2038.06 | 8374.54 | 10537.5 | 0.24 | 1.25 | 17.851 | 12.375 | 1 | 1 | 2760 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3583235.5696 | 289023.3935 | 7419.1186 | 25496.8008 | 263526.5926 | 13381.4471 | 0.10516 | -103327.9876 | 103327.9876
C | Xist Rating 4801 | -23.01 | 1759.4 | 150.29 | 35.6 | 2037.73 | 8369.08 | 10537.4 | 0.24 | 1.25 | 17.844 | 12.384 | 1 | 1 | 2770 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3585182.162 | 291028.8456 | 7472.9777 | 25589.1806 | 265439.6651 | 13392.5054 | 0.10554 | -103413.3767 | 103413.3767
C | Xist Rating 4802 | -23 | 1760.95 | 150.29 | 35.6 | 2036.59 | 8349.73 | 10537.6 | 0.24 | 1.25 | 17.883 | 12.394 | 1 | 1 | 2780 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3586333.1605 | 293041.2167 | 7527.0316 | 25681.5603 | 267359.6564 | 13405.9764 | 0.10592 | -103517.3962 | 103517.3962
C | Xist Rating 4803 | -22.97 | 1762.36 | 150.29 | 35.6 | 2036.45 | 8347.39 | 10537.6 | 0.23 | 1.25 | 17.882 | 12.404 | 1 | 1 | 2790 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3588958.022 | 295060.5066 | 7581.2803 | 25773.94 | 269286.5666 | 13395.8918 | 0.1063 | -103439.5259 | 103439.5259
C | Xist Rating 4804 | -22.96 | 1763.33 | 150.29 | 35.6 | 2036.32 | 8345.17 | 10537.6 | 0.23 | 1.25 | 17.877 | 12.411 | 1 | 1 | 2800 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3590704.1456 | 297086.7154 | 7635.7238 | 25866.3197 | 271220.3957 | 13404.8606 | 0.10668 | -103508.7801 | 103508.7801
C | Xist Rating 4805 | -22.91 | 1765.07 | 150.29 | 35.6 | 2036.27 | 8344.31 | 10537.6 | 0.23 | 1.25 | 17.884 | 12.423 | 1 | 1 | 2810 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 19 | E | Rod | 3594159.0889 | 299119.8431 | 7690.3621 | 25958.6994 | 273161.1437 | 13419.3684 | 0.10706 | -103620.8057 | 103620.8057
C | Xist Rating 4806 | -22.84 | 1766.55 | 150.29 | 35.6 | 2037.26 | 8360.93 | 10537.7 | 0.23 | 1.25 | 17.896 | 12.433 | 1 | 1 | 2820 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3598921.653 | 301159.8897 | 7745.1952 | 26051.0791 | 275108.8105 | 13431.946 | 0.10744 | -103717.927 | 103717.927
C | Xist Rating 4807 | -22.81 | 1767.92 | 150.29 | 35.6 | 2036.98 | 8356.21 | 10537.7 | 0.22 | 1.25 | 17.937 | 12.442 | 1 | 1 | 2830 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3601217.6816 | 303206.8551 | 7800.223 | 26143.4588 | 277063.3963 | 13421.58 | 0.10783 | -103637.8833 | 103637.8833
C | Xist Rating 4808 | -22.53 | 1769.24 | 150.29 | 35.6 | 2043.73 | 8470.81 | 10537.9 | 0.22 | 1.25 | 17.98 | 12.452 | 1 | 1 | 2840 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3615848.8652 | 305260.7395 | 7855.4457 | 26235.8386 | 279024.901 | 13434.9381 | 0.10821 | -103741.031 | 103741.031
C | Xist Rating 4809 | -22.09 | 1770.68 | 150.29 | 35.6 | 2054.42 | 8657.41 | 10538 | 0.22 | 1.25 | 18.052 | 12.462 | 1 | 1 | 2850 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3637720.4056 | 307321.5428 | 7910.8631 | 26328.2183 | 280993.3245 | 13449.1198 | 0.10859 | -103850.5378 | 103850.5378
C | Xist Rating 4810 | -22.64 | 1772.09 | 150.29 | 35.6 | 2038.84 | 8387.52 | 10537.8 | 0.22 | 1.25 | 17.955 | 12.47 | 1 | 1 | 2860 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3613007.9756 | 309389.2649 | 7966.4753 | 26420.598 | 282968.6669 | 13456.4722 | 0.10897 | -103907.3112 | 103907.3112
C | Xist Rating 4811 | -21.82 | 1773.28 | 150.29 | 35.6 | 2060.17 | 8760.41 | 10538.1 | 0.21 | 1.25 | 18.084 | 12.48 | 1 | 1 | 2870 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3653258.2576 | 311463.9059 | 8022.2824 | 26512.9777 | 284950.9282 | 13449.0143 | 0.10935 | -103849.7234 | 103849.7234
C | Xist Rating 4812 | -21.42 | 1774.79 | 150.291 | 35.6 | 2069.91 | 8939.19 | 10538.1 | 0.21 | 1.25 | 18.166 | 12.491 | 1 | 1 | 2880 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3673655.5689 | 313545.4658 | 8078.2842 | 26605.3574 | 286940.1084 | 13464.3631 | 0.10973 | -103968.2426 | 103968.2426
C | Xist Rating 4813 | -21.16 | 1776.13 | 150.291 | 35.6 | 2075.91 | 9052.22 | 10538.2 | 0.2 | 1.25 | 18.19 | 12.501 | 1 | 1 | 2890 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3687086.0283 | 315633.9446 | 8134.4807 | 26697.7371 | 288936.2075 | 13453.547 | 0.11011 | -103884.7241 | 103884.7241
C | Xist Rating 4814 | -20.98 | 1777.52 | 150.291 | 35.6 | 2079.69 | 9124.6 | 10538.1 | 0.2 | 1.25 | 18.209 | 12.51 | 1 | 1 | 2900 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3696690.5688 | 317729.3423 | 8190.8721 | 26790.1168 | 290939.2255 | 13465.0182 | 0.11049 | -103973.3014 | 103973.3014
C | Xist Rating 4815 | -20.85 | 1779.06 | 150.291 | 35.6 | 2082.08 | 9170.76 | 10538.1 | 0.2 | 1.25 | 18.22 | 12.52 | 1 | 1 | 2910 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3704145.2448 | 319831.6589 | 8247.4583 | 26882.4965 | 292949.1623 | 13477.3226 | 0.11087 | -104068.3126 | 104068.3126
C | Xist Rating 4816 | -20.68 | 1780.45 | 150.291 | 35.6 | 2085.66 | 9240.68 | 10538.1 | 0.2 | 1.25 | 18.233 | 12.53 | 1 | 1 | 2920 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3713413.347 | 321940.8944 | 8304.2393 | 26974.8763 | 294966.0181 | 13489.6813 | 0.11125 | -104163.7432 | 104163.7432
C | Xist Rating 4817 | -20.55 | 1781.83 | 150.291 | 35.6 | 2088.41 | 9294.93 | 10538.1 | 0.19 | 1.25 | 18.282 | 12.539 | 1 | 1 | 2930 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3721191.5903 | 324057.0487 | 8361.215 | 27067.256 | 296989.7927 | 13477.9386 | 0.11164 | -104073.0689 | 104073.0689
C | Xist Rating 4818 | -20.33 | 1783.2 | 150.291 | 35.6 | 2093.28 | 9392.23 | 10538 | 0.19 | 1.25 | 18.3 | 12.549 | 1 | 1 | 2940 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3732736.896 | 326180.1219 | 8418.3855 | 27159.6357 | 299020.4863 | 13490.3313 | 0.11202 | -104168.7621 | 104168.7621
C | Xist Rating 4819 | -20.03 | 1784.61 | 150.291 | 35.5 | 2100.45 | 9538.56 | 10537.8 | 0.19 | 1.25 | 18.312 | 12.558 | 1 | 1 | 2950 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3748484.0745 | 328310.1141 | 8475.7509 | 27252.0154 | 301058.0987 | 13501.5378 | 0.1124 | -104255.296 | 104255.296
C | Xist Rating 4820 | -20.02 | 1785.98 | 150.291 | 35.5 | 2099.78 | 9524.72 | 10537.8 | 0.19 | 1.25 | 18.308 | 12.567 | 1 | 1 | 2960 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3750165.0844 | 330447.0251 | 8533.311 | 27344.3951 | 303102.63 | 13512.343 | 0.11278 | -104338.7311 | 104338.7311
C | Xist Rating 4821 | -20.01 | 1787.36 | 150.291 | 35.5 | 2099.12 | 9511.17 | 10537.9 | 0.18 | 1.25 | 18.305 | 12.576 | 1 | 1 | 2970 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3751883.1232 | 332590.855 | 8591.0659 | 27436.7748 | 305154.0801 | 13498.8036 | 0.11316 | -104234.1829 | 104234.1829
C | Xist Rating 4822 | -20 | 1788.59 | 150.291 | 35.5 | 2098.54 | 9499.13 | 10537.9 | 0.18 | 1.25 | 18.341 | 12.585 | 1 | 1 | 2980 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3753427.6586 | 334741.6038 | 8649.0156 | 27529.1545 | 307212.4492 | 13510.4925 | 0.11354 | -104324.4422 | 104324.4422
C | Xist Rating 4823 | -19.98 | 1790.15 | 150.291 | 35.5 | 2097.81 | 9484.19 | 10537.9 | 0.18 | 1.25 | 18.337 | 12.595 | 1 | 1 | 2990 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3755394.5715 | 336899.2714 | 8707.16 | 27621.5343 | 309277.7372 | 13522.2609 | 0.11392 | -104415.314 | 104415.314
C | Xist Rating 4824 | -19.97 | 1791.58 | 150.291 | 35.5 | 2097.25 | 9472.88 | 10537.8 | 0.18 | 1.25 | 18.331 | 12.604 | 1 | 1 | 3000 | 152.4 | 2 | 3.3 | 19.05 | 1.3333 | 18 | E | Rod | 3757391.155 | 339063.858 | 8765.4993 | 27713.914 | 311349.944 | 13532.9416 | 0.1143 | -104497.7881 | 104497.7881
C | Xist Rating 4825 | -90.27 | 177.524 | 150.294 | 35.9 | 2384.27 | 7259.82 | 58745.9 | 2.46 | 10.95 | 19.661 | 473.792 | 1 | 1 | 1000 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 423265.1475 | 45160.6644 | 973.9444 | 9517.9098 | 35642.7545 | 494200.2346 | 0.038101 | -3816083.2136 | 3816083.2136
C | Xist Rating 4826 | -90.19 | 179.375 | 150.295 | 35.9 | 2381.88 | 7245.84 | 58284.3 | 2.44 | 10.85 | 19.711 | 464.909 | 1 | 1 | 1010 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 427249.725 | 45972.2628 | 993.5206 | 9613.0889 | 36359.1739 | 484984.6542 | 0.038482 | -3744922.9441 | 3744922.9441
C | Xist Rating 4827 | -89.46 | 193.344 | 150.295 | 35.9 | 2375.4 | 7248.23 | 54967.7 | 2.45 | 10.07 | 19.763 | 402.89 | 1 | 1 | 1020 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 459269.3376 | 46790.9899 | 1013.2917 | 9708.268 | 37082.7218 | 420614.416 | 0.038863 | -3247873.0279 | 3247873.0279
C | Xist Rating 4828 | -89.34 | 197.191 | 150.294 | 35.8 | 2355.86 | 7084.58 | 54179.2 | 2.37 | 9.89 | 19.334 | 389.411 | 1 | 1 | 1030 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 464554.3893 | 47616.8454 | 1033.2576 | 9803.4471 | 37813.3983 | 406518.2622 | 0.039244 | -3139026.2644 | 3139026.2644
C | Xist Rating 4829 | -89.27 | 199.117 | 150.293 | 35.8 | 2350.09 | 7040.19 | 53793.7 | 2.32 | 9.8 | 19.227 | 382.953 | 1 | 1 | 1040 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 467942.8705 | 48449.8295 | 1053.4182 | 9898.6262 | 38551.2033 | 399775.5411 | 0.039625 | -3086960.7597 | 3086960.7597
C | Xist Rating 4830 | -89.09 | 202.843 | 150.293 | 35.8 | 2346.53 | 7023.18 | 53043.3 | 2.28 | 9.63 | 19.163 | 370.283 | 1 | 1 | 1050 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 475977.1848 | 49289.9422 | 1073.7737 | 9993.8053 | 39296.1369 | 386594.6956 | 0.040006 | -2985181.7648 | 2985181.7648
C | Xist Rating 4831 | -88.92 | 204.75 | 150.293 | 35.8 | 2360.55 | 7158.09 | 52676.7 | 2.23 | 9.54 | 19.158 | 364.294 | 1 | 1 | 1060 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 483322.6125 | 50137.1834 | 1094.3239 | 10088.9844 | 40048.199 | 380348.6578 | 0.040387 | -2936951.5161 | 2936951.5161
C | Xist Rating 4832 | -88.21 | 219.799 | 150.293 | 35.8 | 2341.74 | 7048.67 | 49857.3 | 2.22 | 8.9 | 19.003 | 318.763 | 1 | 1 | 1070 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 514712.1103 | 50991.5532 | 1115.0689 | 10184.1635 | 40807.3897 | 333058.2439 | 0.040768 | -2571787.4756 | 2571787.4756
C | Xist Rating 4833 | -88.02 | 222.662 | 150.293 | 35.8 | 2349.07 | 7126.79 | 49380.7 | 2.16 | 8.79 | 18.919 | 311.638 | 1 | 1 | 1080 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 523048.6243 | 51853.0515 | 1136.0087 | 10279.3426 | 41573.7089 | 325613.8723 | 0.041149 | -2514304.011 | 2514304.011
C | Xist Rating 4834 | -87.81 | 226.468 | 150.292 | 35.8 | 2351.44 | 7163.76 | 48761.6 | 2.1 | 8.65 | 18.787 | 302.478 | 1 | 1 | 1090 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 532525.9139 | 52721.6784 | 1157.1433 | 10374.5217 | 42347.1567 | 316050.539 | 0.04153 | -2440458.4867 | 2440458.4867
C | Xist Rating 4835 | -87.62 | 229.299 | 150.292 | 35.8 | 2358.94 | 7245.48 | 48308.2 | 2.06 | 8.55 | 18.783 | 295.863 | 1 | 1 | 1100 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 540902.5831 | 53597.4338 | 1178.4727 | 10469.7008 | 43127.733 | 309161.0969 | 0.041911 | -2387260.0409 | 2387260.0409
C | Xist Rating 4836 | -87.54 | 231.392 | 150.292 | 35.8 | 2355.16 | 7217.62 | 48011.1 | 1.99 | 8.49 | 18.516 | 291.834 | 1 | 1 | 1110 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 544965.1827 | 54480.3178 | 1199.9969 | 10564.8799 | 43915.4379 | 304902.4754 | 0.042292 | -2354376.0945 | 2354376.0945
C | Xist Rating 4837 | -86.66 | 248.117 | 150.292 | 35.8 | 2351.46 | 7253.32 | 45448.4 | 2.03 | 7.92 | 18.751 | 255.354 | 1 | 1 | 1120 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 583437.2008 | 55370.3303 | 1221.7158 | 10660.059 | 44710.2713 | 267095.702 | 0.042673 | -2062442.2116 | 2062442.2116
C | Xist Rating 4838 | -86.56 | 250.165 | 150.292 | 35.8 | 2351.65 | 7262.84 | 45188.6 | 1.97 | 7.86 | 18.576 | 252.094 | 1 | 1 | 1130 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 588300.5223 | 56267.4714 | 1243.6296 | 10755.2381 | 45512.2333 | 263652.8109 | 0.043054 | -2035857.1187 | 2035857.1187
C | Xist Rating 4839 | -86.38 | 254.042 | 150.291 | 35.8 | 2347.25 | 7236.07 | 44681.7 | 1.91 | 7.75 | 18.421 | 245.539 | 1 | 1 | 1140 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 596300.0845 | 57171.741 | 1265.7381 | 10850.4172 | 46321.3238 | 256789.7749 | 0.043435 | -1982862.574 | 1982862.574
C | Xist Rating 4840 | -86.17 | 257.856 | 150.291 | 35.8 | 2348.7 | 7265.06 | 44186.8 | 1.87 | 7.64 | 18.262 | 239.188 | 1 | 1 | 1150 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 605626.3872 | 58083.1392 | 1288.0414 | 10945.5963 | 47137.5429 | 250156.7328 | 0.043816 | -1931643.9814 | 1931643.9814
C | Xist Rating 4841 | -85.97 | 261.748 | 150.291 | 35.8 | 2348.38 | 7277.28 | 43703.8 | 1.82 | 7.53 | 18.132 | 233.152 | 1 | 1 | 1160 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 614683.7682 | 59001.6659 | 1310.5395 | 11040.7754 | 47960.8905 | 243843.8834 | 0.044197 | -1882897.8321 | 1882897.8321
C | Xist Rating 4842 | -85.18 | 276.784 | 150.291 | 35.8 | 2347.01 | 7326.78 | 41832.9 | 1.84 | 7.13 | 18.267 | 209.735 | 1 | 1 | 1170 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 649614.8158 | 59927.3212 | 1333.2324 | 11135.9545 | 48791.3667 | 219572.2041 | 0.044578 | -1695478.3579 | 1695478.3579
C | Xist Rating 4843 | -85.07 | 277.901 | 150.291 | 35.8 | 2356.28 | 7421.74 | 41725.2 | 1.79 | 7.11 | 18.198 | 208.618 | 1 | 1 | 1180 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 654812.5683 | 60860.105 | 1356.1201 | 11231.1336 | 49628.9714 | 218372.4248 | 0.044959 | -1686213.9801 | 1686213.9801
C | Xist Rating 4844 | -84.73 | 285.514 | 150.291 | 35.8 | 2346.84 | 7359.43 | 40886.2 | 1.74 | 6.93 | 18.053 | 198.859 | 1 | 1 | 1190 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 670055.6758 | 61800.0174 | 1379.2026 | 11326.3127 | 50473.7047 | 208190.3268 | 0.04534 | -1607590.5183 | 1607590.5183
C | Xist Rating 4845 | -84.56 | 287.453 | 150.291 | 35.8 | 2358 | 7478.17 | 40682.6 | 1.71 | 6.88 | 18.082 | 196.584 | 1 | 1 | 1200 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 677814.174 | 62747.0583 | 1402.4799 | 11421.4918 | 51325.5665 | 205815.3588 | 0.045721 | -1589251.6452 | 1589251.6452
C | Xist Rating 4846 | -84.38 | 291.415 | 150.29 | 35.8 | 2354.8 | 7461.72 | 40281.5 | 1.66 | 6.8 | 17.956 | 192.166 | 1 | 1 | 1210 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 686224.042 | 63701.2278 | 1425.9519 | 11516.6709 | 52184.5569 | 201180.7519 | 0.046102 | -1553464.439 | 1553464.439
C | Xist Rating 4847 | -83.55 | 308.495 | 150.29 | 35.8 | 2341.94 | 7404.27 | 38538.6 | 1.66 | 6.43 | 17.975 | 172.826 | 1 | 1 | 1220 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 722476.7803 | 64662.5259 | 1449.6188 | 11611.85 | 53050.6759 | 181111.2781 | 0.046483 | -1398493.2825 | 1398493.2825
C | Xist Rating 4848 | -83.31 | 312.306 | 150.29 | 35.8 | 2348.59 | 7486.68 | 38183.4 | 1.63 | 6.35 | 17.978 | 169.128 | 1 | 1 | 1230 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 733478.7485 | 65630.9524 | 1473.4804 | 11707.0291 | 53923.9233 | 177254.8244 | 0.046864 | -1368714.769 | 1368714.769
C | Xist Rating 4849 | -83.11 | 316.258 | 150.29 | 35.8 | 2347.99 | 7496.09 | 37835.8 | 1.59 | 6.28 | 17.892 | 165.621 | 1 | 1 | 1240 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 742570.6214 | 66606.5076 | 1497.5369 | 11802.2082 | 54804.2994 | 173578.375 | 0.047245 | -1340326.2015 | 1340326.2015
C | Xist Rating 4850 | -82.98 | 318.342 | 150.29 | 35.8 | 2351.84 | 7543.3 | 37664.6 | 1.55 | 6.24 | 17.833 | 163.98 | 1 | 1 | 1250 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 748689.4493 | 67589.1913 | 1521.7881 | 11897.3873 | 55691.804 | 171841.7268 | 0.047626 | -1326916.2643 | 1326916.2643
C | Xist Rating 4851 | -82.7 | 324.084 | 150.29 | 35.8 | 2350.13 | 7549.25 | 37161.5 | 1.52 | 6.14 | 17.792 | 158.904 | 1 | 1 | 1260 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 761639.5309 | 68579.0035 | 1546.2341 | 11992.5664 | 56586.4371 | 166548.9634 | 0.048007 | -1286046.9481 | 1286046.9481
C | Xist Rating 4852 | -81.9 | 340.262 | 150.29 | 35.8 | 2342.84 | 7542 | 35777.6 | 1.53 | 5.85 | 17.853 | 145.137 | 1 | 1 | 1270 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 797179.4241 | 69575.9443 | 1570.8749 | 12087.7455 | 57488.1988 | 152279.5195 | 0.048388 | -1175862.0847 | 1175862.0847
C | Xist Rating 4853 | -81.72 | 344.283 | 150.29 | 35.8 | 2339.85 | 7526.52 | 35477.3 | 1.49 | 5.79 | 17.762 | 142.399 | 1 | 1 | 1280 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 805570.5776 | 70580.0136 | 1595.7105 | 12182.9246 | 58397.089 | 149399.6021 | 0.048769 | -1153624.1263 | 1153624.1263
C | Xist Rating 4854 | -81.52 | 348.251 | 150.29 | 35.8 | 2338.86 | 7531.59 | 35182.8 | 1.45 | 5.73 | 17.728 | 139.721 | 1 | 1 | 1290 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 814510.3339 | 71591.2115 | 1620.7408 | 12278.1037 | 59313.1078 | 146586.433 | 0.04915 | -1131901.58 | 1131901.58
C | Xist Rating 4855 | -81.18 | 353.971 | 150.29 | 35.8 | 2345.03 | 7619.43 | 34751.5 | 1.43 | 5.64 | 17.762 | 135.754 | 1 | 1 | 1300 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 830072.6141 | 72609.538 | 1645.966 | 12373.2828 | 60236.2552 | 142460.4045 | 0.049531 | -1100041.4814 | 1100041.4814
C | Xist Rating 4856 | -80.98 | 357.026 | 150.29 | 35.8 | 2350.3 | 7687.38 | 34540.1 | 1.39 | 5.59 | 17.719 | 133.921 | 1 | 1 | 1310 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 839118.2078 | 73634.993 | 1671.3859 | 12468.4619 | 61166.5311 | 140522.9929 | 0.049912 | -1085081.3026 | 1085081.3026
C | Xist Rating 4857 | -80.17 | 373.303 | 150.29 | 35.8 | 2344.57 | 7695.29 | 33363 | 1.4 | 5.35 | 17.768 | 123.349 | 1 | 1 | 1320 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 875235.0147 | 74667.5765 | 1697.0007 | 12563.641 | 62103.9355 | 129569.5707 | 0.050293 | -1000501.8798 | 1000501.8798
C | Xist Rating 4858 | -79.89 | 379.239 | 150.29 | 35.8 | 2340.97 | 7680.22 | 32980.1 | 1.36 | 5.28 | 17.683 | 120.146 | 1 | 1 | 1330 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 887787.1218 | 75707.2886 | 1722.8102 | 12658.8201 | 63048.4685 | 126205.1479 | 0.050674 | -974522.6991 | 974522.6991
C | Xist Rating 4859 | -79.58 | 385.074 | 150.289 | 35.8 | 2342.94 | 7725.21 | 32607.3 | 1.33 | 5.2 | 17.61 | 117.044 | 1 | 1 | 1340 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 902205.2776 | 76754.1292 | 1748.8145 | 12753.9992 | 64000.13 | 122956.8101 | 0.051055 | -949439.895 | 949439.895
C | Xist Rating 4860 | -79.38 | 388.146 | 150.289 | 35.8 | 2347.21 | 7783.92 | 32424.3 | 1.3 | 5.16 | 17.579 | 115.597 | 1 | 1 | 1350 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 911060.1727 | 77808.0984 | 1775.0136 | 12849.1783 | 64958.9201 | 121430.1935 | 0.051436 | -937651.7667 | 937651.7667
C | Xist Rating 4861 | -79.15 | 390.032 | 150.29 | 35.7 | 2364.05 | 7980.65 | 32303.8 | 1.29 | 5.14 | 17.644 | 114.614 | 1 | 1 | 1360 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 922055.1496 | 78869.1962 | 1801.4075 | 12944.3574 | 65924.8388 | 120413.9884 | 0.051817 | -929804.9002 | 929804.9002
C | Xist Rating 4862 | -78.17 | 413.192 | 150.29 | 35.8 | 2336.62 | 7772.77 | 30902.8 | 1.28 | 4.86 | 17.588 | 103.305 | 1 | 1 | 1370 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 965472.691 | 79937.4225 | 1827.9962 | 13039.5365 | 66897.886 | 108664.5752 | 0.052198 | -839079.0461 | 839079.0461
C | Xist Rating 4863 | -78.06 | 415.34 | 150.289 | 35.7 | 2337.62 | 7791.77 | 30794.5 | 1.26 | 4.84 | 17.555 | 102.542 | 1 | 1 | 1380 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 970907.0908 | 81012.7773 | 1854.7797 | 13134.7156 | 67878.0617 | 107857.9609 | 0.052579 | -832850.5841 | 832850.5841
C | Xist Rating 4864 | -77.8 | 420.321 | 150.289 | 35.7 | 2338.39 | 7820.26 | 30527.3 | 1.23 | 4.78 | 17.522 | 100.551 | 1 | 1 | 1390 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 21 | E | Rod | 982874.4232 | 82095.2607 | 1881.7579 | 13229.8947 | 68865.366 | 105764.8828 | 0.05296 | -816688.3902 | 816688.3902
C | Xist Rating 4865 | -77.54 | 425.298 | 150.289 | 35.7 | 2339.56 | 7853.4 | 30265.5 | 1.2 | 4.73 | 17.462 | 98.62 | 1 | 1 | 1400 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 995010.1889 | 83184.8727 | 1908.931 | 13325.0738 | 69859.7989 | 103731.6972 | 0.053341 | -800988.6694 | 800988.6694
C | Xist Rating 4866 | -77.23 | 431.194 | 150.289 | 35.7 | 2340.04 | 7882.96 | 29957.8 | 1.18 | 4.67 | 17.443 | 96.359 | 1 | 1 | 1410 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1009011.2078 | 84281.6132 | 1936.2988 | 13420.2529 | 70861.3603 | 101369.5551 | 0.053722 | -782748.834 | 782748.834
C | Xist Rating 4867 | -76.37 | 448.516 | 150.289 | 35.7 | 2335.73 | 7908.42 | 29052.1 | 1.19 | 4.49 | 17.508 | 89.68 | 1 | 1 | 1420 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1047612.2767 | 85385.4822 | 1963.8614 | 13515.432 | 71870.0502 | 94458.6763 | 0.054103 | -729384.8602 | 729384.8602
C | Xist Rating 4868 | -76.23 | 451.829 | 150.289 | 35.7 | 2333.27 | 7892.4 | 28910.9 | 1.15 | 4.47 | 17.438 | 88.776 | 1 | 1 | 1430 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1054239.0508 | 86496.4798 | 1991.6188 | 13610.6111 | 72885.8688 | 93479.1628 | 0.054484 | -721821.3162 | 721821.3162
C | Xist Rating 4869 | -75.85 | 459.611 | 150.289 | 35.7 | 2331.17 | 7900.32 | 28542.1 | 1.14 | 4.39 | 17.422 | 86.218 | 1 | 1 | 1440 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1071431.3749 | 87614.606 | 2019.571 | 13705.7902 | 73908.8158 | 90819.2397 | 0.054865 | -701282.0952 | 701282.0952
C | Xist Rating 4870 | -75.6 | 464.626 | 150.289 | 35.7 | 2330.87 | 7916.92 | 28317.1 | 1.12 | 4.35 | 17.399 | 84.712 | 1 | 1 | 1450 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1082982.8046 | 88739.8607 | 2047.718 | 13800.9693 | 74938.8914 | 89239.8423 | 0.055246 | -689086.4073 | 689086.4073
C | Xist Rating 4871 | -75.38 | 467.58 | 150.289 | 35.7 | 2338.22 | 8014.71 | 28183.9 | 1.11 | 4.32 | 17.42 | 83.829 | 1 | 1 | 1460 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1093304.9076 | 89872.2439 | 2076.0598 | 13896.1484 | 75976.0956 | 88321.722 | 0.055627 | -681996.9259 | 681996.9259
C | Xist Rating 4872 | -74.53 | 487.217 | 150.289 | 35.7 | 2322.43 | 7913.04 | 27310.5 | 1.1 | 4.16 | 17.408 | 77.973 | 1 | 1 | 1470 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1131527.3773 | 91011.7558 | 2104.5964 | 13991.3275 | 77020.4283 | 82236.5945 | 0.056008 | -635009.1839 | 635009.1839
C | Xist Rating 4873 | -74.23 | 493.156 | 150.289 | 35.7 | 2322.34 | 7935.9 | 27066.2 | 1.08 | 4.11 | 17.393 | 76.424 | 1 | 1 | 1480 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1145275.905 | 92158.3961 | 2133.3277 | 14086.5066 | 78071.8895 | 80612.372 | 0.056389 | -622467.3684 | 622467.3684
C | Xist Rating 4874 | -73.96 | 498.174 | 150.289 | 35.7 | 2324.25 | 7978.25 | 26866.4 | 1.06 | 4.07 | 17.384 | 75.184 | 1 | 1 | 1490 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1157880.9195 | 93312.165 | 2162.2539 | 14181.6857 | 79130.4793 | 79309.1837 | 0.05677 | -612404.494 | 612404.494
C | Xist Rating 4875 | -73.68 | 503.283 | 150.289 | 35.7 | 2326.36 | 8023.36 | 26670.3 | 1.04 | 4.03 | 17.365 | 73.988 | 1 | 1 | 1500 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1170817.4399 | 94473.0625 | 2191.3748 | 14276.8648 | 80196.1977 | 78050.6939 | 0.057151 | -602686.7693 | 602686.7693
C | Xist Rating 4876 | -73.32 | 509.249 | 150.289 | 35.7 | 2331.7 | 8112.13 | 26438.7 | 1.02 | 3.99 | 17.368 | 72.569 | 1 | 1 | 1510 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1187415.8933 | 95641.0885 | 2220.6906 | 14372.0439 | 81269.0446 | 76561.8598 | 0.057532 | -591190.3873 | 591190.3873
C | Xist Rating 4877 | -72.34 | 528.569 | 150.289 | 35.7 | 2329.4 | 8169.05 | 25681.2 | 1.03 | 3.85 | 17.445 | 67.869 | 1 | 1 | 1520 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1231248.6286 | 96816.243 | 2250.2011 | 14467.223 | 82349.0201 | 71706.0952 | 0.057913 | -553695.4599 | 553695.4599
C | Xist Rating 4878 | -72.1 | 534.88 | 150.289 | 35.7 | 2323.3 | 8119.08 | 25468.5 | 1 | 3.8 | 17.384 | 66.673 | 1 | 1 | 1530 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1242686.704 | 97998.5262 | 2279.9064 | 14562.4021 | 83436.1241 | 70432.0296 | 0.058294 | -543857.4632 | 543857.4632
C | Xist Rating 4879 | -71.88 | 538.108 | 150.289 | 35.7 | 2328.45 | 8194.88 | 25363.7 | 0.98 | 3.78 | 17.375 | 66.106 | 1 | 1 | 1540 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1252957.5726 | 99187.9378 | 2309.8065 | 14657.5812 | 84530.3567 | 69826.3841 | 0.058675 | -539180.8294 | 539180.8294
C | Xist Rating 4880 | -71.39 | 547.902 | 150.289 | 35.7 | 2327.01 | 8218.79 | 25021.2 | 0.97 | 3.72 | 17.369 | 64.126 | 1 | 1 | 1550 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1274973.433 | 100384.478 | 2339.9013 | 14752.7603 | 85631.7178 | 67765.3136 | 0.059056 | -523265.7889 | 523265.7889
C | Xist Rating 4881 | -71.11 | 550.906 | 150.289 | 35.7 | 2338.49 | 8376.76 | 24920.6 | 0.95 | 3.7 | 17.4 | 63.57 | 1 | 1 | 1560 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1288288.1719 | 101588.1468 | 2370.191 | 14847.9394 | 86740.2074 | 67173.2288 | 0.059437 | -518693.8669 | 518693.8669
C | Xist Rating 4882 | -70.18 | 573.678 | 150.289 | 35.7 | 2318.66 | 8224.72 | 24162.1 | 0.95 | 3.56 | 17.382 | 59.293 | 1 | 1 | 1570 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1330164.2315 | 102798.9441 | 2400.6755 | 14943.1185 | 87855.8257 | 62737.7771 | 0.059818 | -484444.4852 | 484444.4852
C | Xist Rating 4883 | -69.88 | 578.816 | 150.289 | 35.7 | 2321.95 | 8287.26 | 24007.4 | 0.93 | 3.53 | 17.376 | 58.484 | 1 | 1 | 1580 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1343981.8112 | 104016.87 | 2431.3547 | 15038.2976 | 88978.5724 | 61880.0177 | 0.0602 | -477821.094 | 477821.094
C | Xist Rating 4884 | -69.59 | 583.989 | 150.289 | 35.7 | 2324.53 | 8341.38 | 23855.1 | 0.91 | 3.5 | 17.365 | 57.696 | 1 | 1 | 1590 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1357499.9502 | 105241.9244 | 2462.2288 | 15133.4767 | 90108.4477 | 61043.4429 | 0.060581 | -471361.285 | 471361.285
C | Xist Rating 4885 | -69.19 | 590.905 | 150.289 | 35.7 | 2328.71 | 8425.78 | 23645.3 | 0.9 | 3.46 | 17.376 | 56.587 | 1 | 1 | 1600 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1376046.3825 | 106474.1074 | 2493.2976 | 15228.6558 | 91245.4516 | 59887.0873 | 0.060962 | -462432.214 | 462432.214
C | Xist Rating 4886 | -69.01 | 594.329 | 150.289 | 35.7 | 2329.74 | 8452.38 | 23556.7 | 0.88 | 3.45 | 17.352 | 56.171 | 1 | 1 | 1610 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1384632.0445 | 107713.4189 | 2524.5612 | 15323.8349 | 92389.584 | 59435.4779 | 0.061343 | -458945.0061 | 458945.0061
C | Xist Rating 4887 | -67.89 | 619.769 | 150.289 | 35.7 | 2315.89 | 8384.4 | 22805.1 | 0.88 | 3.31 | 17.363 | 52.224 | 1 | 1 | 1620 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1435316.8294 | 108959.859 | 2556.0196 | 15419.014 | 93540.845 | 55344.0722 | 0.061724 | -427352.2556 | 427352.2556
C | Xist Rating 4888 | -67.59 | 622.848 | 150.289 | 35.7 | 2326.05 | 8532.32 | 22723.6 | 0.87 | 3.29 | 17.382 | 51.836 | 1 | 1 | 1630 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1448775.5904 | 110213.4276 | 2587.6728 | 15514.1931 | 94699.2345 | 54936.5054 | 0.062105 | -424205.1327 | 424205.1327
C | Xist Rating 4889 | -67.34 | 628.168 | 150.289 | 35.7 | 2325.72 | 8549.96 | 22588.7 | 0.85 | 3.27 | 17.361 | 51.201 | 1 | 1 | 1640 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1460942.881 | 111474.1247 | 2619.5208 | 15609.3721 | 95864.7526 | 54256.9694 | 0.062486 | -418957.9357 | 418957.9357
C | Xist Rating 4890 | -67.01 | 635.442 | 150.289 | 35.7 | 2322.93 | 8542.97 | 22403.4 | 0.84 | 3.24 | 17.333 | 50.316 | 1 | 1 | 1650 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1476087.2851 | 112741.9505 | 2651.5635 | 15704.5512 | 97037.3992 | 53329.9331 | 0.062867 | -411799.6074 | 411799.6074
C | Xist Rating 4891 | -66.63 | 642.472 | 150.289 | 35.7 | 2325.04 | 8602.62 | 22221 | 0.83 | 3.2 | 17.338 | 49.439 | 1 | 1 | 1660 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1493773.0989 | 114016.9047 | 2683.8011 | 15799.7303 | 98217.1744 | 52413.1079 | 0.063248 | -404720.1257 | 404720.1257
C | Xist Rating 4892 | -65.64 | 665.288 | 150.289 | 35.7 | 2312.81 | 8538.86 | 21633.2 | 0.83 | 3.1 | 17.362 | 46.594 | 1 | 1 | 1670 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1538684.7393 | 115298.9876 | 2716.2334 | 15894.9094 | 99404.0781 | 49466.5215 | 0.063629 | -381967.367 | 381967.367
C | Xist Rating 4893 | -65.41 | 668.479 | 150.289 | 35.7 | 2318.31 | 8627.58 | 21560.6 | 0.81 | 3.08 | 17.366 | 46.28 | 1 | 1 | 1680 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1549741.5505 | 116588.1989 | 2748.8606 | 15990.0885 | 100598.1104 | 49120.9874 | 0.06401 | -379299.2441 | 379299.2441
C | Xist Rating 4894 | -65.02 | 677.754 | 150.289 | 35.7 | 2313.23 | 8597.12 | 21346.3 | 0.8 | 3.04 | 17.341 | 45.314 | 1 | 1 | 1690 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1567800.8854 | 117884.5389 | 2781.6825 | 16085.2676 | 101799.2712 | 48109.4327 | 0.064391 | -371488.287 | 371488.287
C | Xist Rating 4895 | -64.69 | 683.877 | 150.289 | 35.7 | 2314.96 | 8647.68 | 21206.1 | 0.79 | 3.02 | 17.341 | 44.69 | 1 | 1 | 1700 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1583147.8999 | 119188.0073 | 2814.6992 | 16180.4467 | 103007.5606 | 47454.414 | 0.064772 | -366430.4058 | 366430.4058
C | Xist Rating 4896 | -64.35 | 691.1 | 150.29 | 35.7 | 2313.65 | 8660.37 | 21045.1 | 0.78 | 2.99 | 17.334 | 43.983 | 1 | 1 | 1710 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1598963.515 | 120498.6044 | 2847.9107 | 16275.6258 | 104222.9785 | 46712.6259 | 0.065153 | -360702.5148 | 360702.5148
C | Xist Rating 4897 | -63.42 | 712.118 | 150.29 | 35.7 | 2304.64 | 8628.94 | 20567.6 | 0.77 | 2.9 | 17.363 | 41.837 | 1 | 1 | 1720 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1641175.6275 | 121816.33 | 2881.317 | 16370.8049 | 105445.525 | 44478.4262 | 0.065534 | -343450.6168 | 343450.6168
C | Xist Rating 4898 | -63 | 721.264 | 150.289 | 35.7 | 2302.44 | 8637.47 | 20374.8 | 0.76 | 2.87 | 17.354 | 41.015 | 1 | 1 | 1730 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1660667.0842 | 123141.1841 | 2914.9181 | 16465.984 | 106675.2001 | 43616.7784 | 0.065915 | -336797.2016 | 336797.2016
C | Xist Rating 4899 | -62.73 | 725.525 | 150.29 | 35.7 | 2306.29 | 8709.65 | 20290.4 | 0.75 | 2.85 | 17.354 | 40.676 | 1 | 1 | 1740 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1673271.0522 | 124473.1668 | 2948.714 | 16561.1631 | 107912.0036 | 43257.1042 | 0.066296 | -334019.8924 | 334019.8924
C | Xist Rating 4900 | -62.4 | 733.879 | 150.29 | 35.6 | 2303.05 | 8699.25 | 20123.2 | 0.74 | 2.82 | 17.335 | 39.989 | 1 | 1 | 1750 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1690160.031 | 125812.278 | 2982.7046 | 16656.3422 | 109155.9358 | 42534.774 | 0.066677 | -328442.2501 | 328442.2501
C | Xist Rating 4901 | -62.09 | 740.119 | 150.29 | 35.7 | 2301.5 | 8703.42 | 20001.2 | 0.73 | 2.8 | 17.333 | 39.492 | 1 | 1 | 1760 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1703383.8785 | 127158.5178 | 3016.8901 | 16751.5213 | 110406.9965 | 42010.5993 | 0.067058 | -324394.7123 | 324394.7123
C | Xist Rating 4902 | -61.02 | 765.026 | 150.29 | 35.7 | 2290.64 | 8660.12 | 19497.8 | 0.73 | 2.71 | 17.369 | 37.379 | 1 | 1 | 1770 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1752399.1566 | 128511.8861 | 3051.2703 | 16846.7004 | 111665.1857 | 39824.0089 | 0.067439 | -307510.4408 | 307510.4408
C | Xist Rating 4903 | -60.9 | 771.375 | 150.29 | 35.6 | 2281.09 | 8550.45 | 19383.8 | 0.72 | 2.69 | 17.555 | 36.931 | 1 | 1 | 1780 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1759575.7988 | 129872.383 | 3085.8453 | 16941.8795 | 112930.5035 | 39361.272 | 0.06782 | -303937.3085 | 303937.3085
C | Xist Rating 4904 | -60.73 | 774.825 | 150.29 | 35.6 | 2281.46 | 8568.32 | 19327.2 | 0.7 | 2.68 | 17.544 | 36.731 | 1 | 1 | 1790 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1767732.2445 | 131240.0084 | 3120.6151 | 17037.0586 | 114202.9498 | 39130.4492 | 0.068201 | -302154.9565 | 302154.9565
C | Xist Rating 4905 | -60.26 | 786.011 | 150.29 | 35.6 | 2278.83 | 8578.1 | 19121.9 | 0.7 | 2.65 | 17.528 | 35.926 | 1 | 1 | 1800 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1791185.4471 | 132614.7624 | 3155.5797 | 17132.2377 | 115482.5247 | 38299.0591 | 0.068582 | -295735.1828 | 295735.1828
C | Xist Rating 4906 | -59.95 | 792.233 | 150.29 | 35.6 | 2278.99 | 8606.03 | 19012.5 | 0.69 | 2.63 | 17.53 | 35.511 | 1 | 1 | 1810 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1805491.0847 | 133996.645 | 3190.7391 | 17227.4168 | 116769.2281 | 37859.4731 | 0.068963 | -292340.8162 | 292340.8162
C | Xist Rating 4907 | -58.9 | 817.398 | 150.29 | 35.6 | 2267.51 | 8550.35 | 18562.8 | 0.69 | 2.55 | 17.56 | 33.756 | 1 | 1 | 1820 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1853458.139 | 135385.656 | 3226.0933 | 17322.5959 | 118063.0601 | 36044.019 | 0.069344 | -278322.3605 | 278322.3605
C | Xist Rating 4908 | -58.88 | 813.392 | 150.29 | 35.6 | 2280.89 | 8726.41 | 18631.2 | 0.68 | 2.56 | 17.587 | 34.032 | 1 | 1 | 1830 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1855257.6789 | 136781.7957 | 3261.6423 | 17417.775 | 119364.0207 | 36323.1774 | 0.069725 | -280477.948 | 280477.948
C | Xist Rating 4909 | -58.48 | 818.491 | 150.29 | 35.6 | 2288.94 | 8867.86 | 18545.2 | 0.68 | 2.55 | 17.607 | 33.716 | 1 | 1 | 1840 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1873476.7895 | 138185.0639 | 3297.386 | 17512.9541 | 120672.1098 | 36001.4943 | 0.070106 | -277993.9959 | 277993.9959
C | Xist Rating 4910 | -58.1 | 826.961 | 150.29 | 35.6 | 2286.53 | 8867.75 | 18409.4 | 0.66 | 2.52 | 17.597 | 33.225 | 1 | 1 | 1850 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1890871.1353 | 139595.4606 | 3333.3246 | 17608.1332 | 121987.3274 | 35467.2096 | 0.070487 | -273868.391 | 273868.391
C | Xist Rating 4911 | -57.7 | 836.449 | 150.29 | 35.6 | 2282.41 | 8846.1 | 18259.3 | 0.65 | 2.5 | 17.587 | 32.685 | 1 | 1 | 1860 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1909119.5621 | 141012.9859 | 3369.4579 | 17703.3123 | 123309.6736 | 34896.4131 | 0.070868 | -269460.8523 | 269460.8523
C | Xist Rating 4912 | -56.66 | 859.545 | 150.29 | 35.6 | 2276.79 | 8866.16 | 17879.7 | 0.65 | 2.43 | 17.633 | 31.277 | 1 | 1 | 1870 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1957003.4605 | 142437.6398 | 3405.7861 | 17798.4914 | 124639.1483 | 33441.8378 | 0.071249 | -258229.0071 | 258229.0071
C | Xist Rating 4913 | -56.24 | 869.018 | 150.29 | 35.6 | 2274.33 | 8868.8 | 17739.1 | 0.64 | 2.41 | 17.625 | 30.791 | 1 | 1 | 1880 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1976433.7079 | 143869.4221 | 3442.309 | 17893.6705 | 125975.7516 | 32926.9743 | 0.07163 | -254253.3674 | 254253.3674
C | Xist Rating 4914 | -55.89 | 875.288 | 150.29 | 35.6 | 2276.51 | 8929.12 | 17646.7 | 0.63 | 2.39 | 17.635 | 30.476 | 1 | 1 | 1890 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 1992601.8849 | 145308.3331 | 3479.0267 | 17988.8496 | 127319.4835 | 32590.5056 | 0.072011 | -251655.2452 | 251655.2452
C | Xist Rating 4915 | -55.61 | 882.016 | 150.29 | 35.6 | 2274.21 | 8920.65 | 17555.4 | 0.62 | 2.38 | 17.624 | 30.181 | 1 | 1 | 1900 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2005889.6074 | 146754.3726 | 3515.9392 | 18084.0287 | 128670.3439 | 32273.5286 | 0.072392 | -249207.6328 | 249207.6328
C | Xist Rating 4916 | -55.32 | 888.465 | 150.29 | 35.6 | 2272.69 | 8924.18 | 17465.2 | 0.61 | 2.36 | 17.632 | 29.883 | 1 | 1 | 1910 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2019205.5209 | 148207.5406 | 3553.0464 | 18179.2078 | 130028.3328 | 31954.283 | 0.072773 | -246742.503 | 246742.503
C | Xist Rating 4917 | -54.11 | 916.52 | 150.29 | 35.6 | 2263.62 | 8911.45 | 17050.4 | 0.61 | 2.29 | 17.676 | 28.433 | 1 | 1 | 1920 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2074653.0024 | 149667.8372 | 3590.3485 | 18274.3869 | 131393.4503 | 30455.5913 | 0.073154 | -235170.0034 | 235170.0034
C | Xist Rating 4918 | -53.7 | 926.07 | 150.29 | 35.6 | 2260.97 | 8910.35 | 16923.9 | 0.6 | 2.27 | 17.664 | 28.025 | 1 | 1 | 1930 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2093816.4879 | 151135.2624 | 3627.8454 | 18369.566 | 132765.6964 | 30020.8025 | 0.073535 | -231812.679 | 231812.679
C | Xist Rating 4919 | -53.38 | 929.158 | 150.29 | 35.6 | 2269.57 | 9059.33 | 16882 | 0.6 | 2.26 | 17.684 | 27.896 | 1 | 1 | 1940 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2108789.1221 | 152609.8161 | 3665.537 | 18464.7451 | 134145.071 | 29892.6304 | 0.073916 | -230822.9681 | 230822.9681
C | Xist Rating 4920 | -53.09 | 938.199 | 150.29 | 35.6 | 2262.27 | 8979.9 | 16772.2 | 0.58 | 2.24 | 17.666 | 27.56 | 1 | 1 | 1950 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2122459.4517 | 154091.4983 | 3703.4235 | 18559.9242 | 135531.5741 | 29516.624 | 0.074297 | -227919.5462 | 227919.5462
C | Xist Rating 4921 | -52.66 | 948.647 | 150.29 | 35.6 | 2258.31 | 8962.35 | 16637 | 0.58 | 2.22 | 17.679 | 27.128 | 1 | 1 | 1960 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2142339.0066 | 155580.3091 | 3741.5047 | 18655.1033 | 136925.2058 | 29073.2479 | 0.074678 | -224495.9141 | 224495.9141
C | Xist Rating 4922 | -51.57 | 973.941 | 150.29 | 35.6 | 2251.12 | 8962.57 | 16303.2 | 0.58 | 2.16 | 17.742 | 26.036 | 1 | 1 | 1970 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2192458.0639 | 157076.2485 | 3779.7807 | 18750.2824 | 138325.9661 | 27947.0306 | 0.075059 | -215799.562 | 215799.562
C | Xist Rating 4923 | -51.21 | 981.388 | 150.29 | 35.6 | 2251.16 | 8994.22 | 16214.4 | 0.57 | 2.15 | 17.772 | 25.767 | 1 | 1 | 1980 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2209261.4101 | 158579.3164 | 3818.2515 | 18845.4615 | 139733.8549 | 27658.0582 | 0.07544 | -213568.1944 | 213568.1944
C | Xist Rating 4924 | -50.83 | 991.133 | 150.29 | 35.6 | 2247.01 | 8968.22 | 16101.5 | 0.56 | 2.13 | 17.77 | 25.431 | 1 | 1 | 1990 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2227085.7623 | 160089.5128 | 3856.9171 | 18940.6406 | 141148.8722 | 27297.7108 | 0.075821 | -210785.6871 | 210785.6871
C | Xist Rating 4925 | -50.5 | 998.705 | 150.29 | 35.6 | 2245.39 | 8973.47 | 16015 | 0.55 | 2.12 | 17.773 | 25.177 | 1 | 1 | 2000 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2242482.2199 | 161606.8378 | 3895.7775 | 19035.8197 | 142571.0181 | 27022.61 | 0.076202 | -208661.4319 | 208661.4319
C | Xist Rating 4926 | -50.23 | 1004.28 | 150.29 | 35.6 | 2245.82 | 9002.52 | 15953.9 | 0.54 | 2.11 | 17.775 | 25.004 | 1 | 1 | 2010 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2255432.1096 | 163131.2914 | 3934.8326 | 19130.9988 | 144000.2926 | 26831.4158 | 0.076583 | -207185.0803 | 207185.0803
C | Xist Rating 4927 | -49.06 | 1032.78 | 150.29 | 35.6 | 2235.86 | 8968.75 | 15614.9 | 0.54 | 2.05 | 17.812 | 23.959 | 1 | 1 | 2020 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2309151.4908 | 164662.8735 | 3974.0826 | 19226.1779 | 145436.6956 | 25752.2965 | 0.076964 | -198852.4075 | 198852.4075
C | Xist Rating 4928 | -48.59 | 1043.17 | 150.29 | 35.7 | 2234.83 | 8996.28 | 15499.8 | 0.54 | 2.03 | 17.815 | 23.624 | 1 | 1 | 2030 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2331307.6111 | 166201.5842 | 4013.5273 | 19321.357 | 146880.2272 | 25408.8584 | 0.077345 | -196200.4695 | 196200.4695
C | Xist Rating 4929 | -48.32 | 1050.1 | 150.29 | 35.7 | 2232.1 | 8978.55 | 15431.8 | 0.53 | 2.02 | 17.81 | 23.443 | 1 | 1 | 2040 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2343928.21 | 167747.4234 | 4053.1669 | 19416.5361 | 148330.8873 | 25208.6696 | 0.077726 | -194654.6646 | 194654.6646
C | Xist Rating 4930 | -47.94 | 1056.21 | 150.29 | 35.7 | 2235.98 | 9068.49 | 15364.3 | 0.52 | 2.01 | 17.825 | 23.25 | 1 | 1 | 2050 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2361664.4358 | 169300.3911 | 4093.0012 | 19511.7152 | 149788.6759 | 24996.8216 | 0.078107 | -193018.8304 | 193018.8304
C | Xist Rating 4931 | -47.61 | 1066.35 | 150.29 | 35.7 | 2229.82 | 9007.64 | 15264.3 | 0.51 | 1.99 | 17.81 | 22.979 | 1 | 1 | 2060 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2377768.557 | 170860.4874 | 4133.0303 | 19606.8943 | 151253.5931 | 24702.3775 | 0.078488 | -190745.2114 | 190745.2114
C | Xist Rating 4932 | -46.37 | 1096.95 | 150.29 | 35.7 | 2219.52 | 8973.14 | 14936.2 | 0.51 | 1.94 | 17.848 | 22.025 | 1 | 1 | 2070 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2434702.464 | 172427.7123 | 4173.2542 | 19702.0734 | 152725.6389 | 23717.5197 | 0.078869 | -183140.4005 | 183140.4005
C | Xist Rating 4933 | -46.08 | 1103.68 | 150.29 | 35.7 | 2218.29 | 8979.3 | 14873.5 | 0.51 | 1.93 | 17.844 | 21.864 | 1 | 1 | 2080 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2448282.3072 | 174002.0657 | 4213.6729 | 19797.2525 | 154204.8132 | 23554.2114 | 0.07925 | -181879.3771 | 181879.3771
C | Xist Rating 4934 | -45.72 | 1112.36 | 150.29 | 35.7 | 2216.45 | 8983.97 | 14790.8 | 0.5 | 1.91 | 17.842 | 21.645 | 1 | 1 | 2090 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2465490.322 | 175583.5477 | 4254.2864 | 19892.4316 | 155691.1161 | 23314.0489 | 0.079631 | -180024.9061 | 180024.9061
C | Xist Rating 4935 | -45.37 | 1121.03 | 150.29 | 35.7 | 2214.53 | 8987.14 | 14709.3 | 0.49 | 1.9 | 17.845 | 21.43 | 1 | 1 | 2100 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2482554.5659 | 177172.1582 | 4295.0947 | 19987.6107 | 157184.5475 | 23078.114 | 0.080012 | -178203.0788 | 178203.0788
C | Xist Rating 4936 | -45.01 | 1128.7 | 150.29 | 35.7 | 2214.69 | 9020.46 | 14638.5 | 0.49 | 1.89 | 17.844 | 21.248 | 1 | 1 | 2110 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2499720.603 | 178767.8972 | 4336.0977 | 20082.7898 | 158685.1075 | 22892.9804 | 0.080393 | -176773.5265 | 176773.5265
C | Xist Rating 4937 | -43.87 | 1157.64 | 150.29 | 35.7 | 2204.63 | 8977.56 | 14358.9 | 0.49 | 1.84 | 17.879 | 20.483 | 1 | 1 | 2120 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2552167.8732 | 180370.7649 | 4377.2956 | 20177.9689 | 160192.796 | 22104.0781 | 0.080774 | -170681.8321 | 170681.8321
C | Xist Rating 4938 | -43.43 | 1168.38 | 150.29 | 35.7 | 2202.03 | 8977.5 | 14263.6 | 0.48 | 1.83 | 17.874 | 20.239 | 1 | 1 | 2130 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2572807.8114 | 181980.761 | 4418.6882 | 20273.148 | 161707.6131 | 21837.3121 | 0.081155 | -168621.9355 | 168621.9355
C | Xist Rating 4939 | -43.04 | 1179.14 | 150.29 | 35.7 | 2197.72 | 8948.72 | 14169.9 | 0.47 | 1.81 | 17.868 | 20.001 | 1 | 1 | 2140 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2591419.5608 | 183597.8857 | 4460.2756 | 20368.3271 | 163229.5587 | 21576.5791 | 0.081536 | -166608.6245 | 166608.6245
C | Xist Rating 4940 | -42.79 | 1184.86 | 150.29 | 35.7 | 2197.66 | 8969.13 | 14123.5 | 0.47 | 1.8 | 17.867 | 19.893 | 1 | 1 | 2150 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2603919.4276 | 185222.139 | 4502.0578 | 20463.5062 | 164758.6328 | 21468.1403 | 0.081917 | -165771.2891 | 165771.2891
C | Xist Rating 4941 | -42.48 | 1192.47 | 150.29 | 35.7 | 2195.81 | 8968.31 | 14059 | 0.46 | 1.79 | 17.871 | 19.734 | 1 | 1 | 2160 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2618437.5507 | 186853.5208 | 4544.0348 | 20558.6853 | 166294.8356 | 21289.6623 | 0.082298 | -164393.1292 | 164393.1292
C | Xist Rating 4942 | -41.3 | 1223.73 | 150.29 | 35.7 | 2184.45 | 8908.55 | 13786 | 0.46 | 1.75 | 17.904 | 19.028 | 1 | 1 | 2170 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2673176.9985 | 188492.0312 | 4586.2066 | 20653.8644 | 167838.1668 | 20561.6439 | 0.082679 | -158771.5637 | 158771.5637
C | Xist Rating 4943 | -40.85 | 1234.24 | 150.29 | 35.7 | 2183.31 | 8931.81 | 13699 | 0.46 | 1.74 | 17.905 | 18.815 | 1 | 1 | 2180 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2694728.5344 | 190137.6701 | 4628.5732 | 20749.0435 | 169388.6267 | 20344.1803 | 0.08306 | -157092.368 | 157092.368
C | Xist Rating 4944 | -40.52 | 1242.08 | 150.29 | 35.7 | 2182.05 | 8940.19 | 13639 | 0.45 | 1.73 | 17.907 | 18.676 | 1 | 1 | 2190 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2710280.664 | 191790.4376 | 4671.1346 | 20844.2226 | 170946.215 | 20186.0327 | 0.083441 | -155871.1937 | 155871.1937
C | Xist Rating 4945 | -40.24 | 1250.33 | 150.29 | 35.7 | 2178.65 | 8912.55 | 13579.4 | 0.44 | 1.72 | 17.899 | 18.544 | 1 | 1 | 2200 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2724031.4545 | 193450.3336 | 4713.8907 | 20939.4017 | 172510.932 | 20034.557 | 0.083822 | -154701.5383 | 154701.5383
C | Xist Rating 4946 | -39.8 | 1261.1 | 150.29 | 35.7 | 2176.71 | 8922.05 | 13495.3 | 0.44 | 1.7 | 17.899 | 18.345 | 1 | 1 | 2210 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2745048.981 | 195117.3582 | 4756.8417 | 21034.5808 | 174082.7774 | 19831.426 | 0.084203 | -153133.0146 | 153133.0146
C | Xist Rating 4947 | -38.61 | 1292.22 | 150.29 | 35.7 | 2167 | 8886.03 | 13246.2 | 0.44 | 1.66 | 17.936 | 17.732 | 1 | 1 | 2220 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2800240.74 | 196791.5113 | 4799.9874 | 21129.7599 | 175661.7515 | 19199.9767 | 0.084584 | -148257.1305 | 148257.1305
C | Xist Rating 4948 | -38.23 | 1300.87 | 150.29 | 35.7 | 2166.59 | 8912.35 | 13182.4 | 0.43 | 1.65 | 17.937 | 17.587 | 1 | 1 | 2230 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2818451.9333 | 198472.793 | 4843.3279 | 21224.939 | 177247.854 | 19035.0462 | 0.084965 | -146983.5813 | 146983.5813
C | Xist Rating 4949 | -37.87 | 1310.97 | 150.29 | 35.6 | 2163.21 | 8892.45 | 13111.7 | 0.43 | 1.64 | 17.931 | 17.43 | 1 | 1 | 2240 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2835903.4137 | 200161.2032 | 4886.8633 | 21320.1181 | 178841.0852 | 18875.2002 | 0.085346 | -145749.2928 | 145749.2928
C | Xist Rating 4950 | -37.49 | 1322.05 | 150.29 | 35.7 | 2158.75 | 8858.37 | 13034 | 0.42 | 1.63 | 17.929 | 17.258 | 1 | 1 | 2250 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2853975.4375 | 201856.742 | 4930.5934 | 21415.2972 | 180441.4448 | 18681.8655 | 0.085727 | -144256.4134 | 144256.4134
C | Xist Rating 4951 | -37.24 | 1327.73 | 150.29 | 35.6 | 2158.94 | 8882.24 | 12995.5 | 0.42 | 1.62 | 17.931 | 17.177 | 1 | 1 | 2260 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2866489.4062 | 203559.4093 | 4974.5182 | 21510.4763 | 182048.9331 | 18601.2076 | 0.086108 | -143633.5945 | 143633.5945
C | Xist Rating 4952 | -36 | 1361.27 | 150.29 | 35.7 | 2147.94 | 8828.87 | 12751.8 | 0.42 | 1.59 | 17.966 | 16.609 | 1 | 1 | 2270 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2923926.2838 | 205269.2052 | 5018.6379 | 21605.6554 | 183663.5498 | 18016.212 | 0.086489 | -139116.4135 | 139116.4135
C | Xist Rating 4953 | -35.61 | 1371.32 | 150.29 | 35.7 | 2145.72 | 8827.74 | 12686.2 | 0.41 | 1.58 | 17.962 | 16.47 | 1 | 1 | 2280 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2942468.7504 | 206986.1296 | 5062.9524 | 21700.8345 | 185285.2952 | 17856.7142 | 0.08687 | -137884.8135 | 137884.8135
C | Xist Rating 4954 | -35.15 | 1383.16 | 150.29 | 35.6 | 2143.4 | 8832.87 | 12606.9 | 0.41 | 1.56 | 17.96 | 16.297 | 1 | 1 | 2290 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2964665.144 | 208710.1826 | 5107.4617 | 21796.0135 | 186914.1691 | 17680.2708 | 0.087251 | -136522.365 | 136522.365
C | Xist Rating 4955 | -34.84 | 1391.17 | 150.29 | 35.6 | 2142.06 | 8838.42 | 12557 | 0.4 | 1.56 | 17.959 | 16.196 | 1 | 1 | 2300 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2979969.6102 | 210441.3641 | 5152.1657 | 21891.1926 | 188550.1715 | 17560.1258 | 0.087632 | -135594.6368 | 135594.6368
| Xist Rating 4956 | -34.54 | 1399.44 | 150.29 | 35.6 | 2139.72 | 8826.8 | 12507.5 | 0.4 | 1.55 | 17.955 | 16.098 | 1 | 1 | 2310 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 2994409.7568 | 212179.6742 | 5197.0645 | 21986.3717 | 190193.3025 | 17461.4073 | 0.088013 | -134832.3588 | 134832.3588
| Xist Rating 4957 | -33.24 | 1433.83 | 150.29 | 35.6 | 2130.4 | 8802.07 | 12277 | 0.4 | 1.51 | 17.991 | 15.585 | 1 | 1 | 2320 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 3054631.432 | 213925.1129 | 5242.1582 | 22081.5508 | 191843.562 | 16933.3744 | 0.088394 | -130755.0289 | 130755.0289
| Xist Rating 4958 | -32.91 | 1443.91 | 150.29 | 35.6 | 2126.74 | 8775.28 | 12216.8 | 0.39 | 1.5 | 17.991 | 15.463 | 1 | 1 | 2330 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 3070821.1534 | 215677.68 | 5287.4466 | 22176.7299 | 193500.9501 | 16791.1133 | 0.088775 | -129656.5263 | 129656.5263
| Xist Rating 4959 | -32.53 | 1453.97 | 150.29 | 35.6 | 2124.84 | 8778.43 | 12157.2 | 0.39 | 1.49 | 17.983 | 15.344 | 1 | 1 | 2340 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 3089453.6148 | 217437.3758 | 5332.9298 | 22271.909 | 195165.4667 | 16670.3499 | 0.089156 | -128724.023 | 128724.023
| Xist Rating 4960 | -32.2 | 1463.11 | 150.29 | 35.6 | 2122.46 | 8769.53 | 12104.8 | 0.38 | 1.49 | 17.977 | 15.241 | 1 | 1 | 2350 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 3105392.4506 | 219204.2001 | 5378.6078 | 22367.0881 | 196837.1119 | 16547.3452 | 0.089537 | -127774.2132 | 127774.2132
| Xist Rating 4961 | -31.8 | 1474.24 | 150.29 | 35.6 | 2119.61 | 8760.14 | 12039.9 | 0.38 | 1.48 | 17.971 | 15.111 | 1 | 1 | 2360 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 3124813.8464 | 220978.1529 | 5424.4805 | 22462.2672 | 198515.8857 | 16415.1613 | 0.089918 | -126753.5242 | 126753.5242
| Xist Rating 4962 | -30.63 | 1505.79 | 150.29 | 35.6 | 2111.56 | 8741.71 | 11846.8 | 0.38 | 1.45 | 18.001 | 14.704 | 1 | 1 | 2370 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 3179565.9324 | 222759.2343 | 5470.5481 | 22557.4463 | 200201.788 | 15996.7646 | 0.090299 | -123522.7756 | 123522.7756
| Xist Rating 4963 | -30.27 | 1516.09 | 150.29 | 35.6 | 2108.75 | 8728.55 | 11791.2 | 0.37 | 1.44 | 17.993 | 14.598 | 1 | 1 | 2380 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 3197054.7875 | 224547.4442 | 5516.8105 | 22652.6254 | 201894.8188 | 15870.2302 | 0.09068 | -122545.7107 | 122545.7107
| Xist Rating 4964 | -29.88 | 1526.77 | 150.29 | 35.6 | 2106.54 | 8729.23 | 11730 | 0.37 | 1.43 | 17.987 | 14.477 | 1 | 1 | 2390 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 3216202.0758 | 226342.7827 | 5563.2676 | 22747.8045 | 203594.9782 | 15747.3182 | 0.091061 | -121596.6169 | 121596.6169
C | Xist Rating 4967 | -21.58 | 1752.81 | 150.29 | 35.7 | 2052.03 | 8614.42 | 10539 | 0.39 | 1.25 | 18.034 | 12.157 | 1 | 1 | 2420 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 3596818.7043 | 231771.5695 | 5703.8078 | 23033.3418 | 208738.2277 | 13387.9628 | 0.092204 | -103378.2996 | 103378.2996
C | Xist Rating 4968 | -21.7 | 1754.16 | 150.29 | 35.6 | 2049.49 | 8570.56 | 10537.9 | 0.39 | 1.25 | 18.019 | 12.167 | 1 | 1 | 2430 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 3595133.3784 | 233595.4222 | 5751.0441 | 23128.5209 | 210466.9013 | 13400.8632 | 0.092585 | -103477.9132 | 103477.9132
C | Xist Rating 4969 | -21.68 | 1755.53 | 150.29 | 35.6 | 2049.3 | 8567.34 | 10537.9 | 0.38 | 1.25 | 18.011 | 12.178 | 1 | 1 | 2440 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 3597607.629 | 235426.4034 | 5798.4752 | 23223.7 | 212202.7034 | 13395.3964 | 0.092966 | -103435.7003 | 103435.7003
C | Xist Rating 4970 | -21.68 | 1756.86 | 150.29 | 35.6 | 2048.41 | 8551.79 | 10537.8 | 0.38 | 1.25 | 18.006 | 12.188 | 1 | 1 | 2450 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 20 | E | Rod | 3598769.5926 | 237264.5132 | 5846.1011 | 23318.8791 | 213945.6341 | 13408.6406 | 0.093347 | -103537.9685 | 103537.9685
C | Xist Rating 4971 | -21.66 | 1758.33 | 150.29 | 35.6 | 2047.88 | 8542.65 | 10537.8 | 0.37 | 1.25 | 17.996 | 12.199 | 1 | 1 | 2460 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3600848.8404 | 239109.7516 | 5893.9217 | 23414.0582 | 215695.6933 | 13402.8682 | 0.093728 | -103493.3952 | 103493.3952
C | Xist Rating 4972 | -21.63 | 1759.69 | 150.29 | 35.6 | 2047.71 | 8539.71 | 10537.8 | 0.36 | 1.25 | 18.031 | 12.21 | 1 | 1 | 2470 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3603334.8099 | 240962.1185 | 5941.9372 | 23509.2373 | 217452.8811 | 13398.7467 | 0.094109 | -103461.5705 | 103461.5705
C | Xist Rating 4973 | -21.61 | 1761.03 | 150.29 | 35.6 | 2047.39 | 8534.19 | 10537.8 | 0.36 | 1.25 | 18.024 | 12.221 | 1 | 1 | 2480 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3605515.2117 | 242821.6139 | 5990.1474 | 23604.4164 | 219217.1975 | 13412.7997 | 0.09449 | -103570.0839 | 103570.0839
C | Xist Rating 4974 | -21.6 | 1762.43 | 150.29 | 35.6 | 2046.92 | 8525.93 | 10537.8 | 0.35 | 1.25 | 18.021 | 12.231 | 1 | 1 | 2490 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3607553.2156 | 244688.2379 | 6038.5525 | 23699.5955 | 220988.6424 | 13405.8588 | 0.094871 | -103516.4882 | 103516.4882
C | Xist Rating 4975 | -21.57 | 1763.42 | 150.29 | 35.6 | 2047.27 | 8532.12 | 10537.8 | 0.35 | 1.25 | 18.017 | 12.24 | 1 | 1 | 2500 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3610196.8634 | 246561.9905 | 6087.1523 | 23794.7746 | 222767.2158 | 13417.8757 | 0.095252 | -103609.2791 | 103609.2791
C | Xist Rating 4976 | -21.56 | 1765.27 | 150.29 | 35.6 | 2046.01 | 8510.26 | 10537.7 | 0.34 | 1.25 | 18.01 | 12.253 | 1 | 1 | 2510 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3611760.0727 | 248442.8716 | 6135.9469 | 23889.9537 | 224552.9179 | 13413.6641 | 0.095633 | -103576.7584 | 103576.7584
C | Xist Rating 4977 | -21.57 | 1766.72 | 150.29 | 35.6 | 2044.93 | 8491.56 | 10537.7 | 0.34 | 1.25 | 18.048 | 12.264 | 1 | 1 | 2520 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3612818.7296 | 250330.8812 | 6184.9363 | 23985.1328 | 226345.7484 | 13429.2918 | 0.096014 | -103697.4313 | 103697.4313
C | Xist Rating 4978 | -21.55 | 1768.06 | 150.29 | 35.6 | 2044.26 | 8479.97 | 10537.8 | 0.33 | 1.25 | 18.044 | 12.274 | 1 | 1 | 2530 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3614374.3356 | 252226.0194 | 6234.1205 | 24080.3119 | 228145.7075 | 13421.8101 | 0.096395 | -103639.6596 | 103639.6596
C | Xist Rating 4979 | -21.53 | 1769.21 | 150.29 | 35.6 | 2044.18 | 8478.65 | 10537.7 | 0.33 | 1.25 | 18.039 | 12.283 | 1 | 1 | 2540 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3616583.6978 | 254128.2862 | 6283.4995 | 24175.491 | 229952.7952 | 13433.6378 | 0.096776 | -103730.9901 | 103730.9901
C | Xist Rating 4980 | -21.52 | 1770.76 | 150.29 | 35.6 | 2043.34 | 8464.28 | 10537.7 | 0.32 | 1.25 | 18.035 | 12.294 | 1 | 1 | 2550 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3618264.7384 | 256037.6815 | 6333.0732 | 24270.6701 | 231767.0114 | 13426.9642 | 0.097157 | -103679.4586 | 103679.4586
C | Xist Rating 4981 | -21.49 | 1772.2 | 150.29 | 35.6 | 2043.09 | 8460.01 | 10537.7 | 0.32 | 1.25 | 18.029 | 12.305 | 1 | 1 | 2560 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3620764.098 | 257954.2053 | 6382.8418 | 24365.8492 | 233588.3561 | 13440.7543 | 0.097538 | -103785.9419 | 103785.9419
C | Xist Rating 4982 | -21.47 | 1773.59 | 150.29 | 35.6 | 2042.63 | 8452.12 | 10537.7 | 0.31 | 1.25 | 18.025 | 12.315 | 1 | 1 | 2570 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3622788.1417 | 259877.8577 | 6432.8051 | 24461.0283 | 235416.8294 | 13432.8132 | 0.097919 | -103724.6229 | 103724.6229
C | Xist Rating 4983 | -21.44 | 1774.96 | 150.291 | 35.6 | 2042.8 | 8454.99 | 10537.7 | 0.31 | 1.25 | 18.078 | 12.325 | 1 | 1 | 2580 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3625888.288 | 261808.6387 | 6482.9633 | 24556.2074 | 237252.4313 | 13447.603 | 0.0983 | -103838.8255 | 103838.8255
C | Xist Rating 4984 | -21.42 | 1776.32 | 150.291 | 35.6 | 2042.52 | 8450.19 | 10537.7 | 0.3 | 1.25 | 18.076 | 12.336 | 1 | 1 | 2590 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3628169.1264 | 263746.5482 | 6533.3162 | 24651.3865 | 239095.1617 | 13440.481 | 0.098681 | -103783.8319 | 103783.8319
C | Xist Rating 4985 | -21.4 | 1777.5 | 150.291 | 35.6 | 2042.38 | 8447.95 | 10537.7 | 0.3 | 1.25 | 18.072 | 12.345 | 1 | 1 | 2600 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3630330.45 | 265691.5863 | 6583.8639 | 24746.5656 | 240945.0207 | 13452.1184 | 0.099062 | -103873.6927 | 103873.6927
C | Xist Rating 4986 | -21.37 | 1779.18 | 150.291 | 35.6 | 2041.74 | 8436.94 | 10537.7 | 0.29 | 1.25 | 18.072 | 12.356 | 1 | 1 | 2610 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3632622.9732 | 267643.7529 | 6634.6064 | 24841.7447 | 242802.0082 | 13444.8293 | 0.099443 | -103817.4077 | 103817.4077
C | Xist Rating 4987 | -21.34 | 1780.58 | 150.291 | 35.6 | 2041.55 | 8433.63 | 10537.7 | 0.29 | 1.25 | 18.073 | 12.367 | 1 | 1 | 2620 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3635143.099 | 269603.048 | 6685.5437 | 24936.9238 | 244666.1242 | 13458.636 | 0.099824 | -103924.0198 | 103924.0198
C | Xist Rating 4988 | -21.32 | 1782.01 | 150.291 | 35.6 | 2041.07 | 8425.6 | 10537.6 | 0.29 | 1.25 | 18.108 | 12.377 | 1 | 1 | 2630 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3637207.1507 | 271569.4717 | 6736.6758 | 25032.1029 | 246537.3688 | 13472.5669 | 0.10021 | -104031.5904 | 104031.5904
C | Xist Rating 4989 | -21.29 | 1783.25 | 150.291 | 35.6 | 2041.23 | 8428.31 | 10537.6 | 0.28 | 1.25 | 18.106 | 12.386 | 1 | 1 | 2640 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3640023.3975 | 273543.024 | 6788.0027 | 25127.282 | 248415.742 | 13462.7725 | 0.10059 | -103955.9608 | 103955.9608
C | Xist Rating 4990 | -21.25 | 1784.76 | 150.291 | 35.6 | 2041.11 | 8426.24 | 10537.6 | 0.28 | 1.25 | 18.104 | 12.397 | 1 | 1 | 2650 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3642891.4836 | 275523.7048 | 6839.5243 | 25222.4611 | 250301.2437 | 13476.402 | 0.10097 | -104061.2037 | 104061.2037
C | Xist Rating 4991 | -21.23 | 1786.1 | 150.291 | 35.6 | 2041 | 8424.3 | 10537.7 | 0.28 | 1.25 | 18.1 | 12.407 | 1 | 1 | 2660 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3645430.1 | 277511.5142 | 6891.2408 | 25317.6402 | 252193.874 | 13488.9256 | 0.10135 | -104157.9081 | 104157.9081
C | Xist Rating 4992 | -21.19 | 1787.48 | 150.291 | 35.6 | 2041.07 | 8425.47 | 10537.7 | 0.27 | 1.25 | 18.099 | 12.417 | 1 | 1 | 2670 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3648371.8036 | 279506.4521 | 6943.152 | 25412.8193 | 254093.6328 | 13479.8876 | 0.10173 | -104088.1188 | 104088.1188
C | Xist Rating 4993 | -21.16 | 1788.9 | 150.291 | 35.6 | 2040.9 | 8422.58 | 10537.6 | 0.27 | 1.25 | 18.135 | 12.427 | 1 | 1 | 2680 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3650966.01 | 281508.5186 | 6995.258 | 25507.9984 | 256000.5202 | 13493.6307 | 0.10211 | -104194.2395 | 104194.2395
C | Xist Rating 4994 | -21.12 | 1790.28 | 150.291 | 35.6 | 2041.13 | 8426.61 | 10537.6 | 0.26 | 1.25 | 18.133 | 12.436 | 1 | 1 | 2690 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3654194.2164 | 283517.7136 | 7047.5588 | 25603.1775 | 257914.5361 | 13483.2424 | 0.10249 | -104114.0239 | 104114.0239
C | Xist Rating 4995 | -21.06 | 1791.48 | 150.291 | 35.6 | 2042.12 | 8443.46 | 10537.5 | 0.26 | 1.25 | 18.13 | 12.445 | 1 | 1 | 2700 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3658417.1376 | 285534.0372 | 7100.0544 | 25698.3566 | 259835.6806 | 13494.6078 | 0.10287 | -104201.7844 | 104201.7844
C | Xist Rating 4996 | -21.03 | 1793.13 | 150.291 | 35.6 | 2041.87 | 8439.33 | 10537.5 | 0.26 | 1.25 | 18.122 | 12.457 | 1 | 1 | 2710 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3661338.3531 | 287557.4893 | 7152.7448 | 25793.5357 | 261763.9536 | 13508.9301 | 0.10325 | -104312.3771 | 104312.3771
C | Xist Rating 4997 | -21.01 | 1794.48 | 150.291 | 35.6 | 2041.45 | 8432.09 | 10537.5 | 0.25 | 1.25 | 18.12 | 12.466 | 1 | 1 | 2720 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3663341.196 | 289588.0699 | 7205.63 | 25888.7148 | 263699.3552 | 13498.2327 | 0.10363 | -104229.7749 | 104229.7749
C | Xist Rating 4998 | -21.02 | 1795.8 | 150.291 | 35.6 | 2040.37 | 8413.67 | 10537.5 | 0.25 | 1.25 | 18.152 | 12.476 | 1 | 1 | 2730 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3664096.446 | 291625.7792 | 7258.71 | 25983.8939 | 265641.8853 | 13511.6272 | 0.10402 | -104333.2038 | 104333.2038
C | Xist Rating 4999 | -21 | 1797.08 | 150.291 | 35.6 | 2040.12 | 8409.37 | 10537.5 | 0.25 | 1.25 | 18.15 | 12.485 | 1 | 1 | 2740 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3666258.8496 | 293670.6169 | 7311.9847 | 26079.073 | 267591.544 | 13522.9464 | 0.1044 | -104420.6078 | 104420.6078
C | Xist Rating 5000 | -21.02 | 1798.63 | 150.291 | 35.6 | 2038.31 | 8378.84 | 10537.5 | 0.25 | 1.25 | 18.143 | 12.495 | 1 | 1 | 2750 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3666165.5153 | 295722.5833 | 7365.4543 | 26174.2521 | 269548.3312 | 13535.1496 | 0.10478 | -104514.8375 | 104514.8375
C | Xist Rating 5001 | -21 | 1800.06 | 150.291 | 35.6 | 2037.84 | 8370.87 | 10537.5 | 0.24 | 1.25 | 18.142 | 12.505 | 1 | 1 | 2760 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3668234.2704 | 297781.6781 | 7419.1186 | 26269.4312 | 271512.247 | 13525.0922 | 0.10516 | -104437.1772 | 104437.1772
C | Xist Rating 5002 | -21 | 1801.29 | 150.291 | 35.6 | 2037.12 | 8358.66 | 10537.6 | 0.24 | 1.25 | 18.142 | 12.514 | 1 | 1 | 2770 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3669443.8848 | 299847.9016 | 7472.9777 | 26364.6103 | 273483.2913 | 13536.3904 | 0.10554 | -104524.4188 | 104524.4188
C | Xist Rating 5003 | -20.98 | 1802.84 | 150.291 | 35.6 | 2036.51 | 8348.37 | 10537.5 | 0.24 | 1.25 | 18.175 | 12.524 | 1 | 1 | 2780 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3671501.6884 | 301921.2535 | 7527.0316 | 26459.7894 | 275461.4642 | 13549.714 | 0.10592 | -104627.3002 | 104627.3002
C | Xist Rating 5004 | -20.97 | 1804.25 | 150.291 | 35.6 | 2035.85 | 8337.21 | 10537.6 | 0.23 | 1.25 | 18.175 | 12.534 | 1 | 1 | 2790 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3673182.3625 | 304001.7341 | 7581.2803 | 26554.9685 | 277446.7656 | 13539.3245 | 0.1063 | -104547.0748 | 104547.0748
C | Xist Rating 5005 | -20.89 | 1805.22 | 150.291 | 35.6 | 2037.4 | 8363.28 | 10537.7 | 0.23 | 1.25 | 18.183 | 12.542 | 1 | 1 | 2800 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3677955.228 | 306089.3431 | 7635.7238 | 26650.1476 | 279439.1956 | 13549.7372 | 0.10668 | -104627.4789 | 104627.4789
C | Xist Rating 5006 | -20.94 | 1806.97 | 150.291 | 35.6 | 2034.99 | 8322.82 | 10537.6 | 0.23 | 1.25 | 18.173 | 12.553 | 1 | 1 | 2810 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3677165.8803 | 308184.0808 | 7690.3621 | 26745.3267 | 281438.7541 | 13562.7456 | 0.10706 | -104727.9262 | 104727.9262
C | Xist Rating 5007 | -20.88 | 1808.44 | 150.291 | 35.6 | 2035.49 | 8331.25 | 10537.7 | 0.23 | 1.25 | 18.183 | 12.563 | 1 | 1 | 2820 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3681061.5356 | 310285.9469 | 7745.1952 | 26840.5058 | 283445.4412 | 13575.2949 | 0.10744 | -104824.8286 | 104824.8286
C | Xist Rating 5008 | -20.86 | 1809.81 | 150.291 | 35.6 | 2035 | 8322.96 | 10537.7 | 0.22 | 1.25 | 18.223 | 12.572 | 1 | 1 | 2830 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3682963.35 | 312394.9417 | 7800.223 | 26935.6849 | 285459.2568 | 13564.5665 | 0.10783 | -104741.9866 | 104741.9866
C | Xist Rating 5009 | -20.65 | 1811.13 | 150.291 | 35.6 | 2039.75 | 8403.04 | 10537.8 | 0.22 | 1.25 | 18.256 | 12.582 | 1 | 1 | 2840 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3694252.4175 | 314511.0649 | 7855.4457 | 27030.864 | 287480.201 | 13577.6727 | 0.10821 | -104843.1895 | 104843.1895
C | Xist Rating 5010 | -20.27 | 1812.58 | 150.291 | 35.6 | 2048.51 | 8553.52 | 10538 | 0.22 | 1.25 | 18.318 | 12.592 | 1 | 1 | 2850 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3713088.2558 | 316634.3168 | 7910.8631 | 27126.0431 | 289508.2737 | 13591.6005 | 0.10859 | -104950.7363 | 104950.7363
C | Xist Rating 5011 | -20.68 | 1813.98 | 150.291 | 35.6 | 2036.95 | 8355.56 | 10537.8 | 0.22 | 1.25 | 18.246 | 12.601 | 1 | 1 | 2860 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3694986.561 | 318764.6972 | 7966.4753 | 27221.2222 | 291543.475 | 13600.7227 | 0.10897 | -105021.1758 | 105021.1758
C | Xist Rating 5012 | -20.16 | 1815.17 | 150.291 | 35.6 | 2050.08 | 8580.97 | 10538 | 0.21 | 1.25 | 18.339 | 12.61 | 1 | 1 | 2870 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3721243.7136 | 320902.2061 | 8022.2824 | 27316.4013 | 293585.8048 | 13590.9081 | 0.10935 | -104945.39 | 104945.39
C | Xist Rating 5013 | -19.57 | 1816.68 | 150.291 | 35.6 | 2064.45 | 8838.42 | 10538.1 | 0.21 | 1.25 | 18.448 | 12.621 | 1 | 1 | 2880 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3750445.026 | 323046.8436 | 8078.2842 | 27411.5804 | 295635.2632 | 13607.0129 | 0.10973 | -105069.7466 | 105069.7466
C | Xist Rating 5014 | -19.22 | 1818.02 | 150.291 | 35.6 | 2072.59 | 8989.38 | 10538.1 | 0.2 | 1.25 | 18.482 | 12.631 | 1 | 1 | 2890 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3768010.0718 | 325198.6096 | 8134.4807 | 27506.7595 | 297691.8502 | 13596.1172 | 0.11011 | -104985.6127 | 104985.6127
C | Xist Rating 5015 | -19.01 | 1819.41 | 150.291 | 35.6 | 2077.34 | 9079.62 | 10538.1 | 0.2 | 1.25 | 18.501 | 12.64 | 1 | 1 | 2900 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3779533.1694 | 327357.5042 | 8190.8721 | 27601.9386 | 299755.5656 | 13607.6145 | 0.11049 | -105074.3923 | 105074.3923
C | Xist Rating 5016 | -18.87 | 1820.95 | 150.291 | 35.6 | 2079.81 | 9126.98 | 10538.1 | 0.2 | 1.25 | 18.512 | 12.651 | 1 | 1 | 2910 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3787230.0195 | 329523.5273 | 8247.4583 | 27697.1177 | 301826.4097 | 13620.9836 | 0.11087 | -105177.6245 | 105177.6245
C | Xist Rating 5017 | -18.71 | 1822.34 | 150.291 | 35.6 | 2082.97 | 9188.15 | 10538.1 | 0.2 | 1.25 | 18.525 | 12.66 | 1 | 1 | 2920 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3795879.5498 | 331696.679 | 8304.2393 | 27792.2968 | 303904.3823 | 13632.3299 | 0.11125 | -105265.2383 | 105265.2383
C | Xist Rating 5018 | -18.51 | 1823.72 | 150.291 | 35.6 | 2087.34 | 9273.66 | 10538.1 | 0.19 | 1.25 | 18.583 | 12.67 | 1 | 1 | 2930 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3806723.7048 | 333876.9593 | 8361.215 | 27887.4759 | 305989.4834 | 13621.493 | 0.11164 | -105181.558 | 105181.558
C | Xist Rating 5019 | -18.34 | 1825.09 | 150.291 | 35.6 | 2090.76 | 9341.76 | 10538 | 0.19 | 1.25 | 18.595 | 12.679 | 1 | 1 | 2940 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3815825.1684 | 336064.3681 | 8418.3855 | 27982.6549 | 308081.7131 | 13632.7226 | 0.11202 | -105268.2701 | 105268.2701
C | Xist Rating 5020 | -17.98 | 1826.5 | 150.291 | 35.5 | 2099.51 | 9518.95 | 10537.9 | 0.19 | 1.25 | 18.614 | 12.689 | 1 | 1 | 2950 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3834755.015 | 338258.9054 | 8475.7509 | 28077.834 | 310181.0713 | 13645.1686 | 0.1124 | -105364.375 | 105364.375
C | Xist Rating 5021 | -17.95 | 1827.87 | 150.291 | 35.5 | 2099.24 | 9513.54 | 10537.8 | 0.19 | 1.25 | 18.611 | 12.698 | 1 | 1 | 2960 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3837137.8188 | 340460.5713 | 8533.311 | 28173.0131 | 312287.5581 | 13656.0248 | 0.11278 | -105448.2033 | 105448.2033
C | Xist Rating 5022 | -17.94 | 1829.26 | 150.291 | 35.5 | 2098.55 | 9499.38 | 10537.9 | 0.18 | 1.25 | 18.608 | 12.707 | 1 | 1 | 2970 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3838793.573 | 342669.3657 | 8591.0659 | 28268.1922 | 314401.1735 | 13642.1077 | 0.11316 | -105340.7396 | 105340.7396
C | Xist Rating 5023 | -17.94 | 1830.48 | 150.291 | 35.5 | 2097.97 | 9487.48 | 10537.9 | 0.18 | 1.25 | 18.644 | 12.715 | 1 | 1 | 2980 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3840292.1256 | 344885.2887 | 8649.0156 | 28363.3713 | 316521.9174 | 13652.7827 | 0.11354 | -105423.1687 | 105423.1687
C | Xist Rating 5024 | -17.92 | 1832.04 | 150.291 | 35.5 | 2097.23 | 9472.47 | 10537.9 | 0.18 | 1.25 | 18.64 | 12.725 | 1 | 1 | 2990 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3842209.2492 | 347108.3403 | 8707.16 | 28458.5504 | 318649.7898 | 13664.5754 | 0.11392 | -105514.2293 | 105514.2293
C | Xist Rating 5025 | -17.91 | 1833.47 | 150.291 | 35.5 | 2096.64 | 9460.33 | 10537.8 | 0.18 | 1.25 | 18.634 | 12.734 | 1 | 1 | 3000 | 152.4 | 2 | 3.4 | 19.05 | 1.3333 | 19 | E | Rod | 3844126.5408 | 349338.5204 | 8765.4993 | 28553.7295 | 320784.7908 | 13675.2806 | 0.1143 | -105596.8921 | 105596.8921
C | Xist Rating 5026 | -90.01 | 182.3 | 150.295 | 35.9 | 2382.36 | 7242.15 | 58745.8 | 2.46 | 10.95 | 20.058 | 481.861 | 1 | 1 | 1000 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 22 | E | Rod | 434304.228 | 46488.9192 | 973.9444 | 9797.8484 | 36691.0708 | 502623.655 | 0.038101 | -3881126.633 | 3881126.633
C | Xist Rating 5027 | -89.92 | 184.199 | 150.295 | 35.9 | 2379.94 | 7227.9 | 58284.2 | 2.44 | 10.85 | 20.112 | 472.824 | 1 | 1 | 1010 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 22 | E | Rod | 438382.5681 | 47324.3882 | 993.5206 | 9895.8269 | 37428.5614 | 493248.6659 | 0.038482 | -3808735.4526 | 3808735.4526
C | Xist Rating 5028 | -89.17 | 198.539 | 150.296 | 35.9 | 2373.23 | 7228.06 | 54967.7 | 2.45 | 10.07 | 20.163 | 409.748 | 1 | 1 | 1020 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 22 | E | Rod | 471178.711 | 48167.1954 | 1013.2917 | 9993.8053 | 38173.3901 | 427781.2449 | 0.038863 | -3303213.3808 | 3303213.3808
C | Xist Rating 5029 | -89.05 | 202.482 | 150.295 | 35.8 | 2354.46 | 7071.9 | 54178.5 | 2.37 | 9.89 | 19.716 | 396.025 | 1 | 1 | 1030 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 22 | E | Rod | 476735.7697 | 49017.3409 | 1033.2576 | 10091.7838 | 38925.5571 | 413428.6897 | 0.039244 | -3192386.7541 | 3192386.7541
C | Xist Rating 5030 | -88.98 | 204.456 | 150.294 | 35.8 | 2348.37 | 7024.72 | 53793.7 | 2.32 | 9.8 | 19.49 | 389.46 | 1 | 1 | 1040 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 480138.3367 | 49874.8245 | 1053.4182 | 10189.7623 | 39685.0622 | 406561.4946 | 0.039625 | -3139360.0933 | 3139360.0933
C | Xist Rating 5031 | -88.79 | 208.278 | 150.294 | 35.8 | 2344.07 | 7001.26 | 53042.7 | 2.29 | 9.63 | 19.422 | 376.562 | 1 | 1 | 1050 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 488218.2115 | 50739.6464 | 1073.7737 | 10287.7408 | 40451.9056 | 393152.3617 | 0.040006 | -3035818.3238 | 3035818.3238
C | Xist Rating 5032 | -88.63 | 210.232 | 150.294 | 35.8 | 2357.13 | 7126.75 | 52676.7 | 2.23 | 9.54 | 19.419 | 370.475 | 1 | 1 | 1060 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 495544.1542 | 51611.8065 | 1094.3239 | 10385.7193 | 41226.0872 | 386795.2712 | 0.040387 | -2986730.5558 | 2986730.5558
C | Xist Rating 5033 | -87.89 | 225.676 | 150.293 | 35.8 | 2338.58 | 7020.15 | 49857.3 | 2.22 | 8.9 | 19.264 | 324.167 | 1 | 1 | 1070 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 527761.3801 | 52491.3048 | 1115.0689 | 10483.6978 | 42007.607 | 338698.0798 | 0.040768 | -2615336.7929 | 2615336.7929
C | Xist Rating 5034 | -87.7 | 228.61 | 150.293 | 35.8 | 2345.93 | 7098 | 49380.7 | 2.16 | 8.79 | 19.18 | 316.919 | 1 | 1 | 1080 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 536303.0573 | 53378.1413 | 1136.0087 | 10581.6762 | 42796.465 | 331125.4744 | 0.041149 | -2556863.1416 | 2556863.1416
C | Xist Rating 5035 | -87.49 | 232.512 | 150.293 | 35.8 | 2348.3 | 7134.75 | 48761.6 | 2.11 | 8.65 | 19.048 | 307.599 | 1 | 1 | 1090 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 546007.9296 | 54272.316 | 1157.1433 | 10679.6547 | 43592.6613 | 321404.7756 | 0.04153 | -2481802.4823 | 2481802.4823
C | Xist Rating 5036 | -87.29 | 235.415 | 150.293 | 35.8 | 2355.86 | 7216.5 | 48308.6 | 2.07 | 8.55 | 19.046 | 300.873 | 1 | 1 | 1100 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 554604.7819 | 55173.8289 | 1178.4727 | 10777.6332 | 44396.1957 | 314400.0786 | 0.041911 | -2427714.069 | 2427714.069
C | Xist Rating 5037 | -87.2 | 237.556 | 150.292 | 35.8 | 2352.29 | 7190.69 | 48011 | 1.99 | 8.49 | 18.777 | 296.765 | 1 | 1 | 1110 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 558800.6032 | 56082.6801 | 1199.9969 | 10875.6117 | 45207.0684 | 310049.1536 | 0.042292 | -2394117.3789 | 2394117.3789
C | Xist Rating 5038 | -86.3 | 254.725 | 150.293 | 35.8 | 2348.76 | 7227.77 | 45448.3 | 2.03 | 7.92 | 19.014 | 259.669 | 1 | 1 | 1120 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 598287.891 | 56998.8694 | 1221.7158 | 10973.5902 | 46025.2793 | 271603.6259 | 0.042673 | -2097251.2049 | 2097251.2049
C | Xist Rating 5039 | -86.2 | 256.82 | 150.292 | 35.8 | 2348.66 | 7234.34 | 45189.3 | 1.97 | 7.86 | 18.842 | 256.355 | 1 | 1 | 1130 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 603182.8612 | 57922.397 | 1243.6296 | 11071.5687 | 46850.8284 | 268104.3952 | 0.043054 | -2070231.0731 | 2070231.0731
C | Xist Rating 5040 | -86.01 | 260.792 | 150.292 | 35.8 | 2345.05 | 7215.2 | 44681.4 | 1.91 | 7.75 | 18.683 | 249.679 | 1 | 1 | 1140 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 611570.2796 | 58853.2628 | 1265.7381 | 11169.5471 | 47683.7157 | 261114.7298 | 0.043435 | -2016258.7298 | 2016258.7298
C | Xist Rating 5041 | -85.81 | 264.702 | 150.292 | 35.8 | 2344.79 | 7227.81 | 44186.6 | 1.88 | 7.64 | 18.521 | 243.214 | 1 | 1 | 1150 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 620670.6026 | 59791.4668 | 1288.0414 | 11267.5256 | 48523.9412 | 254372.2411 | 0.043816 | -1964195.0192 | 1964195.0192
C | Xist Rating 5042 | -85.6 | 268.691 | 150.291 | 35.8 | 2345.1 | 7245.82 | 43703.9 | 1.82 | 7.53 | 18.392 | 237.075 | 1 | 1 | 1160 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 630107.2641 | 60737.009 | 1310.5395 | 11365.5041 | 49371.5049 | 247942.5175 | 0.044197 | -1914546.3981 | 1914546.3981
C | Xist Rating 5043 | -84.8 | 284.121 | 150.292 | 35.8 | 2342.48 | 7282.82 | 41832.8 | 1.84 | 7.13 | 18.527 | 213.26 | 1 | 1 | 1170 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 665547.7601 | 61689.8895 | 1333.2324 | 11463.4826 | 50226.4069 | 223258.0006 | 0.044578 | -1723939.1018 | 1723939.1018
C | Xist Rating 5044 | -84.67 | 285.262 | 150.292 | 35.8 | 2353.54 | 7394.65 | 41725.1 | 1.79 | 7.11 | 18.46 | 212.123 | 1 | 1 | 1180 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 671375.5275 | 62650.1081 | 1356.1201 | 11561.4611 | 51088.647 | 222037.1675 | 0.044959 | -1714512.1522 | 1714512.1522
C | Xist Rating 5045 | -84.32 | 293.066 | 150.291 | 35.8 | 2344.37 | 7335.15 | 40886.2 | 1.74 | 6.93 | 18.315 | 202.196 | 1 | 1 | 1190 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 687055.1384 | 63617.665 | 1379.2026 | 11659.4396 | 51958.2254 | 211680.1133 | 0.04534 | -1634537.7244 | 1634537.7244
C | Xist Rating 5046 | -84.15 | 295.054 | 150.291 | 35.8 | 2354.75 | 7445.56 | 40682.2 | 1.71 | 6.88 | 18.345 | 199.881 | 1 | 1 | 1200 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 694778.4065 | 64592.5601 | 1402.4799 | 11757.418 | 52835.142 | 209263.4789 | 0.045721 | -1615877.1145 | 1615877.1145
C | Xist Rating 5047 | -83.96 | 299.112 | 150.291 | 35.8 | 2351.7 | 7430.67 | 40281.5 | 1.66 | 6.8 | 18.218 | 195.384 | 1 | 1 | 1210 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 703421.6904 | 65574.7934 | 1425.9519 | 11855.3965 | 53719.3968 | 204546.2289 | 0.046102 | -1579451.7605 | 1579451.7605
C | Xist Rating 5048 | -83.12 | 316.634 | 150.291 | 35.8 | 2339.91 | 7384.03 | 38538.1 | 1.66 | 6.43 | 18.234 | 175.714 | 1 | 1 | 1220 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 740895.0629 | 66564.3649 | 1449.6188 | 11953.375 | 54610.9898 | 184133.9733 | 0.046483 | -1421833.7333 | 1421833.7333
C | Xist Rating 5049 | -82.87 | 320.541 | 150.291 | 35.8 | 2345.52 | 7455.55 | 38183.3 | 1.63 | 6.35 | 18.24 | 171.954 | 1 | 1 | 1230 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 751835.3263 | 67561.2746 | 1473.4804 | 12051.3535 | 55509.9211 | 180213.1666 | 0.046864 | -1391558.3033 | 1391558.3033
C | Xist Rating 5050 | -82.67 | 324.589 | 150.291 | 35.8 | 2345.37 | 7469.46 | 37835.8 | 1.59 | 6.28 | 18.155 | 168.386 | 1 | 1 | 1240 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 761281.3029 | 68565.5225 | 1497.5369 | 12149.332 | 56416.1905 | 176473.0661 | 0.047245 | -1362678.2388 | 1362678.2388
C | Xist Rating 5051 | -82.53 | 326.721 | 150.291 | 35.8 | 2349.11 | 7515.27 | 37664.6 | 1.55 | 6.24 | 18.096 | 166.714 | 1 | 1 | 1250 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 767503.5683 | 69577.1087 | 1521.7881 | 12247.3105 | 57329.7982 | 174703.8225 | 0.047626 | -1349016.6082 | 1349016.6082
C | Xist Rating 5052 | -82.24 | 332.606 | 150.291 | 35.8 | 2347.71 | 7524.33 | 37161.5 | 1.52 | 6.14 | 18.056 | 161.551 | 1 | 1 | 1260 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 780862.4323 | 70596.033 | 1546.2341 | 12345.2889 | 58250.7441 | 169320.5326 | 0.048007 | -1307448.271 | 1307448.271
C | Xist Rating 5053 | -81.41 | 349.203 | 150.291 | 35.8 | 2340.66 | 7519.5 | 35777.7 | 1.53 | 5.85 | 18.118 | 147.551 | 1 | 1 | 1270 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 817365.494 | 71622.2956 | 1570.8749 | 12443.2674 | 59179.0282 | 154809.5359 | 0.048388 | -1195398.2004 | 1195398.2004
C | Xist Rating 5054 | -81.23 | 353.319 | 150.29 | 35.8 | 2337.71 | 7504.45 | 35477.4 | 1.49 | 5.79 | 18.026 | 144.763 | 1 | 1 | 1280 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 825957.3595 | 72655.8964 | 1595.7105 | 12541.2459 | 60114.6505 | 151877.1817 | 0.048769 | -1172755.3385 | 1172755.3385
C | Xist Rating 5055 | -81.03 | 357.384 | 150.29 | 35.8 | 2336.95 | 7511.88 | 35183 | 1.46 | 5.73 | 17.991 | 142.039 | 1 | 1 | 1290 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 835188.5388 | 73696.8354 | 1620.7408 | 12639.2244 | 61057.611 | 149026.1265 | 0.04915 | -1150740.2467 | 1150740.2467
C | Xist Rating 5056 | -80.68 | 363.247 | 150.29 | 35.8 | 2342.13 | 7588.92 | 34751.5 | 1.43 | 5.64 | 18.027 | 138.004 | 1 | 1 | 1300 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 850771.6961 | 74745.1126 | 1645.966 | 12737.2029 | 62007.9097 | 144819.1081 | 0.049531 | -1118254.7656 | 1118254.7656
C | Xist Rating 5057 | -80.48 | 366.374 | 150.29 | 35.8 | 2347.59 | 7658.39 | 34540.1 | 1.4 | 5.59 | 17.984 | 136.138 | 1 | 1 | 1310 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 860095.9387 | 75800.728 | 1671.3859 | 12835.1814 | 62965.5467 | 142857.5338 | 0.049912 | -1103108.0084 | 1103108.0084
C | Xist Rating 5058 | -79.65 | 383.07 | 150.29 | 35.8 | 2341.6 | 7663.43 | 33363 | 1.4 | 5.35 | 18.033 | 125.387 | 1 | 1 | 1320 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 896996.712 | 76863.6817 | 1697.0007 | 12933.1599 | 63930.5218 | 131707.982 | 0.050293 | -1017014.125 | 1017014.125
C | Xist Rating 5059 | -79.36 | 389.15 | 150.29 | 35.8 | 2338.42 | 7652.88 | 32979.9 | 1.36 | 5.28 | 17.948 | 122.128 | 1 | 1 | 1330 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 909996.143 | 77933.9736 | 1722.8102 | 13031.1383 | 64902.8352 | 128284.9377 | 0.050674 | -990582.2843 | 990582.2843
C | Xist Rating 5060 | -79.04 | 395.128 | 150.29 | 35.8 | 2340.13 | 7694.79 | 32606.9 | 1.34 | 5.2 | 17.875 | 118.973 | 1 | 1 | 1340 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 924650.8866 | 79011.6036 | 1748.8145 | 13129.1168 | 65882.4868 | 124991.98 | 0.051055 | -965154.9382 | 965154.9382
C | Xist Rating 5061 | -78.84 | 398.272 | 150.29 | 35.8 | 2344.92 | 7758.8 | 32424.2 | 1.3 | 5.16 | 17.844 | 117.5 | 1 | 1 | 1350 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 933915.9782 | 80096.5719 | 1775.0136 | 13227.0953 | 66869.4766 | 123427.3028 | 0.051436 | -953072.9154 | 953072.9154
C | Xist Rating 5062 | -78.6 | 400.206 | 150.29 | 35.8 | 2361.22 | 7948.44 | 32303.7 | 1.29 | 5.14 | 17.911 | 116.5 | 1 | 1 | 1360 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 944974.4113 | 81188.8784 | 1801.4075 | 13325.0738 | 67863.8046 | 122393.5934 | 0.051817 | -945090.8853 | 945090.8853
C | Xist Rating 5063 | -77.59 | 423.953 | 150.29 | 35.8 | 2334.46 | 7748.92 | 30902.7 | 1.28 | 4.86 | 17.854 | 104.999 | 1 | 1 | 1370 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 989701.3204 | 82288.5231 | 1827.9962 | 13423.0523 | 68865.4709 | 110444.7003 | 0.052198 | -852824.7004 | 852824.7004
C | Xist Rating 5064 | -77.49 | 426.148 | 150.29 | 35.7 | 2333.66 | 7747.89 | 30794.3 | 1.26 | 4.84 | 17.819 | 104.22 | 1 | 1 | 1380 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 994484.5417 | 83395.5061 | 1854.7797 | 13521.0308 | 69874.4753 | 109621.1377 | 0.052579 | -846465.368 | 846465.368
C | Xist Rating 5065 | -77.22 | 431.249 | 150.29 | 35.7 | 2335.74 | 7790.67 | 30527.3 | 1.23 | 4.78 | 17.788 | 102.195 | 1 | 1 | 1390 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1007285.5393 | 84509.8272 | 1881.7579 | 13619.0092 | 70890.818 | 107492.5596 | 0.05296 | -830029.0522 | 830029.0522
C | Xist Rating 5066 | -76.95 | 436.346 | 150.29 | 35.7 | 2336.9 | 7823.44 | 30265.5 | 1.21 | 4.73 | 17.762 | 100.231 | 1 | 1 | 1400 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1019696.9674 | 85631.4866 | 1908.931 | 13716.9877 | 71914.4989 | 105438.4562 | 0.053341 | -814167.8102 | 814167.8102
C | Xist Rating 5067 | -76.63 | 442.385 | 150.29 | 35.7 | 2337.73 | 7856.82 | 29957.8 | 1.18 | 4.67 | 17.742 | 97.931 | 1 | 1 | 1410 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1034176.6861 | 86760.4842 | 1936.2988 | 13814.9662 | 72945.5179 | 103024.3738 | 0.053722 | -795526.9054 | 795526.9054
C | Xist Rating 5068 | -75.75 | 460.15 | 150.29 | 35.7 | 2332.95 | 7876.7 | 29052.1 | 1.19 | 4.49 | 17.807 | 91.139 | 1 | 1 | 1420 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1073506.9425 | 87896.8199 | 1963.8614 | 13912.9447 | 73983.8753 | 95996.4932 | 0.054103 | -741259.4743 | 741259.4743
C | Xist Rating 5069 | -75.6 | 463.535 | 150.29 | 35.7 | 2331.24 | 7869.13 | 28910.9 | 1.16 | 4.47 | 17.736 | 90.219 | 1 | 1 | 1430 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1080611.3334 | 89040.4939 | 1991.6188 | 14010.9232 | 75029.5708 | 95011.0514 | 0.054484 | -733650.1545 | 733650.1545
C | Xist Rating 5070 | -75.21 | 471.508 | 150.29 | 35.7 | 2329.36 | 7879.57 | 28542.1 | 1.14 | 4.39 | 17.72 | 87.617 | 1 | 1 | 1440 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1098311.8749 | 90191.5062 | 2019.571 | 14108.9017 | 76082.6045 | 92294.027 | 0.054865 | -712670.0123 | 712670.0123
C | Xist Rating 5071 | -74.95 | 476.643 | 150.29 | 35.7 | 2329.25 | 7898.21 | 28317.1 | 1.12 | 4.35 | 17.697 | 86.085 | 1 | 1 | 1450 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1110220.7077 | 91349.8566 | 2047.718 | 14206.8801 | 77142.9765 | 90687.3936 | 0.055246 | -700264.0148 | 700264.0148
C | Xist Rating 5072 | -74.74 | 479.669 | 150.29 | 35.7 | 2335.5 | 7982.79 | 28183.9 | 1.11 | 4.32 | 17.716 | 85.185 | 1 | 1 | 1460 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1120266.9495 | 92515.5452 | 2076.0598 | 14304.8586 | 78210.6866 | 89751.4282 | 0.055627 | -693036.7377 | 693036.7377
C | Xist Rating 5073 | -73.86 | 499.796 | 150.29 | 35.7 | 2320.52 | 7890.89 | 27310.5 | 1.1 | 4.16 | 17.704 | 79.231 | 1 | 1 | 1470 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1159786.6139 | 93688.5721 | 2104.5964 | 14402.8371 | 79285.735 | 83564.48 | 0.056008 | -645262.7639 | 645262.7639
C | Xist Rating 5074 | -73.55 | 505.88 | 150.29 | 35.7 | 2320.67 | 7916.4 | 27066.2 | 1.08 | 4.11 | 17.69 | 77.654 | 1 | 1 | 1480 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1173980.5396 | 94868.9372 | 2133.3277 | 14500.8156 | 80368.1216 | 81911.0044 | 0.056389 | -632495.0638 | 632495.0638
C | Xist Rating 5075 | -73.28 | 511.017 | 150.29 | 35.7 | 2321.54 | 7946.44 | 26866.4 | 1.06 | 4.07 | 17.677 | 76.392 | 1 | 1 | 1490 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1186346.4062 | 96056.6405 | 2162.2539 | 14598.7941 | 81457.8464 | 80584.433 | 0.05677 | -622251.6313 | 622251.6313
C | Xist Rating 5076 | -72.99 | 516.245 | 150.29 | 35.7 | 2323.85 | 7993.59 | 26670.3 | 1.04 | 4.03 | 17.658 | 75.176 | 1 | 1 | 1500 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1199675.9433 | 97251.682 | 2191.3748 | 14696.7726 | 82554.9094 | 79304.9185 | 0.057151 | -612371.559 | 612371.559
C | Xist Rating 5077 | -72.62 | 522.356 | 150.29 | 35.7 | 2328.62 | 8074.86 | 26439 | 1.02 | 3.99 | 17.663 | 73.733 | 1 | 1 | 1510 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1216368.6287 | 98454.0617 | 2220.6906 | 14794.751 | 83659.3106 | 77791.0385 | 0.057532 | -600681.7789 | 600681.7789
C | Xist Rating 5078 | -71.62 | 542.166 | 150.29 | 35.7 | 2326.67 | 8135.59 | 25681.2 | 1.03 | 3.85 | 17.739 | 68.954 | 1 | 1 | 1520 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1261441.3672 | 99663.7796 | 2250.2011 | 14892.7295 | 84771.0501 | 72853.4982 | 0.057913 | -562555.4014 | 562555.4014
C | Xist Rating 5079 | -71.37 | 548.62 | 150.29 | 35.7 | 2320.78 | 8088.46 | 25468.5 | 1 | 3.8 | 17.676 | 67.736 | 1 | 1 | 1530 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1273226.3236 | 100880.8358 | 2279.9064 | 14990.708 | 85890.1277 | 71555.9793 | 0.058294 | -552536.3047 | 552536.3047
C | Xist Rating 5080 | -71.14 | 551.921 | 150.29 | 35.7 | 2326.05 | 8165.28 | 25363.6 | 0.98 | 3.78 | 17.666 | 67.159 | 1 | 1 | 1540 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1283795.8421 | 102105.2301 | 2309.8065 | 15088.6865 | 87016.5436 | 70939.6089 | 0.058675 | -547776.8562 | 547776.8562
C | Xist Rating 5081 | -70.65 | 561.954 | 150.29 | 35.7 | 2324.61 | 8188.89 | 25021.2 | 0.97 | 3.72 | 17.66 | 65.144 | 1 | 1 | 1550 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1306323.8879 | 103336.9627 | 2339.9013 | 15186.665 | 88150.2977 | 68842.1166 | 0.059056 | -531580.5763 | 531580.5763
C | Xist Rating 5082 | -70.35 | 565.029 | 150.29 | 35.7 | 2336.05 | 8345.59 | 24920.5 | 0.96 | 3.7 | 17.694 | 64.579 | 1 | 1 | 1560 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1319935.9955 | 104576.0335 | 2370.191 | 15284.6435 | 89291.39 | 68252.9769 | 0.059437 | -527031.3959 | 527031.3959
C | Xist Rating 5083 | -69.4 | 588.365 | 150.29 | 35.7 | 2316.33 | 8195.36 | 24162.1 | 0.95 | 3.56 | 17.654 | 60.23 | 1 | 1 | 1570 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1362847.5004 | 105822.4425 | 2400.6755 | 15382.6219 | 90439.8205 | 63729.035 | 0.059818 | -492098.7155 | 492098.7155
C | Xist Rating 5084 | -69.09 | 593.622 | 150.29 | 35.7 | 2319.6 | 8257.38 | 24007.4 | 0.93 | 3.53 | 17.666 | 59.406 | 1 | 1 | 1580 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1376965.5912 | 107076.1897 | 2431.3547 | 15480.6004 | 91595.5893 | 62856.6142 | 0.0602 | -485362.1133 | 485362.1133
C | Xist Rating 5085 | -68.8 | 598.915 | 150.29 | 35.7 | 2322.02 | 8309.27 | 23854.9 | 0.91 | 3.5 | 17.654 | 58.604 | 1 | 1 | 1590 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1390692.6083 | 108337.2751 | 2462.2288 | 15578.5789 | 92758.6962 | 62005.143 | 0.060581 | -478787.2788 | 478787.2788
C | Xist Rating 5086 | -68.39 | 605.998 | 150.29 | 35.7 | 2326.2 | 8393.05 | 23645.2 | 0.9 | 3.46 | 17.665 | 57.476 | 1 | 1 | 1600 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1409672.5476 | 109605.6988 | 2493.2976 | 15676.5574 | 93929.1414 | 60828.9666 | 0.060962 | -469705.1564 | 469705.1564
C | Xist Rating 5087 | -68.2 | 609.494 | 150.29 | 35.7 | 2327.79 | 8426.65 | 23556.6 | 0.88 | 3.45 | 17.641 | 57.052 | 1 | 1 | 1610 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1418774.0383 | 110881.4606 | 2524.5612 | 15774.5359 | 95106.9247 | 60368.7487 | 0.061343 | -466151.4757 | 466151.4757
C | Xist Rating 5088 | -67.05 | 635.569 | 150.29 | 35.7 | 2313.6 | 8354.45 | 22805.1 | 0.88 | 3.31 | 17.651 | 53.039 | 1 | 1 | 1620 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1470452.4384 | 112164.5607 | 2556.0196 | 15872.5144 | 96292.0463 | 56208.8522 | 0.061724 | -434029.8575 | 434029.8575
C | Xist Rating 5089 | -66.76 | 638.719 | 150.29 | 35.7 | 2323.38 | 8496.56 | 22723.3 | 0.87 | 3.29 | 17.671 | 52.643 | 1 | 1 | 1630 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1483986.9502 | 113454.999 | 2587.6728 | 15970.4928 | 97484.5061 | 55792.9442 | 0.062105 | -430818.3257 | 430818.3257
C | Xist Rating 5090 | -66.48 | 644.159 | 150.29 | 35.7 | 2323.7 | 8522.67 | 22588.7 | 0.86 | 3.27 | 17.65 | 51.998 | 1 | 1 | 1640 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1496832.2683 | 114752.7755 | 2619.5208 | 16068.4713 | 98684.3041 | 55115.6859 | 0.062486 | -425588.717 | 425588.717
C | Xist Rating 5091 | -66.15 | 651.6 | 150.29 | 35.7 | 2320.73 | 8513.29 | 22403.1 | 0.84 | 3.23 | 17.625 | 51.097 | 1 | 1 | 1650 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1512187.668 | 116057.8902 | 2651.5635 | 16166.4498 | 99891.4404 | 54159.1415 | 0.062867 | -418202.5344 | 418202.5344
C | Xist Rating 5092 | -65.76 | 658.798 | 150.29 | 35.7 | 2322.61 | 8569.47 | 22221 | 0.83 | 3.2 | 17.623 | 50.205 | 1 | 1 | 1660 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1530130.8228 | 117370.3431 | 2683.8011 | 16264.4283 | 101105.9148 | 53226.1991 | 0.063248 | -410998.6006 | 410998.6006
C | Xist Rating 5093 | -64.74 | 682.177 | 150.29 | 35.7 | 2310.72 | 8510.48 | 21633.3 | 0.83 | 3.1 | 17.65 | 47.312 | 1 | 1 | 1670 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1576320.0374 | 118690.1343 | 2716.2334 | 16362.4068 | 102327.7275 | 50230.0572 | 0.063629 | -387863.1875 | 387863.1875
C | Xist Rating 5094 | -64.5 | 685.439 | 150.29 | 35.7 | 2316.3 | 8599.82 | 21560.7 | 0.82 | 3.08 | 17.653 | 46.992 | 1 | 1 | 1680 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1587682.3557 | 120017.2636 | 2748.8606 | 16460.3853 | 103556.8784 | 49891.1982 | 0.06401 | -385246.6077 | 385246.6077
C | Xist Rating 5095 | -64.1 | 694.93 | 150.29 | 35.7 | 2311.37 | 8571.55 | 21346.3 | 0.8 | 3.04 | 17.628 | 46.01 | 1 | 1 | 1690 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1606240.3541 | 121351.7312 | 2781.6825 | 16558.3637 | 104793.3674 | 48849.6206 | 0.064391 | -377203.822 | 377203.822
C | Xist Rating 5096 | -63.76 | 701.197 | 150.29 | 35.7 | 2313.27 | 8624.08 | 21206.1 | 0.79 | 3.02 | 17.628 | 45.375 | 1 | 1 | 1700 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1622057.9842 | 122693.537 | 2814.6992 | 16656.3422 | 106037.1947 | 48183.0626 | 0.064772 | -372056.8377 | 372056.8377
C | Xist Rating 5097 | -63.4 | 708.587 | 150.29 | 35.7 | 2312.43 | 8643.27 | 21045.2 | 0.78 | 2.99 | 17.62 | 44.655 | 1 | 1 | 1710 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1638557.8364 | 124042.681 | 2847.9107 | 16754.3207 | 107288.3603 | 47427.5959 | 0.065153 | -366223.324 | 366223.324
C | Xist Rating 5098 | -62.47 | 730.12 | 150.29 | 35.7 | 2302.53 | 8599.52 | 20567.4 | 0.77 | 2.9 | 17.648 | 42.473 | 1 | 1 | 1720 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1681123.2036 | 125399.1632 | 2881.317 | 16852.2992 | 108546.864 | 45155.8304 | 0.065534 | -348681.3528 | 348681.3528
C | Xist Rating 5099 | -62.03 | 739.481 | 150.29 | 35.7 | 2300.83 | 8614.9 | 20374.7 | 0.76 | 2.87 | 17.64 | 41.637 | 1 | 1 | 1730 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1701420.0692 | 126762.9836 | 2914.9181 | 16950.2777 | 109812.7059 | 44279.58 | 0.065915 | -341915.1796 | 341915.1796
C | Xist Rating 5100 | -61.77 | 743.838 | 150.29 | 35.7 | 2304.32 | 8681.75 | 20290.1 | 0.75 | 2.85 | 17.641 | 41.291 | 1 | 1 | 1740 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1714040.7802 | 128134.1423 | 2948.714 | 17048.2562 | 111085.8861 | 43912.5691 | 0.066296 | -339081.2188 | 339081.2188
C | Xist Rating 5101 | -61.42 | 752.383 | 150.29 | 35.6 | 2300.19 | 8658.39 | 20123.5 | 0.74 | 2.82 | 17.619 | 40.594 | 1 | 1 | 1750 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1730623.8528 | 129512.6391 | 2982.7046 | 17146.2347 | 112366.4045 | 43179.5512 | 0.066677 | -333421.0483 | 333421.0483
C | Xist Rating 5102 | -61.1 | 758.767 | 150.29 | 35.7 | 2299.81 | 8679.33 | 20001.2 | 0.73 | 2.8 | 17.619 | 40.087 | 1 | 1 | 1760 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1745019.9343 | 130898.4742 | 3016.8901 | 17244.2131 | 113654.2611 | 42644.9768 | 0.067058 | -329293.2073 | 329293.2073
C | Xist Rating 5103 | -60.03 | 784.284 | 150.29 | 35.7 | 2287.03 | 8608.67 | 19497.7 | 0.73 | 2.71 | 17.652 | 37.939 | 1 | 1 | 1770 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1793681.0365 | 132291.6475 | 3051.2703 | 17342.1916 | 114949.4559 | 40421.9588 | 0.067439 | -312127.6513 | 312127.6513
C | Xist Rating 5104 | -59.88 | 790.777 | 150.29 | 35.6 | 2279.19 | 8523.73 | 19383.8 | 0.72 | 2.69 | 17.845 | 37.483 | 1 | 1 | 1780 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1802331.0306 | 133692.159 | 3085.8453 | 17440.1701 | 116251.9889 | 39951.1828 | 0.06782 | -308492.4437 | 308492.4437
C | Xist Rating 5105 | -59.7 | 794.299 | 150.29 | 35.6 | 2279.86 | 8545.86 | 19327.1 | 0.71 | 2.68 | 17.835 | 37.28 | 1 | 1 | 1790 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1810890.5181 | 135100.0087 | 3120.6151 | 17538.1486 | 117561.8601 | 39731.2391 | 0.068201 | -306794.0964 | 306794.0964
C | Xist Rating 5106 | -59.22 | 805.748 | 150.29 | 35.6 | 2277.27 | 8556.1 | 19121.9 | 0.7 | 2.65 | 17.818 | 36.461 | 1 | 1 | 1800 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1834905.748 | 136515.1966 | 3155.5797 | 17636.1271 | 118879.0695 | 38871.0347 | 0.068582 | -300151.8266 | 300151.8266
C | Xist Rating 5107 | -58.9 | 812.113 | 150.29 | 35.6 | 2274.73 | 8545.29 | 19013.4 | 0.69 | 2.63 | 17.828 | 36.042 | 1 | 1 | 1810 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1847337.8045 | 137937.7228 | 3190.7391 | 17734.1056 | 120203.6172 | 38427.5983 | 0.068963 | -296727.728 | 296727.728
C | Xist Rating 5108 | -57.62 | 837.89 | 150.29 | 35.6 | 2274.97 | 8657.45 | 18562.7 | 0.69 | 2.55 | 17.654 | 34.263 | 1 | 1 | 1820 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1906174.6133 | 139367.5871 | 3226.0933 | 17832.084 | 121535.5031 | 36575.829 | 0.069344 | -282428.8566 | 282428.8566
C | Xist Rating 5109 | -57.8 | 833.787 | 150.29 | 35.6 | 2279.72 | 8709.34 | 18631.3 | 0.68 | 2.56 | 17.878 | 34.534 | 1 | 1 | 1830 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1900800.8996 | 140804.7897 | 3261.6423 | 17930.0625 | 122874.7272 | 36860.7356 | 0.069725 | -284628.8293 | 284628.8293
C | Xist Rating 5110 | -57.4 | 839.006 | 150.29 | 35.6 | 2286.91 | 8837.53 | 18545.2 | 0.68 | 2.55 | 17.898 | 34.213 | 1 | 1 | 1840 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1918731.2115 | 142249.3305 | 3297.386 | 18028.041 | 124221.2895 | 36533.9486 | 0.070106 | -282105.4671 | 282105.4671
C | Xist Rating 5111 | -57.02 | 847.668 | 150.29 | 35.6 | 2284.54 | 8837.88 | 18409.4 | 0.66 | 2.52 | 17.887 | 33.714 | 1 | 1 | 1850 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1936531.4527 | 143701.2095 | 3333.3246 | 18126.0195 | 125575.19 | 35990.9073 | 0.070487 | -277912.2457 | 277912.2457
C | Xist Rating 5112 | -56.61 | 857.371 | 150.29 | 35.6 | 2280.37 | 8815.48 | 18259.2 | 0.65 | 2.5 | 17.876 | 33.164 | 1 | 1 | 1860 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 1955123.1073 | 145160.4267 | 3369.4579 | 18223.998 | 126936.4287 | 35409.5157 | 0.070868 | -273422.8939 | 273422.8939
C | Xist Rating 5113 | -55.54 | 881.03 | 150.29 | 35.6 | 2274.76 | 8835.47 | 17879.7 | 0.65 | 2.43 | 17.922 | 31.732 | 1 | 1 | 1870 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2004131.8028 | 146626.9821 | 3405.7861 | 18321.9765 | 128305.0056 | 33930.1006 | 0.071249 | -261999.2427 | 261999.2427
C | Xist Rating 5114 | -55.1 | 890.719 | 150.29 | 35.6 | 2272.53 | 8841.52 | 17739.1 | 0.64 | 2.41 | 17.915 | 31.238 | 1 | 1 | 1880 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2024185.6491 | 148100.8757 | 3442.309 | 18419.9549 | 129680.9208 | 33406.8236 | 0.07163 | -257958.637 | 257958.637
C | Xist Rating 5115 | -54.73 | 897.132 | 150.29 | 35.6 | 2275.25 | 8909.74 | 17646.8 | 0.63 | 2.39 | 17.928 | 30.918 | 1 | 1 | 1890 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2041199.583 | 149582.1076 | 3479.0267 | 18517.9334 | 131064.1742 | 33065.1601 | 0.072011 | -255320.4015 | 255320.4015
C | Xist Rating 5116 | -54.47 | 904.004 | 150.29 | 35.6 | 2271.37 | 8877.17 | 17555.4 | 0.62 | 2.38 | 17.914 | 30.617 | 1 | 1 | 1900 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2053327.5655 | 151070.6777 | 3515.9392 | 18615.9119 | 132454.7658 | 32741.6269 | 0.072392 | -252822.1639 | 252822.1639
C | Xist Rating 5117 | -54.15 | 910.596 | 150.29 | 35.6 | 2271.29 | 8902.71 | 17465.3 | 0.61 | 2.36 | 17.921 | 30.314 | 1 | 1 | 1910 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2068227.5888 | 152566.5859 | 3553.0464 | 18713.8904 | 133852.6956 | 32416.9689 | 0.072773 | -250315.2409 | 250315.2409
C | Xist Rating 5118 | -52.91 | 939.333 | 150.29 | 35.6 | 2262.04 | 8886.92 | 17050.5 | 0.61 | 2.29 | 17.966 | 28.84 | 1 | 1 | 1920 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2124808.8193 | 154069.8324 | 3590.3485 | 18811.8689 | 135257.9636 | 30893.4848 | 0.073154 | -238551.3006 | 238551.3006
C | Xist Rating 5119 | -52.5 | 949.099 | 150.29 | 35.6 | 2259.05 | 8880.57 | 16923.9 | 0.6 | 2.27 | 17.954 | 28.425 | 1 | 1 | 1930 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2144062.096 | 155580.4172 | 3627.8454 | 18909.8474 | 136670.5698 | 30451.2548 | 0.073535 | -235136.5182 | 235136.5182
C | Xist Rating 5120 | -52.18 | 952.259 | 150.29 | 35.6 | 2267.45 | 9025.67 | 16882 | 0.6 | 2.26 | 17.974 | 28.293 | 1 | 1 | 1940 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2159199.6695 | 157098.3401 | 3665.537 | 19007.8258 | 138090.5142 | 30320.0453 | 0.073916 | -234123.3525 | 234123.3525
C | Xist Rating 5121 | -51.89 | 961.492 | 150.29 | 35.6 | 2260.11 | 8945.99 | 16772.1 | 0.58 | 2.24 | 17.956 | 27.951 | 1 | 1 | 1950 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2173077.6841 | 158623.6012 | 3703.4235 | 19105.8043 | 139517.7969 | 29937.3789 | 0.074297 | -231168.5042 | 231168.5042
C | Xist Rating 5122 | -51.43 | 972.179 | 150.29 | 35.6 | 2256.65 | 8936.22 | 16637 | 0.58 | 2.22 | 17.971 | 27.511 | 1 | 1 | 1960 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2193867.7404 | 160156.2006 | 3741.5047 | 19203.7828 | 140952.4178 | 29485.8722 | 0.074678 | -227682.0891 | 227682.0891
C | Xist Rating 5123 | -50.33 | 998.083 | 150.291 | 35.6 | 2248.79 | 8925.71 | 16303.2 | 0.58 | 2.16 | 18.032 | 26.401 | 1 | 1 | 1970 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2244479.0696 | 161696.1381 | 3779.7807 | 19301.7613 | 142394.3768 | 28340.9353 | 0.075059 | -218841.1901 | 218841.1901
C | Xist Rating 5124 | -49.95 | 1005.7 | 150.291 | 35.6 | 2249.03 | 8960.44 | 16214.4 | 0.57 | 2.15 | 18.064 | 26.128 | 1 | 1 | 1980 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2261849.471 | 163243.4139 | 3818.2515 | 19399.7398 | 143843.6741 | 28047.7282 | 0.07544 | -216577.1225 | 216577.1225
C | Xist Rating 5125 | -49.56 | 1015.66 | 150.291 | 35.6 | 2244.84 | 8933.73 | 16101.5 | 0.56 | 2.13 | 18.062 | 25.786 | 1 | 1 | 1990 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2279994.1944 | 164798.0279 | 3856.9171 | 19497.7183 | 145300.3097 | 27680.9639 | 0.075821 | -213745.0659 | 213745.0659
C | Xist Rating 5126 | -49.22 | 1023.4 | 150.291 | 35.6 | 2243.57 | 8944.39 | 16015 | 0.55 | 2.12 | 18.066 | 25.527 | 1 | 1 | 2000 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2296069.538 | 166359.9801 | 3895.7775 | 19595.6967 | 146764.2834 | 27400.5315 | 0.076202 | -211579.641 | 211579.641
C | Xist Rating 5127 | -48.94 | 1029.09 | 150.291 | 35.7 | 2243.98 | 8973.13 | 15953.9 | 0.54 | 2.11 | 18.068 | 25.351 | 1 | 1 | 2010 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2309257.3782 | 167929.2706 | 3934.8326 | 19693.6752 | 148235.5953 | 27206.03 | 0.076583 | -210077.7518 | 210077.7518
C | Xist Rating 5128 | -47.75 | 1058.27 | 150.291 | 35.7 | 2234.04 | 8939.65 | 15614.9 | 0.54 | 2.05 | 18.105 | 24.289 | 1 | 1 | 2020 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2364217.5108 | 169505.8992 | 3974.0826 | 19791.6537 | 149714.2455 | 26109.3272 | 0.076964 | -201609.3034 | 201609.3034
C | Xist Rating 5129 | -47.26 | 1068.9 | 150.291 | 35.7 | 2233.01 | 8966.79 | 15499.8 | 0.54 | 2.03 | 18.108 | 23.948 | 1 | 1 | 2030 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2386864.389 | 171089.866 | 4013.5273 | 19889.6322 | 151200.2338 | 25759.729 | 0.077345 | -198909.799 | 198909.799
C | Xist Rating 5130 | -46.99 | 1075.97 | 150.291 | 35.7 | 2230.33 | 8949.86 | 15431.8 | 0.53 | 2.02 | 18.102 | 23.764 | 1 | 1 | 2040 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2399768.1701 | 172681.1711 | 4053.1669 | 19987.6107 | 152693.5604 | 25556.1792 | 0.077726 | -197338.0416 | 197338.0416
C | Xist Rating 5131 | -46.6 | 1082.23 | 150.291 | 35.7 | 2234.23 | 9039.79 | 15364.2 | 0.52 | 2.01 | 18.119 | 23.567 | 1 | 1 | 2050 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2417950.7329 | 174279.8144 | 4093.0012 | 20085.5892 | 154194.2252 | 25340.0738 | 0.078107 | -195669.333 | 195669.333
C | Xist Rating 5132 | -46.25 | 1092.59 | 150.291 | 35.7 | 2228.1 | 8979.58 | 15264.3 | 0.51 | 1.99 | 18.103 | 23.292 | 1 | 1 | 2060 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2434399.779 | 175885.7959 | 4133.0303 | 20183.5676 | 155702.2282 | 25041.2257 | 0.078488 | -193361.7073 | 193361.7073
C | Xist Rating 5133 | -44.99 | 1123.92 | 150.291 | 35.7 | 2217.83 | 8945.73 | 14936.2 | 0.51 | 1.94 | 18.141 | 22.322 | 1 | 1 | 2070 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2492663.4936 | 177499.1156 | 4173.2542 | 20281.5461 | 157217.5695 | 24039.8189 | 0.078869 | -185629.1094 | 185629.1094
C | Xist Rating 5134 | -44.7 | 1130.8 | 150.291 | 35.7 | 2216.61 | 8951.81 | 14873.5 | 0.51 | 1.93 | 18.138 | 22.158 | 1 | 1 | 2080 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2506542.588 | 179119.7735 | 4213.6729 | 20379.5246 | 158740.2489 | 23873.5097 | 0.07925 | -184344.9134 | 184344.9134
C | Xist Rating 5135 | -44.33 | 1139.66 | 150.291 | 35.7 | 2214.6 | 8953.63 | 14790.9 | 0.5 | 1.91 | 18.139 | 21.935 | 1 | 1 | 2090 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 21 | E | Rod | 2523891.036 | 180747.7697 | 4254.2864 | 20477.5031 | 160270.2666 | 23629.1255 | 0.079631 | -182457.8436 | 182457.8436
C | Xist Rating 5136 | -43.96 | 1148.53 | 150.291 | 35.7 | 2212.78 | 8958.46 | 14709.2 | 0.49 | 1.9 | 18.131 | 21.717 | 1 | 1 | 2100 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2541444.2134 | 182383.104 | 4295.0947 | 20575.4816 | 161807.6224 | 23389.3546 | 0.080012 | -180606.3968 | 180606.3968
C | Xist Rating 5137 | -43.59 | 1156.36 | 150.291 | 35.7 | 2213.05 | 8993.21 | 14638.5 | 0.49 | 1.89 | 18.131 | 21.531 | 1 | 1 | 2110 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2559082.498 | 184025.7766 | 4336.0977 | 20673.4601 | 163352.3165 | 23200.1763 | 0.080393 | -179145.6113 | 179145.6113
C | Xist Rating 5138 | -42.43 | 1185.98 | 150.291 | 35.7 | 2203.02 | 8950.91 | 14358.9 | 0.49 | 1.84 | 18.166 | 20.753 | 1 | 1 | 2120 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2612737.6596 | 185675.7874 | 4377.2956 | 20771.4385 | 164904.3488 | 22397.8365 | 0.080774 | -172950.1566 | 172950.1566
C | Xist Rating 5139 | -41.97 | 1196.96 | 150.291 | 35.7 | 2200.49 | 8951.97 | 14263.7 | 0.48 | 1.83 | 18.161 | 20.505 | 1 | 1 | 2130 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2633898.5104 | 187333.1364 | 4418.6882 | 20869.417 | 166463.7193 | 22126.7055 | 0.081155 | -170856.5548 | 170856.5548
C | Xist Rating 5140 | -41.59 | 1207.96 | 150.291 | 35.7 | 2195.64 | 8914.45 | 14169.8 | 0.47 | 1.81 | 18.156 | 20.264 | 1 | 1 | 2140 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2652245.2944 | 188997.8236 | 4460.2756 | 20967.3955 | 168030.428 | 21862.6886 | 0.081536 | -168817.8859 | 168817.8859
C | Xist Rating 5141 | -41.33 | 1213.8 | 150.291 | 35.7 | 2195.23 | 8928.91 | 14123.4 | 0.47 | 1.8 | 18.155 | 20.153 | 1 | 1 | 2150 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2664570.174 | 190669.849 | 4502.0578 | 21065.374 | 169604.475 | 21751.195 | 0.081917 | -167956.9619 | 167956.9619
C | Xist Rating 5142 | -41 | 1221.58 | 150.291 | 35.7 | 2194.41 | 8945.16 | 14059 | 0.46 | 1.79 | 18.158 | 19.991 | 1 | 1 | 2160 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2680647.3678 | 192349.2126 | 4544.0348 | 21163.3525 | 171185.8601 | 21569.3388 | 0.082298 | -166552.7165 | 166552.7165
C | Xist Rating 5143 | -39.78 | 1253.57 | 150.291 | 35.7 | 2183.15 | 8887.14 | 13785.9 | 0.46 | 1.75 | 18.19 | 19.274 | 1 | 1 | 2170 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2736731.3455 | 194035.9145 | 4586.2066 | 21261.331 | 172774.5835 | 20829.9113 | 0.082679 | -160843.0534 | 160843.0534
C | Xist Rating 5144 | -39.32 | 1264.32 | 150.291 | 35.7 | 2182.01 | 8909.99 | 13699 | 0.46 | 1.74 | 18.192 | 19.057 | 1 | 1 | 2180 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2758758.8832 | 195729.9545 | 4628.5732 | 21359.3095 | 174370.6451 | 20608.3977 | 0.08306 | -159132.5841 | 159132.5841
C | Xist Rating 5145 | -39 | 1272.33 | 150.291 | 35.7 | 2180.52 | 8914.58 | 13638.8 | 0.45 | 1.73 | 18.189 | 18.916 | 1 | 1 | 2190 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2774341.0116 | 197431.3328 | 4671.1346 | 21457.2879 | 175974.0449 | 20447.7296 | 0.083441 | -157891.9477 | 157891.9477
C | Xist Rating 5146 | -38.73 | 1280.75 | 150.291 | 35.7 | 2176.52 | 8877.15 | 13579.3 | 0.44 | 1.72 | 18.185 | 18.781 | 1 | 1 | 2200 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2787577.99 | 199140.0493 | 4713.8907 | 21555.2664 | 177584.7829 | 20293.0907 | 0.083822 | -156697.8673 | 156697.8673
C | Xist Rating 5147 | -38.3 | 1291.75 | 150.291 | 35.6 | 2174.42 | 8883.8 | 13495.3 | 0.44 | 1.7 | 18.186 | 18.578 | 1 | 1 | 2210 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2808807.035 | 200856.104 | 4756.8417 | 21653.2449 | 179202.8591 | 20085.9057 | 0.084203 | -155098.0397 | 155098.0397
C | Xist Rating 5148 | -37.06 | 1323.61 | 150.291 | 35.7 | 2164.63 | 8846.21 | 13246.2 | 0.44 | 1.66 | 18.226 | 17.955 | 1 | 1 | 2220 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2865125.9143 | 202579.4969 | 4799.9874 | 21751.2234 | 180828.2736 | 19444.2594 | 0.084584 | -150143.4169 | 150143.4169
C | Xist Rating 5149 | -36.67 | 1332.44 | 150.291 | 35.7 | 2164.22 | 8872.38 | 13182.5 | 0.43 | 1.65 | 18.229 | 17.808 | 1 | 1 | 2230 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2883693.2968 | 204310.2281 | 4843.3279 | 21849.2019 | 182461.0262 | 19277.1052 | 0.084965 | -148852.6968 | 148852.6968
C | Xist Rating 5150 | -36.29 | 1342.76 | 150.291 | 35.7 | 2161.12 | 8857.33 | 13111.7 | 0.43 | 1.64 | 18.224 | 17.649 | 1 | 1 | 2240 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2901865.4912 | 206048.2974 | 4886.8633 | 21947.1804 | 184101.1171 | 19115.2817 | 0.085346 | -147603.1382 | 147603.1382
C | Xist Rating 5151 | -35.87 | 1354.08 | 150.291 | 35.7 | 2157.69 | 8840.62 | 13034 | 0.42 | 1.63 | 18.219 | 17.473 | 1 | 1 | 2250 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2921684.8752 | 207793.705 | 4930.5934 | 22045.1588 | 185748.5462 | 18917.4269 | 0.085727 | -146075.3557 | 146075.3557
C | Xist Rating 5152 | -35.63 | 1359.88 | 150.291 | 35.7 | 2157.38 | 8855.86 | 12995.5 | 0.42 | 1.62 | 18.219 | 17.391 | 1 | 1 | 2260 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2933777.9144 | 209546.4508 | 4974.5182 | 22143.1373 | 187403.3135 | 18835.7 | 0.086108 | -145444.2823 | 145444.2823
C | Xist Rating 5153 | -34.34 | 1394.19 | 150.291 | 35.7 | 2146.97 | 8812.53 | 12751.8 | 0.42 | 1.59 | 18.255 | 16.813 | 1 | 1 | 2270 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 2993284.1043 | 211306.5348 | 5018.6379 | 22241.1158 | 189065.419 | 18240.4163 | 0.086489 | -140847.6599 | 140847.6599
C | Xist Rating 5154 | -33.99 | 1404.46 | 150.291 | 35.7 | 2143.47 | 8789.76 | 12686.2 | 0.41 | 1.58 | 18.252 | 16.672 | 1 | 1 | 2280 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3010417.8762 | 213073.957 | 5062.9524 | 22339.0943 | 190734.8627 | 18078.6425 | 0.08687 | -139598.4849 | 139598.4849
C | Xist Rating 5155 | -33.5 | 1416.56 | 150.291 | 35.7 | 2141.54 | 8801.27 | 12606.9 | 0.41 | 1.56 | 18.252 | 16.496 | 1 | 1 | 2290 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3033619.9024 | 214848.7174 | 5107.4617 | 22437.0728 | 192411.6446 | 17899.2211 | 0.087251 | -138213.0408 | 138213.0408
C | Xist Rating 5156 | -33.16 | 1424.74 | 150.291 | 35.7 | 2140.73 | 8815.66 | 12557 | 0.4 | 1.56 | 18.252 | 16.393 | 1 | 1 | 2300 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3049983.6602 | 216630.816 | 5152.1657 | 22535.0513 | 194095.7648 | 17776.7929 | 0.087632 | -137267.6829 | 137267.6829
| Xist Rating 5157 | -32.86 | 1433.18 | 150.291 | 35.7 | 2138.27 | 8802.12 | 12507.6 | 0.4 | 1.55 | 18.247 | 16.293 | 1 | 1 | 2310 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3064525.7986 | 218420.2529 | 5197.0645 | 22633.0297 | 195787.2231 | 17676.0086 | 0.088013 | -136489.4527 | 136489.4527
| Xist Rating 5158 | -31.53 | 1468.37 | 150.291 | 35.7 | 2129.11 | 8780.08 | 12277.1 | 0.4 | 1.51 | 18.283 | 15.772 | 1 | 1 | 2320 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3126321.2507 | 220217.0279 | 5242.1582 | 22731.0082 | 197486.0197 | 17139.72 | 0.088394 | -132348.375 | 132348.375
| Xist Rating 5159 | -31.16 | 1478.67 | 150.291 | 35.7 | 2126.49 | 8771.06 | 12216.8 | 0.39 | 1.5 | 18.275 | 15.648 | 1 | 1 | 2330 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3144376.9683 | 222021.1412 | 5287.4466 | 22828.9867 | 199192.1545 | 16994.8035 | 0.088775 | -131229.3676 | 131229.3676
| Xist Rating 5160 | -30.77 | 1488.95 | 150.291 | 35.6 | 2124.47 | 8772.27 | 12157.2 | 0.39 | 1.49 | 18.27 | 15.526 | 1 | 1 | 2340 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3163229.6065 | 223832.5927 | 5332.9298 | 22926.9652 | 200905.6275 | 16871.0969 | 0.089156 | -130274.1382 | 130274.1382
| Xist Rating 5161 | -30.44 | 1498.28 | 150.291 | 35.6 | 2122.24 | 8765.75 | 12104.7 | 0.38 | 1.49 | 18.263 | 15.422 | 1 | 1 | 2350 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3179709.7472 | 225651.3824 | 5378.6078 | 23024.9437 | 202626.4387 | 16746.7615 | 0.089537 | -129314.0533 | 129314.0533
| Xist Rating 5162 | -30.02 | 1509.64 | 150.291 | 35.6 | 2119.44 | 8757.23 | 12039.9 | 0.38 | 1.48 | 18.257 | 15.29 | 1 | 1 | 2360 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3199591.4016 | 227477.5103 | 5424.4805 | 23122.9222 | 204354.5882 | 16612.5493 | 0.089918 | -128277.7025 | 128277.7025
| Xist Rating 5163 | -28.82 | 1541.93 | 150.291 | 35.6 | 2111.41 | 8739.05 | 11846.8 | 0.38 | 1.45 | 18.287 | 14.875 | 1 | 1 | 2370 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3255646.4213 | 229310.9765 | 5470.5481 | 23220.9006 | 206090.0758 | 16185.8933 | 0.090299 | -124983.178 | 124983.178
| Xist Rating 5164 | -28.46 | 1552.44 | 150.291 | 35.6 | 2108.64 | 8726.6 | 11791.1 | 0.38 | 1.44 | 18.278 | 14.768 | 1 | 1 | 2380 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3273537.0816 | 231151.7808 | 5516.8105 | 23318.8791 | 207832.9017 | 16077.5241 | 0.09068 | -124146.379 | 124146.379
| Xist Rating 5165 | -28.07 | 1563.36 | 150.291 | 35.6 | 2105.89 | 8718.12 | 11729.9 | 0.37 | 1.43 | 18.273 | 14.645 | 1 | 1 | 2390 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3292264.1904 | 232999.9234 | 5563.2676 | 23416.8576 | 209583.0658 | 15933.1225 | 0.091061 | -123031.3487 | 123031.3487
C | Xist Rating 5168 | -20.43 | 1794.7 | 150.291 | 35.6 | 2031.6 | 8266.19 | 10537.9 | 0.39 | 1.25 | 18.317 | 12.289 | 1 | 1 | 2420 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3646112.52 | 238588.3804 | 5703.8078 | 23710.7931 | 214877.5873 | 13537.017 | 0.092204 | -104529.257 | 104529.257
C | Xist Rating 5169 | -19.71 | 1796.06 | 150.291 | 35.6 | 2048.16 | 8547.56 | 10537.8 | 0.39 | 1.25 | 18.309 | 12.297 | 1 | 1 | 2430 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3678618.2496 | 240465.8758 | 5751.0441 | 23808.7715 | 216657.1042 | 13548.1873 | 0.092585 | -104615.5107 | 104615.5107
C | Xist Rating 5170 | -19.69 | 1797.43 | 150.291 | 35.6 | 2047.86 | 8542.36 | 10537.8 | 0.38 | 1.25 | 18.302 | 12.308 | 1 | 1 | 2440 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3680884.9998 | 242350.7094 | 5798.4752 | 23906.75 | 218443.9594 | 13542.4956 | 0.092966 | -104571.561 | 104571.561
C | Xist Rating 5171 | -19.67 | 1798.75 | 150.291 | 35.6 | 2047.6 | 8537.7 | 10537.8 | 0.38 | 1.25 | 18.295 | 12.318 | 1 | 1 | 2450 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3683120.5 | 244242.8813 | 5846.1011 | 24004.7285 | 220238.1528 | 13555.7059 | 0.093347 | -104673.5675 | 104673.5675
C | Xist Rating 5172 | -19.65 | 1800.22 | 150.291 | 35.6 | 2047.06 | 8528.46 | 10537.8 | 0.37 | 1.25 | 18.289 | 12.33 | 1 | 1 | 2460 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3685158.3532 | 246142.3913 | 5893.9217 | 24102.707 | 222039.6843 | 13550.8657 | 0.093728 | -104636.1927 | 104636.1927
C | Xist Rating 5173 | -19.62 | 1801.58 | 150.291 | 35.6 | 2046.92 | 8525.93 | 10537.8 | 0.36 | 1.25 | 18.324 | 12.34 | 1 | 1 | 2470 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3687690.1336 | 248049.2396 | 5941.9372 | 24200.6855 | 223848.5541 | 13545.4299 | 0.094109 | -104594.2194 | 104594.2194
C | Xist Rating 5174 | -19.61 | 1802.93 | 150.291 | 35.6 | 2046.52 | 8519.05 | 10537.8 | 0.36 | 1.25 | 18.32 | 12.351 | 1 | 1 | 2480 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3689732.3036 | 249963.4261 | 5990.1474 | 24298.664 | 225664.7621 | 13559.6503 | 0.09449 | -104704.025 | 104704.025
C | Xist Rating 5175 | -19.59 | 1804.32 | 150.291 | 35.6 | 2046.15 | 8512.65 | 10537.8 | 0.35 | 1.25 | 18.314 | 12.361 | 1 | 1 | 2490 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3691909.368 | 251884.9508 | 6038.5525 | 24396.6424 | 227488.3084 | 13552.3096 | 0.094871 | -104647.342 | 104647.342
C | Xist Rating 5176 | -19.56 | 1805.31 | 150.291 | 35.6 | 2046.52 | 8519.15 | 10537.7 | 0.35 | 1.25 | 18.309 | 12.37 | 1 | 1 | 2500 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3694603.0212 | 253813.8137 | 6087.1523 | 24494.6209 | 229319.1928 | 13564.3331 | 0.095252 | -104740.185 | 104740.185
C | Xist Rating 5177 | -19.58 | 1807.16 | 150.291 | 35.6 | 2044.24 | 8479.6 | 10537.8 | 0.34 | 1.25 | 18.307 | 12.383 | 1 | 1 | 2510 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3694268.7584 | 255750.0148 | 6135.9469 | 24592.5994 | 231157.4154 | 13560.0301 | 0.095633 | -104706.9582 | 104706.9582
C | Xist Rating 5178 | -19.56 | 1808.61 | 150.291 | 35.6 | 2043.68 | 8470.12 | 10537.8 | 0.34 | 1.25 | 18.344 | 12.394 | 1 | 1 | 2520 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3696220.0848 | 257693.5542 | 6184.9363 | 24690.5779 | 233002.9763 | 13575.6647 | 0.096014 | -104827.6841 | 104827.6841
C | Xist Rating 5179 | -19.55 | 1809.95 | 150.291 | 35.6 | 2043.28 | 8463.19 | 10537.8 | 0.33 | 1.25 | 18.338 | 12.404 | 1 | 1 | 2530 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3698234.636 | 259644.4318 | 6234.1205 | 24788.5564 | 234855.8754 | 13567.8175 | 0.096395 | -104767.0906 | 104767.0906
C | Xist Rating 5180 | -19.54 | 1811.1 | 150.291 | 35.6 | 2042.82 | 8455.25 | 10537.8 | 0.33 | 1.25 | 18.334 | 12.414 | 1 | 1 | 2540 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3699751.302 | 261602.6475 | 6283.4995 | 24886.5349 | 236716.1127 | 13580.7648 | 0.096776 | -104867.0661 | 104867.0661
C | Xist Rating 5181 | -19.5 | 1812.65 | 150.291 | 35.6 | 2042.77 | 8454.46 | 10537.7 | 0.32 | 1.25 | 18.327 | 12.425 | 1 | 1 | 2550 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3702827.0405 | 263568.2015 | 6333.0732 | 24984.5133 | 238583.6882 | 13573.688 | 0.097157 | -104812.4205 | 104812.4205
C | Xist Rating 5182 | -19.49 | 1814.1 | 150.291 | 35.6 | 2042.25 | 8445.58 | 10537.7 | 0.32 | 1.25 | 18.322 | 12.435 | 1 | 1 | 2560 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3704845.725 | 265541.0937 | 6382.8418 | 25082.4918 | 240458.6019 | 13586.5182 | 0.097538 | -104911.4918 | 104911.4918
C | Xist Rating 5183 | -19.47 | 1815.49 | 150.291 | 35.6 | 2042.06 | 8442.41 | 10537.7 | 0.31 | 1.25 | 18.332 | 12.446 | 1 | 1 | 2570 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3707339.5094 | 267521.3241 | 6432.8051 | 25180.4703 | 242340.8538 | 13579.82 | 0.097919 | -104859.7705 | 104859.7705
C | Xist Rating 5184 | -19.44 | 1816.85 | 150.291 | 35.6 | 2041.85 | 8438.85 | 10537.7 | 0.31 | 1.25 | 18.371 | 12.456 | 1 | 1 | 2580 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3709735.1725 | 269508.8928 | 6482.9633 | 25278.4488 | 244230.444 | 13594.1505 | 0.0983 | -104970.427 | 104970.427
C | Xist Rating 5185 | -19.42 | 1818.21 | 150.291 | 35.6 | 2041.68 | 8435.85 | 10537.7 | 0.3 | 1.25 | 18.369 | 12.466 | 1 | 1 | 2590 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3712202.9928 | 271503.7996 | 6533.3162 | 25376.4273 | 246127.3723 | 13585.6907 | 0.098681 | -104905.1021 | 104905.1021
C | Xist Rating 5186 | -19.39 | 1819.39 | 150.291 | 35.6 | 2041.7 | 8436.15 | 10537.7 | 0.3 | 1.25 | 18.367 | 12.475 | 1 | 1 | 2600 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3714648.563 | 273506.0447 | 6583.8639 | 25474.4058 | 248031.6389 | 13597.4374 | 0.099062 | -104995.8071 | 104995.8071
C | Xist Rating 5187 | -19.39 | 1821.08 | 150.292 | 35.6 | 2040.59 | 8417.38 | 10537.6 | 0.3 | 1.25 | 18.361 | 12.487 | 1 | 1 | 2610 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3716077.6372 | 275515.628 | 6634.6064 | 25572.3842 | 249943.2437 | 13612.1586 | 0.099443 | -105109.4809 | 105109.4809
C | Xist Rating 5188 | -19.37 | 1822.47 | 150.292 | 35.6 | 2040.24 | 8411.38 | 10537.6 | 0.29 | 1.25 | 18.359 | 12.497 | 1 | 1 | 2620 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3718276.1928 | 277532.5494 | 6685.5437 | 25670.3627 | 251862.1867 | 13603.3813 | 0.099824 | -105041.7047 | 105041.7047
C | Xist Rating 5189 | -19.32 | 1823.9 | 150.292 | 35.6 | 2040.36 | 8413.48 | 10537.6 | 0.29 | 1.25 | 18.403 | 12.507 | 1 | 1 | 2630 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3721412.604 | 279556.8092 | 6736.6758 | 25768.3412 | 253788.4679 | 13617.6571 | 0.10021 | -105151.9384 | 105151.9384
C | Xist Rating 5190 | -19.29 | 1825.15 | 150.292 | 35.6 | 2040.28 | 8412.07 | 10537.6 | 0.28 | 1.25 | 18.398 | 12.516 | 1 | 1 | 2640 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3723817.042 | 281588.4071 | 6788.0027 | 25866.3197 | 255722.0874 | 13607.4526 | 0.10059 | -105073.1417 | 105073.1417
C | Xist Rating 5191 | -19.25 | 1826.65 | 150.292 | 35.6 | 2040.36 | 8413.49 | 10537.6 | 0.28 | 1.25 | 18.398 | 12.527 | 1 | 1 | 2650 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3727023.594 | 283627.3432 | 6839.5243 | 25964.2982 | 257663.045 | 13621.1852 | 0.10097 | -105179.1812 | 105179.1812
C | Xist Rating 5192 | -19.22 | 1827.99 | 150.292 | 35.6 | 2040.34 | 8413.16 | 10537.6 | 0.28 | 1.25 | 18.395 | 12.537 | 1 | 1 | 2660 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3729721.1166 | 285673.6175 | 6891.2408 | 26062.2767 | 259611.3409 | 13633.7791 | 0.10135 | -105276.4283 | 105276.4283
C | Xist Rating 5193 | -19.2 | 1829.38 | 150.292 | 35.6 | 2040.1 | 8409.05 | 10537.7 | 0.27 | 1.25 | 18.391 | 12.547 | 1 | 1 | 2670 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3732118.138 | 287727.2301 | 6943.152 | 26160.2552 | 261566.975 | 13624.3281 | 0.10173 | -105203.4501 | 105203.4501
C | Xist Rating 5194 | -19.15 | 1830.79 | 150.292 | 35.6 | 2040.42 | 8414.44 | 10537.7 | 0.27 | 1.25 | 18.431 | 12.557 | 1 | 1 | 2680 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3735580.5318 | 289788.1809 | 6995.258 | 26258.2336 | 263529.9472 | 13638.2363 | 0.10211 | -105310.8455 | 105310.8455
C | Xist Rating 5195 | -19.1 | 1832.17 | 150.292 | 35.6 | 2040.72 | 8419.54 | 10537.6 | 0.26 | 1.25 | 18.428 | 12.567 | 1 | 1 | 2690 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3738945.9624 | 291856.4699 | 7047.5588 | 26356.2121 | 265500.2577 | 13628.5341 | 0.10249 | -105235.9276 | 105235.9276
C | Xist Rating 5196 | -19.03 | 1833.37 | 150.292 | 35.6 | 2042.13 | 8443.75 | 10537.5 | 0.26 | 1.25 | 18.424 | 12.576 | 1 | 1 | 2700 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3743979.8781 | 293932.0971 | 7100.0544 | 26454.1906 | 267477.9065 | 13639.9024 | 0.10287 | -105323.7105 | 105323.7105
C | Xist Rating 5197 | -19.04 | 1835.03 | 150.292 | 35.6 | 2040.9 | 8422.77 | 10537.5 | 0.26 | 1.25 | 18.42 | 12.587 | 1 | 1 | 2710 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3745112.727 | 296015.0625 | 7152.7448 | 26552.1691 | 269462.8934 | 13653.3467 | 0.10325 | -105427.5243 | 105427.5243
C | Xist Rating 5198 | -19 | 1836.37 | 150.292 | 35.6 | 2040.88 | 8422.45 | 10537.5 | 0.25 | 1.25 | 18.415 | 12.596 | 1 | 1 | 2720 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3747810.8056 | 298105.3661 | 7205.63 | 26650.1476 | 271455.2185 | 13642.2293 | 0.10363 | -105341.6786 | 105341.6786
C | Xist Rating 5199 | -19 | 1837.69 | 150.292 | 35.6 | 2039.94 | 8406.36 | 10537.5 | 0.25 | 1.25 | 18.448 | 12.606 | 1 | 1 | 2730 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3748777.3386 | 300203.008 | 7258.71 | 26748.1261 | 273454.8819 | 13655.6875 | 0.10402 | -105445.599 | 105445.599
C | Xist Rating 5200 | -19 | 1838.98 | 150.292 | 35.6 | 2039.28 | 8395.19 | 10537.5 | 0.25 | 1.25 | 18.444 | 12.615 | 1 | 1 | 2740 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3750195.1344 | 302307.988 | 7311.9847 | 26846.1045 | 275461.8835 | 13666.9785 | 0.1044 | -105532.7849 | 105532.7849
C | Xist Rating 5201 | -19.01 | 1840.52 | 150.292 | 35.6 | 2037.87 | 8371.35 | 10537.5 | 0.25 | 1.25 | 18.438 | 12.625 | 1 | 1 | 2750 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3750740.4924 | 304420.3063 | 7365.4543 | 26944.083 | 277476.2233 | 13679.2454 | 0.10478 | -105627.5071 | 105627.5071
C | Xist Rating 5202 | -19 | 1841.95 | 150.292 | 35.6 | 2037.09 | 8358.26 | 10537.5 | 0.24 | 1.25 | 18.436 | 12.635 | 1 | 1 | 2760 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3752217.9255 | 306539.9628 | 7419.1186 | 27042.0615 | 279497.9013 | 13668.8264 | 0.10516 | -105547.0545 | 105547.0545
C | Xist Rating 5203 | -18.98 | 1843.18 | 150.292 | 35.6 | 2037.04 | 8357.3 | 10537.5 | 0.24 | 1.25 | 18.435 | 12.644 | 1 | 1 | 2770 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3754631.3872 | 308666.9575 | 7472.9777 | 27140.04 | 281526.9175 | 13680.1265 | 0.10554 | -105634.3103 | 105634.3103
C | Xist Rating 5204 | -18.98 | 1844.73 | 150.292 | 35.6 | 2035.84 | 8337.23 | 10537.5 | 0.24 | 1.25 | 18.47 | 12.655 | 1 | 1 | 2780 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3755575.1232 | 310801.2904 | 7527.0316 | 27238.0185 | 283563.2719 | 13694.5799 | 0.10592 | -105745.916 | 105745.916
C | Xist Rating 5205 | -18.96 | 1846.14 | 150.292 | 35.6 | 2035.62 | 8333.48 | 10537.5 | 0.23 | 1.25 | 18.467 | 12.664 | 1 | 1 | 2790 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3758039.5068 | 312942.9615 | 7581.2803 | 27335.997 | 285606.9646 | 13682.7284 | 0.1063 | -105654.4015 | 105654.4015
C | Xist Rating 5206 | -18.92 | 1847.12 | 150.292 | 35.6 | 2036.15 | 8342.32 | 10537.6 | 0.23 | 1.25 | 18.474 | 12.672 | 1 | 1 | 2800 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3761013.388 | 315091.9709 | 7635.7238 | 27433.9754 | 287657.9954 | 13693.1423 | 0.10668 | -105734.8152 | 105734.8152
C | Xist Rating 5207 | -18.95 | 1848.86 | 150.292 | 35.6 | 2034.07 | 8307.55 | 10537.6 | 0.23 | 1.25 | 18.466 | 12.683 | 1 | 1 | 2810 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3760710.6602 | 317248.3184 | 7690.3621 | 27531.9539 | 289716.3645 | 13706.2386 | 0.10706 | -105835.9416 | 105835.9416
C | Xist Rating 5208 | -18.89 | 1850.34 | 150.292 | 35.6 | 2034.58 | 8316.06 | 10537.7 | 0.23 | 1.25 | 18.479 | 12.693 | 1 | 1 | 2820 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3764664.7572 | 319412.0042 | 7745.1952 | 27629.9324 | 291782.0718 | 13718.9054 | 0.10744 | -105933.7506 | 105933.7506
C | Xist Rating 5209 | -18.82 | 1851.71 | 150.292 | 35.6 | 2035.46 | 8330.75 | 10537.7 | 0.22 | 1.25 | 18.536 | 12.703 | 1 | 1 | 2830 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3769081.6366 | 321583.0282 | 7800.223 | 27727.9109 | 293855.1173 | 13709.3449 | 0.10783 | -105859.9274 | 105859.9274
C | Xist Rating 5210 | -18.78 | 1853.02 | 150.292 | 35.6 | 2035.67 | 8334.15 | 10537.7 | 0.22 | 1.25 | 18.539 | 12.712 | 1 | 1 | 2840 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3772137.2234 | 323761.3904 | 7855.4457 | 27825.8894 | 295935.501 | 13720.6033 | 0.10821 | -105946.8619 | 105946.8619
C | Xist Rating 5211 | -18.51 | 1854.47 | 150.292 | 35.6 | 2041.46 | 8431.95 | 10537.8 | 0.22 | 1.25 | 18.581 | 12.722 | 1 | 1 | 2850 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3785826.3262 | 325947.0908 | 7910.8631 | 27923.8679 | 298023.2229 | 13733.9969 | 0.10859 | -106050.2838 | 106050.2838
C | Xist Rating 5212 | -18.04 | 1855.87 | 150.292 | 35.6 | 2052.55 | 8624.28 | 10538 | 0.21 | 1.25 | 18.662 | 12.732 | 1 | 1 | 2860 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3809265.9685 | 328140.1294 | 7966.4753 | 28021.8463 | 300118.2831 | 13724.5744 | 0.10897 | -105977.5252 | 105977.5252
C | Xist Rating 5213 | -18.42 | 1857.06 | 150.292 | 35.6 | 2042.31 | 8446.46 | 10537.9 | 0.21 | 1.25 | 18.591 | 12.74 | 1 | 1 | 2870 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3792692.2086 | 330340.5063 | 8022.2824 | 28119.8248 | 302220.6815 | 13732.7209 | 0.10935 | -106040.4307 | 106040.4307
C | Xist Rating 5214 | -17.79 | 1858.57 | 150.292 | 35.6 | 2057.49 | 8712.15 | 10538 | 0.21 | 1.25 | 18.719 | 12.751 | 1 | 1 | 2880 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3823989.1893 | 332548.2213 | 8078.2842 | 28217.8033 | 304330.418 | 13749.3645 | 0.10973 | -106168.9478 | 106168.9478
C | Xist Rating 5215 | -17.29 | 1859.92 | 150.292 | 35.6 | 2069.36 | 8928.95 | 10538.1 | 0.2 | 1.25 | 18.771 | 12.761 | 1 | 1 | 2890 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3848844.0512 | 334763.2746 | 8134.4807 | 28315.7818 | 306447.4928 | 13738.6095 | 0.11011 | -106085.9012 | 106085.9012
C | Xist Rating 5216 | -17.04 | 1861.3 | 150.292 | 35.6 | 2074.99 | 9034.77 | 10538.1 | 0.2 | 1.25 | 18.794 | 12.771 | 1 | 1 | 2900 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3862178.887 | 336985.6661 | 8190.8721 | 28413.7603 | 308571.9058 | 13751.2753 | 0.11049 | -106183.7028 | 106183.7028
C | Xist Rating 5217 | -16.89 | 1862.84 | 150.292 | 35.6 | 2077.57 | 9083.89 | 10538.1 | 0.2 | 1.25 | 18.806 | 12.781 | 1 | 1 | 2910 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3870180.4988 | 339215.3958 | 8247.4583 | 28511.7388 | 310703.657 | 13763.6582 | 0.11087 | -106279.3204 | 106279.3204
C | Xist Rating 5218 | -16.7 | 1864.23 | 150.292 | 35.6 | 2081.51 | 9159.76 | 10538.1 | 0.2 | 1.25 | 18.823 | 12.79 | 1 | 1 | 2920 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3880413.3873 | 341452.4637 | 8304.2393 | 28609.7172 | 312842.7465 | 13775.1357 | 0.11125 | -106367.9462 | 106367.9462
C | Xist Rating 5219 | -16.53 | 1865.62 | 150.292 | 35.6 | 2084.91 | 9225.97 | 10538 | 0.19 | 1.25 | 18.877 | 12.8 | 1 | 1 | 2930 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3889649.7942 | 343696.8698 | 8361.215 | 28707.6957 | 314989.1741 | 13763.8342 | 0.11164 | -106280.6793 | 106280.6793
C | Xist Rating 5220 | -16.35 | 1866.98 | 150.292 | 35.6 | 2088.65 | 9299.69 | 10538 | 0.19 | 1.25 | 18.89 | 12.809 | 1 | 1 | 2940 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3899467.777 | 345948.6142 | 8418.3855 | 28805.6742 | 317142.94 | 13775.1139 | 0.11202 | -106367.7781 | 106367.7781
C | Xist Rating 5221 | -15.92 | 1868.39 | 150.292 | 35.5 | 2099.01 | 9508.85 | 10537.9 | 0.19 | 1.25 | 18.919 | 12.819 | 1 | 1 | 2950 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3921769.2939 | 348207.6967 | 8475.7509 | 28903.6527 | 319304.044 | 13787.8363 | 0.1124 | -106466.017 | 106466.017
C | Xist Rating 5222 | -15.91 | 1869.76 | 150.292 | 35.5 | 2098.32 | 9494.62 | 10537.9 | 0.19 | 1.25 | 18.914 | 12.828 | 1 | 1 | 2960 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3923354.8032 | 350474.1175 | 8533.311 | 29001.6312 | 321472.4863 | 13798.668 | 0.11278 | -106549.6566 | 106549.6566
C | Xist Rating 5223 | -15.88 | 1871.15 | 150.292 | 35.5 | 2098.08 | 9489.74 | 10537.8 | 0.18 | 1.25 | 18.911 | 12.837 | 1 | 1 | 2970 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3925822.392 | 352747.8765 | 8591.0659 | 29099.6097 | 323648.2668 | 13784.3734 | 0.11316 | -106439.2774 | 106439.2774
C | Xist Rating 5224 | -15.87 | 1872.37 | 150.292 | 35.5 | 2097.5 | 9477.99 | 10537.8 | 0.18 | 1.25 | 18.947 | 12.845 | 1 | 1 | 2980 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3927296.075 | 355028.9737 | 8649.0156 | 29197.5881 | 325831.3855 | 13795.0728 | 0.11354 | -106521.8952 | 106521.8952
C | Xist Rating 5225 | -15.86 | 1873.93 | 150.292 | 35.5 | 2096.8 | 9463.73 | 10537.8 | 0.18 | 1.25 | 18.942 | 12.855 | 1 | 1 | 2990 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3929256.424 | 357317.4091 | 8707.16 | 29295.5666 | 328021.8425 | 13806.8659 | 0.11392 | -106612.9583 | 106612.9583
C | Xist Rating 5226 | -15.84 | 1875.36 | 150.292 | 35.5 | 2096.17 | 9450.81 | 10537.8 | 0.18 | 1.25 | 18.938 | 12.864 | 1 | 1 | 3000 | 152.4 | 2 | 3.5 | 19.05 | 1.3333 | 20 | E | Rod | 3931073.3712 | 359613.1827 | 8765.4993 | 29393.5451 | 330219.6376 | 13817.6438 | 0.1143 | -106696.1831 | 106696.1831
C | Xist Rating 5227 | -89.75 | 187.075 | 150.296 | 35.9 | 2380.43 | 7224.39 | 58745.2 | 2.46 | 10.95 | 20.32 | 489.92 | 1 | 1 | 1000 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 445318.9422 | 47817.1741 | 973.9444 | 10077.7869 | 37739.3872 | 511021.8041 | 0.038101 | -3945974.9146 | 3945974.9146
C | Xist Rating 5228 | -89.65 | 189.022 | 150.296 | 35.9 | 2377.94 | 7209.53 | 58284.2 | 2.44 | 10.85 | 20.376 | 480.739 | 1 | 1 | 1010 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 449482.9747 | 48676.5136 | 993.5206 | 10178.5648 | 38497.9488 | 501497.5439 | 0.038482 | -3872431.1018 | 3872431.1018
C | Xist Rating 5229 | -88.88 | 203.733 | 150.296 | 35.9 | 2371.29 | 7210.12 | 54967.6 | 2.45 | 10.07 | 20.429 | 416.608 | 1 | 1 | 1020 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 483110.0256 | 49543.401 | 1013.2917 | 10279.3426 | 39264.0584 | 434935.1405 | 0.038863 | -3358453.8665 | 3358453.8665
C | Xist Rating 5230 | -88.76 | 207.772 | 150.295 | 35.9 | 2351.95 | 7049.34 | 54179.2 | 2.37 | 9.89 | 19.981 | 402.654 | 1 | 1 | 1030 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 488669.3554 | 50417.8363 | 1033.2576 | 10380.1205 | 40037.7158 | 420341.8924 | 0.039244 | -3245768.6729 | 3245768.6729
C | Xist Rating 5231 | -88.68 | 209.794 | 150.295 | 35.8 | 2346.24 | 7005.77 | 53793.8 | 2.33 | 9.8 | 19.871 | 395.967 | 1 | 1 | 1040 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 492227.0746 | 51299.8195 | 1053.4182 | 10480.8984 | 40818.9211 | 413369.4734 | 0.039625 | -3191929.5015 | 3191929.5015
C | Xist Rating 5232 | -88.5 | 213.712 | 150.295 | 35.8 | 2341.16 | 6975.37 | 53042.8 | 2.29 | 9.63 | 19.799 | 382.849 | 1 | 1 | 1050 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 500333.9859 | 52189.3506 | 1073.7737 | 10581.6762 | 41607.6743 | 399722.0346 | 0.040006 | -3086547.5969 | 3086547.5969
C | Xist Rating 5233 | -88.34 | 215.714 | 150.295 | 35.8 | 2353.73 | 7095.71 | 52676.7 | 2.24 | 9.54 | 19.795 | 376.657 | 1 | 1 | 1060 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 507732.5132 | 53086.4295 | 1094.3239 | 10682.4541 | 42403.9754 | 393264.5135 | 0.040387 | -3036684.33 | 3036684.33
C | Xist Rating 5234 | -87.58 | 231.553 | 150.294 | 35.8 | 2334.93 | 6987.32 | 49857.4 | 2.22 | 8.9 | 19.63 | 329.571 | 1 | 1 | 1070 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 540660.0463 | 53991.0563 | 1115.0689 | 10783.232 | 43207.8244 | 344349.0956 | 0.040768 | -2658972.4393 | 2658972.4393
C | Xist Rating 5235 | -87.39 | 234.559 | 150.294 | 35.8 | 2342.51 | 7066.78 | 49380.6 | 2.17 | 8.79 | 19.544 | 322.198 | 1 | 1 | 1080 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 549456.8031 | 54903.231 | 1136.0087 | 10884.0098 | 44019.2212 | 336655.2313 | 0.041149 | -2599562.4586 | 2599562.4586
C | Xist Rating 5236 | -87.16 | 238.557 | 150.294 | 35.8 | 2345.25 | 7106.68 | 48761.5 | 2.11 | 8.65 | 19.407 | 312.72 | 1 | 1 | 1090 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 559475.8042 | 55822.9536 | 1157.1433 | 10984.7877 | 44838.1659 | 326759.9361 | 0.04153 | -2523153.6123 | 2523153.6123
C | Xist Rating 5237 | -86.96 | 241.531 | 150.294 | 35.8 | 2353.36 | 7193.03 | 48308.1 | 2.07 | 8.55 | 19.404 | 305.874 | 1 | 1 | 1100 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 568409.3942 | 56750.224 | 1178.4727 | 11085.5656 | 45664.6585 | 319630.1488 | 0.041911 | -2468099.2842 | 2468099.2842
C | Xist Rating 5238 | -86.87 | 243.72 | 150.293 | 35.8 | 2349.62 | 7165.82 | 48011 | 1.99 | 8.49 | 19.126 | 301.696 | 1 | 1 | 1110 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 572649.3864 | 57685.0424 | 1199.9969 | 11186.3435 | 46498.6989 | 315204.5449 | 0.042292 | -2433925.944 | 2433925.944
C | Xist Rating 5239 | -85.95 | 261.332 | 150.294 | 35.8 | 2345.92 | 7200.9 | 45448.3 | 2.03 | 7.92 | 19.37 | 263.984 | 1 | 1 | 1120 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 613063.9654 | 58627.4086 | 1221.7158 | 11287.1213 | 47340.2872 | 276121.0277 | 0.042673 | -2132133.3843 | 2132133.3843
C | Xist Rating 5240 | -85.84 | 263.475 | 150.293 | 35.8 | 2345.84 | 7207.69 | 45189.3 | 1.97 | 7.86 | 19.193 | 260.61 | 1 | 1 | 1130 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 618070.194 | 59577.3227 | 1243.6296 | 11387.8992 | 48189.4235 | 272558.2302 | 0.043054 | -2104622.4064 | 2104622.4064
C | Xist Rating 5241 | -85.65 | 267.543 | 150.293 | 35.8 | 2342.34 | 7189.62 | 44681.5 | 1.92 | 7.75 | 19.027 | 253.819 | 1 | 1 | 1140 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 626676.6706 | 60534.7846 | 1265.7381 | 11488.6771 | 49046.1075 | 265457.4109 | 0.043435 | -2049791.762 | 2049791.762
C | Xist Rating 5242 | -85.44 | 271.549 | 150.292 | 35.8 | 2342.61 | 7207.14 | 44186.3 | 1.88 | 7.64 | 18.859 | 247.244 | 1 | 1 | 1150 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 636133.4029 | 61499.7944 | 1288.0414 | 11589.4549 | 49910.3395 | 258590.1456 | 0.043816 | -1996764.5598 | 1996764.5598
C | Xist Rating 5243 | -85.24 | 275.633 | 150.292 | 35.8 | 2340.66 | 7203.61 | 43703.7 | 1.82 | 7.53 | 18.722 | 240.994 | 1 | 1 | 1160 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 645163.1378 | 62472.3522 | 1310.5395 | 11690.2328 | 50782.1194 | 252043.622 | 0.044197 | -1946214.0396 | 1946214.0396
C | Xist Rating 5244 | -84.41 | 291.458 | 150.292 | 35.8 | 2339 | 7249.26 | 41832.7 | 1.84 | 7.13 | 18.861 | 216.785 | 1 | 1 | 1170 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 681720.262 | 63452.4577 | 1333.2324 | 11791.0107 | 51661.4471 | 226950.9381 | 0.044578 | -1752454.9857 | 1752454.9857
C | Xist Rating 5245 | -84.28 | 292.623 | 150.292 | 35.8 | 2350.52 | 7364.9 | 41725.1 | 1.79 | 7.11 | 18.793 | 215.629 | 1 | 1 | 1180 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 687816.214 | 64440.1112 | 1356.1201 | 11891.7885 | 52548.3227 | 225709.671 | 0.044959 | -1742870.2503 | 1742870.2503
C | Xist Rating 5246 | -83.92 | 300.619 | 150.292 | 35.8 | 2341.38 | 7305.98 | 40886.1 | 1.74 | 6.93 | 18.642 | 205.532 | 1 | 1 | 1190 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 703863.3142 | 65435.3126 | 1379.2026 | 11992.5664 | 53442.7462 | 215174.8941 | 0.04534 | -1661523.4959 | 1661523.4959
C | Xist Rating 5247 | -83.74 | 302.654 | 150.292 | 35.8 | 2352.21 | 7420.25 | 40682.3 | 1.71 | 6.88 | 18.674 | 203.178 | 1 | 1 | 1200 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 711905.7653 | 66438.0618 | 1402.4799 | 12093.3443 | 54344.7175 | 212717.6697 | 0.045721 | -1642549.46 | 1642549.46
C | Xist Rating 5248 | -83.55 | 306.808 | 150.292 | 35.8 | 2349.14 | 7405.19 | 40281.4 | 1.66 | 6.8 | 18.542 | 198.602 | 1 | 1 | 1210 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 720734.9451 | 67448.3589 | 1425.9519 | 12194.1221 | 55254.2367 | 207917.2881 | 0.046102 | -1605482.1859 | 1605482.1859
C | Xist Rating 5249 | -82.68 | 324.773 | 150.292 | 35.8 | 2337.45 | 7359.55 | 38538.1 | 1.66 | 6.43 | 18.557 | 178.605 | 1 | 1 | 1220 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 759140.6488 | 68466.2039 | 1449.6188 | 12294.9 | 56171.3038 | 187165.5938 | 0.046483 | -1445243.1032 | 1445243.1032
C | Xist Rating 5250 | -82.43 | 328.776 | 150.292 | 35.8 | 2342.96 | 7429.71 | 38183.3 | 1.63 | 6.35 | 18.563 | 174.78 | 1 | 1 | 1230 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 770309.017 | 69491.5967 | 1473.4804 | 12395.6779 | 57095.9188 | 183176.9908 | 0.046864 | -1414444.1681 | 1414444.1681
C | Xist Rating 5251 | -82.22 | 332.92 | 150.292 | 35.8 | 2342.34 | 7438.79 | 37835.8 | 1.59 | 6.28 | 18.474 | 171.15 | 1 | 1 | 1240 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 779811.8328 | 70524.5374 | 1497.5369 | 12496.4558 | 58028.0817 | 179371.6678 | 0.047245 | -1385060.4725 | 1385060.4725
C | Xist Rating 5252 | -82.08 | 335.099 | 150.291 | 35.8 | 2346.63 | 7489.9 | 37664.5 | 1.55 | 6.24 | 18.414 | 169.448 | 1 | 1 | 1250 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 786353.3664 | 71565.0261 | 1521.7881 | 12597.2336 | 58967.7924 | 177570.6947 | 0.047626 | -1371153.8359 | 1371153.8359
C | Xist Rating 5253 | -81.78 | 341.128 | 150.291 | 35.8 | 2345.28 | 7499.4 | 37161.6 | 1.52 | 6.14 | 18.374 | 164.197 | 1 | 1 | 1260 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 800040.6758 | 72613.0625 | 1546.2341 | 12698.0115 | 59915.051 | 172095.6992 | 0.048007 | -1328877.3714 | 1328877.3714
C | Xist Rating 5254 | -80.93 | 358.144 | 150.291 | 35.8 | 2337.93 | 7491.38 | 35777.8 | 1.53 | 5.85 | 18.435 | 149.964 | 1 | 1 | 1270 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 837315.6019 | 73668.6469 | 1570.8749 | 12798.7894 | 60869.8575 | 157343.0429 | 0.048388 | -1214961.2699 | 1214961.2699
C | Xist Rating 5255 | -80.74 | 362.356 | 150.291 | 35.8 | 2335.34 | 7480.01 | 35477.4 | 1.49 | 5.79 | 18.338 | 147.128 | 1 | 1 | 1280 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 846224.461 | 74731.7791 | 1595.7105 | 12899.5672 | 61832.2119 | 154359.9032 | 0.048769 | -1191926.2559 | 1191926.2559
C | Xist Rating 5256 | -80.54 | 366.516 | 150.291 | 35.8 | 2334.4 | 7485.52 | 35182.7 | 1.46 | 5.73 | 18.302 | 144.357 | 1 | 1 | 1290 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 855594.9504 | 75802.4593 | 1620.7408 | 13000.3451 | 62802.1142 | 151459.6214 | 0.04915 | -1169531.0486 | 1169531.0486
C | Xist Rating 5257 | -80.19 | 372.523 | 150.291 | 35.8 | 2339.29 | 7559.25 | 34751.5 | 1.43 | 5.64 | 18.339 | 140.254 | 1 | 1 | 1300 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 871439.3287 | 76880.6873 | 1645.966 | 13101.123 | 63779.5643 | 147181.7282 | 0.049531 | -1136498.2918 | 1136498.2918
C | Xist Rating 5258 | -79.98 | 375.722 | 150.291 | 35.8 | 2344.66 | 7627.34 | 34540.1 | 1.4 | 5.59 | 18.295 | 138.354 | 1 | 1 | 1310 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 880940.3445 | 77966.4631 | 1671.3859 | 13201.9008 | 64764.5623 | 145184.4131 | 0.049912 | -1121075.5536 | 1121075.5536
C | Xist Rating 5259 | -79.13 | 392.837 | 150.291 | 35.8 | 2338.72 | 7632.65 | 33363 | 1.4 | 5.35 | 18.344 | 127.426 | 1 | 1 | 1320 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 918735.7486 | 79059.7869 | 1697.0007 | 13302.6787 | 65757.1082 | 133851.2423 | 0.050293 | -1033563.8126 | 1033563.8126
C | Xist Rating 5260 | -78.84 | 399.06 | 150.291 | 35.8 | 2335.55 | 7622.2 | 32979.9 | 1.36 | 5.28 | 18.255 | 124.111 | 1 | 1 | 1330 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 932024.583 | 80160.6585 | 1722.8102 | 13403.4566 | 66757.2019 | 130369.1713 | 0.050674 | -1006676.1834 | 1006676.1834
C | Xist Rating 5261 | -78.5 | 405.183 | 150.291 | 35.8 | 2337.51 | 7666.46 | 32606.8 | 1.34 | 5.2 | 18.18 | 120.901 | 1 | 1 | 1340 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 947119.3143 | 81269.078 | 1748.8145 | 13504.2344 | 67764.8436 | 127018.7536 | 0.051055 | -980805.1462 | 980805.1462
C | Xist Rating 5262 | -78.3 | 408.399 | 150.291 | 35.8 | 2342.17 | 7728.72 | 32424.1 | 1.31 | 5.16 | 18.148 | 119.402 | 1 | 1 | 1350 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 956539.8858 | 82385.0454 | 1775.0136 | 13605.0123 | 68780.0331 | 125437.4236 | 0.051436 | -968594.5353 | 968594.5353
C | Xist Rating 5263 | -78.05 | 410.38 | 150.291 | 35.8 | 2358.44 | 7917.06 | 32303.7 | 1.29 | 5.14 | 18.217 | 118.386 | 1 | 1 | 1360 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 967856.6072 | 83508.5607 | 1801.4075 | 13705.7902 | 69802.7705 | 124376.2654 | 0.051817 | -960400.5527 | 960400.5527
C | Xist Rating 5264 | -77.02 | 434.713 | 150.291 | 35.8 | 2331.77 | 7719.34 | 30902.6 | 1.29 | 4.86 | 18.156 | 106.693 | 1 | 1 | 1370 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1013650.732 | 84639.6238 | 1827.9962 | 13806.568 | 70833.0558 | 112238.8048 | 0.052198 | -866678.2993 | 866678.2993
C | Xist Rating 5265 | -76.92 | 436.956 | 150.291 | 35.7 | 2331.43 | 7723.44 | 30794.3 | 1.26 | 4.84 | 18.12 | 105.9 | 1 | 1 | 1380 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1018732.3271 | 85778.2348 | 1854.7797 | 13907.3459 | 71870.8889 | 111389.2753 | 0.052579 | -860118.458 | 860118.458
C | Xist Rating 5266 | -76.65 | 442.177 | 150.291 | 35.7 | 2331.8 | 7747 | 30527.1 | 1.23 | 4.78 | 18.086 | 103.839 | 1 | 1 | 1390 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1031068.3286 | 86924.3937 | 1881.7579 | 14008.1238 | 72916.2699 | 109222.6888 | 0.05296 | -843388.6508 | 843388.6508
C | Xist Rating 5267 | -76.36 | 447.393 | 150.291 | 35.7 | 2334.29 | 7794.3 | 30265.5 | 1.21 | 4.73 | 18.061 | 101.842 | 1 | 1 | 1400 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1044345.006 | 88078.1005 | 1908.931 | 14108.9017 | 73969.1988 | 107134.1811 | 0.053341 | -827261.7484 | 827261.7484
C | Xist Rating 5268 | -76.03 | 453.576 | 150.29 | 35.7 | 2335.09 | 7827.14 | 29957.8 | 1.19 | 4.67 | 18.041 | 99.502 | 1 | 1 | 1410 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1059140.7818 | 89239.3551 | 1936.2988 | 14209.6795 | 75029.6756 | 104689.5564 | 0.053722 | -808385.0043 | 808385.0043
C | Xist Rating 5269 | -75.13 | 471.784 | 150.291 | 35.7 | 2330.25 | 7845.93 | 29052.1 | 1.19 | 4.49 | 18.107 | 92.599 | 1 | 1 | 1420 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1099374.666 | 90408.1577 | 1963.8614 | 14310.4574 | 76097.7003 | 97535.4243 | 0.054103 | -753142.6923 | 753142.6923
C | Xist Rating 5270 | -74.98 | 475.241 | 150.29 | 35.7 | 2328.78 | 7841.2 | 28910.9 | 1.16 | 4.47 | 18.033 | 91.661 | 1 | 1 | 1430 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1106731.736 | 91584.5081 | 1991.6188 | 14411.2353 | 77173.2728 | 96530.6496 | 0.054484 | -745384.0889 | 745384.0889
C | Xist Rating 5271 | -74.57 | 483.406 | 150.29 | 35.7 | 2327.12 | 7854.03 | 28542.1 | 1.14 | 4.39 | 18.017 | 89.015 | 1 | 1 | 1440 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1124943.7707 | 92768.4063 | 2019.571 | 14512.0131 | 78256.3932 | 93767.7023 | 0.054865 | -724049.3421 | 724049.3421
C | Xist Rating 5272 | -74.31 | 488.661 | 150.29 | 35.7 | 2327.37 | 7876.7 | 28316.9 | 1.12 | 4.35 | 17.994 | 87.457 | 1 | 1 | 1450 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1137294.9516 | 93959.8525 | 2047.718 | 14612.791 | 79347.0615 | 92133.8336 | 0.055246 | -711433.0412 | 711433.0412
C | Xist Rating 5273 | -74.09 | 491.758 | 150.29 | 35.7 | 2333.66 | 7961.33 | 28183.9 | 1.11 | 4.32 | 18.015 | 86.542 | 1 | 1 | 1460 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1147595.9743 | 95158.8465 | 2076.0598 | 14713.5689 | 80445.2777 | 91182.3907 | 0.055627 | -704086.2513 | 704086.2513
C | Xist Rating 5274 | -73.18 | 512.376 | 150.29 | 35.7 | 2318.64 | 7869.17 | 27310.5 | 1.1 | 4.16 | 17.999 | 80.488 | 1 | 1 | 1470 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1188015.4886 | 96365.3884 | 2104.5964 | 14814.3467 | 81551.0417 | 84891.2545 | 0.056008 | -655507.7652 | 655507.7652
C | Xist Rating 5275 | -72.87 | 518.603 | 150.29 | 35.7 | 2318.74 | 7894.03 | 27066.2 | 1.08 | 4.11 | 17.986 | 78.885 | 1 | 1 | 1480 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1202505.5202 | 97579.4782 | 2133.3277 | 14915.1246 | 82664.3536 | 83210.6037 | 0.056389 | -642530.2249 | 642530.2249
C | Xist Rating 5276 | -72.59 | 523.86 | 150.29 | 35.7 | 2319.6 | 7923.71 | 26866.4 | 1.06 | 4.07 | 17.972 | 77.601 | 1 | 1 | 1490 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1215145.656 | 98801.1159 | 2162.2539 | 15015.9025 | 83785.2134 | 81860.8625 | 0.05677 | -632107.881 | 632107.881
C | Xist Rating 5277 | -72.31 | 529.208 | 150.29 | 35.7 | 2320.86 | 7958.41 | 26670 | 1.04 | 4.03 | 17.949 | 76.363 | 1 | 1 | 1500 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1228217.6789 | 100030.3014 | 2191.3748 | 15116.6803 | 84913.6211 | 80557.9647 | 0.057151 | -622047.2497 | 622047.2497
C | Xist Rating 5278 | -71.93 | 535.462 | 150.29 | 35.7 | 2326.03 | 8043.85 | 26439 | 1.02 | 3.99 | 17.955 | 74.896 | 1 | 1 | 1510 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1245500.6759 | 101267.0349 | 2220.6906 | 15217.4582 | 86049.5767 | 79018.9715 | 0.057532 | -610163.5523 | 610163.5523
C | Xist Rating 5279 | -70.89 | 555.763 | 150.29 | 35.7 | 2324.22 | 8105.75 | 25681.2 | 1.03 | 3.85 | 18.033 | 70.038 | 1 | 1 | 1520 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1291715.4799 | 102511.3162 | 2250.2011 | 15318.2361 | 87193.0801 | 73999.8626 | 0.057913 | -571407.3239 | 571407.3239
C | Xist Rating 5280 | -70.63 | 562.361 | 150.29 | 35.7 | 2318.43 | 8059.94 | 25468.5 | 1 | 3.8 | 17.967 | 68.799 | 1 | 1 | 1530 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1303794.6132 | 103763.1453 | 2279.9064 | 15419.014 | 88344.1314 | 72679.8604 | 0.058294 | -561214.6166 | 561214.6166
C | Xist Rating 5281 | -70.41 | 565.733 | 150.29 | 35.7 | 2323.47 | 8133.49 | 25363.6 | 0.98 | 3.78 | 17.957 | 68.211 | 1 | 1 | 1540 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1314463.6535 | 105022.5224 | 2309.8065 | 15519.7918 | 89502.7306 | 72051.7952 | 0.058675 | -556364.864 | 556364.864
C | Xist Rating 5282 | -69.9 | 576.006 | 150.29 | 35.7 | 2322.27 | 8159.95 | 25021.2 | 0.97 | 3.72 | 17.951 | 66.163 | 1 | 1 | 1550 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1337641.4536 | 106289.4473 | 2339.9013 | 15620.5697 | 90668.8776 | 69919.9581 | 0.059056 | -539903.3827 | 539903.3827
C | Xist Rating 5283 | -69.6 | 579.153 | 150.29 | 35.7 | 2333.55 | 8313.75 | 24920.5 | 0.96 | 3.7 | 17.986 | 65.588 | 1 | 1 | 1560 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1351482.4832 | 107563.9201 | 2370.191 | 15721.3476 | 91842.5726 | 69320.4236 | 0.059437 | -535273.9363 | 535273.9363
C | Xist Rating 5284 | -68.62 | 603.051 | 150.29 | 35.7 | 2314.02 | 8166.54 | 24162.1 | 0.95 | 3.56 | 17.943 | 61.166 | 1 | 1 | 1570 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1395472.075 | 108845.9408 | 2400.6755 | 15822.1254 | 93023.8154 | 64720.3909 | 0.059818 | -499753.7029 | 499753.7029
C | Xist Rating 5285 | -68.31 | 608.428 | 150.29 | 35.7 | 2317.23 | 8227.39 | 24007.4 | 0.93 | 3.53 | 17.936 | 60.328 | 1 | 1 | 1580 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1409867.6144 | 110135.5094 | 2431.3547 | 15922.9033 | 94212.6061 | 63831.8934 | 0.0602 | -492892.9606 | 492892.9606
C | Xist Rating 5286 | -68.01 | 613.841 | 150.29 | 35.7 | 2319.62 | 8278.56 | 23854.9 | 0.91 | 3.5 | 17.925 | 59.512 | 1 | 1 | 1590 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1423877.8604 | 111432.6258 | 2462.2288 | 16023.6812 | 95408.9447 | 62965.6758 | 0.060581 | -486204.2581 | 486204.2581
C | Xist Rating 5287 | -67.58 | 621.092 | 150.29 | 35.7 | 2323.84 | 8362.38 | 23645.1 | 0.9 | 3.46 | 17.955 | 58.365 | 1 | 1 | 1600 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1443318.4333 | 112737.2902 | 2493.2976 | 16124.459 | 96612.8311 | 61770.9105 | 0.060962 | -476978.5973 | 476978.5973
C | Xist Rating 5288 | -67.39 | 624.659 | 150.29 | 35.7 | 2325.45 | 8396.18 | 23556.6 | 0.88 | 3.45 | 17.93 | 57.933 | 1 | 1 | 1610 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1452613.2715 | 114049.5023 | 2524.5612 | 16225.2369 | 97824.2654 | 61302.0195 | 0.061343 | -473357.9454 | 473357.9454
C | Xist Rating 5289 | -66.21 | 651.368 | 150.29 | 35.7 | 2311.28 | 8324.35 | 22805 | 0.88 | 3.31 | 17.939 | 53.854 | 1 | 1 | 1620 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1505493.831 | 115369.2624 | 2556.0196 | 16326.0148 | 99043.2477 | 57073.6322 | 0.061724 | -440707.4594 | 440707.4594
C | Xist Rating 5290 | -65.91 | 654.591 | 150.29 | 35.7 | 2321.09 | 8466 | 22723.3 | 0.87 | 3.29 | 17.96 | 53.451 | 1 | 1 | 1630 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1519364.6242 | 116696.5704 | 2587.6728 | 16426.7926 | 100269.7777 | 56650.4214 | 0.062105 | -437439.5377 | 437439.5377
C | Xist Rating 5291 | -65.64 | 660.15 | 150.29 | 35.7 | 2320.69 | 8482.29 | 22588.6 | 0.86 | 3.27 | 17.936 | 52.794 | 1 | 1 | 1640 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1532003.5035 | 118031.4262 | 2619.5208 | 16527.5705 | 101503.8557 | 55960.4118 | 0.062486 | -432111.4661 | 432111.4661
C | Xist Rating 5292 | -65.31 | 667.759 | 150.29 | 35.7 | 2317.16 | 8465.48 | 22403 | 0.84 | 3.23 | 17.909 | 51.878 | 1 | 1 | 1650 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1547304.4444 | 119373.8299 | 2651.5635 | 16628.3484 | 102745.4815 | 54987.8528 | 0.062867 | -424601.6236 | 424601.6236
C | Xist Rating 5293 | -64.89 | 675.124 | 150.29 | 35.7 | 2320.74 | 8544.08 | 22221 | 0.83 | 3.2 | 17.912 | 50.971 | 1 | 1 | 1660 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1566787.2718 | 120723.7815 | 2683.8011 | 16729.1262 | 103994.6552 | 54039.5373 | 0.063248 | -417278.983 | 417278.983
C | Xist Rating 5294 | -63.91 | 699.065 | 150.29 | 35.7 | 2305.22 | 8436.44 | 21632.6 | 0.83 | 3.1 | 17.927 | 48.03 | 1 | 1 | 1670 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1611498.6193 | 122081.281 | 2716.2334 | 16829.9041 | 105251.3768 | 50992.9095 | 0.063629 | -393753.7306 | 393753.7306
C | Xist Rating 5295 | -63.64 | 702.4 | 150.29 | 35.7 | 2312.5 | 8547.81 | 21560.3 | 0.82 | 3.08 | 17.934 | 47.704 | 1 | 1 | 1680 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1624300 | 123446.3283 | 2748.8606 | 16930.682 | 106515.6463 | 50647.9609 | 0.06401 | -391090.129 | 391090.129
C | Xist Rating 5296 | -63.23 | 712.106 | 150.29 | 35.7 | 2307.39 | 8517.11 | 21345.9 | 0.8 | 3.04 | 17.907 | 46.705 | 1 | 1 | 1690 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1643106.2633 | 124818.9235 | 2781.6825 | 17031.4599 | 107787.4637 | 49588.2853 | 0.064391 | -382907.5944 | 382907.5944
C | Xist Rating 5297 | -62.88 | 718.516 | 150.29 | 35.7 | 2309.67 | 8574.35 | 21205.7 | 0.79 | 3.02 | 17.908 | 46.059 | 1 | 1 | 1700 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1659534.8497 | 126199.0666 | 2814.6992 | 17132.2377 | 109066.8289 | 48910.2514 | 0.064772 | -377671.9967 | 377671.9967
C | Xist Rating 5298 | -62.52 | 726.074 | 150.29 | 35.7 | 2308.8 | 8592.99 | 21044.6 | 0.78 | 2.99 | 17.898 | 45.326 | 1 | 1 | 1710 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1676359.6512 | 127586.7576 | 2847.9107 | 17233.0156 | 110353.742 | 48141.0492 | 0.065153 | -371732.421 | 371732.421
C | Xist Rating 5299 | -61.55 | 748.122 | 150.29 | 35.7 | 2299.28 | 8554.41 | 20567 | 0.78 | 2.9 | 17.928 | 43.109 | 1 | 1 | 1720 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 22 | E | Rod | 1720141.9522 | 128981.9964 | 2881.317 | 17333.7935 | 111648.203 | 45846.76 | 0.065534 | -354016.5281 | 354016.5281
C | Xist Rating 5300 | -61.06 | 757.698 | 150.291 | 35.7 | 2299.07 | 8590.32 | 20374.7 | 0.76 | 2.87 | 17.913 | 42.26 | 1 | 1 | 1730 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 1742000.7409 | 130384.7831 | 2914.9181 | 17434.5713 | 112950.2118 | 44942.6539 | 0.065915 | -347035.2604 | 347035.2604
C | Xist Rating 5301 | -60.84 | 762.151 | 150.29 | 35.6 | 2301.14 | 8636.9 | 20289.6 | 0.75 | 2.85 | 17.906 | 41.906 | 1 | 1 | 1740 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 1753816.1521 | 131795.1178 | 2948.714 | 17535.3492 | 114259.7686 | 44566.7471 | 0.066296 | -344132.608 | 344132.608
C | Xist Rating 5302 | -60.4 | 770.888 | 150.291 | 35.7 | 2299.54 | 8649.08 | 20124 | 0.74 | 2.82 | 17.897 | 41.199 | 1 | 1 | 1750 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 1772687.7915 | 133213.0002 | 2982.7046 | 17636.1271 | 115576.8732 | 43823.98 | 0.066677 | -338397.1572 | 338397.1572
C | Xist Rating 5303 | -60.13 | 777.415 | 150.291 | 35.7 | 2296.36 | 8630.38 | 20001.2 | 0.73 | 2.8 | 17.892 | 40.683 | 1 | 1 | 1760 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 1785224.7094 | 134638.4306 | 3016.8901 | 17736.9049 | 116901.5257 | 43279.6442 | 0.067058 | -334193.9401 | 334193.9401
C | Xist Rating 5304 | -58.98 | 803.543 | 150.291 | 35.7 | 2287.19 | 8611.01 | 19497.8 | 0.73 | 2.71 | 17.929 | 38.499 | 1 | 1 | 1770 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 1837855.5142 | 136071.4088 | 3051.2703 | 17837.6828 | 118233.726 | 41019.5612 | 0.067439 | -316742.1785 | 316742.1785
C | Xist Rating 5305 | -58.85 | 810.179 | 150.291 | 35.6 | 2277.69 | 8502.88 | 19383.9 | 0.72 | 2.69 | 18.125 | 38.035 | 1 | 1 | 1780 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 1845336.6065 | 137511.9349 | 3085.8453 | 17938.4607 | 119573.4743 | 40540.5192 | 0.06782 | -313043.1428 | 313043.1428
C | Xist Rating 5306 | -58.49 | 813.773 | 150.291 | 35.6 | 2287.44 | 8653.51 | 19326.5 | 0.71 | 2.68 | 17.905 | 37.836 | 1 | 1 | 1790 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 1861456.9111 | 138960.0089 | 3120.6151 | 18039.2385 | 120920.7704 | 40312.6319 | 0.068201 | -311283.4579 | 311283.4579
C | Xist Rating 5307 | -58.18 | 825.485 | 150.291 | 35.6 | 2275.78 | 8535.13 | 19121.9 | 0.7 | 2.65 | 18.097 | 36.996 | 1 | 1 | 1800 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 1878622.2533 | 140415.6308 | 3155.5797 | 18140.0164 | 122275.6144 | 39442.389 | 0.068582 | -304563.6731 | 304563.6731
C | Xist Rating 5308 | -57.65 | 831.994 | 150.291 | 35.6 | 2284.77 | 8689.03 | 19012.4 | 0.69 | 2.63 | 17.896 | 36.575 | 1 | 1 | 1810 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 1900914.9314 | 141878.8005 | 3190.7391 | 18240.7943 | 123638.0063 | 38984.9247 | 0.068963 | -301031.2547 | 301031.2547
C | Xist Rating 5309 | -56.76 | 858.381 | 150.291 | 35.6 | 2261.75 | 8468.85 | 18563.5 | 0.69 | 2.55 | 18.14 | 34.755 | 1 | 1 | 1820 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 1941443.2267 | 143349.5182 | 3226.0933 | 18341.5722 | 125007.946 | 37114.1276 | 0.069344 | -286585.4553 | 286585.4553
C | Xist Rating 5310 | -56.73 | 854.183 | 150.291 | 35.6 | 2277.78 | 8681.08 | 18631.2 | 0.68 | 2.56 | 18.156 | 35.037 | 1 | 1 | 1830 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 1945640.9537 | 144827.7837 | 3261.6423 | 18442.35 | 126385.4336 | 37398.6071 | 0.069725 | -288782.1304 | 288782.1304
C | Xist Rating 5311 | -56.33 | 859.521 | 150.291 | 35.6 | 2284.91 | 8807.75 | 18545.2 | 0.68 | 2.55 | 18.177 | 34.71 | 1 | 1 | 1840 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 1963928.1281 | 146313.597 | 3297.386 | 18543.1279 | 127770.4692 | 37065.7299 | 0.070106 | -286211.7415 | 286211.7415
C | Xist Rating 5312 | -55.93 | 868.375 | 150.291 | 35.6 | 2282.48 | 8807.16 | 18409.3 | 0.67 | 2.52 | 18.166 | 34.202 | 1 | 1 | 1850 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 1982048.57 | 147806.9583 | 3333.3246 | 18643.9058 | 129163.0525 | 36528.0287 | 0.070487 | -282059.7549 | 282059.7549
C | Xist Rating 5313 | -55.51 | 878.294 | 150.291 | 35.6 | 2278.34 | 8785.19 | 18259.2 | 0.65 | 2.5 | 18.155 | 33.643 | 1 | 1 | 1860 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2001052.352 | 149307.8674 | 3369.4579 | 18744.6836 | 130563.1838 | 35922.0763 | 0.070868 | -277380.751 | 277380.751
C | Xist Rating 5314 | -54.42 | 902.515 | 150.291 | 35.6 | 2272.34 | 8799.01 | 17879.8 | 0.65 | 2.43 | 18.204 | 32.188 | 1 | 1 | 1870 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2050820.9351 | 150816.3244 | 3405.7861 | 18845.4615 | 131970.8629 | 34419.0204 | 0.071249 | -265774.5523 | 265774.5523
C | Xist Rating 5315 | -53.97 | 912.419 | 150.291 | 35.6 | 2270.44 | 8810 | 17739 | 0.64 | 2.41 | 18.191 | 31.685 | 1 | 1 | 1880 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2071592.5944 | 152332.3293 | 3442.309 | 18946.2394 | 133386.09 | 33885.918 | 0.07163 | -261658.0762 | 261658.0762
C | Xist Rating 5316 | -53.59 | 918.976 | 150.291 | 35.6 | 2273.16 | 8877.73 | 17646.8 | 0.63 | 2.39 | 18.206 | 31.359 | 1 | 1 | 1890 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2088979.4842 | 153855.8821 | 3479.0267 | 19047.0172 | 134808.8649 | 33537.9755 | 0.072011 | -258971.3568 | 258971.3568
C | Xist Rating 5317 | -53.32 | 925.991 | 150.291 | 35.6 | 2269.87 | 8854.36 | 17555.2 | 0.62 | 2.38 | 18.191 | 31.053 | 1 | 1 | 1900 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2101879.1912 | 155386.9827 | 3515.9392 | 19147.7951 | 136239.1876 | 33209.0387 | 0.072392 | -256431.3944 | 256431.3944
C | Xist Rating 5318 | -53 | 932.728 | 150.291 | 35.6 | 2269.29 | 8872.09 | 17465.2 | 0.61 | 2.36 | 18.201 | 30.745 | 1 | 1 | 1910 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2116630.3231 | 156925.6313 | 3553.0464 | 19248.573 | 137677.0583 | 32879.1847 | 0.072773 | -253884.3493 | 253884.3493
C | Xist Rating 5319 | -51.75 | 962.146 | 150.291 | 35.6 | 2259.13 | 8842.28 | 17050.4 | 0.61 | 2.29 | 18.245 | 29.247 | 1 | 1 | 1920 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2173612.893 | 158471.8277 | 3590.3485 | 19349.3508 | 139122.4768 | 31330.8008 | 0.073154 | -241928.1386 | 241928.1386
C | Xist Rating 5320 | -51.3 | 972.128 | 150.291 | 35.6 | 2257.22 | 8852.45 | 16923.8 | 0.6 | 2.27 | 18.235 | 28.824 | 1 | 1 | 1930 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2194306.7642 | 160025.5719 | 3627.8454 | 19450.1287 | 140575.4432 | 30880.2016 | 0.073535 | -238448.731 | 238448.731
C | Xist Rating 5321 | -50.96 | 975.359 | 150.291 | 35.6 | 2265.95 | 9001.83 | 16882.2 | 0.6 | 2.26 | 18.261 | 28.691 | 1 | 1 | 1940 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2210114.726 | 161586.8641 | 3665.537 | 19550.9066 | 142035.9575 | 30748.3421 | 0.073916 | -237430.5473 | 237430.5473
C | Xist Rating 5322 | -50.69 | 984.784 | 150.291 | 35.6 | 2257.43 | 8904.2 | 16772.2 | 0.58 | 2.24 | 18.241 | 28.342 | 1 | 1 | 1950 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2223080.9451 | 163155.7041 | 3703.4235 | 19651.6844 | 143504.0197 | 30357.8803 | 0.074297 | -234415.5048 | 234415.5048
C | Xist Rating 5323 | -50.22 | 995.71 | 150.291 | 35.6 | 2254.56 | 8903.66 | 16637 | 0.58 | 2.22 | 18.252 | 27.895 | 1 | 1 | 1960 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2244887.9376 | 164732.092 | 3741.5047 | 19752.4623 | 144979.6297 | 29898.9744 | 0.074678 | -230871.9549 | 230871.9549
C | Xist Rating 5324 | -49.07 | 1022.23 | 150.291 | 35.6 | 2247.21 | 8900.79 | 16303.2 | 0.58 | 2.16 | 18.314 | 26.767 | 1 | 1 | 1970 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2297165.4783 | 166316.0278 | 3779.7807 | 19853.2402 | 146462.7876 | 28735.4688 | 0.075059 | -221887.6733 | 221887.6733
C | Xist Rating 5325 | -48.69 | 1030.01 | 150.291 | 35.6 | 2247.22 | 8931.7 | 16214.3 | 0.57 | 2.15 | 18.347 | 26.489 | 1 | 1 | 1980 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2314659.0722 | 167907.5115 | 3818.2515 | 19954.0181 | 147953.4934 | 28436.9428 | 0.07544 | -219582.5348 | 219582.5348
C | Xist Rating 5326 | -48.29 | 1040.18 | 150.291 | 35.6 | 2243.14 | 8906.95 | 16101.5 | 0.56 | 2.13 | 18.346 | 26.141 | 1 | 1 | 1990 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2333269.3652 | 169506.543 | 3856.9171 | 20054.7959 | 149451.7471 | 28063.8174 | 0.075821 | -216701.3589 | 216701.3589
C | Xist Rating 5327 | -47.95 | 1048.09 | 150.291 | 35.6 | 2241.77 | 8915.94 | 16015 | 0.55 | 2.12 | 18.35 | 25.878 | 1 | 1 | 2000 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2349576.7193 | 171113.1224 | 3895.7775 | 20155.5738 | 150957.5486 | 27779.0476 | 0.076202 | -214502.4425 | 214502.4425
C | Xist Rating 5328 | -47.66 | 1053.9 | 150.291 | 35.7 | 2242.19 | 8944.47 | 15953.9 | 0.54 | 2.11 | 18.353 | 25.698 | 1 | 1 | 2010 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2363044.041 | 172727.2497 | 3934.8326 | 20256.3517 | 152470.898 | 27580.2549 | 0.076583 | -212967.4177 | 212967.4177
C | Xist Rating 5329 | -46.43 | 1083.77 | 150.291 | 35.7 | 2232.27 | 8911.33 | 15614.9 | 0.54 | 2.05 | 18.39 | 24.619 | 1 | 1 | 2020 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2419267.2579 | 174348.9249 | 3974.0826 | 20357.1295 | 153991.7954 | 26465.9666 | 0.076964 | -204363.1789 | 204363.1789
C | Xist Rating 5330 | -45.93 | 1094.64 | 150.291 | 35.7 | 2231.33 | 8939.79 | 15499.8 | 0.54 | 2.03 | 18.393 | 24.272 | 1 | 1 | 2030 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2442503.0712 | 175978.1479 | 4013.5273 | 20457.9074 | 155520.2405 | 26110.2064 | 0.077345 | -201616.0931 | 201616.0931
C | Xist Rating 5331 | -45.66 | 1101.85 | 150.291 | 35.7 | 2228.53 | 8921 | 15431.7 | 0.53 | 2.02 | 18.388 | 24.084 | 1 | 1 | 2040 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2455505.7805 | 177614.9189 | 4053.1669 | 20558.6853 | 157056.2336 | 25902.3595 | 0.077726 | -200011.1543 | 200011.1543
C | Xist Rating 5332 | -45.26 | 1108.25 | 150.291 | 35.7 | 2232.56 | 9012.56 | 15364.2 | 0.52 | 2.01 | 18.406 | 23.885 | 1 | 1 | 2050 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2474234.62 | 179259.2377 | 4093.0012 | 20659.4631 | 158599.7745 | 25684.03 | 0.078107 | -198325.272 | 198325.272
C | Xist Rating 5333 | -44.9 | 1118.82 | 150.291 | 35.7 | 2226.45 | 8952.82 | 15264.3 | 0.51 | 1.99 | 18.389 | 23.604 | 1 | 1 | 2060 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2490996.789 | 180911.1043 | 4133.0303 | 20760.241 | 160150.8633 | 25378.7058 | 0.078488 | -195967.6387 | 195967.6387
C | Xist Rating 5334 | -43.6 | 1150.89 | 150.291 | 35.7 | 2216.21 | 8919.4 | 14936.2 | 0.51 | 1.94 | 18.427 | 22.619 | 1 | 1 | 2070 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2550613.9269 | 182570.5189 | 4173.2542 | 20861.0189 | 161709.5 | 24361.7869 | 0.078869 | -188115.2606 | 188115.2606
C | Xist Rating 5335 | -43.31 | 1157.91 | 150.291 | 35.7 | 2214.98 | 8925.26 | 14873.5 | 0.51 | 1.93 | 18.424 | 22.452 | 1 | 1 | 2080 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2564747.4918 | 184237.4813 | 4213.6729 | 20961.7967 | 163275.6846 | 24192.4275 | 0.07925 | -186807.5124 | 186807.5124
C | Xist Rating 5336 | -42.93 | 1166.96 | 150.291 | 35.7 | 2213.15 | 8929.88 | 14790.8 | 0.5 | 1.91 | 18.422 | 22.225 | 1 | 1 | 2090 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2582657.524 | 185911.9916 | 4254.2864 | 21062.5746 | 164849.417 | 23943.5462 | 0.079631 | -184885.7174 | 184885.7174
C | Xist Rating 5337 | -42.53 | 1176.02 | 150.291 | 35.7 | 2212.39 | 8951.95 | 14709.2 | 0.49 | 1.9 | 18.427 | 22.003 | 1 | 1 | 2100 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2601814.8878 | 187594.0498 | 4295.0947 | 21163.3525 | 166430.6974 | 23700.0181 | 0.080012 | -183005.2573 | 183005.2573
C | Xist Rating 5338 | -42.17 | 1184.02 | 150.291 | 35.7 | 2211.56 | 8968.66 | 14638.6 | 0.49 | 1.89 | 18.423 | 21.814 | 1 | 1 | 2110 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2618531.2712 | 189283.6559 | 4336.0977 | 21264.1304 | 168019.5256 | 23507.6038 | 0.080393 | -181519.4854 | 181519.4854
C | Xist Rating 5339 | -40.98 | 1214.33 | 150.291 | 35.7 | 2201.58 | 8927.11 | 14358.9 | 0.49 | 1.84 | 18.458 | 21.024 | 1 | 1 | 2120 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2673444.6414 | 190980.8099 | 4377.2956 | 21364.9082 | 169615.9016 | 22692.8662 | 0.080774 | -175228.2979 | 175228.2979
C | Xist Rating 5340 | -40.52 | 1225.54 | 150.291 | 35.7 | 2198.9 | 8925.69 | 14263.7 | 0.48 | 1.83 | 18.454 | 20.772 | 1 | 1 | 2130 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2694839.906 | 192685.5117 | 4418.6882 | 21465.6861 | 171219.8256 | 22417.4124 | 0.081155 | -173101.3163 | 173101.3163
C | Xist Rating 5341 | -40.12 | 1236.78 | 150.291 | 35.7 | 2194.39 | 8893.89 | 14169.7 | 0.47 | 1.81 | 18.448 | 20.526 | 1 | 1 | 2140 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2713977.6642 | 194397.7614 | 4460.2756 | 21566.464 | 172831.2974 | 22147.9399 | 0.081536 | -171020.5208 | 171020.5208
C | Xist Rating 5342 | -39.87 | 1242.74 | 150.291 | 35.7 | 2193.49 | 8900.23 | 14123.4 | 0.47 | 1.8 | 18.448 | 20.413 | 1 | 1 | 2150 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2725937.7626 | 196117.559 | 4502.0578 | 21667.2418 | 174450.3171 | 22034.4761 | 0.081917 | -170144.3836 | 170144.3836
C | Xist Rating 5343 | -39.52 | 1250.69 | 150.291 | 35.7 | 2192.89 | 8919.91 | 14058.9 | 0.46 | 1.79 | 18.451 | 20.249 | 1 | 1 | 2160 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2742625.5941 | 197844.9044 | 4544.0348 | 21768.0197 | 176076.8847 | 21850.3209 | 0.082298 | -168722.3863 | 168722.3863
C | Xist Rating 5344 | -38.28 | 1283.41 | 150.292 | 35.7 | 2181.55 | 8860.66 | 13785.9 | 0.46 | 1.75 | 18.484 | 19.519 | 1 | 1 | 2170 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2799823.0855 | 199579.7977 | 4586.2066 | 21868.7976 | 177711.0002 | 21097.4981 | 0.082679 | -162909.288 | 162909.288
C | Xist Rating 5345 | -37.8 | 1294.39 | 150.292 | 35.7 | 2180.46 | 8884.25 | 13699 | 0.46 | 1.74 | 18.485 | 19.299 | 1 | 1 | 2180 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2822365.6194 | 201322.239 | 4628.5732 | 21969.5754 | 179352.6635 | 20872.8847 | 0.08306 | -161174.8827 | 161174.8827
C | Xist Rating 5346 | -37.5 | 1302.57 | 150.292 | 35.7 | 2178.05 | 8873.38 | 13638.9 | 0.45 | 1.73 | 18.489 | 19.155 | 1 | 1 | 2190 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2837062.5885 | 203072.228 | 4671.1346 | 22070.3533 | 181001.8747 | 20709.1831 | 0.083441 | -159910.8225 | 159910.8225
C | Xist Rating 5347 | -37.2 | 1311.16 | 150.291 | 35.7 | 2174.5 | 8843.7 | 13579.4 | 0.44 | 1.72 | 18.483 | 19.018 | 1 | 1 | 2200 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2851117.42 | 204829.765 | 4713.8907 | 22171.1312 | 182658.6338 | 20552.1451 | 0.083822 | -158698.2169 | 158698.2169
C | Xist Rating 5348 | -36.74 | 1322.41 | 150.291 | 35.7 | 2172.48 | 8851.44 | 13495.4 | 0.44 | 1.7 | 18.483 | 18.812 | 1 | 1 | 2210 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2872909.2768 | 206594.8498 | 4756.8417 | 22271.909 | 184322.9408 | 20341.8598 | 0.084203 | -157074.4496 | 157074.4496
C | Xist Rating 5349 | -35.5 | 1354.99 | 150.292 | 35.7 | 2162.62 | 8812.87 | 13246.1 | 0.44 | 1.66 | 18.519 | 18.179 | 1 | 1 | 2220 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2930328.4738 | 208367.4826 | 4799.9874 | 22372.6869 | 185994.7957 | 19689.712 | 0.084584 | -152038.7365 | 152038.7365
C | Xist Rating 5350 | -35.09 | 1364.02 | 150.292 | 35.7 | 2162.57 | 8844.69 | 13182.5 | 0.43 | 1.65 | 18.522 | 18.029 | 1 | 1 | 2230 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2949788.7314 | 210147.6632 | 4843.3279 | 22473.4648 | 187674.1984 | 19519.2072 | 0.084965 | -150722.1441 | 150722.1441
C | Xist Rating 5351 | -34.72 | 1374.56 | 150.292 | 35.7 | 2159.22 | 8825.5 | 13111.7 | 0.43 | 1.64 | 18.519 | 17.867 | 1 | 1 | 2240 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2967977.4432 | 211935.3916 | 4886.8633 | 22574.2426 | 189361.149 | 19354.411 | 0.085346 | -149449.6313 | 149449.6313
C | Xist Rating 5352 | -34.28 | 1386.11 | 150.292 | 35.7 | 2155.98 | 8811.93 | 13034.1 | 0.42 | 1.63 | 18.516 | 17.688 | 1 | 1 | 2250 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 2988425.4378 | 213730.668 | 4930.5934 | 22675.0205 | 191055.6475 | 19153.2847 | 0.085727 | -147896.5877 | 147896.5877
C | Xist Rating 5353 | -34.03 | 1392.03 | 150.292 | 35.7 | 2155.73 | 8828.01 | 12995.6 | 0.42 | 1.62 | 18.516 | 17.604 | 1 | 1 | 2260 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3000840.8319 | 215533.4922 | 4974.5182 | 22775.7984 | 192757.6938 | 19069.5367 | 0.086108 | -147249.908 | 147249.908
C | Xist Rating 5354 | -32.7 | 1427.12 | 150.292 | 35.7 | 2145.62 | 8789.68 | 12751.9 | 0.42 | 1.59 | 18.552 | 17.018 | 1 | 1 | 2270 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3062057.2144 | 217343.8643 | 5018.6379 | 22876.5763 | 194467.2881 | 18466.0011 | 0.086489 | -142589.5653 | 142589.5653
C | Xist Rating 5355 | -32.31 | 1437.61 | 150.292 | 35.7 | 2143.06 | 8782.76 | 12686.2 | 0.41 | 1.58 | 18.546 | 16.873 | 1 | 1 | 2280 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3080884.4866 | 219161.7843 | 5062.9524 | 22977.3541 | 196184.4302 | 18299.6999 | 0.08687 | -141305.4315 | 141305.4315
C | Xist Rating 5356 | -31.81 | 1449.97 | 150.292 | 35.7 | 2141.09 | 8793.62 | 12606.9 | 0.41 | 1.56 | 18.545 | 16.695 | 1 | 1 | 2290 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3104516.2673 | 220987.2522 | 5107.4617 | 23078.132 | 197909.1202 | 18118.2134 | 0.087251 | -139904.0417 | 139904.0417
C | Xist Rating 5357 | -31.48 | 1458.31 | 150.292 | 35.7 | 2139.8 | 8799.94 | 12557 | 0.4 | 1.56 | 18.543 | 16.59 | 1 | 1 | 2300 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3120491.738 | 222820.2679 | 5152.1657 | 23178.9099 | 199641.3581 | 17993.3776 | 0.087632 | -138940.0921 | 138940.0921
| Xist Rating 5358 | -31.16 | 1466.92 | 150.292 | 35.7 | 2138.02 | 8797.91 | 12507.6 | 0.4 | 1.55 | 18.539 | 16.488 | 1 | 1 | 2310 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3136304.2984 | 224660.8315 | 5197.0645 | 23279.6877 | 201381.1438 | 17890.6098 | 0.088013 | -138146.5466 | 138146.5466
| Xist Rating 5359 | -29.79 | 1502.91 | 150.292 | 35.7 | 2128.88 | 8776.19 | 12277.1 | 0.4 | 1.51 | 18.574 | 15.958 | 1 | 1 | 2320 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3199515.0408 | 226508.943 | 5242.1582 | 23380.4656 | 203128.4774 | 17344.9856 | 0.088394 | -133933.3808 | 133933.3808
| Xist Rating 5360 | -29.4 | 1513.43 | 150.292 | 35.6 | 2126.77 | 8775.78 | 12216.8 | 0.39 | 1.5 | 18.567 | 15.832 | 1 | 1 | 2330 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3218717.5211 | 228364.6024 | 5287.4466 | 23481.2435 | 204883.3589 | 17197.781 | 0.088775 | -132796.706 | 132796.706
| Xist Rating 5361 | -29.01 | 1523.92 | 150.292 | 35.6 | 2124.3 | 8769.42 | 12157.2 | 0.39 | 1.49 | 18.56 | 15.708 | 1 | 1 | 2340 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3237263.256 | 230227.8096 | 5332.9298 | 23582.0213 | 206645.7883 | 17071.9666 | 0.089156 | -131825.201 | 131825.201
| Xist Rating 5362 | -28.69 | 1533.44 | 150.292 | 35.6 | 2121.36 | 8750.73 | 12104.6 | 0.38 | 1.49 | 18.555 | 15.602 | 1 | 1 | 2350 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3252978.2784 | 232098.5648 | 5378.6078 | 23682.7992 | 208415.7656 | 16945.3795 | 0.089537 | -130847.729 | 130847.729
| Xist Rating 5363 | -28.28 | 1545.05 | 150.292 | 35.6 | 2118.34 | 8738.47 | 12039.8 | 0.38 | 1.48 | 18.55 | 15.468 | 1 | 1 | 2360 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3272941.217 | 233976.8678 | 5424.4805 | 23783.5771 | 210193.2907 | 16809.1803 | 0.089918 | -129796.0345 | 129796.0345
| Xist Rating 5364 | -27.05 | 1578.06 | 150.292 | 35.6 | 2110.17 | 8717.88 | 11846.7 | 0.38 | 1.45 | 18.581 | 15.047 | 1 | 1 | 2370 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3329974.8702 | 235862.7187 | 5470.5481 | 23884.3549 | 211978.3637 | 16376.3836 | 0.090299 | -126454.0931 | 126454.0931
| Xist Rating 5365 | -26.7 | 1588.79 | 150.292 | 35.6 | 2106.65 | 8692.67 | 11791.1 | 0.38 | 1.44 | 18.571 | 14.937 | 1 | 1 | 2380 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3347024.4535 | 237756.1174 | 5516.8105 | 23985.1328 | 213770.9846 | 16264.9083 | 0.09068 | -125593.3108 | 125593.3108
| Xist Rating 5366 | -26.28 | 1599.95 | 150.292 | 35.6 | 2104.78 | 8699.16 | 11730 | 0.37 | 1.43 | 18.572 | 14.812 | 1 | 1 | 2390 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3367542.761 | 239657.0641 | 5563.2676 | 24085.9107 | 215571.1534 | 16118.4037 | 0.091061 | -124462.0405 | 124462.0405
C | Xist Rating 5370 | -17.7 | 1837.95 | 150.292 | 35.6 | 2047.36 | 8533.63 | 10537.8 | 0.39 | 1.25 | 18.603 | 12.427 | 1 | 1 | 2430 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3762945.312 | 247336.3294 | 5751.0441 | 24489.0222 | 222847.3072 | 13695.6813 | 0.092585 | -105754.4204 | 105754.4204
C | Xist Rating 5371 | -17.68 | 1839.32 | 150.292 | 35.6 | 2047.05 | 8528.15 | 10537.8 | 0.38 | 1.25 | 18.595 | 12.438 | 1 | 1 | 2440 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3765180.006 | 249275.0154 | 5798.4752 | 24589.8 | 224685.2154 | 13689.6779 | 0.092966 | -105708.0637 | 105708.0637
C | Xist Rating 5372 | -17.66 | 1840.65 | 150.292 | 35.6 | 2046.84 | 8524.55 | 10537.8 | 0.38 | 1.25 | 18.588 | 12.449 | 1 | 1 | 2450 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3767516.046 | 251221.2493 | 5846.1011 | 24690.5779 | 226530.6714 | 13703.9766 | 0.093347 | -105818.4746 | 105818.4746
C | Xist Rating 5373 | -17.64 | 1842.12 | 150.292 | 35.6 | 2046.32 | 8515.56 | 10537.8 | 0.37 | 1.25 | 18.582 | 12.46 | 1 | 1 | 2460 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3769566.9984 | 253175.0311 | 5893.9217 | 24791.3558 | 228383.6753 | 13697.8247 | 0.093728 | -105770.9713 | 105770.9713
C | Xist Rating 5374 | -17.61 | 1843.47 | 150.292 | 35.6 | 2046.19 | 8513.42 | 10537.8 | 0.37 | 1.25 | 18.617 | 12.47 | 1 | 1 | 2470 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3772089.8793 | 255136.3607 | 5941.9372 | 24892.1336 | 230244.2271 | 13712.7253 | 0.094109 | -105886.0299 | 105886.0299
C | Xist Rating 5375 | -17.59 | 1844.82 | 150.292 | 35.6 | 2045.91 | 8508.6 | 10537.7 | 0.36 | 1.25 | 18.609 | 12.481 | 1 | 1 | 2480 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3774335.6862 | 257105.2383 | 5990.1474 | 24992.9115 | 232112.3268 | 13706.2207 | 0.09449 | -105835.8029 | 105835.8029
C | Xist Rating 5376 | -17.61 | 1846.22 | 150.292 | 35.6 | 2044.43 | 8482.95 | 10537.8 | 0.35 | 1.25 | 18.611 | 12.492 | 1 | 1 | 2490 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3774467.5546 | 259081.6637 | 6038.5525 | 25093.6894 | 233987.9743 | 13699.9551 | 0.094871 | -105787.4215 | 105787.4215
C | Xist Rating 5377 | -17.58 | 1847.2 | 150.292 | 35.6 | 2044.68 | 8487.24 | 10537.8 | 0.35 | 1.25 | 18.607 | 12.501 | 1 | 1 | 2500 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3776932.896 | 261065.637 | 6087.1523 | 25194.4672 | 235871.1697 | 13712.0645 | 0.095252 | -105880.9271 | 105880.9271
C | Xist Rating 5378 | -17.58 | 1849.05 | 150.292 | 35.6 | 2043.28 | 8463.08 | 10537.8 | 0.34 | 1.25 | 18.601 | 12.513 | 1 | 1 | 2510 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3778126.884 | 263057.1581 | 6135.9469 | 25295.2451 | 237761.913 | 13706.2814 | 0.095633 | -105836.2718 | 105836.2718
C | Xist Rating 5379 | -17.57 | 1850.51 | 150.292 | 35.6 | 2042.62 | 8451.84 | 10537.8 | 0.34 | 1.25 | 18.638 | 12.524 | 1 | 1 | 2520 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3779888.7362 | 265056.2272 | 6184.9363 | 25396.023 | 239660.2042 | 13721.9608 | 0.096014 | -105957.3437 | 105957.3437
C | Xist Rating 5380 | -17.56 | 1851.84 | 150.292 | 35.6 | 2042.09 | 8442.73 | 10537.8 | 0.33 | 1.25 | 18.633 | 12.534 | 1 | 1 | 2530 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3781623.9456 | 267062.8441 | 6234.1205 | 25496.8008 | 241566.0432 | 13713.8624 | 0.096395 | -105894.8106 | 105894.8106
C | Xist Rating 5381 | -17.54 | 1852.99 | 150.292 | 35.6 | 2041.93 | 8440.05 | 10537.8 | 0.33 | 1.25 | 18.628 | 12.544 | 1 | 1 | 2540 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3783675.8707 | 269077.0089 | 6283.4995 | 25597.5787 | 243479.4302 | 13726.8158 | 0.096776 | -105994.8329 | 105994.8329
C | Xist Rating 5382 | -17.5 | 1854.54 | 150.292 | 35.6 | 2041.9 | 8439.55 | 10537.7 | 0.32 | 1.25 | 18.62 | 12.555 | 1 | 1 | 2550 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3786785.226 | 271098.7216 | 6333.0732 | 25698.3566 | 245400.365 | 13719.4098 | 0.097157 | -105937.6458 | 105937.6458
C | Xist Rating 5383 | -17.49 | 1855.99 | 150.292 | 35.6 | 2041.37 | 8430.61 | 10537.7 | 0.32 | 1.25 | 18.616 | 12.565 | 1 | 1 | 2560 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3788762.3063 | 273127.9821 | 6382.8418 | 25799.1345 | 247328.8477 | 13732.3187 | 0.097538 | -106037.3252 | 106037.3252
C | Xist Rating 5384 | -17.47 | 1857.38 | 150.292 | 35.6 | 2040.93 | 8423.11 | 10537.7 | 0.31 | 1.25 | 18.612 | 12.576 | 1 | 1 | 2570 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3790782.5634 | 275164.7905 | 6432.8051 | 25899.9123 | 249264.8782 | 13724.8241 | 0.097919 | -105979.4538 | 105979.4538
C | Xist Rating 5385 | -17.44 | 1858.74 | 150.292 | 35.6 | 2040.98 | 8423.98 | 10537.7 | 0.31 | 1.25 | 18.664 | 12.586 | 1 | 1 | 2580 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3793651.1652 | 277209.1469 | 6482.9633 | 26000.6902 | 251208.4567 | 13739.6596 | 0.0983 | -106094.0094 | 106094.0094
C | Xist Rating 5386 | -17.42 | 1860.1 | 150.292 | 35.6 | 2040.6 | 8417.51 | 10537.6 | 0.3 | 1.25 | 18.66 | 12.596 | 1 | 1 | 2590 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3795720.06 | 279261.051 | 6533.3162 | 26101.4681 | 253159.583 | 13730.8306 | 0.098681 | -106025.8344 | 106025.8344
C | Xist Rating 5387 | -17.4 | 1861.28 | 150.292 | 35.6 | 2040.51 | 8415.9 | 10537.6 | 0.3 | 1.25 | 18.656 | 12.605 | 1 | 1 | 2600 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3797960.4528 | 281320.5031 | 6583.8639 | 26202.2459 | 255118.2572 | 13742.5465 | 0.099062 | -106116.3016 | 106116.3016
C | Xist Rating 5388 | -17.38 | 1862.97 | 150.292 | 35.6 | 2039.93 | 8406.11 | 10537.6 | 0.29 | 1.25 | 18.656 | 12.617 | 1 | 1 | 2610 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3800328.3921 | 283387.503 | 6634.6064 | 26303.0238 | 257084.4792 | 13735.6912 | 0.099443 | -106063.3663 | 106063.3663
C | Xist Rating 5389 | -17.36 | 1864.37 | 150.292 | 35.6 | 2039.6 | 8400.56 | 10537.6 | 0.29 | 1.25 | 18.654 | 12.627 | 1 | 1 | 2620 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3802569.052 | 285462.0509 | 6685.5437 | 26403.8017 | 259058.2492 | 13748.4332 | 0.099824 | -106161.7566 | 106161.7566
C | Xist Rating 5390 | -17.33 | 1865.79 | 150.292 | 35.6 | 2039.34 | 8396.06 | 10537.6 | 0.29 | 1.25 | 18.692 | 12.637 | 1 | 1 | 2630 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3804980.1786 | 287544.1466 | 6736.6758 | 26504.5795 | 261039.567 | 13762.5421 | 0.10021 | -106270.7024 | 106270.7024
C | Xist Rating 5391 | -17.28 | 1867.04 | 150.292 | 35.6 | 2039.85 | 8404.85 | 10537.6 | 0.28 | 1.25 | 18.694 | 12.647 | 1 | 1 | 2640 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3808481.544 | 289633.7901 | 6788.0027 | 26605.3574 | 263028.4327 | 13753.3036 | 0.10059 | -106199.365 | 106199.365
C | Xist Rating 5392 | -17.25 | 1868.54 | 150.292 | 35.6 | 2039.52 | 8399.23 | 10537.6 | 0.28 | 1.25 | 18.69 | 12.657 | 1 | 1 | 2650 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3810924.7008 | 291730.9816 | 6839.5243 | 26706.1353 | 265024.8463 | 13765.9018 | 0.10097 | -106296.6451 | 106296.6451
C | Xist Rating 5393 | -17.23 | 1869.88 | 150.292 | 35.6 | 2039.35 | 8396.37 | 10537.6 | 0.28 | 1.25 | 18.687 | 12.667 | 1 | 1 | 2660 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3813339.778 | 293835.7209 | 6891.2408 | 26806.9131 | 267028.8078 | 13778.5324 | 0.10135 | -106394.1751 | 106394.1751
C | Xist Rating 5394 | -17.18 | 1871.27 | 150.292 | 35.6 | 2039.68 | 8401.86 | 10537.7 | 0.27 | 1.25 | 18.687 | 12.677 | 1 | 1 | 2670 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3816791.9936 | 295948.0081 | 6943.152 | 26907.691 | 269040.3171 | 13768.8979 | 0.10173 | -106319.7795 | 106319.7795
C | Xist Rating 5395 | -17.14 | 1872.68 | 150.292 | 35.6 | 2039.78 | 8403.55 | 10537.7 | 0.27 | 1.25 | 18.725 | 12.687 | 1 | 1 | 2680 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3819855.2104 | 298067.8432 | 6995.258 | 27008.4689 | 271059.3743 | 13782.777 | 0.10211 | -106426.9506 | 106426.9506
C | Xist Rating 5396 | -17.1 | 1874.06 | 150.292 | 35.6 | 2040.13 | 8409.63 | 10537.6 | 0.26 | 1.25 | 18.722 | 12.697 | 1 | 1 | 2690 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3823326.0278 | 300195.2261 | 7047.5588 | 27109.2468 | 273085.9794 | 13772.7559 | 0.10249 | -106349.5701 | 106349.5701
C | Xist Rating 5397 | -17.03 | 1875.26 | 150.292 | 35.6 | 2041.35 | 8430.29 | 10537.5 | 0.26 | 1.25 | 18.721 | 12.706 | 1 | 1 | 2700 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3828062.001 | 302330.157 | 7100.0544 | 27210.0246 | 275120.1324 | 13784.2528 | 0.10287 | -106438.3465 | 106438.3465
C | Xist Rating 5398 | -17.03 | 1876.92 | 150.292 | 35.6 | 2040.21 | 8411.01 | 10537.5 | 0.26 | 1.25 | 18.717 | 12.717 | 1 | 1 | 2710 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3829310.9532 | 304472.6357 | 7152.7448 | 27310.8025 | 277161.8332 | 13797.7318 | 0.10325 | -106542.4276 | 106542.4276
C | Xist Rating 5399 | -17.01 | 1878.26 | 150.292 | 35.6 | 2039.81 | 8404.1 | 10537.5 | 0.25 | 1.25 | 18.71 | 12.727 | 1 | 1 | 2720 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3831293.5306 | 306622.6623 | 7205.63 | 27411.5804 | 279211.0819 | 13787.2644 | 0.10363 | -106461.6014 | 106461.6014
C | Xist Rating 5400 | -17.01 | 1879.59 | 150.292 | 35.6 | 2038.89 | 8388.54 | 10537.5 | 0.25 | 1.25 | 18.742 | 12.736 | 1 | 1 | 2730 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3832277.2551 | 308780.2368 | 7258.71 | 27512.3582 | 281267.8785 | 13799.6866 | 0.10402 | -106557.5218 | 106557.5218
C | Xist Rating 5401 | -17.01 | 1880.87 | 150.292 | 35.6 | 2038.19 | 8376.81 | 10537.5 | 0.25 | 1.25 | 18.739 | 12.745 | 1 | 1 | 2740 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3833570.4253 | 310945.3591 | 7311.9847 | 27613.1361 | 283332.223 | 13811.0412 | 0.1044 | -106645.1992 | 106645.1992
C | Xist Rating 5402 | -16.99 | 1882.42 | 150.292 | 35.6 | 2037.48 | 8364.75 | 10537.5 | 0.25 | 1.25 | 18.738 | 12.756 | 1 | 1 | 2750 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3835393.1016 | 313118.0293 | 7365.4543 | 27713.914 | 285404.1154 | 13824.5338 | 0.10478 | -106749.3854 | 106749.3854
C | Xist Rating 5403 | -17.01 | 1883.84 | 150.292 | 35.6 | 2036.15 | 8342.42 | 10537.5 | 0.24 | 1.25 | 18.73 | 12.766 | 1 | 1 | 2760 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3835780.816 | 315298.2474 | 7419.1186 | 27814.6918 | 287483.5556 | 13813.5991 | 0.10516 | -106664.9509 | 106664.9509
C | Xist Rating 5404 | -16.98 | 1885.08 | 150.292 | 35.6 | 2036.19 | 8342.95 | 10537.5 | 0.24 | 1.25 | 18.732 | 12.774 | 1 | 1 | 2770 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3838381.0452 | 317486.0134 | 7472.9777 | 27915.4697 | 289570.5437 | 13823.9817 | 0.10554 | -106745.1222 | 106745.1222
C | Xist Rating 5405 | -16.98 | 1886.62 | 150.292 | 35.6 | 2035.05 | 8323.96 | 10537.5 | 0.24 | 1.25 | 18.771 | 12.785 | 1 | 1 | 2780 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 21 | E | Rod | 3839366.031 | 319681.3273 | 7527.0316 | 28016.2476 | 291665.0797 | 13838.5867 | 0.10592 | -106857.8983 | 106857.8983
C | Xist Rating 5406 | -16.98 | 1888.03 | 150.292 | 35.6 | 2034.21 | 8309.96 | 10537.5 | 0.23 | 1.25 | 18.765 | 12.795 | 1 | 1 | 2790 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3840649.5063 | 321884.189 | 7581.2803 | 28117.0254 | 293767.1636 | 13827.3433 | 0.1063 | -106771.0799 | 106771.0799
C | Xist Rating 5407 | -16.95 | 1889.01 | 150.292 | 35.6 | 2034.79 | 8319.54 | 10537.6 | 0.23 | 1.25 | 18.77 | 12.802 | 1 | 1 | 2800 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3843738.6579 | 324094.5986 | 7635.7238 | 28217.8033 | 295876.7953 | 13836.6917 | 0.10668 | -106843.266 | 106843.266
C | Xist Rating 5408 | -16.91 | 1890.75 | 150.292 | 35.6 | 2034.28 | 8310.97 | 10537.6 | 0.23 | 1.25 | 18.777 | 12.813 | 1 | 1 | 2810 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3846314.91 | 326312.5561 | 7690.3621 | 28318.5812 | 297993.9749 | 13850.2531 | 0.10706 | -106947.9835 | 106947.9835
C | Xist Rating 5409 | -16.93 | 1892.23 | 150.292 | 35.6 | 2033.03 | 8290.24 | 10537.6 | 0.23 | 1.25 | 18.773 | 12.823 | 1 | 1 | 2820 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3846960.3569 | 328538.0615 | 7745.1952 | 28419.359 | 300118.7024 | 13862.4577 | 0.10744 | -107042.2237 | 107042.2237
C | Xist Rating 5410 | -16.84 | 1893.6 | 150.292 | 35.6 | 2034.21 | 8309.77 | 10537.6 | 0.22 | 1.25 | 18.828 | 12.833 | 1 | 1 | 2830 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3851980.056 | 330771.1147 | 7800.223 | 28520.1369 | 302250.9778 | 13852.4988 | 0.10783 | -106965.3237 | 106965.3237
C | Xist Rating 5411 | -16.66 | 1894.92 | 150.292 | 35.6 | 2037.85 | 8370.9 | 10537.7 | 0.22 | 1.25 | 18.856 | 12.842 | 1 | 1 | 2840 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3861562.722 | 333011.7158 | 7855.4457 | 28620.9148 | 304390.801 | 13864.4862 | 0.10821 | -107057.887 | 107057.887
C | Xist Rating 5412 | -16.64 | 1896.36 | 150.292 | 35.6 | 2037.5 | 8364.94 | 10537.8 | 0.22 | 1.25 | 18.857 | 12.852 | 1 | 1 | 2850 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3863833.5 | 335259.8648 | 7910.8631 | 28721.6927 | 306538.1722 | 13876.7587 | 0.10859 | -107152.6525 | 107152.6525
C | Xist Rating 5413 | -16.25 | 1897.77 | 150.292 | 35.6 | 2046.43 | 8517.35 | 10537.9 | 0.21 | 1.25 | 18.924 | 12.862 | 1 | 1 | 2860 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3883653.4611 | 337515.5617 | 7966.4753 | 28822.4705 | 308693.0912 | 13866.6326 | 0.10897 | -107074.4615 | 107074.4615
C | Xist Rating 5414 | -16.58 | 1898.96 | 150.292 | 35.6 | 2037.44 | 8364 | 10537.8 | 0.21 | 1.25 | 18.86 | 12.87 | 1 | 1 | 2870 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3869017.0624 | 339778.8065 | 8022.2824 | 28923.2484 | 310855.5581 | 13874.993 | 0.10935 | -107139.0177 | 107139.0177
C | Xist Rating 5415 | -15.99 | 1900.46 | 150.293 | 35.6 | 2051.28 | 8601.93 | 10538 | 0.21 | 1.25 | 18.993 | 12.881 | 1 | 1 | 2880 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3898375.5888 | 342049.5991 | 8078.2842 | 29024.0263 | 313025.5728 | 13891.7974 | 0.10973 | -107268.7771 | 107268.7771
C | Xist Rating 5416 | -15.43 | 1901.81 | 150.293 | 35.6 | 2064.42 | 8837.77 | 10538.1 | 0.2 | 1.25 | 19.05 | 12.891 | 1 | 1 | 2890 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3926134.6002 | 344327.9396 | 8134.4807 | 29124.8041 | 315203.1355 | 13880.8429 | 0.11011 | -107184.1891 | 107184.1891
C | Xist Rating 5417 | -15.1 | 1903.19 | 150.293 | 35.6 | 2071.84 | 8975.38 | 10538.1 | 0.2 | 1.25 | 19.083 | 12.901 | 1 | 1 | 2900 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3943105.1696 | 346613.828 | 8190.8721 | 29225.582 | 317388.246 | 13893.7936 | 0.11049 | -107284.1914 | 107284.1914
C | Xist Rating 5418 | -14.92 | 1904.73 | 150.293 | 35.6 | 2075.3 | 9040.74 | 10538.1 | 0.2 | 1.25 | 19.099 | 12.911 | 1 | 1 | 2910 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3952886.169 | 348907.2642 | 8247.4583 | 29326.3599 | 319580.9044 | 13906.3068 | 0.11087 | -107380.8147 | 107380.8147
C | Xist Rating 5419 | -14.72 | 1906.12 | 150.293 | 35.6 | 2079.23 | 9115.87 | 10538.1 | 0.2 | 1.25 | 19.117 | 12.92 | 1 | 1 | 2920 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3963261.8876 | 351208.2484 | 8304.2393 | 29427.1377 | 321781.1106 | 13917.8367 | 0.11125 | -107469.8455 | 107469.8455
C | Xist Rating 5420 | -14.51 | 1907.51 | 150.293 | 35.6 | 2083.56 | 9199.57 | 10538 | 0.19 | 1.25 | 19.176 | 12.93 | 1 | 1 | 2930 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3974411.5356 | 353516.7804 | 8361.215 | 29527.9156 | 323988.8648 | 13906.3002 | 0.11164 | -107380.7641 | 107380.7641
C | Xist Rating 5421 | -14.33 | 1908.88 | 150.293 | 35.6 | 2087.32 | 9273.33 | 10538 | 0.19 | 1.25 | 19.189 | 12.939 | 1 | 1 | 2940 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 3984443.4016 | 355832.8603 | 8418.3855 | 29628.6935 | 326204.1668 | 13917.6054 | 0.11202 | -107468.0595 | 107468.0595
C | Xist Rating 5422 | -13.91 | 1910.29 | 150.293 | 35.5 | 2096.85 | 9464.6 | 10537.9 | 0.19 | 1.25 | 19.22 | 12.949 | 1 | 1 | 2950 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 4005591.5865 | 358156.4881 | 8475.7509 | 29729.4713 | 328427.0167 | 13930.4035 | 0.1124 | -107566.883 | 107566.883
C | Xist Rating 5423 | -13.87 | 1911.66 | 150.293 | 35.5 | 2097.01 | 9467.87 | 10537.9 | 0.19 | 1.25 | 19.214 | 12.958 | 1 | 1 | 2960 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 4008770.1366 | 360487.6637 | 8533.311 | 29830.2492 | 330657.4145 | 13941.2356 | 0.11278 | -107650.5259 | 107650.5259
C | Xist Rating 5424 | -13.87 | 1913.04 | 150.293 | 35.5 | 2096.31 | 9453.63 | 10537.9 | 0.18 | 1.25 | 19.211 | 12.967 | 1 | 1 | 2970 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 4010324.8824 | 362826.3872 | 8591.0659 | 29931.0271 | 332895.3602 | 13926.5671 | 0.11316 | -107537.26 | 107537.26
C | Xist Rating 5425 | -13.84 | 1914.26 | 150.293 | 35.5 | 2096.16 | 9450.6 | 10537.8 | 0.18 | 1.25 | 19.247 | 12.976 | 1 | 1 | 2980 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 4012595.2416 | 365172.6586 | 8649.0156 | 30031.805 | 335140.8537 | 13938.3292 | 0.11354 | -107628.0838 | 107628.0838
C | Xist Rating 5426 | -13.83 | 1915.82 | 150.293 | 35.5 | 2095.43 | 9435.75 | 10537.8 | 0.18 | 1.25 | 19.243 | 12.985 | 1 | 1 | 2990 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 4014466.7026 | 367526.4779 | 8707.16 | 30132.5828 | 337393.8951 | 13949.1322 | 0.11392 | -107711.501 | 107711.501
C | Xist Rating 5427 | -13.81 | 1917.25 | 150.293 | 35.5 | 2094.84 | 9423.98 | 10537.8 | 0.18 | 1.25 | 19.238 | 12.995 | 1 | 1 | 3000 | 152.4 | 2 | 3.6 | 19.05 | 1.3333 | 20 | E | Rod | 4016331.99 | 369887.8451 | 8765.4993 | 30233.3607 | 339654.4844 | 13960.9487 | 0.1143 | -107802.7454 | 107802.7454
C | Xist Rating 5428 | -89.48 | 191.851 | 150.297 | 35.9 | 2378.03 | 7202.32 | 58745.9 | 2.46 | 10.95 | 20.72 | 497.997 | 1 | 1 | 1000 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 456227.4335 | 49145.4289 | 973.9444 | 10357.7254 | 38787.7035 | 519453.8633 | 0.038101 | -4011085.0405 | 4011085.0405
C | Xist Rating 5429 | -89.39 | 193.846 | 150.297 | 35.9 | 2375.94 | 7191.12 | 58283.6 | 2.44 | 10.85 | 20.775 | 488.643 | 1 | 1 | 1010 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 460566.4652 | 50028.639 | 993.5206 | 10461.3027 | 39567.3363 | 509749.9113 | 0.038482 | -3936153.6953 | 3936153.6953
C | Xist Rating 5430 | -88.6 | 208.928 | 150.297 | 35.9 | 2369.44 | 7192.99 | 54967.7 | 2.45 | 10.07 | 20.83 | 423.467 | 1 | 1 | 1020 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 495042.3603 | 50919.6066 | 1013.2917 | 10564.8799 | 40354.7267 | 442103.1199 | 0.038863 | -3413803.1033 | 3413803.1033
C | Xist Rating 5431 | -88.47 | 213.063 | 150.296 | 35.8 | 2350.62 | 7037.4 | 54178.5 | 2.37 | 9.89 | 20.362 | 409.266 | 1 | 1 | 1030 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 500830.1491 | 51818.3318 | 1033.2576 | 10668.4572 | 41149.8746 | 427250.1335 | 0.039244 | -3299112.2797 | 3299112.2797
C | Xist Rating 5432 | -88.39 | 215.132 | 150.296 | 35.8 | 2344.6 | 6991.12 | 53793.7 | 2.33 | 9.8 | 20.251 | 402.473 | 1 | 1 | 1040 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 504398.4872 | 52724.8145 | 1053.4182 | 10772.0344 | 41952.7801 | 420167.2194 | 0.039625 | -3244419.894 | 3244419.894
C | Xist Rating 5433 | -88.21 | 219.146 | 150.296 | 35.8 | 2339.13 | 6957.34 | 53042.7 | 2.29 | 9.63 | 20.176 | 389.135 | 1 | 1 | 1050 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 512610.983 | 53639.0548 | 1073.7737 | 10875.6117 | 42763.4431 | 406290.6691 | 0.040006 | -3137268.851 | 3137268.851
C | Xist Rating 5434 | -88.05 | 221.195 | 150.296 | 35.9 | 2350.12 | 7063 | 52676.8 | 2.24 | 9.54 | 20.17 | 382.837 | 1 | 1 | 1060 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 519834.7934 | 54561.0526 | 1094.3239 | 10979.1889 | 43581.8636 | 399722.3456 | 0.040387 | -3086549.9977 | 3086549.9977
C | Xist Rating 5435 | -87.27 | 237.43 | 150.295 | 35.8 | 2332 | 6961.19 | 49857.3 | 2.23 | 8.9 | 19.996 | 334.976 | 1 | 1 | 1070 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 553686.76 | 55490.8079 | 1115.0689 | 11082.7662 | 44408.0417 | 350010.7405 | 0.040768 | -2702690.1605 | 2702690.1605
C | Xist Rating 5436 | -87.07 | 240.508 | 150.295 | 35.8 | 2339.44 | 7038.93 | 49380.6 | 2.17 | 8.79 | 19.907 | 327.478 | 1 | 1 | 1080 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 562654.0355 | 56428.3208 | 1136.0087 | 11186.3435 | 45241.9773 | 342176.6365 | 0.041149 | -2642197.2858 | 2642197.2858
C | Xist Rating 5437 | -86.84 | 244.601 | 150.295 | 35.8 | 2341.93 | 7076.3 | 48761.5 | 2.11 | 8.65 | 19.766 | 317.84 | 1 | 1 | 1090 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 572838.4199 | 57373.5912 | 1157.1433 | 11289.9207 | 46083.6705 | 332114.0581 | 0.04153 | -2564496.7232 | 2564496.7232
C | Xist Rating 5438 | -86.63 | 247.648 | 150.295 | 35.8 | 2350.34 | 7164.94 | 48308.2 | 2.07 | 8.55 | 19.764 | 310.881 | 1 | 1 | 1100 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 582057.0003 | 58326.6192 | 1178.4727 | 11393.498 | 46933.1212 | 324866.654 | 0.041911 | -2508534.1897 | 2508534.1897
C | Xist Rating 5439 | -86.54 | 249.885 | 150.294 | 35.8 | 2346.8 | 7139.64 | 48011 | 1.99 | 8.49 | 19.475 | 306.628 | 1 | 1 | 1110 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 586430.118 | 59287.4047 | 1199.9969 | 11497.0752 | 47790.3294 | 320360.9747 | 0.042292 | -2473742.528 | 2473742.528
C | Xist Rating 5440 | -85.6 | 267.939 | 150.295 | 35.8 | 2343.1 | 7174.44 | 45448.3 | 2.03 | 7.92 | 19.727 | 268.299 | 1 | 1 | 1120 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 627807.8709 | 60255.9477 | 1221.7158 | 11600.6525 | 48655.2952 | 280638.5314 | 0.042673 | -2167016.3507 | 2167016.3507
C | Xist Rating 5441 | -85.48 | 270.13 | 150.294 | 35.8 | 2343.3 | 7183.78 | 45189.4 | 1.97 | 7.86 | 19.544 | 264.866 | 1 | 1 | 1130 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 632995.629 | 61232.2483 | 1243.6296 | 11704.2297 | 49528.0186 | 277013.1037 | 0.043054 | -2139021.7588 | 2139021.7588
C | Xist Rating 5442 | -85.29 | 274.294 | 150.294 | 35.8 | 2339.66 | 7164.43 | 44681.4 | 1.92 | 7.75 | 19.372 | 257.959 | 1 | 1 | 1140 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 641754.7 | 62216.3064 | 1265.7381 | 11807.807 | 50408.4994 | 269790.6431 | 0.043435 | -2083251.8321 | 2083251.8321
C | Xist Rating 5443 | -85.07 | 278.395 | 150.293 | 35.8 | 2340.14 | 7183.83 | 44186.4 | 1.88 | 7.64 | 19.198 | 251.273 | 1 | 1 | 1150 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 651483.2753 | 63208.1221 | 1288.0414 | 11911.3842 | 51296.7378 | 262807.1085 | 0.043816 | -2029326.8297 | 2029326.8297
C | Xist Rating 5444 | -84.87 | 282.575 | 150.293 | 35.8 | 2337.86 | 7177.21 | 43703.6 | 1.83 | 7.53 | 19.052 | 244.917 | 1 | 1 | 1160 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 660620.7895 | 64207.6953 | 1310.5395 | 12014.9615 | 52192.7338 | 256158.7868 | 0.044197 | -1977990.2517 | 1977990.2517
C | Xist Rating 5445 | -84.02 | 298.796 | 150.293 | 35.8 | 2336.23 | 7222.68 | 41832.4 | 1.85 | 7.13 | 19.195 | 220.313 | 1 | 1 | 1170 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 698056.1791 | 65215.026 | 1333.2324 | 12118.5387 | 53096.4873 | 230657.0578 | 0.044578 | -1781072.6598 | 1781072.6598
C | Xist Rating 5446 | -83.89 | 299.984 | 150.293 | 35.8 | 2347.44 | 7334.73 | 41725.1 | 1.79 | 7.11 | 19.125 | 219.134 | 1 | 1 | 1180 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 704194.441 | 66230.1143 | 1356.1201 | 12222.116 | 54007.9983 | 229381.0412 | 0.044959 | -1771219.5983 | 1771219.5983
C | Xist Rating 5447 | -83.52 | 308.172 | 150.293 | 35.8 | 2338.48 | 7277.78 | 40886.1 | 1.74 | 6.93 | 18.968 | 208.869 | 1 | 1 | 1190 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 720654.0586 | 67252.9601 | 1379.2026 | 12325.6933 | 54927.2669 | 218670.6207 | 0.04534 | -1688516.5698 | 1688516.5698
C | Xist Rating 5448 | -83.33 | 310.255 | 150.293 | 35.8 | 2349.71 | 7395.41 | 40682.3 | 1.71 | 6.88 | 19.003 | 206.475 | 1 | 1 | 1200 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 729009.276 | 68283.5635 | 1402.4799 | 12429.2705 | 55854.293 | 216171.8604 | 0.045721 | -1669221.8055 | 1669221.8055
C | Xist Rating 5449 | -83.13 | 314.504 | 150.292 | 35.8 | 2346.71 | 7381.08 | 40281.4 | 1.66 | 6.8 | 18.865 | 201.821 | 1 | 1 | 1210 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 738049.6818 | 69321.9244 | 1425.9519 | 12532.8478 | 56789.0766 | 211289.2958 | 0.046102 | -1631519.9352 | 1631519.9352
C | Xist Rating 5450 | -82.24 | 332.912 | 150.292 | 35.8 | 2334.83 | 7333.65 | 38538.1 | 1.66 | 6.43 | 18.879 | 181.496 | 1 | 1 | 1220 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 777292.925 | 70368.0429 | 1449.6188 | 12636.425 | 57731.6178 | 190197.1235 | 0.046483 | -1468651.7722 | 1468651.7722
C | Xist Rating 5451 | -81.99 | 337.011 | 150.292 | 35.8 | 2340.55 | 7405.56 | 38183.3 | 1.64 | 6.35 | 18.887 | 177.607 | 1 | 1 | 1230 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 788791.0961 | 71421.9188 | 1473.4804 | 12740.0023 | 58681.9166 | 186152.3566 | 0.046864 | -1437419.154 | 1437419.154
C | Xist Rating 5452 | -81.78 | 341.25 | 150.292 | 35.8 | 2339.88 | 7414 | 37835.7 | 1.59 | 6.28 | 18.794 | 173.914 | 1 | 1 | 1240 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 798484.05 | 72483.5524 | 1497.5369 | 12843.5795 | 59639.9728 | 182270.3578 | 0.047245 | -1407443.3886 | 1407443.3886
C | Xist Rating 5453 | -81.63 | 343.478 | 150.292 | 35.8 | 2343.84 | 7461.62 | 37664.6 | 1.55 | 6.24 | 18.732 | 172.182 | 1 | 1 | 1250 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 805057.4755 | 73552.9434 | 1521.7881 | 12947.1568 | 60605.7867 | 180437.567 | 0.047626 | -1393291.0636 | 1393291.0636
C | Xist Rating 5454 | -81.32 | 349.65 | 150.292 | 35.8 | 2342.86 | 7474.68 | 37161.5 | 1.53 | 6.14 | 18.69 | 166.844 | 1 | 1 | 1260 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 819180.999 | 74630.0921 | 1546.2341 | 13050.734 | 61579.358 | 174882.2884 | 0.048007 | -1350394.6751 | 1350394.6751
C | Xist Rating 5455 | -80.45 | 367.085 | 150.292 | 35.8 | 2335.75 | 7469 | 35777.7 | 1.53 | 5.85 | 18.751 | 152.378 | 1 | 1 | 1270 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 857418.7887 | 75714.9982 | 1570.8749 | 13154.3113 | 62560.6869 | 159877.5013 | 0.048388 | -1234531.6858 | 1234531.6858
C | Xist Rating 5456 | -80.26 | 371.393 | 150.292 | 35.8 | 2332.49 | 7450.87 | 35477.4 | 1.49 | 5.79 | 18.649 | 149.493 | 1 | 1 | 1280 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 866270.4586 | 76807.6619 | 1595.7105 | 13257.8885 | 63549.7734 | 156842.5392 | 0.048769 | -1211096.5131 | 1211096.5131
C | Xist Rating 5457 | -80.05 | 375.649 | 150.292 | 35.8 | 2332.08 | 7461.79 | 35182.7 | 1.46 | 5.73 | 18.613 | 146.675 | 1 | 1 | 1290 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 876043.5199 | 77908.0831 | 1620.7408 | 13361.4658 | 64546.6173 | 153893.1162 | 0.04915 | -1188321.8504 | 1188321.8504
C | Xist Rating 5458 | -79.69 | 381.799 | 150.292 | 35.8 | 2336.19 | 7526.88 | 34751.5 | 1.44 | 5.64 | 18.651 | 142.503 | 1 | 1 | 1300 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 891955.0058 | 79016.2619 | 1645.966 | 13465.043 | 65551.2189 | 149554.1781 | 0.049531 | -1154817.7212 | 1154817.7212
C | Xist Rating 5459 | -79.48 | 385.07 | 150.292 | 35.8 | 2341.8 | 7597.15 | 34540.2 | 1.4 | 5.59 | 18.605 | 140.571 | 1 | 1 | 1310 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 901756.926 | 80132.1982 | 1671.3859 | 13568.6203 | 66563.5779 | 147512.2487 | 0.049912 | -1139050.4831 | 1139050.4831
C | Xist Rating 5460 | -78.61 | 402.603 | 150.292 | 35.8 | 2335.66 | 7600.17 | 33363 | 1.4 | 5.35 | 18.655 | 129.464 | 1 | 1 | 1320 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 940343.723 | 81255.8921 | 1697.0007 | 13672.1976 | 67583.6945 | 135993.464 | 0.050293 | -1050105.4812 | 1050105.4812
C | Xist Rating 5461 | -78.31 | 408.971 | 150.292 | 35.8 | 2332.75 | 7592.5 | 32979.9 | 1.37 | 5.28 | 18.563 | 126.093 | 1 | 1 | 1330 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 954027.1003 | 82387.3435 | 1722.8102 | 13775.7748 | 68611.5687 | 132463.5141 | 0.050674 | -1022848.1434 | 1022848.1434
C | Xist Rating 5462 | -77.96 | 415.237 | 150.291 | 35.8 | 2335.15 | 7641.2 | 32606.9 | 1.34 | 5.2 | 18.486 | 122.83 | 1 | 1 | 1340 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 969640.6806 | 83526.5524 | 1748.8145 | 13879.3521 | 69647.2003 | 129046.6461 | 0.051055 | -996463.9946 | 996463.9946
C | Xist Rating 5463 | -77.76 | 418.525 | 150.291 | 35.8 | 2339.42 | 7698.87 | 32424.1 | 1.31 | 5.16 | 18.451 | 121.305 | 1 | 1 | 1350 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 979105.7555 | 84673.5189 | 1775.0136 | 13982.9293 | 70690.5896 | 127437.7056 | 0.051436 | -984040.1829 | 984040.1829
C | Xist Rating 5464 | -77.52 | 420.554 | 150.292 | 35.8 | 2354.34 | 7871.08 | 32303.6 | 1.3 | 5.14 | 18.521 | 120.27 | 1 | 1 | 1360 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 23 | E | Rod | 990127.1044 | 85828.2429 | 1801.4075 | 14086.5066 | 71741.7363 | 126367.9937 | 0.051817 | -975780.1512 | 975780.1512
C | Xist Rating 5465 | -76.45 | 445.473 | 150.291 | 35.8 | 2329.19 | 7691.11 | 30902.5 | 1.29 | 4.86 | 18.422 | 108.387 | 1 | 1 | 1370 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1037591.2569 | 86990.7245 | 1827.9962 | 14190.0838 | 72800.6406 | 114019.0933 | 0.052198 | -880425.215 | 880425.215
C | Xist Rating 5466 | -76.34 | 447.765 | 150.291 | 35.7 | 2328.71 | 7693.6 | 30794.1 | 1.26 | 4.84 | 18.386 | 107.58 | 1 | 1 | 1380 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1042714.8331 | 88160.9636 | 1854.7797 | 14293.6611 | 73867.3025 | 113154.685 | 0.052579 | -873750.4835 | 873750.4835
C | Xist Rating 5467 | -76.06 | 453.104 | 150.291 | 35.7 | 2329.62 | 7723 | 30527.1 | 1.23 | 4.78 | 18.352 | 105.484 | 1 | 1 | 1390 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1055560.1405 | 89338.9602 | 1881.7579 | 14397.2383 | 74941.7219 | 110951.404 | 0.05296 | -856737.3318 | 856737.3318
C | Xist Rating 5468 | -75.78 | 458.441 | 150.291 | 35.7 | 2330.36 | 7750.7 | 30265.2 | 1.21 | 4.73 | 18.325 | 103.451 | 1 | 1 | 1400 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1068332.5688 | 90524.7144 | 1908.931 | 14500.8156 | 76023.8988 | 108825.1714 | 0.053341 | -840319.127 | 840319.127
C | Xist Rating 5469 | -75.44 | 464.768 | 150.291 | 35.7 | 2332.47 | 7797.78 | 29957.8 | 1.19 | 4.67 | 18.307 | 101.074 | 1 | 1 | 1410 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1084057.417 | 91718.2261 | 1936.2988 | 14604.3928 | 77113.8333 | 106342.0821 | 0.053722 | -821145.3698 | 821145.3698
C | Xist Rating 5470 | -74.52 | 483.418 | 150.291 | 35.7 | 2326.39 | 7802.43 | 29052.1 | 1.19 | 4.49 | 18.373 | 94.058 | 1 | 1 | 1420 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1124618.801 | 92919.4954 | 1963.8614 | 14707.9701 | 78211.5253 | 99070.7415 | 0.054103 | -764998.0054 | 764998.0054
C | Xist Rating 5471 | -74.35 | 486.947 | 150.291 | 35.7 | 2326.35 | 7813.67 | 28910.9 | 1.16 | 4.47 | 18.299 | 93.104 | 1 | 1 | 1430 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1132809.1534 | 94128.5222 | 1991.6188 | 14811.5474 | 79316.9748 | 98048.9813 | 0.054484 | -757108.2437 | 757108.2437
C | Xist Rating 5472 | -73.94 | 495.303 | 150.291 | 35.7 | 2324.72 | 7826.71 | 28542.1 | 1.14 | 4.39 | 18.284 | 90.414 | 1 | 1 | 1440 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1151440.7902 | 95345.3065 | 2019.571 | 14915.1246 | 80430.1819 | 95240.2086 | 0.054865 | -735419.6451 | 735419.6451
C | Xist Rating 5473 | -73.66 | 500.678 | 150.291 | 35.7 | 2325.1 | 7850.8 | 28316.9 | 1.12 | 4.35 | 18.262 | 88.829 | 1 | 1 | 1450 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1164126.4178 | 96569.8484 | 2047.718 | 15018.7019 | 81551.1465 | 93578.1626 | 0.055246 | -722585.7666 | 722585.7666
C | Xist Rating 5474 | -73.44 | 503.847 | 150.291 | 35.7 | 2331.68 | 7938.43 | 28183.7 | 1.11 | 4.32 | 18.283 | 87.898 | 1 | 1 | 1460 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1174809.973 | 97802.1478 | 2076.0598 | 15122.2791 | 82679.8687 | 92610.0628 | 0.055627 | -715110.3571 | 715110.3571
C | Xist Rating 5475 | -72.51 | 524.956 | 150.291 | 35.7 | 2316.45 | 7844.06 | 27310.5 | 1.1 | 4.16 | 18.267 | 81.746 | 1 | 1 | 1470 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1216034.3262 | 99042.2048 | 2104.5964 | 15225.8564 | 83816.3484 | 86217.1106 | 0.056008 | -665745.6741 | 665745.6741
C | Xist Rating 5476 | -72.18 | 531.326 | 150.291 | 35.7 | 2316.97 | 7873.53 | 27066.3 | 1.08 | 4.11 | 18.255 | 80.116 | 1 | 1 | 1480 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1231066.4022 | 100290.0193 | 2133.3277 | 15329.4336 | 84960.5857 | 84508.2685 | 0.056389 | -652550.4484 | 652550.4484
C | Xist Rating 5477 | -71.91 | 536.703 | 150.291 | 35.7 | 2317.66 | 7901.11 | 26866.4 | 1.06 | 4.07 | 18.24 | 78.81 | 1 | 1 | 1490 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1243895.075 | 101545.5913 | 2162.2539 | 15433.0109 | 86112.5805 | 83135.3804 | 0.05677 | -641949.3706 | 641949.3706
C | Xist Rating 5478 | -71.61 | 542.171 | 150.291 | 35.7 | 2318.66 | 7932.53 | 26670.3 | 1.04 | 4.03 | 18.22 | 77.552 | 1 | 1 | 1500 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1257110.2109 | 102808.9209 | 2191.3748 | 15536.5881 | 87272.3328 | 81811.6894 | 0.057151 | -631728.1795 | 631728.1795
C | Xist Rating 5479 | -71.24 | 548.569 | 150.291 | 35.7 | 2322.94 | 8007 | 26439 | 1.02 | 3.99 | 18.222 | 76.059 | 1 | 1 | 1510 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1274292.8729 | 104080.0081 | 2220.6906 | 15640.1654 | 88439.8427 | 80245.1786 | 0.057532 | -619631.9981 | 619631.9981
C | Xist Rating 5480 | -70.18 | 569.36 | 150.291 | 35.7 | 2320.94 | 8065.97 | 25681.2 | 1.03 | 3.84 | 18.3 | 71.122 | 1 | 1 | 1520 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1321450.3984 | 105358.8527 | 2250.2011 | 15743.7426 | 89615.1101 | 75144.3323 | 0.057913 | -580244.6154 | 580244.6154
C | Xist Rating 5481 | -69.91 | 576.102 | 150.291 | 35.7 | 2315.57 | 8025.49 | 25468.5 | 1 | 3.8 | 18.234 | 69.862 | 1 | 1 | 1530 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1334004.5081 | 106645.4549 | 2279.9064 | 15847.3199 | 90798.135 | 73802.0955 | 0.058294 | -569880.2189 | 569880.2189
C | Xist Rating 5482 | -69.67 | 579.546 | 150.291 | 35.7 | 2321.14 | 8105.07 | 25363.6 | 0.98 | 3.78 | 18.225 | 69.263 | 1 | 1 | 1540 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1345207.4024 | 107939.8147 | 2309.8065 | 15950.8971 | 91988.9175 | 73162.4256 | 0.058675 | -564940.8573 | 564940.8573
C | Xist Rating 5483 | -69.15 | 590.058 | 150.291 | 35.7 | 2319.71 | 8128.5 | 25021.2 | 0.97 | 3.72 | 18.219 | 67.181 | 1 | 1 | 1550 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1368763.4432 | 109241.932 | 2339.9013 | 16054.4744 | 93187.4576 | 70995.211 | 0.059056 | -548206.2009 | 548206.2009
C | Xist Rating 5484 | -68.85 | 593.277 | 150.291 | 35.7 | 2331.09 | 8282.65 | 24920.5 | 0.96 | 3.7 | 18.256 | 66.596 | 1 | 1 | 1560 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1382982.0819 | 110551.8068 | 2370.191 | 16158.0517 | 94393.7552 | 70385.355 | 0.059437 | -543497.0539 | 543497.0539
C | Xist Rating 5485 | -67.85 | 617.737 | 150.291 | 35.7 | 2311.38 | 8133.77 | 24162.1 | 0.95 | 3.56 | 18.21 | 62.103 | 1 | 1 | 1570 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1427824.9471 | 111869.4392 | 2400.6755 | 16261.6289 | 95607.8103 | 65711.3144 | 0.059818 | -507405.352 | 507405.352
C | Xist Rating 5486 | -67.52 | 623.234 | 150.291 | 35.7 | 2314.99 | 8199.21 | 24007.4 | 0.93 | 3.53 | 18.205 | 61.25 | 1 | 1 | 1580 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1442780.4777 | 113194.8291 | 2431.3547 | 16365.2062 | 96829.6229 | 64807.1067 | 0.0602 | -500423.2994 | 500423.2994
C | Xist Rating 5487 | -67.21 | 628.766 | 150.291 | 35.7 | 2317.32 | 8249.36 | 23854.9 | 0.91 | 3.5 | 18.194 | 60.42 | 1 | 1 | 1590 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1457052.0271 | 114527.9766 | 2462.2288 | 16468.7834 | 98059.1931 | 63926.0788 | 0.060581 | -493620.2358 | 493620.2358
C | Xist Rating 5488 | -66.78 | 636.185 | 150.291 | 35.7 | 2321.61 | 8333.51 | 23645.1 | 0.9 | 3.46 | 18.207 | 59.254 | 1 | 1 | 1600 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1476973.4578 | 115868.8815 | 2493.2976 | 16572.3607 | 99296.5209 | 62710.4016 | 0.060962 | -484233.0983 | 484233.0983
C | Xist Rating 5489 | -66.58 | 639.824 | 150.291 | 35.7 | 2323.1 | 8365.59 | 23556.5 | 0.88 | 3.45 | 18.182 | 58.815 | 1 | 1 | 1610 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1486375.1344 | 117217.5441 | 2524.5612 | 16675.9379 | 100541.6062 | 62233.979 | 0.061343 | -480554.2897 | 480554.2897
C | Xist Rating 5490 | -65.37 | 667.167 | 150.291 | 35.7 | 2308.93 | 8293.94 | 22805 | 0.89 | 3.31 | 18.208 | 54.67 | 1 | 1 | 1620 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1540441.9013 | 118573.9642 | 2556.0196 | 16779.5152 | 101794.449 | 57951.4585 | 0.061724 | -447485.8011 | 447485.8011
C | Xist Rating 5491 | -65.07 | 670.462 | 150.291 | 35.7 | 2318.81 | 8435.66 | 22723.3 | 0.87 | 3.29 | 18.23 | 54.26 | 1 | 1 | 1630 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1554673.9902 | 119938.1418 | 2587.6728 | 16883.0924 | 103055.0493 | 57507.7294 | 0.062105 | -444059.4428 | 444059.4428
C | Xist Rating 5492 | -64.79 | 676.141 | 150.291 | 35.7 | 2318.4 | 8451.91 | 22588.6 | 0.86 | 3.27 | 18.207 | 53.591 | 1 | 1 | 1640 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1567565.2944 | 121310.0769 | 2619.5208 | 16986.6697 | 104323.4072 | 56805.2278 | 0.062486 | -438634.9117 | 438634.9117
C | Xist Rating 5493 | -64.45 | 683.917 | 150.291 | 35.7 | 2315.55 | 8444.1 | 22403 | 0.84 | 3.23 | 18.18 | 52.659 | 1 | 1 | 1650 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1583644.0094 | 122689.7696 | 2651.5635 | 17090.2469 | 105599.5227 | 55815.7565 | 0.062867 | -430994.4763 | 430994.4763
C | Xist Rating 5494 | -64.09 | 691.45 | 150.291 | 35.7 | 2315.25 | 8470.21 | 22220.3 | 0.83 | 3.2 | 18.171 | 51.736 | 1 | 1 | 1660 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1600879.6125 | 124077.2199 | 2683.8011 | 17193.8242 | 106883.3957 | 54849.9843 | 0.063248 | -423537.0397 | 423537.0397
C | Xist Rating 5495 | -63.02 | 715.954 | 150.291 | 35.7 | 2303.07 | 8407.71 | 21632.6 | 0.83 | 3.1 | 18.198 | 48.748 | 1 | 1 | 1670 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1648892.1788 | 125472.4276 | 2716.2334 | 17297.4015 | 108175.0262 | 51755.389 | 0.063629 | -399641.3951 | 399641.3951
C | Xist Rating 5496 | -62.74 | 719.36 | 150.291 | 35.7 | 2310.44 | 8519.68 | 21560.3 | 0.82 | 3.08 | 18.206 | 48.417 | 1 | 1 | 1680 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1662038.1184 | 126875.393 | 2748.8606 | 17400.9787 | 109474.4143 | 51405.2064 | 0.06401 | -396937.378 | 396937.378
C | Xist Rating 5497 | -62.32 | 729.282 | 150.291 | 35.7 | 2305.38 | 8489.74 | 21345.9 | 0.8 | 3.04 | 18.178 | 47.4 | 1 | 1 | 1690 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1681272.1372 | 128286.1158 | 2781.6825 | 17504.556 | 110781.5599 | 50326.4651 | 0.064391 | -388607.6231 | 388607.6231
C | Xist Rating 5498 | -61.96 | 735.836 | 150.291 | 35.7 | 2307.62 | 8546.12 | 21205.7 | 0.79 | 3.02 | 18.179 | 46.743 | 1 | 1 | 1700 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1698029.8703 | 129704.5962 | 2814.6992 | 17608.1332 | 112096.463 | 49636.8984 | 0.064772 | -383282.9721 | 383282.9721
C | Xist Rating 5499 | -61.59 | 743.561 | 150.291 | 35.7 | 2306.98 | 8567.74 | 21044.6 | 0.78 | 2.99 | 18.17 | 45.999 | 1 | 1 | 1710 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1715380.3558 | 131130.8342 | 2847.9107 | 17711.7105 | 113419.1237 | 48856.2207 | 0.065153 | -377254.786 | 377254.786
C | Xist Rating 5500 | -60.6 | 766.123 | 150.291 | 35.7 | 2297.35 | 8527.75 | 20567.1 | 0.78 | 2.9 | 18.201 | 43.745 | 1 | 1 | 1720 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1760052.6741 | 132564.8297 | 2881.317 | 17815.2877 | 114749.5419 | 46523.6623 | 0.065534 | -359243.3885 | 359243.3885
C | Xist Rating 5501 | -60.1 | 775.915 | 150.291 | 35.7 | 2297.21 | 8564.35 | 20374.7 | 0.77 | 2.87 | 18.199 | 42.882 | 1 | 1 | 1730 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1782439.6971 | 134006.5827 | 2914.9181 | 17918.865 | 116087.7177 | 45619.5682 | 0.065915 | -352262.213 | 352262.213
C | Xist Rating 5502 | -59.86 | 780.464 | 150.291 | 35.6 | 2299.09 | 8608.08 | 20289.8 | 0.76 | 2.85 | 18.191 | 42.523 | 1 | 1 | 1740 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1794356.9778 | 135456.0932 | 2948.714 | 18022.4422 | 117433.651 | 45238.3601 | 0.066296 | -349318.6254 | 349318.6254
C | Xist Rating 5503 | -59.42 | 789.392 | 150.292 | 35.7 | 2297.79 | 8624.43 | 20124 | 0.74 | 2.82 | 18.182 | 41.803 | 1 | 1 | 1750 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1813857.0437 | 136913.3614 | 2982.7046 | 18126.0195 | 118787.3419 | 44467.7767 | 0.066677 | -343368.3847 | 343368.3847
C | Xist Rating 5504 | -59.12 | 796.063 | 150.292 | 35.7 | 2296.35 | 8630.25 | 20001.2 | 0.73 | 2.8 | 18.179 | 41.278 | 1 | 1 | 1760 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1828039.27 | 138378.387 | 3016.8901 | 18229.5967 | 120148.7903 | 43914.0793 | 0.067058 | -339092.8797 | 339092.8797
C | Xist Rating 5505 | -57.95 | 822.801 | 150.292 | 35.7 | 2285.81 | 8591.45 | 19497.8 | 0.73 | 2.71 | 18.215 | 39.06 | 1 | 1 | 1770 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1880766.7538 | 139851.1702 | 3051.2703 | 18333.174 | 121517.9962 | 41618.7233 | 0.067439 | -321368.7497 | 321368.7497
C | Xist Rating 5506 | -57.64 | 829.582 | 150.292 | 35.7 | 2284.87 | 8603.89 | 19383.4 | 0.72 | 2.69 | 18.204 | 38.597 | 1 | 1 | 1780 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1895487.0243 | 141331.7109 | 3085.8453 | 18436.7513 | 122894.9597 | 41128.6936 | 0.06782 | -317584.87 | 317584.87
C | Xist Rating 5507 | -57.67 | 833.247 | 150.292 | 35.6 | 2275.93 | 8491.03 | 19326.8 | 0.71 | 2.68 | 18.404 | 38.377 | 1 | 1 | 1790 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1896411.8447 | 142820.0092 | 3120.6151 | 18540.3285 | 124279.6807 | 40902.8864 | 0.068201 | -315841.2467 | 315841.2467
C | Xist Rating 5508 | -57.14 | 845.223 | 150.292 | 35.6 | 2273.94 | 8509.36 | 19121.9 | 0.7 | 2.65 | 18.387 | 37.53 | 1 | 1 | 1800 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1921986.3886 | 144316.065 | 3155.5797 | 18643.9058 | 125672.1592 | 40013.3261 | 0.068582 | -308972.2979 | 308972.2979
C | Xist Rating 5509 | -56.82 | 851.876 | 150.291 | 35.6 | 2275 | 8549.36 | 19012.3 | 0.69 | 2.63 | 18.382 | 37.093 | 1 | 1 | 1810 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1938017.9 | 145819.8783 | 3190.7391 | 18747.483 | 127072.3953 | 39550.0739 | 0.068963 | -305395.187 | 305395.187
C | Xist Rating 5510 | -55.69 | 878.872 | 150.292 | 35.6 | 2259.85 | 8442.37 | 18563.4 | 0.69 | 2.55 | 18.429 | 35.253 | 1 | 1 | 1820 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1986118.8892 | 147331.4492 | 3226.0933 | 18851.0603 | 128480.389 | 37647.5678 | 0.069344 | -290704.5395 | 290704.5395
C | Xist Rating 5511 | -55.66 | 874.579 | 150.292 | 35.6 | 2275.92 | 8654.17 | 18631.2 | 0.69 | 2.56 | 18.446 | 35.539 | 1 | 1 | 1830 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 1990471.8377 | 148850.7777 | 3261.6423 | 18954.6375 | 129896.1401 | 37951.2405 | 0.069725 | -293049.4193 | 293049.4193
C | Xist Rating 5512 | -55.24 | 880.037 | 150.292 | 35.6 | 2283.55 | 8787.47 | 18545.3 | 0.68 | 2.55 | 18.469 | 35.207 | 1 | 1 | 1840 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2009608.4914 | 150377.8636 | 3297.386 | 19058.2148 | 131319.6489 | 37598.2404 | 0.070106 | -290323.6458 | 290323.6458
C | Xist Rating 5513 | -54.83 | 889.082 | 150.292 | 35.6 | 2281.11 | 8786.81 | 18409.3 | 0.67 | 2.52 | 18.457 | 34.69 | 1 | 1 | 1850 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2028093.841 | 151912.7071 | 3333.3246 | 19161.792 | 132750.9151 | 37050.9839 | 0.070487 | -286097.8766 | 286097.8766
C | Xist Rating 5514 | -54.42 | 899.216 | 150.292 | 35.6 | 2276.61 | 8759.64 | 18259.1 | 0.65 | 2.5 | 18.446 | 34.122 | 1 | 1 | 1860 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2047164.1378 | 153455.3082 | 3369.4579 | 19265.3693 | 134189.9389 | 36435.2872 | 0.070868 | -281343.6295 | 281343.6295
C | Xist Rating 5515 | -53.31 | 923.999 | 150.292 | 35.6 | 2270.26 | 8767.99 | 17879.6 | 0.65 | 2.43 | 18.492 | 32.643 | 1 | 1 | 1870 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2097717.9697 | 155005.6668 | 3405.7861 | 19368.9465 | 135636.7202 | 34907.2287 | 0.071249 | -269544.3672 | 269544.3672
C | Xist Rating 5516 | -52.85 | 934.119 | 150.292 | 35.6 | 2267.89 | 8771.78 | 17738.9 | 0.64 | 2.41 | 18.484 | 32.131 | 1 | 1 | 1880 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2118479.1389 | 156563.7829 | 3442.309 | 19472.5238 | 137091.2591 | 34364.8906 | 0.07163 | -265356.5762 | 265356.5762
C | Xist Rating 5517 | -52.45 | 940.82 | 150.292 | 35.6 | 2271.3 | 8849.4 | 17646.8 | 0.64 | 2.39 | 18.497 | 31.801 | 1 | 1 | 1890 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2136884.466 | 158129.6566 | 3479.0267 | 19576.101 | 138553.5555 | 34028.1936 | 0.072011 | -262756.6915 | 262756.6915
C | Xist Rating 5518 | -52.17 | 947.979 | 150.292 | 35.6 | 2267.99 | 8825.82 | 17555.2 | 0.62 | 2.38 | 18.481 | 31.489 | 1 | 1 | 1900 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2150006.8922 | 159703.2878 | 3515.9392 | 19679.6783 | 140023.6095 | 33677.137 | 0.072392 | -260045.9254 | 260045.9254
C | Xist Rating 5519 | -51.86 | 954.859 | 150.292 | 35.6 | 2266.33 | 8827.05 | 17465.2 | 0.61 | 2.36 | 18.489 | 31.175 | 1 | 1 | 1910 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2164025.5975 | 161284.6766 | 3553.0464 | 19783.2556 | 141501.421 | 33340.7799 | 0.072773 | -257448.6649 | 257448.6649
C | Xist Rating 5520 | -50.52 | 984.96 | 150.292 | 35.6 | 2259.49 | 8847.84 | 17050.2 | 0.62 | 2.29 | 18.53 | 29.653 | 1 | 1 | 1920 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2225507.2704 | 162873.8229 | 3590.3485 | 19886.8328 | 142986.9901 | 31783.3408 | 0.073154 | -245422.5326 | 245422.5326
C | Xist Rating 5521 | -50.13 | 995.157 | 150.292 | 35.6 | 2254.33 | 8808.1 | 16923.8 | 0.61 | 2.27 | 18.524 | 29.224 | 1 | 1 | 1930 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2243412.2798 | 164470.7267 | 3627.8454 | 19990.4101 | 144480.3166 | 31326.6274 | 0.073535 | -241895.9133 | 241895.9133
C | Xist Rating 5522 | -49.78 | 998.46 | 150.292 | 35.6 | 2263.08 | 8956.73 | 16882.2 | 0.6 | 2.26 | 18.555 | 29.088 | 1 | 1 | 1940 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2259594.8568 | 166075.3881 | 3665.537 | 20093.9873 | 145981.4008 | 31175.9657 | 0.073916 | -240732.5433 | 240732.5433
C | Xist Rating 5523 | -49.47 | 1008.08 | 150.292 | 35.6 | 2255.81 | 8878.93 | 16772.2 | 0.58 | 2.24 | 18.533 | 28.734 | 1 | 1 | 1950 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2274036.9448 | 167687.807 | 3703.4235 | 20197.5646 | 147490.2424 | 30779.7751 | 0.074297 | -237673.2647 | 237673.2647
C | Xist Rating 5524 | -48.99 | 1019.24 | 150.292 | 35.6 | 2252.77 | 8875.72 | 16637.2 | 0.58 | 2.22 | 18.554 | 28.279 | 1 | 1 | 1960 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2296113.2948 | 169307.9835 | 3741.5047 | 20301.1418 | 149006.8416 | 30313.1467 | 0.074678 | -234070.0837 | 234070.0837
C | Xist Rating 5525 | -47.82 | 1046.37 | 150.292 | 35.6 | 2245.49 | 8874 | 16303.1 | 0.58 | 2.16 | 18.607 | 27.132 | 1 | 1 | 1970 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2349613.3713 | 170935.9175 | 3779.7807 | 20404.7191 | 150531.1984 | 29129.5272 | 0.075059 | -224930.4878 | 224930.4878
C | Xist Rating 5526 | -47.44 | 1054.32 | 150.292 | 35.6 | 2245.05 | 8897.55 | 16214.3 | 0.57 | 2.15 | 18.638 | 26.85 | 1 | 1 | 1980 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2367001.116 | 172571.609 | 3818.2515 | 20508.2963 | 152063.3127 | 28826.5622 | 0.07544 | -222591.0722 | 222591.0722
C | Xist Rating 5527 | -47.04 | 1064.71 | 150.292 | 35.6 | 2240.94 | 8872.31 | 16101.4 | 0.56 | 2.13 | 18.639 | 26.496 | 1 | 1 | 1990 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2385951.2274 | 174215.0581 | 3856.9171 | 20611.8736 | 153603.1845 | 28447.1204 | 0.075821 | -219661.1235 | 219661.1235
C | Xist Rating 5528 | -46.68 | 1072.78 | 150.292 | 35.7 | 2239.65 | 8882.45 | 16015 | 0.55 | 2.12 | 18.642 | 26.228 | 1 | 1 | 2000 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2402651.727 | 175866.2647 | 3895.7775 | 20715.4508 | 155150.8139 | 28156.9198 | 0.076202 | -217420.2709 | 217420.2709
C | Xist Rating 5529 | -46.38 | 1078.71 | 150.292 | 35.7 | 2240.38 | 8915.73 | 15953.9 | 0.54 | 2.11 | 18.646 | 26.046 | 1 | 1 | 2010 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2416720.3098 | 177525.2289 | 3934.8326 | 20819.0281 | 156706.2008 | 27955.9076 | 0.076583 | -215868.1082 | 215868.1082
C | Xist Rating 5530 | -45.12 | 1109.26 | 150.292 | 35.7 | 2230.48 | 8882.9 | 15614.9 | 0.54 | 2.05 | 18.683 | 24.949 | 1 | 1 | 2020 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2474182.2448 | 179191.9506 | 3974.0826 | 20922.6054 | 158269.3452 | 26822.9973 | 0.076964 | -207120.0749 | 207120.0749
C | Xist Rating 5531 | -44.61 | 1120.37 | 150.292 | 35.7 | 2229.53 | 8911.08 | 15499.8 | 0.54 | 2.03 | 18.686 | 24.596 | 1 | 1 | 2030 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2497898.5261 | 180866.4298 | 4013.5273 | 21026.1826 | 159840.2472 | 26461.077 | 0.077345 | -204325.4226 | 204325.4226
C | Xist Rating 5532 | -44.33 | 1127.73 | 150.292 | 35.7 | 2226.78 | 8893 | 15431.8 | 0.53 | 2.02 | 18.68 | 24.405 | 1 | 1 | 2040 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2511206.6094 | 182548.6666 | 4053.1669 | 21129.7599 | 161418.9067 | 26249.8691 | 0.077726 | -202694.5313 | 202694.5313
C | Xist Rating 5533 | -43.92 | 1134.27 | 150.292 | 35.7 | 2230.87 | 8985.07 | 15364.2 | 0.52 | 2.01 | 18.7 | 24.202 | 1 | 1 | 2050 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2530408.9149 | 184238.6609 | 4093.0012 | 21233.3371 | 163005.3238 | 26027.2823 | 0.078107 | -200975.7746 | 200975.7746
C | Xist Rating 5534 | -43.55 | 1145.06 | 150.292 | 35.7 | 2224.78 | 8925.86 | 15264.3 | 0.51 | 1.99 | 18.683 | 23.917 | 1 | 1 | 2060 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2547506.5868 | 185936.4128 | 4133.0303 | 21336.9144 | 164599.4984 | 25717.601 | 0.078488 | -198584.4983 | 198584.4983
C | Xist Rating 5535 | -42.22 | 1177.86 | 150.292 | 35.7 | 2214.55 | 8892.61 | 14936.2 | 0.51 | 1.94 | 18.721 | 22.916 | 1 | 1 | 2070 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2608429.863 | 187641.9222 | 4173.2542 | 21440.4916 | 166201.4306 | 24684.1334 | 0.078869 | -190604.3349 | 190604.3349
C | Xist Rating 5536 | -41.92 | 1185.02 | 150.292 | 35.7 | 2213.36 | 8898.93 | 14873.5 | 0.51 | 1.93 | 18.717 | 22.746 | 1 | 1 | 2080 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2622875.8672 | 189355.1892 | 4213.6729 | 21544.0689 | 167811.1203 | 24511.6782 | 0.07925 | -189272.6815 | 189272.6815
C | Xist Rating 5537 | -41.53 | 1194.26 | 150.292 | 35.7 | 2211.5 | 8903.13 | 14790.8 | 0.5 | 1.91 | 18.715 | 22.515 | 1 | 1 | 2090 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2641105.99 | 191076.2136 | 4254.2864 | 21647.6461 | 169428.5675 | 24258.4354 | 0.079631 | -187317.2082 | 187317.2082
C | Xist Rating 5538 | -41.11 | 1203.51 | 150.292 | 35.7 | 2211.11 | 8931.2 | 14709.1 | 0.49 | 1.9 | 18.716 | 22.29 | 1 | 1 | 2100 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2661092.9961 | 192804.9957 | 4295.0947 | 21751.2234 | 171053.7723 | 24011.3971 | 0.080012 | -185409.6438 | 185409.6438
C | Xist Rating 5539 | -40.75 | 1211.68 | 150.292 | 35.7 | 2210.29 | 8947.93 | 14638.6 | 0.49 | 1.89 | 18.715 | 22.098 | 1 | 1 | 2110 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2678164.1872 | 194541.5352 | 4336.0977 | 21854.8006 | 172686.7346 | 23816.0699 | 0.080393 | -183901.3786 | 183901.3786
C | Xist Rating 5540 | -39.52 | 1242.67 | 150.292 | 35.7 | 2200.34 | 8906.79 | 14358.9 | 0.49 | 1.84 | 18.749 | 21.294 | 1 | 1 | 2120 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2734296.5078 | 196285.8323 | 4377.2956 | 21958.3779 | 174327.4545 | 22986.8109 | 0.080774 | -177498.0606 | 177498.0606
C | Xist Rating 5541 | -39.06 | 1254.12 | 150.292 | 35.7 | 2197.74 | 8906.53 | 14263.6 | 0.48 | 1.83 | 18.745 | 21.038 | 1 | 1 | 2130 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2756229.6888 | 198037.887 | 4418.6882 | 22061.9551 | 175975.9319 | 22706.9891 | 0.081155 | -175337.3511 | 175337.3511
C | Xist Rating 5542 | -38.67 | 1265.6 | 150.292 | 35.7 | 2192.2 | 8857.93 | 14169.8 | 0.47 | 1.81 | 18.741 | 20.788 | 1 | 1 | 2140 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2774448.32 | 199797.6992 | 4460.2756 | 22165.5324 | 177632.1668 | 22433.2362 | 0.081536 | -173223.5038 | 173223.5038
C | Xist Rating 5543 | -38.43 | 1271.68 | 150.292 | 35.7 | 2191.37 | 8865.45 | 14123.2 | 0.47 | 1.8 | 18.742 | 20.673 | 1 | 1 | 2150 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2786721.4016 | 201565.2689 | 4502.0578 | 22269.1097 | 179296.1593 | 22317.8025 | 0.081917 | -172332.155 | 172332.155
C | Xist Rating 5544 | -38.07 | 1279.8 | 150.292 | 35.7 | 2190.25 | 8876.3 | 14059 | 0.46 | 1.79 | 18.753 | 20.506 | 1 | 1 | 2160 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2803081.95 | 203340.5962 | 4544.0348 | 22372.6869 | 180967.9093 | 22130.6654 | 0.082298 | -170887.1322 | 170887.1322
C | Xist Rating 5545 | -36.8 | 1313.25 | 150.292 | 35.7 | 2178.84 | 8816.03 | 13785.9 | 0.46 | 1.75 | 18.784 | 19.765 | 1 | 1 | 2170 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2861361.63 | 205123.681 | 4586.2066 | 22476.2642 | 182647.4168 | 21366.3919 | 0.082679 | -164985.6146 | 164985.6146
C | Xist Rating 5546 | -36.31 | 1324.47 | 150.292 | 35.7 | 2177.9 | 8841.85 | 13699 | 0.46 | 1.74 | 18.787 | 19.541 | 1 | 1 | 2180 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2884563.213 | 206914.5234 | 4628.5732 | 22579.8414 | 184334.6819 | 21137.7762 | 0.08306 | -163220.3051 | 163220.3051
C | Xist Rating 5547 | -35.98 | 1332.82 | 150.292 | 35.7 | 2176.26 | 8843.85 | 13638.9 | 0.45 | 1.73 | 18.784 | 19.395 | 1 | 1 | 2190 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2900562.8532 | 208713.1233 | 4671.1346 | 22683.4187 | 186029.7046 | 20971.4543 | 0.083441 | -161936.0109 | 161936.0109
C | Xist Rating 5548 | -35.69 | 1341.58 | 150.292 | 35.7 | 2172.33 | 8807.87 | 13579.5 | 0.44 | 1.72 | 18.779 | 19.255 | 1 | 1 | 2200 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2914354.4814 | 210519.4807 | 4713.8907 | 22786.9959 | 187732.4848 | 20811.1128 | 0.083822 | -160697.8964 | 160697.8964
C | Xist Rating 5549 | -35.23 | 1353.06 | 150.292 | 35.7 | 2169.79 | 8806.89 | 13495.4 | 0.44 | 1.7 | 18.778 | 19.045 | 1 | 1 | 2210 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2935856.0574 | 212333.5957 | 4756.8417 | 22890.5732 | 189443.0225 | 20596.6883 | 0.084203 | -159042.1672 | 159042.1672
C | Xist Rating 5550 | -33.92 | 1386.37 | 150.292 | 35.7 | 2161.11 | 8787.8 | 13246.2 | 0.44 | 1.66 | 18.816 | 18.402 | 1 | 1 | 2220 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 2996098.0707 | 214155.4682 | 4799.9874 | 22994.1504 | 191161.3178 | 19934.3012 | 0.084584 | -153927.3896 | 153927.3896
C | Xist Rating 5551 | -33.52 | 1395.59 | 150.292 | 35.7 | 2160.7 | 8813.43 | 13182.7 | 0.43 | 1.65 | 18.817 | 18.25 | 1 | 1 | 2230 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3015451.313 | 215985.0983 | 4843.3279 | 23097.7277 | 192887.3706 | 19761.3952 | 0.084965 | -152592.2552 | 152592.2552
C | Xist Rating 5552 | -33.11 | 1406.35 | 150.292 | 35.7 | 2157.97 | 8804.54 | 13111.9 | 0.43 | 1.64 | 18.812 | 18.085 | 1 | 1 | 2240 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3034861.1095 | 217822.4859 | 4886.8633 | 23201.3049 | 194621.1809 | 19593.4539 | 0.085346 | -151295.4577 | 151295.4577
C | Xist Rating 5553 | -32.65 | 1418.14 | 150.292 | 35.7 | 2155.35 | 8801.44 | 13034.1 | 0.42 | 1.63 | 18.808 | 17.903 | 1 | 1 | 2250 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3056588.049 | 219667.631 | 4930.5934 | 23304.8822 | 196362.7488 | 19388.9308 | 0.085727 | -149716.1842 | 149716.1842
C | Xist Rating 5554 | -32.39 | 1424.18 | 150.292 | 35.7 | 2155.39 | 8822.36 | 12995.6 | 0.42 | 1.62 | 18.809 | 17.818 | 1 | 1 | 2260 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3069663.3302 | 221520.5337 | 4974.5182 | 23408.4595 | 198112.0742 | 19304.2418 | 0.086108 | -149062.2385 | 149062.2385
C | Xist Rating 5555 | -31.03 | 1460.05 | 150.292 | 35.7 | 2145.31 | 8784.52 | 12751.9 | 0.42 | 1.59 | 18.844 | 17.222 | 1 | 1 | 2270 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3132259.8655 | 223381.1939 | 5018.6379 | 23512.0367 | 199869.1572 | 18690.3336 | 0.086489 | -144321.8017 | 144321.8017
C | Xist Rating 5556 | -30.63 | 1470.75 | 150.292 | 35.7 | 2142.75 | 8777.65 | 12686.2 | 0.41 | 1.58 | 18.837 | 17.075 | 1 | 1 | 2280 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3151449.5625 | 225249.6117 | 5062.9524 | 23615.614 | 201633.9977 | 18521.67 | 0.08687 | -143019.4265 | 143019.4265
C | Xist Rating 5557 | -30.14 | 1483.38 | 150.292 | 35.7 | 2140.33 | 8780.97 | 12606.9 | 0.41 | 1.56 | 18.834 | 16.893 | 1 | 1 | 2290 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3174922.7154 | 227125.787 | 5107.4617 | 23719.1912 | 203406.5957 | 18335.999 | 0.087251 | -141585.7236 | 141585.7236
C | Xist Rating 5558 | -29.79 | 1491.89 | 150.292 | 35.7 | 2139.34 | 8792.26 | 12557 | 0.4 | 1.56 | 18.833 | 16.786 | 1 | 1 | 2300 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3191659.9526 | 229009.7198 | 5152.1657 | 23822.7685 | 205186.9513 | 18208.8825 | 0.087632 | -140604.1639 | 140604.1639
| Xist Rating 5559 | -29.48 | 1500.66 | 150.292 | 35.6 | 2137.02 | 8781.06 | 12507.5 | 0.4 | 1.55 | 18.832 | 16.683 | 1 | 1 | 2310 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3206940.4332 | 230901.4102 | 5197.0645 | 23926.3457 | 206975.0645 | 18105.2525 | 0.088013 | -139803.9603 | 139803.9603
| Xist Rating 5560 | -28.07 | 1537.45 | 150.292 | 35.7 | 2128.19 | 8764.45 | 12277 | 0.4 | 1.51 | 18.868 | 16.145 | 1 | 1 | 2320 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3271985.7155 | 232800.8581 | 5242.1582 | 24029.923 | 208770.9351 | 17551.4144 | 0.088394 | -135527.3693 | 135527.3693
| Xist Rating 5561 | -27.68 | 1548.19 | 150.292 | 35.6 | 2125.42 | 8753.01 | 12216.7 | 0.39 | 1.5 | 18.861 | 16.017 | 1 | 1 | 2330 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3290553.9898 | 234708.0636 | 5287.4466 | 24133.5002 | 210574.5633 | 17401.8784 | 0.088775 | -134372.6925 | 134372.6925
| Xist Rating 5562 | -27.3 | 1558.9 | 150.292 | 35.6 | 2122.8 | 8743.94 | 12157.1 | 0.39 | 1.49 | 18.855 | 15.891 | 1 | 1 | 2340 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3309232.92 | 236623.0266 | 5332.9298 | 24237.0775 | 212385.9491 | 17274.0794 | 0.089156 | -133385.8623 | 133385.8623
| Xist Rating 5563 | -26.95 | 1568.61 | 150.292 | 35.6 | 2120.41 | 8734.63 | 12104.6 | 0.38 | 1.49 | 18.849 | 15.783 | 1 | 1 | 2350 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3326096.3301 | 238545.7471 | 5378.6078 | 24340.6547 | 214205.0924 | 17145.1161 | 0.089537 | -132390.0418 | 132390.0418
| Xist Rating 5564 | -26.53 | 1580.45 | 150.292 | 35.6 | 2117.3 | 8720.97 | 12039.8 | 0.38 | 1.48 | 18.848 | 15.646 | 1 | 1 | 2360 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3346286.785 | 240476.2252 | 5424.4805 | 24444.232 | 216031.9932 | 17006.0122 | 0.089918 | -131315.9186 | 131315.9186
| Xist Rating 5565 | -25.29 | 1614.2 | 150.292 | 35.6 | 2108.75 | 8693.83 | 11846.7 | 0.38 | 1.45 | 18.872 | 15.218 | 1 | 1 | 2370 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3403944.25 | 242414.4608 | 5470.5481 | 24547.8092 | 217866.6516 | 16565.7142 | 0.090299 | -127916.0541 | 127916.0541
| Xist Rating 5566 | -24.91 | 1625.14 | 150.292 | 35.6 | 2105.77 | 8677.63 | 11791.1 | 0.38 | 1.44 | 18.863 | 15.107 | 1 | 1 | 2380 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3422171.0578 | 244360.454 | 5516.8105 | 24651.3865 | 219709.0675 | 16453.2906 | 0.09068 | -127047.9485 | 127047.9485
| Xist Rating 5567 | -24.48 | 1636.54 | 150.292 | 35.6 | 2103.93 | 8684.63 | 11730 | 0.37 | 1.43 | 18.865 | 14.98 | 1 | 1 | 2390 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 22 | E | Rod | 3443165.6022 | 246314.2047 | 5563.2676 | 24754.9638 | 221559.241 | 16304.4854 | 0.091061 | -125898.9148 | 125898.9148
C | Xist Rating 5571 | -15.69 | 1879.84 | 150.292 | 35.6 | 2046.58 | 8520.09 | 10537.8 | 0.39 | 1.25 | 18.891 | 12.557 | 1 | 1 | 2430 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3847242.9472 | 254206.783 | 5751.0441 | 25169.2728 | 229037.5102 | 13842.9204 | 0.092585 | -106891.3619 | 106891.3619
C | Xist Rating 5572 | -15.67 | 1881.21 | 150.292 | 35.6 | 2046.26 | 8514.53 | 10537.8 | 0.38 | 1.25 | 18.883 | 12.568 | 1 | 1 | 2440 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3849444.7746 | 256199.3214 | 5798.4752 | 25272.85 | 230926.4714 | 13836.6523 | 0.092966 | -106842.9617 | 106842.9617
C | Xist Rating 5573 | -15.65 | 1882.54 | 150.292 | 35.6 | 2046.05 | 8510.96 | 10537.8 | 0.38 | 1.25 | 18.877 | 12.579 | 1 | 1 | 2450 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3851770.967 | 258199.6173 | 5846.1011 | 25376.4273 | 232823.1901 | 13851.0418 | 0.093347 | -106954.0736 | 106954.0736
C | Xist Rating 5574 | -15.64 | 1884.01 | 150.292 | 35.6 | 2045.55 | 8502.25 | 10537.8 | 0.37 | 1.25 | 18.87 | 12.59 | 1 | 1 | 2460 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3853836.6555 | 260207.6708 | 5893.9217 | 25480.0045 | 234727.6663 | 13844.5797 | 0.093728 | -106904.1747 | 106904.1747
C | Xist Rating 5575 | -15.67 | 1885.36 | 150.292 | 35.6 | 2043.75 | 8471.21 | 10537.9 | 0.36 | 1.25 | 18.916 | 12.601 | 1 | 1 | 2470 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3853204.5 | 262223.4819 | 5941.9372 | 25583.5818 | 236639.9001 | 13840.074 | 0.094109 | -106869.3828 | 106869.3828
C | Xist Rating 5576 | -15.63 | 1886.71 | 150.292 | 35.7 | 2043.44 | 8465.81 | 10537.9 | 0.36 | 1.25 | 18.912 | 12.611 | 1 | 1 | 2480 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3855378.6824 | 264247.0504 | 5990.1474 | 25687.159 | 238559.8914 | 13853.3514 | 0.09449 | -106971.907 | 106971.907
C | Xist Rating 5577 | -15.61 | 1888.11 | 150.292 | 35.6 | 2043.35 | 8464.29 | 10537.8 | 0.35 | 1.25 | 18.902 | 12.622 | 1 | 1 | 2490 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3858069.5685 | 266278.3766 | 6038.5525 | 25790.7363 | 240487.6403 | 13846.3277 | 0.094871 | -106917.672 | 106917.672
C | Xist Rating 5578 | -15.58 | 1889.09 | 150.292 | 35.6 | 2043.67 | 8469.89 | 10537.8 | 0.35 | 1.25 | 18.898 | 12.631 | 1 | 1 | 2500 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3860676.5603 | 268317.4602 | 6087.1523 | 25894.3136 | 242423.1467 | 13858.4827 | 0.095252 | -107011.5302 | 107011.5302
C | Xist Rating 5579 | -15.58 | 1890.94 | 150.292 | 35.6 | 2042.35 | 8447.23 | 10537.8 | 0.34 | 1.25 | 18.891 | 12.644 | 1 | 1 | 2510 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3861961.309 | 270364.3014 | 6135.9469 | 25997.8908 | 244366.4106 | 13853.4182 | 0.095633 | -106972.4229 | 106972.4229
C | Xist Rating 5580 | -15.57 | 1892.4 | 150.292 | 35.6 | 2041.71 | 8436.34 | 10537.8 | 0.34 | 1.25 | 18.929 | 12.654 | 1 | 1 | 2520 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3863732.004 | 272418.9001 | 6184.9363 | 26101.4681 | 246317.4321 | 13868.1416 | 0.096014 | -107086.1136 | 107086.1136
C | Xist Rating 5581 | -15.56 | 1893.74 | 150.292 | 35.6 | 2041.2 | 8427.65 | 10537.8 | 0.33 | 1.25 | 18.923 | 12.665 | 1 | 1 | 2530 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3865502.088 | 274481.2564 | 6234.1205 | 26205.0453 | 248276.2111 | 13860.7587 | 0.096395 | -107029.1048 | 107029.1048
C | Xist Rating 5582 | -15.54 | 1894.89 | 150.292 | 35.6 | 2041.07 | 8425.32 | 10537.8 | 0.33 | 1.25 | 18.919 | 12.674 | 1 | 1 | 2540 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3867603.1323 | 276551.3702 | 6283.4995 | 26308.6226 | 250242.7477 | 13872.754 | 0.096776 | -107121.7294 | 107121.7294
C | Xist Rating 5583 | -15.5 | 1896.43 | 150.292 | 35.6 | 2040.96 | 8423.64 | 10537.7 | 0.32 | 1.25 | 18.911 | 12.685 | 1 | 1 | 2550 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3870537.7728 | 278629.2416 | 6333.0732 | 26412.1998 | 252217.0418 | 13865.0585 | 0.097157 | -107062.3063 | 107062.3063
C | Xist Rating 5584 | -15.49 | 1897.88 | 150.292 | 35.6 | 2040.5 | 8415.68 | 10537.7 | 0.32 | 1.25 | 18.905 | 12.696 | 1 | 1 | 2560 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3872624.14 | 280714.8705 | 6382.8418 | 26515.7771 | 254199.0934 | 13878.9742 | 0.097538 | -107169.7599 | 107169.7599
C | Xist Rating 5585 | -15.47 | 1899.27 | 150.292 | 35.6 | 2040.07 | 8408.47 | 10537.7 | 0.31 | 1.25 | 18.902 | 12.706 | 1 | 1 | 2570 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3874643.7489 | 282808.257 | 6432.8051 | 26619.3543 | 256188.9026 | 13870.1853 | 0.097919 | -107101.8945 | 107101.8945
C | Xist Rating 5586 | -15.46 | 1900.64 | 150.293 | 35.6 | 2039.78 | 8403.48 | 10537.7 | 0.31 | 1.25 | 18.954 | 12.716 | 1 | 1 | 2580 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3876887.4592 | 284909.4009 | 6482.9633 | 26722.9316 | 258186.4693 | 13885.0611 | 0.0983 | -107216.7613 | 107216.7613
C | Xist Rating 5587 | -15.44 | 1902 | 150.293 | 35.6 | 2039.4 | 8397.15 | 10537.6 | 0.3 | 1.25 | 18.951 | 12.726 | 1 | 1 | 2590 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3878938.8 | 287018.3025 | 6533.3162 | 26826.5088 | 260191.7936 | 13875.9706 | 0.098681 | -107146.5667 | 107146.5667
C | Xist Rating 5588 | -15.42 | 1903.17 | 150.293 | 35.6 | 2039.3 | 8395.43 | 10537.6 | 0.3 | 1.25 | 18.947 | 12.735 | 1 | 1 | 2600 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3881134.581 | 289134.9615 | 6583.8639 | 26930.0861 | 262204.8754 | 13887.7256 | 0.099062 | -107237.3361 | 107237.3361
C | Xist Rating 5589 | -15.41 | 1904.86 | 150.293 | 35.6 | 2038.45 | 8381.12 | 10537.6 | 0.3 | 1.25 | 18.945 | 12.747 | 1 | 1 | 2610 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3882961.867 | 291259.3781 | 6634.6064 | 27033.6633 | 264225.7148 | 13902.6653 | 0.099443 | -107352.6962 | 107352.6962
C | Xist Rating 5590 | -15.37 | 1906.26 | 150.293 | 35.6 | 2038.35 | 8379.43 | 10537.6 | 0.29 | 1.25 | 18.945 | 12.757 | 1 | 1 | 2620 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3885625.071 | 293391.5523 | 6685.5437 | 27137.2406 | 266254.3117 | 13893.3488 | 0.099824 | -107280.7564 | 107280.7564
C | Xist Rating 5591 | -15.34 | 1907.68 | 150.293 | 35.6 | 2038.19 | 8376.62 | 10537.6 | 0.29 | 1.25 | 18.984 | 12.767 | 1 | 1 | 2630 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3888214.2992 | 295531.484 | 6736.6758 | 27240.8179 | 268290.6661 | 13907.5298 | 0.10021 | -107390.2583 | 107390.2583
C | Xist Rating 5592 | -15.3 | 1908.93 | 150.293 | 35.6 | 2038.38 | 8379.82 | 10537.6 | 0.28 | 1.25 | 18.984 | 12.777 | 1 | 1 | 2640 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3891124.7334 | 297679.1732 | 6788.0027 | 27344.3951 | 270334.7781 | 13897.9174 | 0.10059 | -107316.0342 | 107316.0342
C | Xist Rating 5593 | -15.28 | 1910.43 | 150.293 | 35.6 | 2038.03 | 8373.96 | 10537.6 | 0.28 | 1.25 | 18.98 | 12.787 | 1 | 1 | 2650 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3893513.6529 | 299834.62 | 6839.5243 | 27447.9724 | 272386.6476 | 13910.552 | 0.10097 | -107413.5953 | 107413.5953
C | Xist Rating 5594 | -15.23 | 1911.77 | 150.293 | 35.6 | 2038.4 | 8380.13 | 10537.6 | 0.28 | 1.25 | 18.981 | 12.797 | 1 | 1 | 2660 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3896951.968 | 301997.8243 | 6891.2408 | 27551.5496 | 274446.2746 | 13923.3525 | 0.10135 | -107512.4376 | 107512.4376
C | Xist Rating 5595 | -15.16 | 1913.16 | 150.293 | 35.6 | 2039.61 | 8400.68 | 10537.6 | 0.27 | 1.25 | 18.98 | 12.807 | 1 | 1 | 2670 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3902100.2676 | 304168.7861 | 6943.152 | 27655.1269 | 276513.6592 | 13913.3707 | 0.10173 | -107435.3604 | 107435.3604
C | Xist Rating 5596 | -15.15 | 1914.58 | 150.293 | 35.6 | 2038.86 | 8387.88 | 10537.7 | 0.27 | 1.25 | 19.017 | 12.817 | 1 | 1 | 2680 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3903560.5788 | 306347.5055 | 6995.258 | 27758.7041 | 278588.8014 | 13927.2529 | 0.10211 | -107542.5548 | 107542.5548
C | Xist Rating 5597 | -15.08 | 1915.95 | 150.293 | 35.6 | 2039.67 | 8401.85 | 10537.6 | 0.26 | 1.25 | 19.017 | 12.827 | 1 | 1 | 2690 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3907905.7365 | 308533.9824 | 7047.5588 | 27862.2814 | 280671.701 | 13917.009 | 0.10249 | -107463.4547 | 107463.4547
C | Xist Rating 5598 | -15.02 | 1917.16 | 150.293 | 35.6 | 2040.77 | 8420.55 | 10537.5 | 0.26 | 1.25 | 19.014 | 12.836 | 1 | 1 | 2700 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3912482.6132 | 310728.2169 | 7100.0544 | 27965.8586 | 282762.3583 | 13928.4774 | 0.10287 | -107552.0106 | 107552.0106
C | Xist Rating 5599 | -15.01 | 1918.81 | 150.293 | 35.6 | 2039.96 | 8406.83 | 10537.4 | 0.26 | 1.25 | 19.009 | 12.847 | 1 | 1 | 2710 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3914295.6476 | 312930.2089 | 7152.7448 | 28069.4359 | 284860.773 | 13941.959 | 0.10325 | -107656.1115 | 107656.1115
C | Xist Rating 5600 | -14.99 | 1920.16 | 150.293 | 35.6 | 2039.36 | 8396.5 | 10537.5 | 0.25 | 1.25 | 19.004 | 12.857 | 1 | 1 | 2720 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3915897.4976 | 315139.9585 | 7205.63 | 28173.0131 | 286966.9453 | 13931.2306 | 0.10363 | -107573.2697 | 107573.2697
C | Xist Rating 5601 | -14.99 | 1921.48 | 150.293 | 35.6 | 2038.74 | 8386.07 | 10537.5 | 0.25 | 1.25 | 19.041 | 12.866 | 1 | 1 | 2730 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3917398.1352 | 317357.4656 | 7258.71 | 28276.5904 | 289080.8752 | 13943.8386 | 0.10402 | -107670.6257 | 107670.6257
C | Xist Rating 5602 | -14.99 | 1922.76 | 150.293 | 35.6 | 2037.74 | 8369.19 | 10537.5 | 0.25 | 1.25 | 19.034 | 12.876 | 1 | 1 | 2740 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3918084.9624 | 319582.7302 | 7311.9847 | 28380.1677 | 291202.5625 | 13956.1424 | 0.1044 | -107765.6325 | 107765.6325
C | Xist Rating 5603 | -14.99 | 1924.31 | 150.293 | 35.6 | 2036.72 | 8352.04 | 10537.5 | 0.25 | 1.25 | 19.03 | 12.886 | 1 | 1 | 2750 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3919280.6632 | 321815.7524 | 7365.4543 | 28483.7449 | 293332.0075 | 13968.5371 | 0.10478 | -107861.341 | 107861.341
C | Xist Rating 5604 | -14.99 | 1925.73 | 150.293 | 35.6 | 2035.78 | 8336.23 | 10537.5 | 0.24 | 1.25 | 19.026 | 12.896 | 1 | 1 | 2760 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3920362.6194 | 324056.5321 | 7419.1186 | 28587.3222 | 295469.2099 | 13957.3927 | 0.10516 | -107775.2868 | 107775.2868
C | Xist Rating 5605 | -15.01 | 1926.97 | 150.293 | 35.6 | 2034.8 | 8319.79 | 10537.4 | 0.24 | 1.25 | 19.024 | 12.905 | 1 | 1 | 2770 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3920998.556 | 326305.0693 | 7472.9777 | 28690.8994 | 297614.1699 | 13968.7264 | 0.10554 | -107862.8026 | 107862.8026
C | Xist Rating 5606 | -14.99 | 1928.52 | 150.293 | 35.6 | 2034.28 | 8311.14 | 10537.5 | 0.24 | 1.25 | 19.065 | 12.915 | 1 | 1 | 2780 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3923149.6656 | 328561.3641 | 7527.0316 | 28794.4767 | 299766.8875 | 13982.3842 | 0.10592 | -107968.2642 | 107968.2642
C | Xist Rating 5607 | -15 | 1929.93 | 150.293 | 35.6 | 2033.15 | 8292.23 | 10537.5 | 0.23 | 1.25 | 19.06 | 12.925 | 1 | 1 | 2790 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3923837.1795 | 330825.4165 | 7581.2803 | 28898.0539 | 301927.3625 | 13970.8335 | 0.1063 | -107879.0729 | 107879.0729
C | Xist Rating 5608 | -14.95 | 1930.9 | 150.293 | 35.6 | 2034.05 | 8307.28 | 10537.6 | 0.23 | 1.25 | 19.067 | 12.932 | 1 | 1 | 2800 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3927547.145 | 333097.2264 | 7635.7238 | 29001.6312 | 304095.5952 | 13980.2701 | 0.10668 | -107951.9397 | 107951.9397
C | Xist Rating 5609 | -14.94 | 1932.64 | 150.293 | 35.6 | 2033.17 | 8292.55 | 10537.6 | 0.23 | 1.25 | 19.07 | 12.944 | 1 | 1 | 2810 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3929385.6688 | 335376.7938 | 7690.3621 | 29105.2084 | 306271.5853 | 13994.7847 | 0.10706 | -108064.0179 | 108064.0179
C | Xist Rating 5610 | -14.94 | 1934.12 | 150.293 | 35.6 | 2032.14 | 8275.5 | 10537.6 | 0.23 | 1.25 | 19.069 | 12.954 | 1 | 1 | 2820 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3930402.6168 | 337664.1187 | 7745.1952 | 29208.7857 | 308455.333 | 14007.1067 | 0.10744 | -108159.1648 | 108159.1648
C | Xist Rating 5611 | -14.87 | 1935.49 | 150.293 | 35.6 | 2032.99 | 8289.59 | 10537.6 | 0.22 | 1.25 | 19.122 | 12.963 | 1 | 1 | 2830 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3934831.8151 | 339959.2012 | 7800.223 | 29312.3629 | 310646.8383 | 13995.7085 | 0.10783 | -108071.151 | 108071.151
C | Xist Rating 5612 | -14.77 | 1936.81 | 150.293 | 35.6 | 2034.68 | 8317.64 | 10537.7 | 0.22 | 1.25 | 19.138 | 12.972 | 1 | 1 | 2840 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3940788.5708 | 342262.0413 | 7855.4457 | 29415.9402 | 312846.1011 | 14007.3888 | 0.10821 | -108161.3431 | 108161.3431
C | Xist Rating 5613 | -14.76 | 1938.25 | 150.293 | 35.6 | 2033.97 | 8305.76 | 10537.7 | 0.22 | 1.25 | 19.137 | 12.982 | 1 | 1 | 2850 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3942342.3525 | 344572.6389 | 7910.8631 | 29519.5175 | 315053.1214 | 14019.6329 | 0.10859 | -108255.8892 | 108255.8892
C | Xist Rating 5614 | -14.45 | 1939.66 | 150.293 | 35.6 | 2040.54 | 8416.35 | 10537.8 | 0.21 | 1.25 | 19.188 | 12.992 | 1 | 1 | 2860 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3957953.8164 | 346890.994 | 7966.4753 | 29623.0947 | 317267.8993 | 14008.7447 | 0.10897 | -108171.8136 | 108171.8136
C | Xist Rating 5615 | -14.7 | 1940.85 | 150.293 | 35.6 | 2033.93 | 8305.12 | 10537.7 | 0.21 | 1.25 | 19.136 | 13 | 1 | 1 | 2870 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3947553.0405 | 349217.1066 | 8022.2824 | 29726.672 | 319490.4347 | 14017.4541 | 0.10935 | -108239.065 | 108239.065
C | Xist Rating 5616 | -14.37 | 1942.36 | 150.293 | 35.6 | 2040.97 | 8423.65 | 10537.8 | 0.21 | 1.25 | 19.234 | 13.01 | 1 | 1 | 2880 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3964298.4892 | 351550.9768 | 8078.2842 | 29830.2492 | 321720.7276 | 14032.2972 | 0.10973 | -108353.6792 | 108353.6792
C | Xist Rating 5617 | -13.69 | 1943.7 | 150.293 | 35.6 | 2056.78 | 8699.53 | 10538 | 0.21 | 1.25 | 19.317 | 13.021 | 1 | 1 | 2890 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 3997763.286 | 353892.6046 | 8134.4807 | 29933.8265 | 323958.7781 | 14047.7891 | 0.11011 | -108473.304 | 108473.304
C | Xist Rating 5618 | -13.18 | 1945.09 | 150.293 | 35.6 | 2068.43 | 8911.73 | 10538.1 | 0.2 | 1.25 | 19.371 | 13.031 | 1 | 1 | 2900 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 4023282.5087 | 356241.9899 | 8190.8721 | 30037.4037 | 326204.5861 | 14036.2859 | 0.11049 | -108384.4792 | 108384.4792
C | Xist Rating 5619 | -12.95 | 1946.63 | 150.293 | 35.6 | 2072.84 | 8994.12 | 10538.1 | 0.2 | 1.25 | 19.391 | 13.041 | 1 | 1 | 2910 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 4035052.5292 | 358599.1327 | 8247.4583 | 30140.981 | 328458.1517 | 14048.9292 | 0.11087 | -108482.1077 | 108482.1077
C | Xist Rating 5620 | -12.75 | 1948.02 | 150.293 | 35.6 | 2077.07 | 9074.51 | 10538.1 | 0.2 | 1.25 | 19.41 | 13.051 | 1 | 1 | 2920 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 4046173.9014 | 360964.0331 | 8304.2393 | 30244.5582 | 330719.4748 | 14061.55 | 0.11125 | -108579.5618 | 108579.5618
C | Xist Rating 5621 | -12.55 | 1949.4 | 150.293 | 35.6 | 2080.95 | 9148.89 | 10538 | 0.19 | 1.25 | 19.468 | 13.06 | 1 | 1 | 2930 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 4056603.93 | 363336.691 | 8361.215 | 30348.1355 | 332988.5555 | 14048.5915 | 0.11164 | -108479.5 | 108479.5
C | Xist Rating 5622 | -12.36 | 1950.77 | 150.293 | 35.6 | 2084.66 | 9221.06 | 10538 | 0.19 | 1.25 | 19.482 | 13.069 | 1 | 1 | 2940 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 4066692.1882 | 365717.1064 | 8418.3855 | 30451.7127 | 335265.3937 | 14059.9466 | 0.11202 | -108567.1808 | 108567.1808
C | Xist Rating 5623 | -12.03 | 1952.18 | 150.293 | 35.6 | 2091.85 | 9363.54 | 10537.9 | 0.19 | 1.25 | 19.518 | 13.079 | 1 | 1 | 2950 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 4083667.733 | 368105.2794 | 8475.7509 | 30555.29 | 337549.9894 | 14072.8953 | 0.1124 | -108667.167 | 108667.167
C | Xist Rating 5624 | -11.81 | 1953.55 | 150.293 | 35.5 | 2096.66 | 9460.83 | 10537.9 | 0.19 | 1.25 | 19.52 | 13.088 | 1 | 1 | 2960 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 4095930.143 | 370501.2099 | 8533.311 | 30658.8672 | 339842.3427 | 14083.9545 | 0.11278 | -108752.5631 | 108752.5631
C | Xist Rating 5625 | -11.8 | 1954.93 | 150.293 | 35.5 | 2095.93 | 9445.96 | 10537.9 | 0.18 | 1.25 | 19.515 | 13.098 | 1 | 1 | 2970 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 4097396.4349 | 372904.898 | 8591.0659 | 30762.4445 | 342142.4535 | 14069.8953 | 0.11316 | -108644.0017 | 108644.0017
C | Xist Rating 5626 | -11.79 | 1956.16 | 150.293 | 35.5 | 2095.34 | 9433.99 | 10537.9 | 0.18 | 1.25 | 19.551 | 13.106 | 1 | 1 | 2980 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 4098820.2944 | 375316.3436 | 8649.0156 | 30866.0218 | 344450.3219 | 14080.6434 | 0.11354 | -108726.9959 | 108726.9959
C | Xist Rating 5627 | -11.78 | 1957.71 | 150.293 | 35.5 | 2094.8 | 9423.13 | 10537.8 | 0.18 | 1.25 | 19.537 | 13.116 | 1 | 1 | 2990 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 4101010.908 | 377735.5468 | 8707.16 | 30969.599 | 346765.9478 | 14092.2681 | 0.11392 | -108816.7588 | 108816.7588
C | Xist Rating 5628 | -11.76 | 1959.15 | 150.293 | 35.5 | 2094.24 | 9411.81 | 10537.8 | 0.18 | 1.25 | 19.531 | 13.125 | 1 | 1 | 3000 | 152.4 | 2 | 3.7 | 19.05 | 1.3333 | 21 | E | Rod | 4102930.296 | 380162.5075 | 8765.4993 | 31073.1763 | 349089.3312 | 14103.0457 | 0.1143 | -108899.9804 | 108899.9804
C | Xist Rating 5629 | -89.22 | 196.627 | 150.297 | 35.9 | 2376.03 | 7183.98 | 58745.8 | 2.46 | 10.95 | 20.984 | 506.065 | 1 | 1 | 1000 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 467191.6508 | 50473.6837 | 973.9444 | 10637.6639 | 39836.0198 | 527861.5795 | 0.038101 | -4076007.1961 | 4076007.1961
C | Xist Rating 5630 | -89.12 | 198.67 | 150.298 | 35.9 | 2374.01 | 7173.48 | 58283.5 | 2.44 | 10.84 | 21.039 | 496.557 | 1 | 1 | 1010 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 471644.5667 | 51380.7644 | 993.5206 | 10744.0406 | 40636.7238 | 517997.7508 | 0.038482 | -3999841.3255 | 3999841.3255
C | Xist Rating 5631 | -88.31 | 214.123 | 150.298 | 35.9 | 2367.16 | 7172.09 | 54967.7 | 2.45 | 10.07 | 21.095 | 430.324 | 1 | 1 | 1020 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 506863.4007 | 52295.8122 | 1013.2917 | 10850.4172 | 41445.395 | 449253.788 | 0.038863 | -3469018.667 | 3469018.667
C | Xist Rating 5632 | -88.18 | 218.353 | 150.297 | 35.9 | 2349.02 | 7023.08 | 54178.4 | 2.37 | 9.89 | 20.626 | 415.888 | 1 | 1 | 1030 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 512915.5641 | 53218.8272 | 1033.2576 | 10956.7939 | 42262.0334 | 434155.9573 | 0.039244 | -3352437.2205 | 3352437.2205
C | Xist Rating 5633 | -88.1 | 220.471 | 150.296 | 35.8 | 2342.98 | 6976.73 | 53793.7 | 2.33 | 9.8 | 20.514 | 408.98 | 1 | 1 | 1040 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 516559.1436 | 54149.8095 | 1053.4182 | 11063.1705 | 43086.639 | 426953.2954 | 0.039625 | -3296820.1744 | 3296820.1744
C | Xist Rating 5634 | -87.92 | 224.58 | 150.296 | 35.8 | 2336.92 | 6937.81 | 53042.6 | 2.29 | 9.63 | 20.437 | 395.422 | 1 | 1 | 1050 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 524825.4936 | 55088.7589 | 1073.7737 | 11169.5471 | 43919.2118 | 412847.8395 | 0.040006 | -3187901.5824 | 3187901.5824
C | Xist Rating 5635 | -87.75 | 226.677 | 150.296 | 35.9 | 2346.79 | 7032.96 | 52676.7 | 2.24 | 9.54 | 20.43 | 389.018 | 1 | 1 | 1060 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 531963.3168 | 56035.6756 | 1094.3239 | 11275.9238 | 44759.7518 | 406168.9765 | 0.040387 | -3136329.1731 | 3136329.1731
C | Xist Rating 5636 | -86.96 | 243.307 | 150.296 | 35.9 | 2329.07 | 6935.15 | 49857.3 | 2.23 | 8.9 | 20.257 | 340.382 | 1 | 1 | 1070 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 566679.0345 | 56990.5595 | 1115.0689 | 11382.3004 | 45608.259 | 355652.7785 | 0.040768 | -2746256.4823 | 2746256.4823
C | Xist Rating 5637 | -86.76 | 246.456 | 150.296 | 35.8 | 2335.94 | 7007.31 | 49380.5 | 2.17 | 8.79 | 20.167 | 332.757 | 1 | 1 | 1080 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 575706.4286 | 57953.4105 | 1136.0087 | 11488.6771 | 46464.7335 | 347686.1829 | 0.041149 | -2684740.5429 | 2684740.5429
C | Xist Rating 5638 | -86.52 | 250.646 | 150.295 | 35.8 | 2338.94 | 7048.99 | 48761.4 | 2.11 | 8.65 | 20.026 | 322.959 | 1 | 1 | 1090 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 586245.9552 | 58924.2288 | 1157.1433 | 11595.0537 | 47329.1751 | 337456.9355 | 0.04153 | -2605753.0061 | 2605753.0061
C | Xist Rating 5639 | -86.31 | 253.764 | 150.295 | 35.8 | 2347.5 | 7138.59 | 48308.2 | 2.07 | 8.55 | 20.025 | 315.887 | 1 | 1 | 1100 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 595710.99 | 59903.0143 | 1178.4727 | 11701.4303 | 48201.5839 | 330092.0163 | 0.041911 | -2548883.0518 | 2548883.0518
C | Xist Rating 5640 | -86.21 | 256.049 | 150.295 | 35.8 | 2344.2 | 7115.61 | 48011 | 1.99 | 8.49 | 19.736 | 311.559 | 1 | 1 | 1110 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 600230.0658 | 60889.7669 | 1199.9969 | 11807.807 | 49081.96 | 325507.6528 | 0.042292 | -2513483.8124 | 2513483.8124
C | Xist Rating 5641 | -85.24 | 274.546 | 150.295 | 35.8 | 2340.09 | 7146.23 | 45448.3 | 2.04 | 7.92 | 19.989 | 272.613 | 1 | 1 | 1120 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 642462.3491 | 61884.4868 | 1221.7158 | 11914.1836 | 49970.3032 | 285155.3501 | 0.042673 | -2201894.0272 | 2201894.0272
C | Xist Rating 5642 | -85.13 | 276.785 | 150.295 | 35.8 | 2340.58 | 7158.26 | 45189.3 | 1.97 | 7.86 | 19.805 | 269.121 | 1 | 1 | 1130 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 647837.4353 | 62887.1739 | 1243.6296 | 12020.5603 | 50866.6137 | 281457.9582 | 0.043054 | -2173343.7466 | 2173343.7466
C | Xist Rating 5643 | -84.93 | 281.044 | 150.294 | 35.8 | 2337.34 | 7142.76 | 44681.5 | 1.92 | 7.75 | 19.635 | 262.099 | 1 | 1 | 1140 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 656895.383 | 63897.8282 | 1265.7381 | 12126.9369 | 51770.8913 | 274115.83 | 0.043435 | -2116649.7794 | 2116649.7794
C | Xist Rating 5644 | -84.71 | 285.241 | 150.294 | 35.8 | 2337.49 | 7158.89 | 44186.4 | 1.88 | 7.64 | 19.459 | 255.302 | 1 | 1 | 1150 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 666747.9851 | 64916.4497 | 1288.0414 | 12233.3135 | 52683.1362 | 267016.5124 | 0.043816 | -2061830.7306 | 2061830.7306
C | Xist Rating 5645 | -84.5 | 289.517 | 150.293 | 35.8 | 2334.67 | 7147.17 | 43703.3 | 1.83 | 7.53 | 19.312 | 248.84 | 1 | 1 | 1160 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 675926.6544 | 65943.0384 | 1310.5395 | 12339.6902 | 53603.3482 | 260257.5561 | 0.044197 | -2009639.8616 | 2009639.8616
C | Xist Rating 5646 | -83.63 | 306.133 | 150.294 | 35.8 | 2333.02 | 7192.16 | 41832.4 | 1.85 | 7.13 | 19.456 | 223.84 | 1 | 1 | 1170 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 714214.4117 | 66977.5943 | 1333.2324 | 12446.0668 | 54531.5275 | 234345.1647 | 0.044578 | -1809551.2438 | 1809551.2438
C | Xist Rating 5647 | -83.5 | 307.345 | 150.294 | 35.8 | 2343.06 | 7292.15 | 41725 | 1.8 | 7.11 | 19.384 | 222.636 | 1 | 1 | 1180 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 720127.7757 | 68020.1174 | 1356.1201 | 12552.4435 | 55467.6739 | 233052.6373 | 0.044959 | -1799570.6895 | 1799570.6895
C | Xist Rating 5648 | -83.13 | 315.724 | 150.293 | 35.8 | 2333.64 | 7231.17 | 40885.4 | 1.75 | 6.92 | 19.226 | 212.202 | 1 | 1 | 1190 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 736786.1554 | 69070.6077 | 1379.2026 | 12658.8201 | 56411.7876 | 222166.1373 | 0.04534 | -1715508.0227 | 1715508.0227
C | Xist Rating 5649 | -82.93 | 317.855 | 150.293 | 35.8 | 2346.99 | 7368.51 | 40682.3 | 1.71 | 6.88 | 19.265 | 209.772 | 1 | 1 | 1200 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 746002.5064 | 70129.0652 | 1402.4799 | 12765.1967 | 57363.8685 | 219619.8885 | 0.045721 | -1695846.5644 | 1695846.5644
C | Xist Rating 5650 | -82.72 | 322.2 | 150.293 | 35.8 | 2344.06 | 7354.91 | 40281.9 | 1.66 | 6.8 | 19.134 | 205.043 | 1 | 1 | 1210 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 755256.132 | 71195.4899 | 1425.9519 | 12871.5734 | 58323.9166 | 214659.557 | 0.046102 | -1657544.1993 | 1657544.1993
C | Xist Rating 5651 | -81.81 | 341.051 | 150.293 | 35.8 | 2332.01 | 7305.93 | 38538.1 | 1.66 | 6.43 | 19.141 | 184.387 | 1 | 1 | 1220 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 795334.3425 | 72269.8818 | 1449.6188 | 12977.95 | 59291.9318 | 193223.2065 | 0.046483 | -1492018.383 | 1492018.383
C | Xist Rating 5652 | -81.55 | 345.246 | 150.293 | 35.8 | 2338.18 | 7381.85 | 38183.3 | 1.64 | 6.35 | 19.15 | 180.434 | 1 | 1 | 1230 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 807247.2923 | 73352.241 | 1473.4804 | 13084.3267 | 60267.9143 | 189111.9722 | 0.046864 | -1460272.5209 | 1460272.5209
C | Xist Rating 5653 | -81.33 | 349.581 | 150.293 | 35.8 | 2337.52 | 7390.39 | 37835.7 | 1.59 | 6.28 | 19.057 | 176.679 | 1 | 1 | 1240 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 817152.5791 | 74442.5673 | 1497.5369 | 13190.7033 | 61251.864 | 185165.0489 | 0.047245 | -1429795.4259 | 1429795.4259
C | Xist Rating 5654 | -81.18 | 351.856 | 150.293 | 35.8 | 2341.5 | 7437.98 | 37664.5 | 1.56 | 6.24 | 18.994 | 174.916 | 1 | 1 | 1250 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 823870.824 | 75540.8608 | 1521.7881 | 13297.0799 | 62243.7809 | 183310.2183 | 0.047626 | -1415472.9153 | 1415472.9153
C | Xist Rating 5655 | -80.86 | 358.172 | 150.293 | 35.8 | 2340.34 | 7449.18 | 37161.6 | 1.53 | 6.14 | 18.951 | 169.489 | 1 | 1 | 1260 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 838244.2585 | 76647.1216 | 1546.2341 | 13403.4566 | 63243.665 | 177651.6705 | 0.048007 | -1371779.1096 | 1371779.1096
C | Xist Rating 5656 | -79.97 | 376.027 | 150.293 | 35.8 | 2333.61 | 7447.19 | 35777.7 | 1.53 | 5.85 | 19.016 | 154.792 | 1 | 1 | 1270 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 877500.3675 | 77761.3495 | 1570.8749 | 13509.8332 | 64251.5163 | 162407.5176 | 0.048388 | -1254067.8015 | 1254067.8015
C | Xist Rating 5657 | -79.78 | 380.43 | 150.292 | 35.8 | 2330.37 | 7429.32 | 35477.4 | 1.49 | 5.79 | 18.912 | 151.858 | 1 | 1 | 1280 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 886542.6591 | 78883.5447 | 1595.7105 | 13616.2099 | 65267.3348 | 159321.0717 | 0.048769 | -1230235.0843 | 1230235.0843
C | Xist Rating 5658 | -79.56 | 384.781 | 150.292 | 35.8 | 2329.49 | 7435.29 | 35182.7 | 1.46 | 5.73 | 18.877 | 148.992 | 1 | 1 | 1290 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 896343.4917 | 80013.707 | 1620.7408 | 13722.5865 | 66291.1205 | 156321.6046 | 0.04915 | -1207073.9945 | 1207073.9945
C | Xist Rating 5659 | -79.2 | 391.075 | 150.292 | 35.8 | 2333.59 | 7499.99 | 34751.5 | 1.44 | 5.64 | 18.916 | 144.753 | 1 | 1 | 1300 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 912608.7093 | 81151.8366 | 1645.966 | 13828.9631 | 67322.8734 | 151913.0362 | 0.049531 | -1173032.1978 | 1173032.1978
C | Xist Rating 5660 | -78.98 | 394.418 | 150.292 | 35.8 | 2338.8 | 7565.71 | 34540.1 | 1.4 | 5.59 | 18.869 | 142.788 | 1 | 1 | 1310 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 922464.8184 | 82297.9333 | 1671.3859 | 13935.3398 | 68362.5935 | 149836.3027 | 0.049912 | -1156996.2122 | 1156996.2122
C | Xist Rating 5661 | -78.09 | 412.37 | 150.292 | 35.8 | 2332.86 | 7570.58 | 33363 | 1.4 | 5.35 | 18.919 | 131.502 | 1 | 1 | 1320 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 962001.4782 | 83451.9973 | 1697.0007 | 14041.7164 | 69410.2809 | 138131.7925 | 0.050293 | -1066617.0868 | 1066617.0868
C | Xist Rating 5662 | -77.78 | 418.881 | 150.292 | 35.8 | 2329.83 | 7561.57 | 32979.9 | 1.37 | 5.28 | 18.827 | 128.075 | 1 | 1 | 1330 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 975921.5202 | 84614.0284 | 1722.8102 | 14148.093 | 70465.9354 | 134543.3801 | 0.050674 | -1038908.3178 | 1038908.3178
C | Xist Rating 5663 | -77.43 | 425.291 | 150.292 | 35.8 | 2332.38 | 7611.61 | 32606.8 | 1.34 | 5.2 | 18.751 | 124.758 | 1 | 1 | 1340 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 991940.2226 | 85784.0268 | 1748.8145 | 14254.4697 | 71529.5571 | 131070.2001 | 0.051055 | -1012089.3426 | 1012089.3426
C | Xist Rating 5664 | -77.21 | 428.65 | 150.292 | 35.8 | 2337.01 | 7672.89 | 32423.8 | 1.31 | 5.16 | 18.717 | 123.207 | 1 | 1 | 1350 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1001759.3365 | 86961.9924 | 1775.0136 | 14360.8463 | 72601.146 | 129434.0161 | 0.051436 | -999455.1631 | 999455.1631
C | Xist Rating 5665 | -76.97 | 430.728 | 150.292 | 35.8 | 2352.06 | 7845.66 | 32303.5 | 1.3 | 5.14 | 18.787 | 122.156 | 1 | 1 | 1360 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1013098.0997 | 88147.9251 | 1801.4075 | 14467.223 | 73680.7022 | 128347.6823 | 0.051817 | -991066.7812 | 991066.7812
C | Xist Rating 5666 | -75.87 | 456.234 | 150.292 | 35.8 | 2326.61 | 7663.1 | 30902.5 | 1.29 | 4.86 | 18.724 | 110.081 | 1 | 1 | 1370 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1061478.5867 | 89341.8251 | 1827.9962 | 14573.5996 | 74768.2255 | 115802.2336 | 0.052198 | -894194.152 | 894194.152
C | Xist Rating 5667 | -75.77 | 458.573 | 150.292 | 35.7 | 2326.13 | 7665.51 | 30794.1 | 1.26 | 4.84 | 18.686 | 109.259 | 1 | 1 | 1380 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1066700.4125 | 90543.6923 | 1854.7797 | 14679.9762 | 75863.7161 | 114921.7062 | 0.052579 | -887394.9527 | 887394.9527
C | Xist Rating 5668 | -75.48 | 464.032 | 150.292 | 35.7 | 2326.98 | 7694.13 | 30526.9 | 1.23 | 4.78 | 18.652 | 107.128 | 1 | 1 | 1390 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1079793.1834 | 91753.5267 | 1881.7579 | 14786.3529 | 76967.1738 | 112681.6864 | 0.05296 | -870098.114 | 870098.114
C | Xist Rating 5669 | -75.19 | 469.488 | 150.292 | 35.7 | 2328.26 | 7727.53 | 30265.1 | 1.21 | 4.73 | 18.623 | 105.062 | 1 | 1 | 1400 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1093090.1309 | 92971.3283 | 1908.931 | 14892.7295 | 78078.5988 | 110520.8203 | 0.053341 | -853412.4789 | 853412.4789
C | Xist Rating 5670 | -74.85 | 475.959 | 150.292 | 35.7 | 2328.55 | 7754.15 | 29957.6 | 1.19 | 4.67 | 18.602 | 102.644 | 1 | 1 | 1410 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1108294.3295 | 94197.0971 | 1936.2988 | 14999.1062 | 79197.9909 | 107994.7119 | 0.053722 | -833906.5394 | 833906.5394
C | Xist Rating 5671 | -73.91 | 495.052 | 150.292 | 35.7 | 2324.17 | 7777.49 | 29051.9 | 1.2 | 4.49 | 18.67 | 95.516 | 1 | 1 | 1420 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1150585.0068 | 95430.8331 | 1963.8614 | 15105.4828 | 80325.3503 | 100619.2521 | 0.054103 | -776955.1931 | 776955.1931
C | Xist Rating 5672 | -73.74 | 498.652 | 150.292 | 35.7 | 2322.83 | 7774.19 | 28910.8 | 1.16 | 4.47 | 18.596 | 94.546 | 1 | 1 | 1430 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1158283.8252 | 96672.5363 | 1991.6188 | 15211.8594 | 81460.6768 | 99568.5795 | 0.054484 | -768842.1782 | 768842.1782
C | Xist Rating 5673 | -73.31 | 507.201 | 150.292 | 35.7 | 2322.37 | 7800.18 | 28542.1 | 1.14 | 4.39 | 18.58 | 91.812 | 1 | 1 | 1440 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1177908.3864 | 97922.2067 | 2019.571 | 15318.2361 | 82603.9706 | 96713.8103 | 0.054865 | -746798.4068 | 746798.4068
C | Xist Rating 5674 | -73.02 | 512.695 | 150.292 | 35.7 | 2322.93 | 7826.06 | 28316.9 | 1.12 | 4.35 | 18.558 | 90.201 | 1 | 1 | 1450 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1190954.5964 | 99179.8443 | 2047.718 | 15424.6127 | 83755.2316 | 95024.5298 | 0.055246 | -733754.2308 | 733754.2308
C | Xist Rating 5675 | -72.79 | 515.936 | 150.292 | 35.7 | 2329.78 | 7916.35 | 28183.7 | 1.11 | 4.32 | 18.58 | 89.255 | 1 | 1 | 1460 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1202017.3741 | 100445.4491 | 2076.0598 | 15530.9894 | 84914.4598 | 94040.8801 | 0.055627 | -726158.7488 | 726158.7488
C | Xist Rating 5676 | -71.84 | 537.535 | 150.292 | 35.7 | 2314.48 | 7821.46 | 27310.6 | 1.1 | 4.16 | 18.563 | 83.003 | 1 | 1 | 1470 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1244114.0068 | 101719.0211 | 2104.5964 | 15637.366 | 86081.6551 | 87543.9576 | 0.056008 | -675991.2352 | 675991.2352
C | Xist Rating 5677 | -71.51 | 544.05 | 150.292 | 35.7 | 2314.85 | 7849.1 | 27066.3 | 1.08 | 4.11 | 18.549 | 81.346 | 1 | 1 | 1480 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1259394.1425 | 103000.5604 | 2133.3277 | 15743.7426 | 87256.8177 | 85806.686 | 0.056389 | -662576.4841 | 662576.4841
C | Xist Rating 5678 | -71.22 | 549.546 | 150.292 | 35.7 | 2315.79 | 7879.47 | 26866.4 | 1.06 | 4.07 | 18.535 | 80.019 | 1 | 1 | 1490 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1272633.1313 | 104290.0668 | 2162.2539 | 15850.1193 | 88439.9475 | 84411.8098 | 0.05677 | -651805.6203 | 651805.6203
C | Xist Rating 5679 | -70.92 | 555.134 | 150.292 | 35.7 | 2316.4 | 7906.19 | 26670.3 | 1.04 | 4.03 | 18.513 | 78.74 | 1 | 1 | 1500 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1285912.3976 | 105587.5404 | 2191.3748 | 15956.4959 | 89631.0445 | 83065.9139 | 0.057151 | -641412.9692 | 641412.9692
C | Xist Rating 5680 | -70.54 | 561.675 | 150.292 | 35.7 | 2320.6 | 7979.31 | 26439 | 1.02 | 3.99 | 18.514 | 77.222 | 1 | 1 | 1510 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1303423.005 | 106892.9812 | 2220.6906 | 16062.8726 | 90830.1087 | 81473.1116 | 0.057532 | -629113.7715 | 629113.7715
C | Xist Rating 5681 | -69.46 | 582.957 | 150.292 | 35.7 | 2318.75 | 8039.61 | 25680.9 | 1.03 | 3.84 | 18.593 | 72.205 | 1 | 1 | 1520 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1351731.5437 | 108206.3893 | 2250.2011 | 16169.2492 | 92037.1401 | 76289.5881 | 0.057913 | -589087.977 | 589087.977
C | Xist Rating 5682 | -69.18 | 589.843 | 150.292 | 35.7 | 2313.48 | 8000.38 | 25468.5 | 1 | 3.8 | 18.526 | 70.925 | 1 | 1 | 1530 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1364589.9836 | 109527.7645 | 2279.9064 | 16275.6258 | 93252.1387 | 74926.0452 | 0.058294 | -578559.0604 | 578559.0604
C | Xist Rating 5683 | -68.94 | 593.358 | 150.292 | 35.7 | 2318.81 | 8076.73 | 25363.6 | 0.98 | 3.78 | 18.516 | 70.316 | 1 | 1 | 1540 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1375884.464 | 110857.107 | 2309.8065 | 16382.0025 | 94475.1045 | 74275.6504 | 0.058675 | -573536.8841 | 573536.8841
C | Xist Rating 5684 | -68.41 | 604.11 | 150.292 | 35.7 | 2317.56 | 8102.05 | 25021.2 | 0.97 | 3.72 | 18.511 | 68.2 | 1 | 1 | 1550 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1400061.1716 | 112194.4166 | 2339.9013 | 16488.3791 | 95706.0375 | 72073.1199 | 0.059056 | -556529.5277 | 556529.5277
C | Xist Rating 5685 | -68.09 | 607.401 | 150.292 | 35.7 | 2328.71 | 8252.67 | 24920.5 | 0.96 | 3.7 | 18.547 | 67.605 | 1 | 1 | 1560 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1414460.7827 | 113539.6935 | 2370.191 | 16594.7558 | 96944.9377 | 71452.7345 | 0.059437 | -551739.0759 | 551739.0759
C | Xist Rating 5686 | -67.07 | 632.424 | 150.292 | 35.7 | 2309.07 | 8105.27 | 24162.1 | 0.95 | 3.56 | 18.499 | 63.039 | 1 | 1 | 1570 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1460311.2857 | 114892.9375 | 2400.6755 | 16701.1324 | 98191.8051 | 66702.6703 | 0.059818 | -515060.3394 | 515060.3394
C | Xist Rating 5687 | -66.74 | 638.04 | 150.292 | 35.7 | 2312.48 | 8167.82 | 24007.4 | 0.93 | 3.53 | 18.493 | 62.173 | 1 | 1 | 1580 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1475454.7392 | 116254.1488 | 2431.3547 | 16807.509 | 99446.6398 | 65784.6099 | 0.0602 | -507971.3204 | 507971.3204
C | Xist Rating 5688 | -66.42 | 643.692 | 150.292 | 35.7 | 2315.18 | 8222.32 | 23854.9 | 0.92 | 3.5 | 18.483 | 61.329 | 1 | 1 | 1590 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1490262.8446 | 117623.3273 | 2462.2288 | 16913.8857 | 100709.4416 | 64901.9906 | 0.060581 | -501155.9675 | 501155.9675
C | Xist Rating 5689 | -65.98 | 651.278 | 150.292 | 35.7 | 2319.09 | 8301.14 | 23645.1 | 0.9 | 3.46 | 18.495 | 60.144 | 1 | 1 | 1600 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1510372.297 | 119000.4729 | 2493.2976 | 17020.2623 | 101980.2106 | 63653.2548 | 0.060962 | -491513.5613 | 491513.5613
C | Xist Rating 5690 | -65.78 | 654.989 | 150.292 | 35.7 | 2320.74 | 8335.05 | 23556.4 | 0.88 | 3.45 | 18.469 | 59.696 | 1 | 1 | 1610 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1520059.1719 | 120385.5858 | 2524.5612 | 17126.639 | 103258.9469 | 63167.1228 | 0.061343 | -487759.7786 | 487759.7786
C | Xist Rating 5691 | -64.59 | 682.967 | 150.291 | 35.7 | 2304.35 | 8235.16 | 22804.4 | 0.89 | 3.31 | 18.482 | 55.484 | 1 | 1 | 1620 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1573795.0064 | 121778.6659 | 2556.0196 | 17233.0156 | 104545.6503 | 58814.5043 | 0.061724 | -454150.0122 | 454150.0122
C | Xist Rating 5692 | -64.27 | 686.333 | 150.291 | 35.7 | 2314.63 | 8380.78 | 22722.8 | 0.88 | 3.29 | 18.504 | 55.067 | 1 | 1 | 1630 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1588606.9518 | 123179.7132 | 2587.6728 | 17339.3922 | 105840.3209 | 58376.7345 | 0.062105 | -450769.6696 | 450769.6696
C | Xist Rating 5693 | -63.99 | 692.132 | 150.291 | 35.7 | 2314.24 | 8396.82 | 22588.1 | 0.86 | 3.27 | 18.481 | 54.387 | 1 | 1 | 1640 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1601759.5597 | 124588.7277 | 2619.5208 | 17445.7689 | 107142.9588 | 57649.195 | 0.062486 | -445151.8028 | 445151.8028
C | Xist Rating 5694 | -63.63 | 700.076 | 150.291 | 35.7 | 2311.31 | 8388.04 | 22402.5 | 0.84 | 3.23 | 18.455 | 53.439 | 1 | 1 | 1650 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1618092.6596 | 126005.7094 | 2651.5635 | 17552.1455 | 108453.5638 | 56642.8701 | 0.062867 | -437381.2289 | 437381.2289
C | Xist Rating 5695 | -63.22 | 707.776 | 150.291 | 35.7 | 2313.2 | 8442.8 | 22220.4 | 0.83 | 3.2 | 18.459 | 52.502 | 1 | 1 | 1660 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1637227.4432 | 127430.6582 | 2683.8011 | 17658.5222 | 109772.1361 | 55663.2608 | 0.063248 | -429816.9452 | 429816.9452
C | Xist Rating 5696 | -62.13 | 732.843 | 150.291 | 35.7 | 2300.92 | 8379.2 | 21632.6 | 0.83 | 3.1 | 18.485 | 49.466 | 1 | 1 | 1670 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1686213.1156 | 128863.5743 | 2716.2334 | 17764.8988 | 111098.6756 | 52518.8626 | 0.063629 | -405536.7357 | 405536.7357
C | Xist Rating 5697 | -61.85 | 736.32 | 150.291 | 35.7 | 2307.54 | 8480.35 | 21560.3 | 0.82 | 3.08 | 18.491 | 49.129 | 1 | 1 | 1680 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1699087.8528 | 130304.4576 | 2748.8606 | 17871.2754 | 112433.1822 | 52162.2162 | 0.06401 | -402782.8066 | 402782.8066
C | Xist Rating 5698 | -61.42 | 746.458 | 150.291 | 35.7 | 2302.61 | 8452.36 | 21345.9 | 0.8 | 3.04 | 18.463 | 48.096 | 1 | 1 | 1690 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1718801.6554 | 131753.3081 | 2781.6825 | 17977.6521 | 113775.6561 | 51066.5318 | 0.064391 | -394322.2223 | 394322.2223
C | Xist Rating 5699 | -61.04 | 753.156 | 150.291 | 35.7 | 2305.63 | 8518.99 | 21205.7 | 0.79 | 3.02 | 18.466 | 47.428 | 1 | 1 | 1700 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1736499.0683 | 133210.1259 | 2814.6992 | 18084.0287 | 115126.0972 | 50365.5471 | 0.064772 | -388909.404 | 388909.404
C | Xist Rating 5700 | -60.66 | 761.048 | 150.291 | 35.7 | 2304.95 | 8539.81 | 21044.6 | 0.78 | 2.99 | 18.457 | 46.671 | 1 | 1 | 1710 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1754177.5876 | 134674.9108 | 2847.9107 | 18190.4053 | 116484.5054 | 49571.2505 | 0.065153 | -382776.0569 | 382776.0569
C | Xist Rating 5701 | -59.65 | 784.125 | 150.291 | 35.7 | 2295.4 | 8500.95 | 20567.1 | 0.78 | 2.9 | 18.487 | 44.382 | 1 | 1 | 1720 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1799880.525 | 136147.6629 | 2881.317 | 18296.782 | 117850.8809 | 47202.3849 | 0.065534 | -364484.3045 | 364484.3045
C | Xist Rating 5702 | -59.13 | 794.132 | 150.292 | 35.7 | 2295.35 | 8538.56 | 20374.7 | 0.77 | 2.87 | 18.485 | 43.505 | 1 | 1 | 1730 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1822810.8862 | 137628.3822 | 2914.9181 | 18403.1586 | 119225.2236 | 46283.63 | 0.065915 | -357389.9224 | 357389.9224
C | Xist Rating 5703 | -58.89 | 798.777 | 150.292 | 35.7 | 2297.33 | 8583.43 | 20289.8 | 0.76 | 2.85 | 18.477 | 43.139 | 1 | 1 | 1740 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1835054.3654 | 139117.0687 | 2948.714 | 18509.5353 | 120607.5335 | 45895.0281 | 0.066296 | -354389.2416 | 354389.2416
C | Xist Rating 5704 | -58.48 | 807.897 | 150.292 | 35.6 | 2294.58 | 8579.46 | 20123.5 | 0.74 | 2.82 | 18.46 | 42.406 | 1 | 1 | 1750 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1853784.2983 | 140613.7225 | 2982.7046 | 18615.9119 | 121997.8106 | 45110.1286 | 0.066677 | -348328.4556 | 348328.4556
C | Xist Rating 5705 | -58.13 | 814.711 | 150.292 | 35.7 | 2294.96 | 8610.56 | 20001.2 | 0.73 | 2.8 | 18.465 | 41.873 | 1 | 1 | 1760 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1869729.1566 | 142118.3434 | 3016.8901 | 18722.2885 | 123396.0549 | 44548.4568 | 0.067058 | -343991.3746 | 343991.3746
C | Xist Rating 5706 | -56.94 | 842.06 | 150.292 | 35.7 | 2284.23 | 8569.18 | 19497.8 | 0.73 | 2.71 | 18.501 | 39.62 | 1 | 1 | 1770 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1923458.7138 | 143630.9315 | 3051.2703 | 18828.6652 | 124802.2664 | 42216.847 | 0.067439 | -325987.302 | 325987.302
C | Xist Rating 5707 | -56.61 | 848.984 | 150.292 | 35.7 | 2283.5 | 8584.5 | 19383.4 | 0.72 | 2.69 | 18.489 | 39.149 | 1 | 1 | 1780 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1938654.964 | 145151.4869 | 3085.8453 | 18935.0418 | 126216.4451 | 41718.3172 | 0.06782 | -322137.7871 | 322137.7871
C | Xist Rating 5708 | -56.65 | 852.721 | 150.292 | 35.6 | 2273.67 | 8459.62 | 19326.8 | 0.71 | 2.68 | 18.694 | 38.925 | 1 | 1 | 1790 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1938806.1561 | 146680.0094 | 3120.6151 | 19041.4185 | 127638.591 | 41488.5042 | 0.068201 | -320363.2318 | 320363.2318
C | Xist Rating 5709 | -56.11 | 864.96 | 150.292 | 35.6 | 2272.38 | 8487.49 | 19121.8 | 0.7 | 2.65 | 18.677 | 38.065 | 1 | 1 | 1800 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1965517.8048 | 148216.4992 | 3155.5797 | 19147.7951 | 129068.7041 | 40585.3017 | 0.068582 | -313388.9418 | 313388.9418
C | Xist Rating 5710 | -55.78 | 871.756 | 150.292 | 35.6 | 2273.12 | 8522.97 | 19012.4 | 0.69 | 2.63 | 18.672 | 37.62 | 1 | 1 | 1810 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 1981605.9987 | 149760.9561 | 3190.7391 | 19254.1717 | 130506.7844 | 40113.5972 | 0.068963 | -309746.5645 | 309746.5645
C | Xist Rating 5711 | -54.41 | 899.364 | 150.292 | 35.6 | 2269.09 | 8572.97 | 18562.6 | 0.69 | 2.55 | 18.496 | 35.757 | 1 | 1 | 1820 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2040737.8588 | 151313.3803 | 3226.0933 | 19360.5484 | 131952.8319 | 38174.7425 | 0.069344 | -294775.2427 | 294775.2427
C | Xist Rating 5712 | -54.59 | 894.974 | 150.292 | 35.6 | 2273.86 | 8624.4 | 18631.4 | 0.69 | 2.56 | 18.737 | 36.042 | 1 | 1 | 1830 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2035045.5796 | 152873.7716 | 3261.6423 | 19466.925 | 133406.8466 | 38490.0758 | 0.069725 | -297210.1629 | 297210.1629
C | Xist Rating 5713 | -54.16 | 900.552 | 150.292 | 35.6 | 2281.55 | 8758.03 | 18545.3 | 0.68 | 2.55 | 18.759 | 35.704 | 1 | 1 | 1840 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2054654.4156 | 154442.1302 | 3297.386 | 19573.3017 | 134868.8286 | 38130.6386 | 0.070106 | -294434.6839 | 294434.6839
C | Xist Rating 5714 | -53.76 | 909.789 | 150.292 | 35.6 | 2278.35 | 8745.99 | 18409.3 | 0.67 | 2.52 | 18.747 | 35.179 | 1 | 1 | 1850 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2072817.7681 | 156018.456 | 3333.3246 | 19679.6783 | 136338.7777 | 37574.9221 | 0.070487 | -290143.5883 | 290143.5883
C | Xist Rating 5715 | -53.33 | 920.138 | 150.292 | 35.6 | 2274.49 | 8728.37 | 18259 | 0.65 | 2.5 | 18.733 | 34.601 | 1 | 1 | 1860 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2092844.6796 | 157602.749 | 3369.4579 | 19786.0549 | 137816.694 | 36948.2813 | 0.070868 | -285304.8343 | 285304.8343
C | Xist Rating 5716 | -52.19 | 945.484 | 150.292 | 35.6 | 2268.29 | 8738.7 | 17879.6 | 0.66 | 2.43 | 18.782 | 33.099 | 1 | 1 | 1870 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2144631.9024 | 159195.0091 | 3405.7861 | 19892.4316 | 139302.5776 | 35412.3279 | 0.071249 | -273444.6094 | 273444.6094
C | Xist Rating 5717 | -51.73 | 955.819 | 150.292 | 35.6 | 2265.89 | 8742.01 | 17738.8 | 0.64 | 2.41 | 18.773 | 32.578 | 1 | 1 | 1880 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2165780.7139 | 160795.2365 | 3442.309 | 19998.8082 | 140796.4283 | 34844.6861 | 0.07163 | -269061.4294 | 269061.4294
C | Xist Rating 5718 | -51.33 | 962.664 | 150.292 | 35.6 | 2268.69 | 8810.13 | 17646.4 | 0.64 | 2.39 | 18.787 | 32.242 | 1 | 1 | 1890 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2183986.1902 | 162403.4311 | 3479.0267 | 20105.1849 | 142298.2462 | 34501.8952 | 0.072011 | -266414.4895 | 266414.4895
C | Xist Rating 5719 | -51.03 | 969.966 | 150.292 | 35.6 | 2266.06 | 8796.67 | 17555.2 | 0.62 | 2.38 | 18.771 | 31.925 | 1 | 1 | 1900 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2198001.154 | 164019.5929 | 3515.9392 | 20211.5615 | 143808.0314 | 34145.2354 | 0.072392 | -263660.4565 | 263660.4565
C | Xist Rating 5720 | -50.7 | 976.99 | 150.292 | 35.6 | 2265.05 | 8807.61 | 17465.1 | 0.61 | 2.36 | 18.778 | 31.606 | 1 | 1 | 1910 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2212931.1995 | 165643.7219 | 3553.0464 | 20317.9381 | 145325.7837 | 33803.4658 | 0.072773 | -261021.4028 | 261021.4028
C | Xist Rating 5721 | -49.34 | 1007.77 | 150.292 | 35.6 | 2257.53 | 8817.92 | 17050.2 | 0.62 | 2.29 | 18.82 | 30.06 | 1 | 1 | 1920 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2275071.0081 | 167275.8181 | 3590.3485 | 20424.3148 | 146851.5033 | 32221.4838 | 0.073154 | -248805.757 | 248805.757
C | Xist Rating 5722 | -48.93 | 1018.19 | 150.292 | 35.6 | 2253.05 | 8788.68 | 16923.7 | 0.61 | 2.27 | 18.813 | 29.623 | 1 | 1 | 1930 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2294032.9795 | 168915.8815 | 3627.8454 | 20530.6914 | 148385.1901 | 31756.2394 | 0.073535 | -245213.2633 | 245213.2633
C | Xist Rating 5723 | -48.58 | 1021.56 | 150.292 | 35.6 | 2261.28 | 8928.6 | 16882.2 | 0.6 | 2.26 | 18.846 | 29.485 | 1 | 1 | 1940 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2310033.1968 | 170563.9121 | 3665.537 | 20637.0681 | 149926.844 | 31603.4328 | 0.073916 | -244033.3306 | 244033.3306
C | Xist Rating 5724 | -48.26 | 1031.37 | 150.292 | 35.6 | 2254.02 | 8851.24 | 16772.2 | 0.59 | 2.24 | 18.824 | 29.125 | 1 | 1 | 1950 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2324728.6074 | 172219.9099 | 3703.4235 | 20743.4447 | 151476.4652 | 31217.0344 | 0.074297 | -241049.6652 | 241049.6652
C | Xist Rating 5725 | -47.77 | 1042.77 | 150.292 | 35.6 | 2251.11 | 8850.03 | 16637.1 | 0.58 | 2.22 | 18.846 | 28.663 | 1 | 1 | 1960 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2347389.9747 | 173883.8749 | 3741.5047 | 20849.8213 | 153034.0536 | 30726.8094 | 0.074678 | -237264.2777 | 237264.2777
C | Xist Rating 5726 | -46.57 | 1070.51 | 150.292 | 35.6 | 2243.71 | 8846.12 | 16303.3 | 0.58 | 2.16 | 18.911 | 27.498 | 1 | 1 | 1970 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2401913.9921 | 175555.8071 | 3779.7807 | 20956.198 | 154599.6091 | 29525.1875 | 0.075059 | -227985.6716 | 227985.6716
C | Xist Rating 5727 | -46.18 | 1078.63 | 150.292 | 35.6 | 2243.49 | 8873.15 | 16214.3 | 0.57 | 2.15 | 18.93 | 27.211 | 1 | 1 | 1980 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2419895.6187 | 177235.7065 | 3818.2515 | 21062.5746 | 156173.1319 | 29216.2321 | 0.07544 | -225600.0002 | 225600.0002
C | Xist Rating 5728 | -45.78 | 1089.23 | 150.292 | 35.6 | 2238.84 | 8839.58 | 16101.4 | 0.56 | 2.13 | 18.93 | 26.851 | 1 | 1 | 1990 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2438611.6932 | 178923.5732 | 3856.9171 | 21168.9513 | 157754.6219 | 28830.3236 | 0.075821 | -222620.1166 | 222620.1166
C | Xist Rating 5729 | -45.4 | 1097.47 | 150.292 | 35.7 | 2237.96 | 8855.93 | 16015 | 0.55 | 2.12 | 18.935 | 26.578 | 1 | 1 | 2000 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2456093.9612 | 180619.407 | 3895.7775 | 21275.3279 | 159344.0791 | 28534.8412 | 0.076202 | -220338.48 | 220338.48
C | Xist Rating 5730 | -45.1 | 1103.53 | 150.293 | 35.7 | 2238.65 | 8888.41 | 15953.9 | 0.54 | 2.11 | 18.939 | 26.393 | 1 | 1 | 2010 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2470417.4345 | 182323.208 | 3934.8326 | 21381.7045 | 160941.5035 | 28330.5218 | 0.076583 | -218760.7796 | 218760.7796
C | Xist Rating 5731 | -43.82 | 1134.76 | 150.293 | 35.7 | 2228.46 | 8850.93 | 15614.9 | 0.54 | 2.05 | 18.975 | 25.279 | 1 | 1 | 2020 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2528767.2696 | 184034.9763 | 3974.0826 | 21488.0812 | 162546.8951 | 27179.979 | 0.076964 | -209876.5932 | 209876.5932
C | Xist Rating 5732 | -43.28 | 1146.11 | 150.293 | 35.7 | 2227.99 | 8886.52 | 15499.8 | 0.54 | 2.03 | 18.98 | 24.921 | 1 | 1 | 2030 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2553521.6189 | 185754.7117 | 4013.5273 | 21594.4578 | 164160.2539 | 26813.0352 | 0.077345 | -207043.1505 | 207043.1505
C | Xist Rating 5733 | -43 | 1153.61 | 150.293 | 35.7 | 2225.15 | 8867.08 | 15431.8 | 0.53 | 2.02 | 18.974 | 24.726 | 1 | 1 | 2040 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2566955.2915 | 187482.4143 | 4053.1669 | 21700.8345 | 165781.5799 | 26597.4757 | 0.077726 | -205378.6568 | 205378.6568
C | Xist Rating 5734 | -42.58 | 1160.3 | 150.293 | 35.7 | 2229.27 | 8959.09 | 15364.2 | 0.52 | 2.01 | 18.993 | 24.52 | 1 | 1 | 2050 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 23 | E | Rod | 2586621.981 | 189218.0842 | 4093.0012 | 21807.2111 | 167410.8731 | 26371.5252 | 0.078107 | -203633.9274 | 203633.9274
C | Xist Rating 5735 | -42.21 | 1171.3 | 150.293 | 35.7 | 2223.19 | 8900.34 | 15264.3 | 0.51 | 1.99 | 18.969 | 24.23 | 1 | 1 | 2060 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2604022.447 | 190961.7212 | 4133.0303 | 21913.5877 | 169048.1335 | 26056.1196 | 0.078488 | -201198.4487 | 201198.4487
C | Xist Rating 5736 | -40.84 | 1204.82 | 150.293 | 35.7 | 2213.15 | 8870.07 | 14936.1 | 0.51 | 1.94 | 19.007 | 23.213 | 1 | 1 | 2070 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2666447.383 | 192713.3255 | 4173.2542 | 22019.9644 | 170693.3611 | 25006.1013 | 0.078869 | -193090.486 | 193090.486
C | Xist Rating 5737 | -40.53 | 1212.13 | 150.293 | 35.7 | 2212.12 | 8879.09 | 14873.4 | 0.51 | 1.93 | 19.003 | 23.04 | 1 | 1 | 2080 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2681377.0156 | 194472.897 | 4213.6729 | 22126.341 | 172346.556 | 24830.596 | 0.07925 | -191735.2805 | 191735.2805
C | Xist Rating 5738 | -40.13 | 1221.56 | 150.293 | 35.7 | 2210.29 | 8883.65 | 14790.7 | 0.5 | 1.91 | 19 | 22.805 | 1 | 1 | 2090 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2700001.8524 | 196240.4356 | 4254.2864 | 22232.7176 | 174007.718 | 24572.9499 | 0.079631 | -189745.8053 | 189745.8053
C | Xist Rating 5739 | -39.7 | 1231.01 | 150.293 | 35.7 | 2209.83 | 8910.2 | 14709.1 | 0.49 | 1.9 | 19.001 | 22.576 | 1 | 1 | 2100 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2720322.8283 | 198015.9415 | 4295.0947 | 22339.0943 | 175676.8472 | 24321.5532 | 0.080012 | -187804.5866 | 187804.5866
C | Xist Rating 5740 | -39.33 | 1239.34 | 150.293 | 35.7 | 2208.77 | 8923.05 | 14638.6 | 0.49 | 1.89 | 19.001 | 22.381 | 1 | 1 | 2110 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2737417.0118 | 199799.4146 | 4336.0977 | 22445.4709 | 177353.9436 | 24123.2194 | 0.080393 | -186273.1056 | 186273.1056
C | Xist Rating 5741 | -38.08 | 1271.01 | 150.293 | 35.7 | 2198.8 | 8881.53 | 14358.9 | 0.49 | 1.84 | 19.036 | 21.565 | 1 | 1 | 2120 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2794696.788 | 201590.8548 | 4377.2956 | 22551.8476 | 179039.0073 | 23281.6078 | 0.080774 | -179774.404 | 179774.404
C | Xist Rating 5742 | -37.61 | 1282.71 | 150.293 | 35.7 | 2196.17 | 8880.76 | 14263.6 | 0.48 | 1.83 | 19.032 | 21.304 | 1 | 1 | 2130 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2817049.2207 | 203390.2623 | 4418.6882 | 22658.2242 | 180732.0381 | 22996.3826 | 0.081155 | -177571.9704 | 177571.9704
C | Xist Rating 5743 | -37.23 | 1294.42 | 150.293 | 35.7 | 2189.78 | 8818.62 | 14169.9 | 0.47 | 1.81 | 19.031 | 21.05 | 1 | 1 | 2140 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2834495.0276 | 205197.637 | 4460.2756 | 22764.6008 | 182433.0362 | 22718.3974 | 0.081536 | -175425.4425 | 175425.4425
C | Xist Rating 5744 | -36.99 | 1300.62 | 150.293 | 35.7 | 2188.41 | 8817.1 | 14123.5 | 0.47 | 1.8 | 19.039 | 20.933 | 1 | 1 | 2150 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2846289.8142 | 207012.9789 | 4502.0578 | 22870.9775 | 184142.0014 | 22601.2648 | 0.081917 | -174520.9758 | 174520.9758
C | Xist Rating 5745 | -36.61 | 1308.91 | 150.293 | 35.7 | 2188.02 | 8839.84 | 14059.1 | 0.46 | 1.79 | 19.043 | 20.764 | 1 | 1 | 2160 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2863921.2582 | 208836.288 | 4544.0348 | 22977.3541 | 185858.9339 | 22411.514 | 0.082298 | -173055.7702 | 173055.7702
C | Xist Rating 5746 | -35.3 | 1343.09 | 150.293 | 35.7 | 2176.97 | 8785.54 | 13786 | 0.46 | 1.75 | 19.075 | 20.011 | 1 | 1 | 2170 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2923866.6373 | 210667.5643 | 4586.2066 | 23083.7308 | 187583.8335 | 21634.883 | 0.082679 | -167058.8318 | 167058.8318
C | Xist Rating 5747 | -34.8 | 1354.55 | 150.293 | 35.7 | 2175.85 | 8808.24 | 13699.2 | 0.46 | 1.74 | 19.077 | 19.783 | 1 | 1 | 2180 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2947297.6175 | 212506.8078 | 4628.5732 | 23190.1074 | 189316.7004 | 21402.1284 | 0.08306 | -165261.5625 | 165261.5625
C | Xist Rating 5748 | -34.45 | 1363.07 | 150.293 | 35.7 | 2174.65 | 8817.17 | 13639 | 0.45 | 1.73 | 19.074 | 19.634 | 1 | 1 | 2190 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2964200.1755 | 214354.0185 | 4671.1346 | 23296.484 | 191057.5344 | 21232.466 | 0.083441 | -163951.4747 | 163951.4747
C | Xist Rating 5749 | -34.14 | 1371.99 | 150.293 | 35.7 | 2171.6 | 8795.74 | 13579.5 | 0.44 | 1.72 | 19.065 | 19.492 | 1 | 1 | 2200 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 2979413.484 | 216209.1964 | 4713.8907 | 23402.8607 | 192806.3357 | 21069.6465 | 0.083822 | -162694.2254 | 162694.2254
C | Xist Rating 5750 | -33.66 | 1383.71 | 150.293 | 35.7 | 2169.63 | 8804.36 | 13495.4 | 0.44 | 1.7 | 19.065 | 19.279 | 1 | 1 | 2210 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3002138.7273 | 218072.3415 | 4756.8417 | 23509.2373 | 194563.1042 | 20852.2065 | 0.084203 | -161015.2114 | 161015.2114
C | Xist Rating 5751 | -32.33 | 1417.76 | 150.293 | 35.7 | 2160.51 | 8777.85 | 13246.2 | 0.44 | 1.66 | 19.102 | 18.625 | 1 | 1 | 2220 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3063084.6576 | 219943.4538 | 4799.9874 | 23615.614 | 196327.8399 | 20178.4087 | 0.084584 | -155812.3236 | 155812.3236
C | Xist Rating 5752 | -31.93 | 1427.17 | 150.293 | 35.7 | 2159.62 | 8795.51 | 13182.5 | 0.43 | 1.65 | 19.102 | 18.471 | 1 | 1 | 2230 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3082144.8754 | 221822.5333 | 4843.3279 | 23721.9906 | 198100.5427 | 20003.1533 | 0.084965 | -154459.0474 | 154459.0474
C | Xist Rating 5753 | -31.5 | 1438.14 | 150.293 | 35.7 | 2157.38 | 8794.71 | 13111.8 | 0.43 | 1.64 | 19.097 | 18.303 | 1 | 1 | 2240 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3102614.4732 | 223709.5801 | 4886.8633 | 23828.3672 | 199881.2128 | 19832.1515 | 0.085346 | -153138.617 | 153138.617
C | Xist Rating 5754 | -31.04 | 1450.17 | 150.293 | 35.7 | 2154.58 | 8788.54 | 13034.1 | 0.42 | 1.63 | 19.092 | 18.118 | 1 | 1 | 2250 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3124507.2786 | 225604.594 | 4930.5934 | 23934.7439 | 201669.8501 | 19624.238 | 0.085727 | -151533.164 | 151533.164
C | Xist Rating 5755 | -30.75 | 1456.33 | 150.293 | 35.7 | 2155.15 | 8818.38 | 12995.6 | 0.42 | 1.62 | 19.095 | 18.031 | 1 | 1 | 2260 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3138609.5995 | 227507.5751 | 4974.5182 | 24041.1205 | 203466.4546 | 19537.6106 | 0.086108 | -150864.2503 | 150864.2503
C | Xist Rating 5756 | -29.4 | 1492.98 | 150.293 | 35.7 | 2144.02 | 8763.09 | 12751.8 | 0.42 | 1.59 | 19.131 | 17.426 | 1 | 1 | 2270 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3200978.9796 | 229418.5235 | 5018.6379 | 24147.4972 | 205271.0263 | 18914.4524 | 0.086489 | -146052.3881 | 146052.3881
C | Xist Rating 5757 | -28.98 | 1503.89 | 150.293 | 35.7 | 2141.56 | 8757.75 | 12686.1 | 0.41 | 1.58 | 19.126 | 17.277 | 1 | 1 | 2280 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3220670.6684 | 231337.439 | 5062.9524 | 24253.8738 | 207083.5652 | 18743.5564 | 0.08687 | -144732.7743 | 144732.7743
C | Xist Rating 5758 | -28.48 | 1516.78 | 150.293 | 35.7 | 2139 | 8758.59 | 12606.9 | 0.41 | 1.56 | 19.124 | 17.092 | 1 | 1 | 2290 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3244392.42 | 233264.3217 | 5107.4617 | 24360.2504 | 208904.0713 | 18554.865 | 0.087251 | -143275.7495 | 143275.7495
C | Xist Rating 5759 | -28.14 | 1525.46 | 150.293 | 35.7 | 2137.75 | 8765.45 | 12557 | 0.4 | 1.56 | 19.123 | 16.983 | 1 | 1 | 2300 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3261052.115 | 235199.1717 | 5152.1657 | 24466.6271 | 210732.5446 | 18425.4259 | 0.087632 | -142276.2547 | 142276.2547
| Xist Rating 5760 | -27.81 | 1534.41 | 150.293 | 35.7 | 2135.77 | 8760.03 | 12507.5 | 0.4 | 1.55 | 19.12 | 16.878 | 1 | 1 | 2310 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3277146.8457 | 237141.9888 | 5197.0645 | 24573.0037 | 212568.9851 | 18319.688 | 0.088013 | -141459.7749 | 141459.7749
| Xist Rating 5761 | -26.38 | 1572 | 150.293 | 35.7 | 2126.34 | 8733.21 | 12277 | 0.4 | 1.51 | 19.153 | 16.331 | 1 | 1 | 2320 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3342606.48 | 239092.7732 | 5242.1582 | 24679.3804 | 214413.3928 | 17756.4303 | 0.088394 | -137110.448 | 137110.448
| Xist Rating 5762 | -25.97 | 1582.95 | 150.293 | 35.7 | 2124.15 | 8731.52 | 12216.7 | 0.39 | 1.5 | 19.148 | 16.201 | 1 | 1 | 2330 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3362423.2425 | 241051.5248 | 5287.4466 | 24785.757 | 216265.7678 | 17604.6523 | 0.088775 | -135938.4584 | 135938.4584
| Xist Rating 5763 | -25.56 | 1593.87 | 150.293 | 35.6 | 2121.96 | 8729.72 | 12157 | 0.39 | 1.49 | 19.144 | 16.073 | 1 | 1 | 2340 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3382128.3852 | 243018.2435 | 5332.9298 | 24892.1336 | 218126.1099 | 17474.9082 | 0.089156 | -134936.6093 | 134936.6093
| Xist Rating 5764 | -25.21 | 1603.78 | 150.293 | 35.6 | 2119.45 | 8718.39 | 12104.5 | 0.38 | 1.49 | 19.138 | 15.963 | 1 | 1 | 2350 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3399131.521 | 244992.9295 | 5378.6078 | 24998.5103 | 219994.4192 | 17343.614 | 0.089537 | -133922.7902 | 133922.7902
| Xist Rating 5765 | -24.79 | 1615.86 | 150.293 | 35.6 | 2116.09 | 8700.44 | 12039.8 | 0.38 | 1.48 | 19.13 | 15.824 | 1 | 1 | 2360 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3419305.1874 | 246975.5827 | 5424.4805 | 25104.8869 | 221870.6957 | 17202.201 | 0.089918 | -132830.8363 | 132830.8363
| Xist Rating 5766 | -23.49 | 1650.33 | 150.293 | 35.6 | 2108.46 | 8688.81 | 11846.7 | 0.38 | 1.45 | 19.163 | 15.39 | 1 | 1 | 2370 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3479654.7918 | 248966.203 | 5470.5481 | 25211.2636 | 223754.9395 | 16756.0833 | 0.090299 | -129386.034 | 129386.034
| Xist Rating 5767 | -23.16 | 1661.49 | 150.293 | 35.6 | 2103.87 | 8645.5 | 11791.1 | 0.37 | 1.44 | 19.161 | 15.277 | 1 | 1 | 2380 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3495558.9663 | 250964.7906 | 5516.8105 | 25317.6402 | 225647.1504 | 16621.4746 | 0.09068 | -128346.6209 | 128346.6209
| Xist Rating 5768 | -22.7 | 1673.13 | 150.293 | 35.6 | 2102.22 | 8655.64 | 11730 | 0.37 | 1.43 | 19.158 | 15.148 | 1 | 1 | 2390 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3517287.3486 | 252971.3454 | 5563.2676 | 25424.0168 | 227547.3286 | 16490.5672 | 0.091061 | -127335.7891 | 127335.7891
C | Xist Rating 5771 | -13.4 | 1920.38 | 150.293 | 35.7 | 2050.31 | 8583.48 | 10540 | 0.39 | 1.25 | 19.196 | 12.68 | 1 | 1 | 2420 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3937374.3178 | 259038.813 | 5703.8078 | 25743.1467 | 233295.6662 | 13980.2564 | 0.092204 | -107951.8343 | 107951.8343
C | Xist Rating 5772 | -13.71 | 1921.73 | 150.293 | 35.6 | 2045.4 | 8499.77 | 10537.7 | 0.39 | 1.25 | 19.182 | 12.688 | 1 | 1 | 2430 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3930706.542 | 261077.2366 | 5751.0441 | 25849.5234 | 235227.7132 | 13991.3255 | 0.092585 | -108037.3065 | 108037.3065
C | Xist Rating 5773 | -13.68 | 1923.1 | 150.293 | 35.6 | 2045.13 | 8495.08 | 10537.8 | 0.38 | 1.25 | 19.175 | 12.698 | 1 | 1 | 2440 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3932989.503 | 263123.6274 | 5798.4752 | 25955.9 | 237167.7273 | 13983.7931 | 0.092966 | -107979.1434 | 107979.1434
C | Xist Rating 5774 | -13.71 | 1924.43 | 150.293 | 35.6 | 2043.87 | 8473.2 | 10537.8 | 0.38 | 1.25 | 19.175 | 12.709 | 1 | 1 | 2450 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3933284.7441 | 265177.9854 | 5846.1011 | 26062.2767 | 239115.7087 | 13998.4827 | 0.093347 | -108092.5728 | 108092.5728
C | Xist Rating 5775 | -13.71 | 1925.9 | 150.293 | 35.6 | 2042.7 | 8453.14 | 10537.9 | 0.37 | 1.25 | 19.173 | 12.72 | 1 | 1 | 2460 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3934035.93 | 267240.3106 | 5893.9217 | 26168.6533 | 241071.6573 | 13991.9467 | 0.093728 | -108042.1037 | 108042.1037
C | Xist Rating 5776 | -13.69 | 1927.26 | 150.293 | 35.6 | 2042.09 | 8442.71 | 10537.9 | 0.36 | 1.25 | 19.211 | 12.731 | 1 | 1 | 2470 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3935638.3734 | 269310.603 | 5941.9372 | 26275.0299 | 243035.573 | 13986.8369 | 0.094109 | -108002.6472 | 108002.6472
C | Xist Rating 5777 | -13.62 | 1928.6 | 150.293 | 35.7 | 2042.73 | 8453.72 | 10537.9 | 0.36 | 1.25 | 19.201 | 12.742 | 1 | 1 | 2480 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3939609.078 | 271388.8626 | 5990.1474 | 26381.4066 | 245007.456 | 14000.9603 | 0.09449 | -108111.7039 | 108111.7039
C | Xist Rating 5778 | -13.62 | 1930 | 150.293 | 35.6 | 2042.39 | 8447.85 | 10537.9 | 0.35 | 1.25 | 19.192 | 12.752 | 1 | 1 | 2490 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3941812.7 | 273475.0894 | 6038.5525 | 26487.7832 | 246987.3062 | 13992.6612 | 0.094871 | -108047.6209 | 108047.6209
C | Xist Rating 5779 | -13.59 | 1930.99 | 150.293 | 35.6 | 2042.63 | 8451.99 | 10537.8 | 0.35 | 1.25 | 19.189 | 12.761 | 1 | 1 | 2500 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3944298.1037 | 275569.2835 | 6087.1523 | 26594.1599 | 248975.1236 | 14004.901 | 0.095252 | -108142.1333 | 108142.1333
C | Xist Rating 5780 | -13.6 | 1932.84 | 150.293 | 35.6 | 2041.08 | 8425.44 | 10537.8 | 0.34 | 1.25 | 19.184 | 12.774 | 1 | 1 | 2510 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3945081.0672 | 277671.4447 | 6135.9469 | 26700.5365 | 250970.9082 | 13999.6312 | 0.095633 | -108101.4412 | 108101.4412
C | Xist Rating 5781 | -13.59 | 1934.29 | 150.293 | 35.6 | 2040.43 | 8414.47 | 10537.8 | 0.34 | 1.25 | 19.221 | 12.785 | 1 | 1 | 2520 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3946783.3447 | 279781.5731 | 6184.9363 | 26806.9131 | 252974.66 | 14015.3994 | 0.096014 | -108223.1991 | 108223.1991
C | Xist Rating 5782 | -13.58 | 1935.63 | 150.293 | 35.6 | 2039.93 | 8406.03 | 10537.8 | 0.33 | 1.25 | 19.215 | 12.795 | 1 | 1 | 2530 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3948549.7059 | 281899.6688 | 6234.1205 | 26913.2898 | 254986.379 | 14006.6914 | 0.096395 | -108155.9579 | 108155.9579
C | Xist Rating 5783 | -13.56 | 1936.78 | 150.293 | 35.6 | 2039.8 | 8403.86 | 10537.8 | 0.33 | 1.25 | 19.21 | 12.804 | 1 | 1 | 2540 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3950643.844 | 284025.7316 | 6283.4995 | 27019.6664 | 257006.0652 | 14018.6923 | 0.096776 | -108248.6259 | 108248.6259
C | Xist Rating 5784 | -13.52 | 1938.33 | 150.293 | 35.6 | 2039.72 | 8402.52 | 10537.7 | 0.32 | 1.25 | 19.203 | 12.815 | 1 | 1 | 2550 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3953650.4676 | 286159.7617 | 6333.0732 | 27126.0431 | 259033.7186 | 14010.7437 | 0.097157 | -108187.2492 | 108187.2492
C | Xist Rating 5785 | -13.51 | 1939.77 | 150.293 | 35.6 | 2039.23 | 8394.18 | 10537.7 | 0.32 | 1.25 | 19.197 | 12.826 | 1 | 1 | 2560 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3955637.1771 | 288301.7589 | 6382.8418 | 27232.4197 | 261069.3392 | 14024.7013 | 0.097538 | -108295.0262 | 108295.0262
C | Xist Rating 5786 | -13.49 | 1941.16 | 150.293 | 35.6 | 2038.8 | 8386.99 | 10537.7 | 0.31 | 1.25 | 19.194 | 12.836 | 1 | 1 | 2570 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3957637.008 | 290451.7234 | 6432.8051 | 27338.7963 | 263112.927 | 14015.618 | 0.097919 | -108224.8868 | 108224.8868
C | Xist Rating 5787 | -13.46 | 1942.53 | 150.293 | 35.6 | 2038.98 | 8389.91 | 10537.7 | 0.31 | 1.25 | 19.247 | 12.846 | 1 | 1 | 2580 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3960779.8194 | 292609.655 | 6482.9633 | 27445.173 | 265164.482 | 14030.5702 | 0.0983 | -108340.3438 | 108340.3438
C | Xist Rating 5788 | -13.44 | 1943.89 | 150.293 | 35.6 | 2038.64 | 8384.27 | 10537.6 | 0.3 | 1.25 | 19.244 | 12.856 | 1 | 1 | 2590 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3962891.9096 | 294775.5539 | 6533.3162 | 27551.5496 | 267224.0043 | 14021.1802 | 0.098681 | -108267.8369 | 108267.8369
C | Xist Rating 5789 | -13.42 | 1945.07 | 150.293 | 35.6 | 2038.55 | 8382.82 | 10537.6 | 0.3 | 1.25 | 19.24 | 12.866 | 1 | 1 | 2600 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3965122.4485 | 296949.4199 | 6583.8639 | 27657.9263 | 269291.4937 | 14034.0131 | 0.099062 | -108366.9295 | 108366.9295
C | Xist Rating 5790 | -13.4 | 1946.75 | 150.293 | 35.6 | 2037.89 | 8371.64 | 10537.6 | 0.29 | 1.25 | 19.24 | 12.877 | 1 | 1 | 2610 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3967262.3575 | 299131.2532 | 6634.6064 | 27764.3029 | 271366.9503 | 14025.5146 | 0.099443 | -108301.3058 | 108301.3058
C | Xist Rating 5791 | -13.37 | 1948.15 | 150.293 | 35.6 | 2037.76 | 8369.46 | 10537.6 | 0.29 | 1.25 | 19.24 | 12.887 | 1 | 1 | 2620 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3969862.144 | 301321.0537 | 6685.5437 | 27870.6795 | 273450.3741 | 14038.4006 | 0.099824 | -108400.8083 | 108400.8083
C | Xist Rating 5792 | -13.33 | 1949.58 | 150.294 | 35.6 | 2037.69 | 8368.27 | 10537.6 | 0.29 | 1.25 | 19.281 | 12.898 | 1 | 1 | 2630 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3972639.6702 | 303518.8214 | 6736.6758 | 27977.0562 | 275541.7652 | 14053.7268 | 0.10021 | -108519.1533 | 108519.1533
C | Xist Rating 5793 | -13.31 | 1950.82 | 150.294 | 35.6 | 2037.55 | 8365.9 | 10537.6 | 0.28 | 1.25 | 19.276 | 12.907 | 1 | 1 | 2640 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3974893.291 | 305724.5562 | 6788.0027 | 28083.4328 | 277641.1234 | 14042.5974 | 0.10059 | -108433.215 | 108433.215
C | Xist Rating 5794 | -13.26 | 1952.33 | 150.294 | 35.6 | 2037.66 | 8367.72 | 10537.6 | 0.28 | 1.25 | 19.277 | 12.918 | 1 | 1 | 2650 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3978184.7478 | 307938.2583 | 6839.5243 | 28189.8095 | 279748.4489 | 14056.4735 | 0.10097 | -108540.3623 | 108540.3623
C | Xist Rating 5795 | -13.24 | 1953.67 | 150.294 | 35.6 | 2037.55 | 8365.85 | 10537.6 | 0.28 | 1.25 | 19.274 | 12.928 | 1 | 1 | 2660 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3980700.3085 | 310159.9276 | 6891.2408 | 28296.1861 | 281863.7415 | 14069.1777 | 0.10135 | -108638.4612 | 108638.4612
C | Xist Rating 5796 | -13.2 | 1955.05 | 150.294 | 35.6 | 2037.58 | 8366.34 | 10537.6 | 0.27 | 1.25 | 19.273 | 12.938 | 1 | 1 | 2670 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3983570.779 | 312389.5641 | 6943.152 | 28402.5627 | 283987.0014 | 14058.882 | 0.10173 | -108558.9602 | 108558.9602
C | Xist Rating 5797 | -13.15 | 1956.47 | 150.294 | 35.6 | 2038.06 | 8374.47 | 10537.6 | 0.27 | 1.25 | 19.31 | 12.948 | 1 | 1 | 2680 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3987403.2482 | 314627.1678 | 6995.258 | 28508.9394 | 286118.2284 | 14072.7996 | 0.10211 | -108666.4285 | 108666.4285
C | Xist Rating 5798 | -13.08 | 1957.85 | 150.294 | 35.6 | 2039.02 | 8390.79 | 10537.6 | 0.26 | 1.25 | 19.311 | 12.957 | 1 | 1 | 2690 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3992095.307 | 316872.7387 | 7047.5588 | 28615.316 | 288257.4227 | 14061.2308 | 0.10249 | -108577.0972 | 108577.0972
C | Xist Rating 5799 | -13.01 | 1959.05 | 150.294 | 35.6 | 2040.3 | 8412.55 | 10537.5 | 0.26 | 1.25 | 19.31 | 12.966 | 1 | 1 | 2700 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3997049.715 | 319126.2768 | 7100.0544 | 28721.6927 | 290404.5842 | 14072.7964 | 0.10287 | -108666.4037 | 108666.4037
C | Xist Rating 5800 | -13.01 | 1960.7 | 150.294 | 35.6 | 2039.11 | 8392.3 | 10537.5 | 0.26 | 1.25 | 19.307 | 12.978 | 1 | 1 | 2710 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 3998082.977 | 321387.7821 | 7152.7448 | 28828.0693 | 292559.7128 | 14087.4141 | 0.10325 | -108779.2777 | 108779.2777
C | Xist Rating 5801 | -12.99 | 1962.05 | 150.294 | 35.6 | 2038.73 | 8385.84 | 10537.5 | 0.25 | 1.25 | 19.299 | 12.987 | 1 | 1 | 2720 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4000090.1965 | 323657.2546 | 7205.63 | 28934.4459 | 294722.8087 | 14075.2272 | 0.10363 | -108685.1734 | 108685.1734
C | Xist Rating 5802 | -12.97 | 1963.37 | 150.294 | 35.6 | 2038.26 | 8377.92 | 10537.5 | 0.25 | 1.25 | 19.336 | 12.997 | 1 | 1 | 2730 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4001858.5362 | 325934.6944 | 7258.71 | 29040.8226 | 296893.8718 | 14088.9068 | 0.10402 | -108790.8037 | 108790.8037
C | Xist Rating 5803 | -12.99 | 1964.65 | 150.294 | 35.6 | 2037.12 | 8358.65 | 10537.5 | 0.25 | 1.25 | 19.328 | 13.006 | 1 | 1 | 2740 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4002227.808 | 328220.1013 | 7311.9847 | 29147.1992 | 299072.9021 | 14100.1745 | 0.1044 | -108877.8096 | 108877.8096
C | Xist Rating 5804 | -13.01 | 1966.2 | 150.294 | 35.6 | 2035.6 | 8333.25 | 10537.5 | 0.25 | 1.25 | 19.326 | 13.016 | 1 | 1 | 2750 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4002396.72 | 330513.4754 | 7365.4543 | 29253.5759 | 301259.8996 | 14112.6637 | 0.10478 | -108974.2485 | 108974.2485
C | Xist Rating 5805 | -13 | 1967.63 | 150.294 | 35.6 | 2035.2 | 8326.42 | 10537.5 | 0.24 | 1.25 | 19.326 | 13.026 | 1 | 1 | 2760 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4004520.576 | 332814.8167 | 7419.1186 | 29359.9525 | 303454.8642 | 14101.3051 | 0.10516 | -108886.5398 | 108886.5398
C | Xist Rating 5806 | -13.01 | 1968.86 | 150.294 | 35.6 | 2034.22 | 8310.19 | 10537.4 | 0.24 | 1.25 | 19.319 | 13.035 | 1 | 1 | 2770 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4005094.3892 | 335124.1253 | 7472.9777 | 29466.3291 | 305657.7961 | 14112.522 | 0.10554 | -108973.1543 | 108973.1543
C | Xist Rating 5807 | -12.99 | 1970.41 | 150.294 | 35.6 | 2033.73 | 8301.91 | 10537.5 | 0.24 | 1.25 | 19.362 | 13.045 | 1 | 1 | 2780 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4007281.9293 | 337441.401 | 7527.0316 | 29572.7058 | 307868.6952 | 14126.2713 | 0.10592 | -109079.3228 | 109079.3228
C | Xist Rating 5808 | -13.01 | 1971.82 | 150.294 | 35.6 | 2032.45 | 8280.6 | 10537.5 | 0.23 | 1.25 | 19.356 | 13.055 | 1 | 1 | 2790 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4007625.559 | 339766.6439 | 7581.2803 | 29679.0824 | 310087.5615 | 14114.3524 | 0.1063 | -108987.288 | 108987.288
C | Xist Rating 5809 | -12.96 | 1972.79 | 150.294 | 35.6 | 2033.24 | 8293.64 | 10537.5 | 0.23 | 1.25 | 19.362 | 13.063 | 1 | 1 | 2800 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4011155.5396 | 342099.8541 | 7635.7238 | 29785.459 | 312314.395 | 14124.8291 | 0.10668 | -109068.1866 | 109068.1866
C | Xist Rating 5810 | -12.94 | 1974.54 | 150.294 | 35.6 | 2032.56 | 8282.5 | 10537.6 | 0.23 | 1.25 | 19.367 | 13.074 | 1 | 1 | 2810 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4013371.0224 | 344441.0314 | 7690.3621 | 29891.8357 | 314549.1957 | 14138.3936 | 0.10706 | -109172.928 | 109172.928
C | Xist Rating 5811 | -12.96 | 1976.01 | 150.294 | 35.6 | 2031.14 | 8258.83 | 10537.5 | 0.23 | 1.25 | 19.362 | 13.084 | 1 | 1 | 2820 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4013552.9514 | 346790.176 | 7745.1952 | 29998.2123 | 316791.9637 | 14150.6299 | 0.10744 | -109267.4134 | 109267.4134
C | Xist Rating 5812 | -12.9 | 1977.38 | 150.294 | 35.6 | 2031.66 | 8267.55 | 10537.6 | 0.22 | 1.25 | 19.412 | 13.093 | 1 | 1 | 2830 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4017363.8508 | 349147.2877 | 7800.223 | 30104.589 | 319042.6988 | 14138.8065 | 0.10783 | -109176.1163 | 109176.1163
C | Xist Rating 5813 | -12.82 | 1978.7 | 150.294 | 35.6 | 2032.72 | 8285.09 | 10537.6 | 0.22 | 1.25 | 19.426 | 13.102 | 1 | 1 | 2840 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4022143.064 | 351512.3667 | 7855.4457 | 30210.9656 | 321301.4011 | 14150.4594 | 0.10821 | -109266.0967 | 109266.0967
C | Xist Rating 5814 | -12.63 | 1980.15 | 150.294 | 35.6 | 2036.36 | 8345.8 | 10537.7 | 0.22 | 1.25 | 19.458 | 13.112 | 1 | 1 | 2850 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4032298.254 | 353885.4129 | 7910.8631 | 30317.3422 | 323568.0706 | 14163.6594 | 0.10859 | -109368.0238 | 109368.0238
C | Xist Rating 5815 | -12.6 | 1981.55 | 150.294 | 35.6 | 2036.25 | 8343.91 | 10537.7 | 0.21 | 1.25 | 19.462 | 13.122 | 1 | 1 | 2860 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4034931.1875 | 356266.4262 | 7966.4753 | 30423.7189 | 325842.7074 | 14151.1261 | 0.10897 | -109271.2446 | 109271.2446
C | Xist Rating 5816 | -11.98 | 1982.74 | 150.294 | 35.6 | 2050.48 | 8587.93 | 10538 | 0.21 | 1.25 | 19.554 | 13.131 | 1 | 1 | 2870 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4065568.7152 | 358655.4068 | 8022.2824 | 30530.0955 | 328125.3113 | 14164.79 | 0.10935 | -109376.7538 | 109376.7538
C | Xist Rating 5817 | -11.54 | 1984.25 | 150.294 | 35.6 | 2059.95 | 8756.53 | 10538.1 | 0.21 | 1.25 | 19.64 | 13.142 | 1 | 1 | 2880 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4087455.7875 | 361052.3546 | 8078.2842 | 30636.4722 | 330415.8824 | 14180.3856 | 0.10973 | -109497.1788 | 109497.1788
C | Xist Rating 5818 | -11.47 | 1985.59 | 150.294 | 35.6 | 2060.93 | 8774.27 | 10538.1 | 0.2 | 1.25 | 19.64 | 13.151 | 1 | 1 | 2890 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4092161.9987 | 363457.2696 | 8134.4807 | 30742.8488 | 332714.4208 | 14166.1385 | 0.11011 | -109387.1668 | 109387.1668
C | Xist Rating 5819 | -11.26 | 1986.98 | 150.294 | 35.6 | 2065.13 | 8850.77 | 10538.1 | 0.2 | 1.25 | 19.656 | 13.161 | 1 | 1 | 2900 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4103372.0074 | 365870.1518 | 8190.8721 | 30849.2254 | 335020.9263 | 14178.7002 | 0.11049 | -109484.1647 | 109484.1647
C | Xist Rating 5820 | -11.02 | 1988.52 | 150.294 | 35.6 | 2069.92 | 8939.62 | 10538 | 0.2 | 1.25 | 19.681 | 13.171 | 1 | 1 | 2910 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4116077.3184 | 368291.0011 | 8247.4583 | 30955.6021 | 337335.3991 | 14191.4995 | 0.11087 | -109582.9977 | 109582.9977
C | Xist Rating 5821 | -10.8 | 1989.91 | 150.294 | 35.6 | 2074.27 | 9021.36 | 10538 | 0.2 | 1.25 | 19.701 | 13.181 | 1 | 1 | 2920 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4127610.6157 | 370719.8177 | 8304.2393 | 31061.9787 | 339657.839 | 14204.1725 | 0.11125 | -109680.8547 | 109680.8547
C | Xist Rating 5822 | -10.54 | 1991.3 | 150.294 | 35.6 | 2079.46 | 9120.12 | 10538.1 | 0.19 | 1.25 | 19.762 | 13.19 | 1 | 1 | 2930 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4140828.698 | 373156.6015 | 8361.215 | 31168.3554 | 341988.2462 | 14190.9328 | 0.11164 | -109578.6213 | 109578.6213
C | Xist Rating 5823 | -10.4 | 1992.66 | 150.294 | 35.6 | 2082.38 | 9176.9 | 10537.8 | 0.19 | 1.25 | 19.776 | 13.199 | 1 | 1 | 2940 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4149475.3308 | 375601.3525 | 8418.3855 | 31274.732 | 344326.6205 | 14202.3129 | 0.11202 | -109666.4954 | 109666.4954
C | Xist Rating 5824 | -10.05 | 1994.07 | 150.294 | 35.6 | 2089.47 | 9316.05 | 10538 | 0.19 | 1.25 | 19.809 | 13.209 | 1 | 1 | 2950 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4166549.4429 | 378054.0707 | 8475.7509 | 31381.1086 | 346672.9621 | 14215.2112 | 0.1124 | -109766.093 | 109766.093
C | Xist Rating 5825 | -9.71 | 1995.44 | 150.294 | 35.5 | 2096.91 | 9465.82 | 10537.9 | 0.19 | 1.25 | 19.824 | 13.219 | 1 | 1 | 2960 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4184258.0904 | 380514.7561 | 8533.311 | 31487.4853 | 349027.2709 | 14227.6614 | 0.11278 | -109862.2301 | 109862.2301
C | Xist Rating 5826 | -9.7 | 1996.83 | 150.294 | 35.5 | 2096.25 | 9452.43 | 10537.9 | 0.18 | 1.25 | 19.821 | 13.228 | 1 | 1 | 2970 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4185854.8875 | 382983.4088 | 8591.0659 | 31593.8619 | 351389.5468 | 14212.2328 | 0.11316 | -109743.0946 | 109743.0946
C | Xist Rating 5827 | -9.7 | 1998.05 | 150.294 | 35.5 | 2095.66 | 9440.48 | 10537.9 | 0.18 | 1.25 | 19.856 | 13.236 | 1 | 1 | 2980 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4187233.463 | 385460.0286 | 8649.0156 | 31700.2386 | 353759.79 | 14222.9816 | 0.11354 | -109826.0937 | 109826.0937
C | Xist Rating 5828 | -9.68 | 1999.61 | 150.294 | 35.5 | 2094.97 | 9426.46 | 10537.9 | 0.18 | 1.25 | 19.851 | 13.246 | 1 | 1 | 2990 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4189122.9617 | 387944.6156 | 8707.16 | 31806.6152 | 356138.0004 | 14234.848 | 0.11392 | -109917.7232 | 109917.7232
C | Xist Rating 5829 | -9.67 | 2001.04 | 150.294 | 35.5 | 2094.47 | 9416.46 | 10537.8 | 0.18 | 1.25 | 19.834 | 13.255 | 1 | 1 | 3000 | 152.4 | 2 | 3.8 | 19.05 | 1.3333 | 22 | E | Rod | 4191118.2488 | 390437.1698 | 8765.4993 | 31912.9918 | 358524.178 | 14245.3847 | 0.1143 | -109999.0845 | 109999.0845
C | Xist Rating 5830 | -88.96 | 201.403 | 150.298 | 35.9 | 2373.96 | 7165.05 | 58745.9 | 2.46 | 10.95 | 21.381 | 514.134 | 1 | 1 | 1000 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 478122.6659 | 51801.9386 | 973.9444 | 10917.6025 | 40884.3361 | 536284.9999 | 0.038101 | -4141050.6156 | 4141050.6156
C | Xist Rating 5831 | -88.86 | 203.493 | 150.298 | 35.9 | 2371.94 | 7154.6 | 58284.3 | 2.45 | 10.85 | 21.443 | 504.481 | 1 | 1 | 1010 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 482673.1864 | 52732.8897 | 993.5206 | 11026.7785 | 41706.1112 | 526281.1483 | 0.038482 | -4063803.5257 | 4063803.5257
C | Xist Rating 5832 | -88.03 | 219.317 | 150.299 | 35.9 | 2365.28 | 7154.81 | 54967.7 | 2.46 | 10.07 | 21.495 | 437.184 | 1 | 1 | 1020 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 518746.1138 | 53672.0178 | 1013.2917 | 11135.9545 | 42536.0633 | 456432.5217 | 0.038863 | -3524450.9453 | 3524450.9453
C | Xist Rating 5833 | -87.89 | 223.644 | 150.298 | 35.9 | 2347.34 | 7008.08 | 54178.4 | 2.37 | 9.89 | 21.009 | 422.51 | 1 | 1 | 1030 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 524968.507 | 54619.3227 | 1033.2576 | 11245.1305 | 43374.1922 | 441074.8023 | 0.039244 | -3405862.7072 | 3405862.7072
C | Xist Rating 5834 | -87.81 | 225.809 | 150.297 | 35.9 | 2341.32 | 6962.05 | 53793.6 | 2.33 | 9.8 | 20.894 | 415.488 | 1 | 1 | 1040 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 528691.1279 | 55574.8045 | 1053.4182 | 11354.3066 | 44220.4979 | 433753.1184 | 0.039625 | -3349326.6049 | 3349326.6049
C | Xist Rating 5835 | -87.62 | 230.014 | 150.297 | 35.9 | 2335.1 | 6921.82 | 53042.7 | 2.29 | 9.63 | 20.817 | 401.71 | 1 | 1 | 1050 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 537105.6914 | 56538.4631 | 1073.7737 | 11463.4826 | 45074.9805 | 419418.8743 | 0.040006 | -3238641.3713 | 3238641.3713
C | Xist Rating 5836 | -87.47 | 232.159 | 150.297 | 35.9 | 2343.08 | 6999.77 | 52676.8 | 2.25 | 9.54 | 20.804 | 395.197 | 1 | 1 | 1060 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 543967.1097 | 57510.2986 | 1094.3239 | 11572.6586 | 45937.64 | 412635.5485 | 0.040387 | -3186262.3281 | 3186262.3281
C | Xist Rating 5837 | -86.65 | 249.184 | 150.297 | 35.9 | 2326.13 | 6909.11 | 49857.2 | 2.23 | 8.9 | 20.623 | 345.787 | 1 | 1 | 1070 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 579634.3779 | 58490.311 | 1115.0689 | 11681.8346 | 46808.4764 | 361305.0084 | 0.040768 | -2789901.5033 | 2789901.5033
C | Xist Rating 5838 | -86.44 | 252.405 | 150.296 | 35.9 | 2333.06 | 6981.4 | 49380.5 | 2.17 | 8.79 | 20.531 | 338.037 | 1 | 1 | 1080 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 588876.0093 | 59478.5003 | 1136.0087 | 11791.0107 | 47687.4896 | 353207.6931 | 0.041149 | -2727376.1813 | 2727376.1813
C | Xist Rating 5839 | -86.2 | 256.69 | 150.296 | 35.8 | 2335.97 | 7022.07 | 48761.4 | 2.12 | 8.65 | 20.384 | 328.079 | 1 | 1 | 1090 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 599620.1393 | 60474.8664 | 1157.1433 | 11900.1867 | 48574.6797 | 342820.9138 | 0.04153 | -2647172.2248 | 2647172.2248
C | Xist Rating 5840 | -85.98 | 259.88 | 150.296 | 35.8 | 2344.38 | 7109.84 | 48308.1 | 2.08 | 8.55 | 20.384 | 320.891 | 1 | 1 | 1100 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 609257.4744 | 61479.4094 | 1178.4727 | 12009.3627 | 49470.0467 | 335335.3547 | 0.041911 | -2589370.7214 | 2589370.7214
C | Xist Rating 5841 | -85.88 | 262.213 | 150.295 | 35.8 | 2341.51 | 7090.94 | 48011 | 2 | 8.49 | 20.085 | 316.49 | 1 | 1 | 1110 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 613974.3616 | 62492.1292 | 1199.9969 | 12118.5387 | 50373.5905 | 330673.0375 | 0.042292 | -2553369.5436 | 2553369.5436
C | Xist Rating 5842 | -84.89 | 281.153 | 150.296 | 35.8 | 2337.32 | 7120.45 | 45448.3 | 2.04 | 7.92 | 20.345 | 276.927 | 1 | 1 | 1120 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 657144.53 | 63513.026 | 1221.7158 | 12227.7148 | 51285.3112 | 289671.8922 | 0.042673 | -2236769.5677 | 2236769.5677
C | Xist Rating 5843 | -84.77 | 283.44 | 150.296 | 35.8 | 2337.95 | 7133.67 | 45189.3 | 1.98 | 7.86 | 20.155 | 273.376 | 1 | 1 | 1130 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 662668.548 | 64542.0995 | 1243.6296 | 12336.8908 | 52205.2087 | 285921.9023 | 0.043054 | -2207813.1397 | 2207813.1397
C | Xist Rating 5844 | -84.57 | 287.795 | 150.295 | 35.8 | 2334.75 | 7118.6 | 44681.5 | 1.92 | 7.75 | 19.979 | 266.239 | 1 | 1 | 1140 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 671929.3763 | 65579.35 | 1265.7381 | 12446.0668 | 53133.2832 | 278448.9641 | 0.043435 | -2150109.0919 | 2150109.0919
C | Xist Rating 5845 | -84.34 | 292.088 | 150.295 | 35.8 | 2335.15 | 7137 | 44186.2 | 1.88 | 7.64 | 19.797 | 259.331 | 1 | 1 | 1150 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 682069.2932 | 66624.7773 | 1288.0414 | 12555.2428 | 54069.5345 | 271233.3784 | 0.043816 | -2094392.2522 | 2094392.2522
C | Xist Rating 5846 | -84.14 | 296.459 | 150.294 | 35.8 | 2331.54 | 7117.93 | 43703.3 | 1.83 | 7.53 | 19.642 | 252.762 | 1 | 1 | 1160 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 691206.0169 | 67678.3815 | 1310.5395 | 12664.4189 | 55013.9626 | 264361.9477 | 0.044197 | -2041332.8851 | 2041332.8851
C | Xist Rating 5847 | -83.24 | 313.47 | 150.295 | 35.8 | 2329.93 | 7162.85 | 41832.4 | 1.85 | 7.13 | 19.79 | 227.366 | 1 | 1 | 1170 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 730363.1571 | 68740.1626 | 1333.2324 | 12773.5949 | 55966.5677 | 238039.3158 | 0.044578 | -1838076.4993 | 1838076.4993
C | Xist Rating 5848 | -83.11 | 314.706 | 150.294 | 35.8 | 2340.41 | 7266.54 | 41724.7 | 1.8 | 7.11 | 19.715 | 226.142 | 1 | 1 | 1180 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 736541.0695 | 69810.1205 | 1356.1201 | 12882.7709 | 56927.3496 | 236725.1264 | 0.044959 | -1827928.6774 | 1827928.6774
C | Xist Rating 5849 | -82.73 | 323.277 | 150.294 | 35.8 | 2331.25 | 7208.27 | 40885.4 | 1.75 | 6.93 | 19.553 | 215.541 | 1 | 1 | 1190 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 753639.5062 | 70888.2553 | 1379.2026 | 12991.9469 | 57896.3083 | 225664.2081 | 0.04534 | -1742519.1981 | 1742519.1981
C | Xist Rating 5850 | -82.52 | 325.456 | 150.294 | 35.8 | 2344.13 | 7340.46 | 40682.3 | 1.72 | 6.88 | 19.594 | 213.069 | 1 | 1 | 1200 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 762911.1733 | 71974.5669 | 1402.4799 | 13101.123 | 58873.444 | 223084.6188 | 0.045721 | -1722600.2934 | 1722600.2934
C | Xist Rating 5851 | -82.31 | 329.897 | 150.294 | 35.8 | 2341.39 | 7328.7 | 40281.9 | 1.66 | 6.8 | 19.457 | 208.261 | 1 | 1 | 1210 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 772417.5368 | 73069.0555 | 1425.9519 | 13210.299 | 59858.7565 | 218030.5262 | 0.046102 | -1683573.9295 | 1683573.9295
C | Xist Rating 5852 | -81.38 | 349.19 | 150.294 | 35.8 | 2329.19 | 7278.3 | 38538.1 | 1.67 | 6.43 | 19.462 | 187.277 | 1 | 1 | 1220 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 813329.8561 | 74171.7208 | 1449.6188 | 13319.475 | 60852.2458 | 196264.25 | 0.046483 | -1515500.5145 | 1515500.5145
C | Xist Rating 5853 | -81.11 | 353.481 | 150.294 | 35.8 | 2335.37 | 7353.92 | 38183.2 | 1.64 | 6.35 | 19.472 | 183.26 | 1 | 1 | 1230 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 825508.923 | 75282.5631 | 1473.4804 | 13428.651 | 61853.9121 | 192075.884 | 0.046864 | -1483159.0627 | 1483159.0627
C | Xist Rating 5854 | -80.88 | 357.912 | 150.294 | 35.8 | 2335.12 | 7366.49 | 37835.6 | 1.6 | 6.28 | 19.376 | 179.443 | 1 | 1 | 1240 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 835767.4694 | 76401.5822 | 1497.5369 | 13537.8271 | 62863.7552 | 188074.4203 | 0.047245 | -1452260.8202 | 1452260.8202
C | Xist Rating 5855 | -80.73 | 360.235 | 150.293 | 35.8 | 2339.32 | 7415.93 | 37664.6 | 1.56 | 6.24 | 19.311 | 177.65 | 1 | 1 | 1250 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 842704.9402 | 77528.7782 | 1521.7881 | 13647.0031 | 63881.7751 | 186177.1813 | 0.047626 | -1437610.844 | 1437610.844
C | Xist Rating 5856 | -80.4 | 366.694 | 150.293 | 35.8 | 2338.28 | 7428.29 | 37161.6 | 1.53 | 6.14 | 19.269 | 172.135 | 1 | 1 | 1260 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 857433.2463 | 78664.1511 | 1546.2341 | 13756.1791 | 64907.972 | 180427.0167 | 0.048007 | -1393209.5968 | 1393209.5968
C | Xist Rating 5857 | -79.49 | 384.968 | 150.293 | 35.8 | 2331.44 | 7425.12 | 35777.7 | 1.54 | 5.85 | 19.333 | 157.206 | 1 | 1 | 1270 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 897529.7939 | 79807.7008 | 1570.8749 | 13865.3551 | 65942.3457 | 164953.0689 | 0.048388 | -1273723.8735 | 1273723.8735
C | Xist Rating 5858 | -79.29 | 389.467 | 150.293 | 35.8 | 2328.45 | 7409.79 | 35477.4 | 1.49 | 5.79 | 19.229 | 154.224 | 1 | 1 | 1280 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 906854.4361 | 80959.4274 | 1595.7105 | 13974.5312 | 66984.8962 | 161805.2591 | 0.048769 | -1249417.3213 | 1249417.3213
C | Xist Rating 5859 | -79.07 | 393.914 | 150.293 | 35.8 | 2327.44 | 7414.49 | 35182.8 | 1.46 | 5.73 | 19.189 | 151.31 | 1 | 1 | 1290 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 916811.2002 | 82119.3309 | 1620.7408 | 14083.7072 | 68035.6237 | 158755.1838 | 0.04915 | -1225865.4482 | 1225865.4482
C | Xist Rating 5860 | -78.71 | 400.352 | 150.293 | 35.8 | 2330.32 | 7466.28 | 34751.5 | 1.44 | 5.64 | 19.227 | 147.002 | 1 | 1 | 1300 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 932948.2726 | 83287.4112 | 1645.966 | 14192.8832 | 69094.528 | 154274.7157 | 0.049531 | -1191268.4609 | 1191268.4609
C | Xist Rating 5861 | -78.49 | 403.766 | 150.293 | 35.8 | 2336.03 | 7536.76 | 34540.1 | 1.4 | 5.59 | 19.179 | 145.005 | 1 | 1 | 1310 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 943209.489 | 84463.6684 | 1671.3859 | 14302.0592 | 70161.6092 | 152164.1383 | 0.049912 | -1174971.1416 | 1174971.1416
C | Xist Rating 5862 | -77.58 | 422.137 | 150.293 | 35.8 | 2329.47 | 7535.02 | 33363.1 | 1.41 | 5.35 | 19.23 | 133.541 | 1 | 1 | 1320 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 983355.4774 | 85648.1025 | 1697.0007 | 14411.2353 | 71236.8672 | 140286.4309 | 0.050293 | -1083254.6332 | 1083254.6332
C | Xist Rating 5863 | -77.25 | 428.792 | 150.293 | 35.8 | 2327.48 | 7536.89 | 32980 | 1.37 | 5.28 | 19.136 | 130.057 | 1 | 1 | 1330 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 998004.8042 | 86840.7134 | 1722.8102 | 14520.4113 | 72320.3021 | 136626.9216 | 0.050674 | -1054996.8725 | 1054996.8725
C | Xist Rating 5864 | -76.89 | 435.345 | 150.293 | 35.8 | 2329.78 | 7584.02 | 32606.8 | 1.34 | 5.2 | 19.055 | 126.687 | 1 | 1 | 1340 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1014258.0741 | 88041.5012 | 1748.8145 | 14629.5873 | 73411.9139 | 133097.9317 | 0.051055 | -1027746.948 | 1027746.948
C | Xist Rating 5865 | -76.68 | 438.777 | 150.293 | 35.8 | 2334.43 | 7645.11 | 32423.8 | 1.31 | 5.16 | 19.02 | 125.11 | 1 | 1 | 1350 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1024294.1921 | 89250.4659 | 1775.0136 | 14738.7633 | 74511.7025 | 131434.2981 | 0.051436 | -1014900.8106 | 1014900.8106
C | Xist Rating 5866 | -76.42 | 440.902 | 150.293 | 35.8 | 2349.28 | 7814.73 | 32303.4 | 1.3 | 5.14 | 19.093 | 124.041 | 1 | 1 | 1360 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1035802.2506 | 90467.6074 | 1801.4075 | 14847.9394 | 75619.668 | 130329.5023 | 0.051817 | -1006369.87 | 1006369.87
C | Xist Rating 5867 | -75.3 | 466.994 | 150.293 | 35.8 | 2323.93 | 7634.09 | 30902.5 | 1.29 | 4.86 | 19.026 | 111.774 | 1 | 1 | 1370 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1085261.3664 | 91692.9258 | 1827.9962 | 14957.1154 | 76735.8104 | 117584.3354 | 0.052198 | -907955.0701 | 907955.0701
C | Xist Rating 5868 | -75.2 | 469.381 | 150.293 | 35.8 | 2323.52 | 7637.28 | 30794.1 | 1.26 | 4.84 | 18.987 | 110.939 | 1 | 1 | 1380 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1090616.1411 | 92926.4211 | 1854.7797 | 15066.2914 | 77860.1296 | 116689.8438 | 0.052579 | -901048.0427 | 901048.0427
C | Xist Rating 5869 | -74.9 | 474.96 | 150.293 | 35.7 | 2324.36 | 7665.57 | 30526.9 | 1.24 | 4.78 | 18.951 | 108.773 | 1 | 1 | 1390 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1103978.0256 | 94168.0932 | 1881.7579 | 15175.4674 | 78992.6258 | 114424.7384 | 0.05296 | -883557.499 | 883557.499
C | Xist Rating 5870 | -74.6 | 480.536 | 150.292 | 35.7 | 2325.64 | 7698.68 | 30265.1 | 1.21 | 4.73 | 18.922 | 106.673 | 1 | 1 | 1400 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1117553.743 | 95417.9422 | 1908.931 | 15284.6435 | 80133.2987 | 112216.5453 | 0.053341 | -866506.4171 | 866506.4171
C | Xist Rating 5871 | -74.25 | 487.15 | 150.292 | 35.7 | 2326.62 | 7732.81 | 29957.4 | 1.19 | 4.67 | 18.901 | 104.216 | 1 | 1 | 1410 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1133412.933 | 96675.9681 | 1936.2988 | 15393.8195 | 81282.1486 | 109649.7196 | 0.053722 | -846686.0701 | 846686.0701
C | Xist Rating 5872 | -73.29 | 506.687 | 150.293 | 35.7 | 2321.51 | 7747.82 | 29051.9 | 1.2 | 4.49 | 18.969 | 96.976 | 1 | 1 | 1420 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1176278.9374 | 97942.1708 | 1963.8614 | 15502.9955 | 82439.1753 | 102158.2977 | 0.054103 | -788839.2958 | 788839.2958
C | Xist Rating 5873 | -73.12 | 510.359 | 150.292 | 35.7 | 2320.81 | 7751.62 | 28910.7 | 1.16 | 4.47 | 18.891 | 95.987 | 1 | 1 | 1430 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1184446.2708 | 99216.5504 | 1991.6188 | 15612.1715 | 83604.3789 | 101086.9905 | 0.054484 | -780566.9453 | 780566.9453
C | Xist Rating 5874 | -72.69 | 519.098 | 150.292 | 35.7 | 2318.65 | 7758.37 | 28542 | 1.14 | 4.39 | 18.874 | 93.21 | 1 | 1 | 1440 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1203606.5777 | 100499.1069 | 2019.571 | 15721.3476 | 84777.7593 | 98187.2648 | 0.054865 | -758176.0321 | 758176.0321
C | Xist Rating 5875 | -72.38 | 524.712 | 150.292 | 35.7 | 2320.63 | 7799.98 | 28316.9 | 1.12 | 4.35 | 18.854 | 91.573 | 1 | 1 | 1450 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1217662.4086 | 101789.8402 | 2047.718 | 15830.5236 | 85959.3166 | 96470.897 | 0.055246 | -744922.6951 | 744922.6951
C | Xist Rating 5876 | -72.14 | 528.025 | 150.292 | 35.7 | 2327.54 | 7890.54 | 28183.6 | 1.11 | 4.32 | 18.877 | 90.612 | 1 | 1 | 1460 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1228999.3085 | 103088.7504 | 2076.0598 | 15939.6996 | 87149.0508 | 95471.6974 | 0.055627 | -737207.1405 | 737207.1405
C | Xist Rating 5877 | -71.17 | 550.115 | 150.292 | 35.7 | 2312.21 | 7795.67 | 27310.3 | 1.1 | 4.16 | 18.858 | 84.261 | 1 | 1 | 1470 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1271981.4042 | 104395.8375 | 2104.5964 | 16048.8756 | 88346.9618 | 88871.7706 | 0.056008 | -686244.2555 | 686244.2555
C | Xist Rating 5878 | -70.83 | 556.773 | 150.292 | 35.7 | 2312.57 | 7822.91 | 27066.3 | 1.08 | 4.11 | 18.843 | 82.577 | 1 | 1 | 1480 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1287576.5366 | 105711.1014 | 2133.3277 | 16158.0517 | 89553.0498 | 87106.1419 | 0.056389 | -672610.5387 | 672610.5387
C | Xist Rating 5879 | -70.53 | 562.389 | 150.292 | 35.7 | 2313.92 | 7857.8 | 26866.5 | 1.07 | 4.07 | 18.83 | 81.228 | 1 | 1 | 1490 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1301323.1549 | 107034.5422 | 2162.2539 | 16267.2277 | 90767.3145 | 85700.8156 | 0.05677 | -661758.9809 | 661758.9809
C | Xist Rating 5880 | -70.24 | 568.096 | 150.292 | 35.7 | 2314.22 | 7880.77 | 26670.3 | 1.04 | 4.03 | 18.806 | 79.927 | 1 | 1 | 1500 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1314699.1251 | 108366.1599 | 2191.3748 | 16376.4037 | 91989.7562 | 84319.1 | 0.057151 | -651089.7398 | 651089.7398
C | Xist Rating 5881 | -69.84 | 574.781 | 150.292 | 35.7 | 2318.52 | 7954.77 | 26438.9 | 1.03 | 3.99 | 18.808 | 78.385 | 1 | 1 | 1510 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1332641.2441 | 109705.9544 | 2220.6906 | 16485.5797 | 93220.3747 | 82713.9129 | 0.057532 | -638694.9105 | 638694.9105
C | Xist Rating 5882 | -68.75 | 596.555 | 150.292 | 35.7 | 2316.29 | 8010.04 | 25681 | 1.03 | 3.84 | 18.886 | 73.289 | 1 | 1 | 1520 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1381794.3809 | 111053.9258 | 2250.2011 | 16594.7558 | 94459.1701 | 77435.8824 | 0.057913 | -597939.3576 | 597939.3576
C | Xist Rating 5883 | -68.45 | 603.583 | 150.292 | 35.7 | 2311.38 | 7975.4 | 25468.5 | 1 | 3.8 | 18.817 | 71.988 | 1 | 1 | 1530 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1395109.6745 | 112410.0741 | 2279.9064 | 16703.9318 | 95706.1423 | 76049.9263 | 0.058294 | -587237.3723 | 587237.3723
C | Xist Rating 5884 | -68.21 | 607.171 | 150.292 | 35.7 | 2316.09 | 8043.82 | 25363.6 | 0.98 | 3.78 | 18.806 | 71.368 | 1 | 1 | 1540 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1406262.6814 | 113774.3993 | 2309.8065 | 16813.1078 | 96961.2915 | 75387.7691 | 0.058675 | -582124.3696 | 582124.3696
C | Xist Rating 5885 | -67.67 | 618.162 | 150.292 | 35.7 | 2314.75 | 8067.87 | 25021.1 | 0.97 | 3.72 | 18.8 | 69.218 | 1 | 1 | 1550 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1430890.4895 | 115146.9013 | 2339.9013 | 16922.2838 | 98224.6174 | 73149.7882 | 0.059056 | -564843.2742 | 564843.2742
C | Xist Rating 5886 | -67.35 | 621.524 | 150.292 | 35.7 | 2326.15 | 8220.6 | 24920.5 | 0.96 | 3.7 | 18.839 | 68.614 | 1 | 1 | 1560 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1445758.0526 | 116527.5802 | 2370.191 | 17031.4599 | 99496.1203 | 72520.1812 | 0.059437 | -559981.6163 | 559981.6163
C | Xist Rating 5887 | -66.3 | 647.11 | 150.292 | 35.7 | 2306.61 | 8074.98 | 24162.2 | 0.95 | 3.56 | 18.788 | 63.975 | 1 | 1 | 1570 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1492630.3971 | 117916.4359 | 2400.6755 | 17140.6359 | 100775.8 | 67694.0262 | 0.059818 | -522715.3268 | 522715.3268
C | Xist Rating 5888 | -65.96 | 652.846 | 150.292 | 35.7 | 2310.21 | 8139.58 | 24007.4 | 0.93 | 3.53 | 18.781 | 63.095 | 1 | 1 | 1580 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1508211.3577 | 119313.4685 | 2431.3547 | 17249.8119 | 102063.6566 | 66761.0747 | 0.0602 | -515511.3225 | 515511.3225
C | Xist Rating 5889 | -65.63 | 658.618 | 150.292 | 35.7 | 2312.73 | 8191.47 | 23854.9 | 0.92 | 3.5 | 18.771 | 62.237 | 1 | 1 | 1590 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1523205.6071 | 120718.678 | 2462.2288 | 17358.9879 | 103359.6901 | 65863.8311 | 0.060581 | -508583.0455 | 508583.0455
C | Xist Rating 5890 | -65.18 | 666.371 | 150.292 | 35.7 | 2316.66 | 8270.11 | 23645.1 | 0.91 | 3.46 | 18.782 | 61.033 | 1 | 1 | 1600 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1543755.0409 | 122132.0643 | 2493.2976 | 17468.164 | 104663.9004 | 64608.4754 | 0.060962 | -498889.5213 | 498889.5213
C | Xist Rating 5891 | -64.97 | 670.155 | 150.292 | 35.7 | 2318.42 | 8305.17 | 23556.4 | 0.88 | 3.45 | 18.757 | 60.577 | 1 | 1 | 1610 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1553700.7551 | 123553.6275 | 2524.5612 | 17577.34 | 105976.2876 | 64100.3301 | 0.061343 | -494965.7579 | 494965.7579
C | Xist Rating 5892 | -63.76 | 698.766 | 150.292 | 35.7 | 2301.98 | 8205.08 | 22804.4 | 0.89 | 3.31 | 18.769 | 56.299 | 1 | 1 | 1620 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1608545.3567 | 124983.3676 | 2556.0196 | 17686.516 | 107296.8516 | 59679.4288 | 0.061724 | -460828.73 | 460828.73
C | Xist Rating 5893 | -63.43 | 702.204 | 150.292 | 35.7 | 2312.13 | 8348.13 | 22722.8 | 0.88 | 3.29 | 18.792 | 55.875 | 1 | 1 | 1630 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1623586.9345 | 126421.2846 | 2587.6728 | 17795.692 | 108625.5925 | 59234.3586 | 0.062105 | -457392.0156 | 457392.0156
C | Xist Rating 5894 | -63.14 | 708.123 | 150.292 | 35.7 | 2312.13 | 8369.16 | 22588 | 0.86 | 3.27 | 18.768 | 55.183 | 1 | 1 | 1640 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1637272.432 | 127867.3784 | 2619.5208 | 17904.8681 | 109962.5103 | 58493.9841 | 0.062486 | -451675.0401 | 451675.0401
C | Xist Rating 5895 | -62.78 | 716.234 | 150.292 | 35.7 | 2309.31 | 8361.68 | 22402.4 | 0.84 | 3.23 | 18.742 | 54.22 | 1 | 1 | 1650 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1654006.3385 | 129321.6491 | 2651.5635 | 18014.0441 | 111307.605 | 57471.7679 | 0.062867 | -443781.7572 | 443781.7572
C | Xist Rating 5896 | -62.35 | 724.102 | 150.292 | 35.7 | 2311.06 | 8414.39 | 22220.3 | 0.83 | 3.2 | 18.746 | 53.268 | 1 | 1 | 1660 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1673443.1681 | 130784.0966 | 2683.8011 | 18123.2201 | 112660.8765 | 56476.4755 | 0.063248 | -436096.3739 | 436096.3739
C | Xist Rating 5897 | -61.24 | 749.731 | 150.292 | 35.7 | 2298.94 | 8352.99 | 21632.5 | 0.83 | 3.1 | 18.771 | 50.185 | 1 | 1 | 1670 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1723586.5851 | 132254.721 | 2716.2334 | 18232.3961 | 114022.3249 | 53283.3126 | 0.063629 | -411439.6157 | 411439.6157
C | Xist Rating 5898 | -60.97 | 753.281 | 150.292 | 35.7 | 2304.78 | 8443.25 | 21560 | 0.82 | 3.08 | 18.778 | 49.842 | 1 | 1 | 1680 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1736146.9832 | 133733.5223 | 2748.8606 | 18341.5722 | 115391.9502 | 52920.3879 | 0.06401 | -408637.2078 | 408637.2078
C | Xist Rating 5899 | -60.53 | 763.634 | 150.292 | 35.7 | 2299.97 | 8416.88 | 21345.7 | 0.8 | 3.04 | 18.75 | 48.792 | 1 | 1 | 1690 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 24 | E | Rod | 1756335.291 | 135220.5005 | 2781.6825 | 18450.7482 | 116769.7523 | 51806.7197 | 0.064391 | -400037.7573 | 400037.7573
C | Xist Rating 5900 | -60.14 | 770.475 | 150.292 | 35.7 | 2302.49 | 8476.17 | 21205.6 | 0.79 | 3.02 | 18.736 | 48.113 | 1 | 1 | 1700 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 1774010.9827 | 136715.6555 | 2814.6992 | 18559.9242 | 118155.7313 | 51093.1724 | 0.064772 | -394527.9336 | 394527.9336
C | Xist Rating 5901 | -59.73 | 778.535 | 150.292 | 35.7 | 2303.11 | 8514.6 | 21044.6 | 0.78 | 2.99 | 18.729 | 47.344 | 1 | 1 | 1710 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 1793051.7438 | 138218.9874 | 2847.9107 | 18669.1002 | 119549.8871 | 50286.4221 | 0.065153 | -388298.4219 | 388298.4219
C | Xist Rating 5902 | -58.72 | 802.127 | 150.292 | 35.7 | 2292.14 | 8456.36 | 20567 | 0.78 | 2.9 | 18.756 | 45.018 | 1 | 1 | 1720 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 1838587.3818 | 139730.4961 | 2881.317 | 18778.2763 | 120952.2199 | 47879.0467 | 0.065534 | -369709.3074 | 369709.3074
C | Xist Rating 5903 | -58.22 | 812.35 | 150.292 | 35.7 | 2291.84 | 8490.25 | 20374.3 | 0.77 | 2.87 | 18.75 | 44.126 | 1 | 1 | 1730 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 1861776.224 | 141250.1817 | 2914.9181 | 18887.4523 | 122362.7295 | 46944.3609 | 0.065915 | -362491.9114 | 362491.9114
C | Xist Rating 5904 | -57.92 | 817.09 | 150.292 | 35.7 | 2295.45 | 8557.17 | 20289.8 | 0.76 | 2.85 | 18.75 | 43.756 | 1 | 1 | 1740 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 1875589.2405 | 142778.0442 | 2948.714 | 18996.6283 | 123781.4159 | 46551.964 | 0.066296 | -359461.9266 | 359461.9266
C | Xist Rating 5905 | -57.51 | 826.401 | 150.292 | 35.7 | 2292.82 | 8554.93 | 20123.5 | 0.74 | 2.82 | 18.733 | 43.011 | 1 | 1 | 1750 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 1894788.7408 | 144314.0836 | 2982.7046 | 19105.8043 | 125208.2793 | 45754.2672 | 0.066677 | -353302.3233 | 353302.3233
C | Xist Rating 5906 | -57.14 | 833.36 | 150.293 | 35.7 | 2293.43 | 8589.12 | 20001.2 | 0.73 | 2.8 | 18.738 | 42.469 | 1 | 1 | 1760 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 1911252.8248 | 145858.2998 | 3016.8901 | 19214.9803 | 126643.3195 | 45183.1241 | 0.067058 | -348892.1074 | 348892.1074
C | Xist Rating 5907 | -55.92 | 861.319 | 150.293 | 35.7 | 2282.62 | 8546.52 | 19497.7 | 0.73 | 2.71 | 18.775 | 40.18 | 1 | 1 | 1770 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 1966063.9758 | 147410.6929 | 3051.2703 | 19324.1564 | 128086.5365 | 42814.2756 | 0.067439 | -330600.4875 | 330600.4875
C | Xist Rating 5908 | -55.59 | 868.386 | 150.293 | 35.7 | 2282.03 | 8563.71 | 19383.4 | 0.72 | 2.69 | 18.763 | 39.701 | 1 | 1 | 1780 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 1981682.9036 | 148971.2629 | 3085.8453 | 19433.3324 | 129537.9305 | 42307.3089 | 0.06782 | -326685.8248 | 326685.8248
C | Xist Rating 5909 | -55.62 | 872.195 | 150.293 | 35.6 | 2272.41 | 8442.13 | 19326.8 | 0.71 | 2.68 | 18.972 | 39.473 | 1 | 1 | 1790 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 1981984.6399 | 150540.0097 | 3120.6151 | 19542.5084 | 130997.5013 | 42073.4383 | 0.068201 | -324879.9381 | 324879.9381
C | Xist Rating 5910 | -55.08 | 884.697 | 150.293 | 35.6 | 2270.46 | 8460.79 | 19121.9 | 0.7 | 2.65 | 18.954 | 38.6 | 1 | 1 | 1800 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2008669.1506 | 152116.9334 | 3155.5797 | 19651.6844 | 132465.2489 | 41156.5431 | 0.068582 | -317799.9161 | 317799.9161
C | Xist Rating 5911 | -54.74 | 891.637 | 150.293 | 35.6 | 2267.82 | 8448.68 | 19013.2 | 0.69 | 2.63 | 18.961 | 38.15 | 1 | 1 | 1810 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2022072.2213 | 153702.0339 | 3190.7391 | 19760.8605 | 133941.1734 | 40680.18 | 0.068963 | -314121.5669 | 314121.5669
C | Xist Rating 5912 | -53.33 | 919.855 | 150.293 | 35.6 | 2267.85 | 8555.25 | 18562.6 | 0.69 | 2.55 | 18.768 | 36.255 | 1 | 1 | 1820 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2086093.1617 | 155295.3113 | 3226.0933 | 19870.0365 | 135425.2748 | 38707.2258 | 0.069344 | -298886.9377 | 298886.9377
C | Xist Rating 5913 | -53.53 | 915.37 | 150.293 | 35.6 | 2272.05 | 8598.35 | 18631.4 | 0.69 | 2.56 | 19.014 | 36.544 | 1 | 1 | 1830 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2079766.4085 | 156896.7656 | 3261.6423 | 19979.2125 | 136917.5531 | 39027.0802 | 0.069725 | -301356.7687 | 301356.7687
C | Xist Rating 5914 | -53.1 | 921.068 | 150.293 | 35.6 | 2278.81 | 8717.78 | 18545.2 | 0.68 | 2.55 | 19.035 | 36.201 | 1 | 1 | 1840 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2098938.9691 | 158506.3968 | 3297.386 | 20088.3885 | 138418.0083 | 38662.2517 | 0.070106 | -298539.6591 | 298539.6591
C | Xist Rating 5915 | -52.68 | 930.496 | 150.293 | 35.6 | 2276.42 | 8717.63 | 18409.3 | 0.67 | 2.52 | 19.024 | 35.667 | 1 | 1 | 1850 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2118199.7043 | 160124.2048 | 3333.3246 | 20197.5646 | 139926.6403 | 38097.0995 | 0.070487 | -294175.7037 | 294175.7037
C | Xist Rating 5916 | -52.23 | 941.061 | 150.293 | 35.6 | 2272.94 | 8705.48 | 18259 | 0.66 | 2.5 | 19.011 | 35.079 | 1 | 1 | 1860 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2138975.1893 | 161750.1897 | 3369.4579 | 20306.7406 | 141443.4491 | 37475.5994 | 0.070868 | -289376.6449 | 289376.6449
C | Xist Rating 5917 | -51.07 | 966.969 | 150.293 | 35.6 | 2266.46 | 8711.51 | 17879.6 | 0.66 | 2.43 | 19.06 | 33.554 | 1 | 1 | 1870 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2191596.5597 | 163384.3515 | 3405.7861 | 20415.9166 | 142968.4349 | 35900.2244 | 0.071249 | -277212.0166 | 277212.0166
C | Xist Rating 5918 | -50.6 | 977.52 | 150.293 | 35.6 | 2264.03 | 8714.3 | 17738.8 | 0.64 | 2.41 | 19.051 | 33.025 | 1 | 1 | 1880 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2213134.6056 | 165026.6901 | 3442.309 | 20525.0926 | 144501.5975 | 35323.8882 | 0.07163 | -272761.7016 | 272761.7016
C | Xist Rating 5919 | -50.2 | 984.508 | 150.293 | 35.6 | 2266.69 | 8780.06 | 17646.3 | 0.64 | 2.39 | 19.066 | 32.684 | 1 | 1 | 1890 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2231574.4385 | 166677.2056 | 3479.0267 | 20634.2687 | 146042.9369 | 34976.0389 | 0.072011 | -270075.7011 | 270075.7011
C | Xist Rating 5920 | -49.88 | 991.954 | 150.293 | 35.6 | 2264.35 | 8771.03 | 17555.2 | 0.62 | 2.38 | 19.051 | 32.361 | 1 | 1 | 1900 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2246131.0399 | 168335.898 | 3515.9392 | 20743.4447 | 147592.4533 | 34612.8056 | 0.072392 | -267270.9102 | 267270.9102
C | Xist Rating 5921 | -49.55 | 999.121 | 150.293 | 35.6 | 2263.19 | 8779.51 | 17465 | 0.61 | 2.36 | 19.059 | 32.037 | 1 | 1 | 1910 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2261200.656 | 170002.7672 | 3553.0464 | 20852.6207 | 149150.1465 | 34265.7339 | 0.072773 | -264590.9146 | 264590.9146
C | Xist Rating 5922 | -48.15 | 1030.59 | 150.293 | 35.6 | 2255.74 | 8790.53 | 17050.4 | 0.62 | 2.29 | 19.105 | 30.467 | 1 | 1 | 1920 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2324743.0866 | 171677.8133 | 3590.3485 | 20961.7967 | 150716.0165 | 32659.3601 | 0.073154 | -252186.9213 | 252186.9213
C | Xist Rating 5923 | -47.74 | 1041.21 | 150.293 | 35.6 | 2251.2 | 8760.63 | 16923.7 | 0.61 | 2.27 | 19.093 | 30.023 | 1 | 1 | 1930 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2343971.952 | 173361.0363 | 3627.8454 | 21070.9728 | 152290.0635 | 32186.415 | 0.073535 | -248534.9648 | 248534.9648
C | Xist Rating 5924 | -47.38 | 1044.66 | 150.293 | 35.6 | 2259.38 | 8899.11 | 16882.2 | 0.6 | 2.26 | 19.128 | 29.883 | 1 | 1 | 1940 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2360283.9108 | 175052.4361 | 3665.537 | 21180.1488 | 153872.2873 | 32031.4687 | 0.073916 | -247338.5109 | 247338.5109
C | Xist Rating 5925 | -47.06 | 1054.66 | 150.293 | 35.6 | 2252.14 | 8822.41 | 16772.2 | 0.59 | 2.24 | 19.105 | 29.516 | 1 | 1 | 1950 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2375241.9724 | 176752.0128 | 3703.4235 | 21289.3248 | 155462.688 | 31637.5787 | 0.074297 | -244296.9965 | 244296.9965
C | Xist Rating 5926 | -46.55 | 1066.31 | 150.293 | 35.6 | 2249.44 | 8824.2 | 16637.2 | 0.58 | 2.22 | 19.129 | 29.046 | 1 | 1 | 1960 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2398600.3664 | 178459.7663 | 3741.5047 | 21398.5008 | 157061.2655 | 31138.9751 | 0.074678 | -240446.9114 | 240446.9114
C | Xist Rating 5927 | -45.32 | 1094.65 | 150.293 | 35.6 | 2242.02 | 8819.96 | 16303.3 | 0.58 | 2.16 | 19.194 | 27.864 | 1 | 1 | 1970 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2454227.193 | 180175.6968 | 3779.7807 | 21507.6769 | 158668.0199 | 29919.7722 | 0.075059 | -231032.5503 | 231032.5503
C | Xist Rating 5928 | -44.92 | 1102.94 | 150.293 | 35.7 | 2241.94 | 8848.99 | 16214.3 | 0.57 | 2.15 | 19.215 | 27.572 | 1 | 1 | 1980 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2472725.3036 | 181899.8041 | 3818.2515 | 21616.8529 | 160282.9512 | 29605.548 | 0.07544 | -228606.1938 | 228606.1938
C | Xist Rating 5929 | -44.51 | 1113.76 | 150.293 | 35.7 | 2237.28 | 8815.17 | 16101.4 | 0.56 | 2.13 | 19.215 | 27.206 | 1 | 1 | 1990 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2491792.9728 | 183632.0882 | 3856.9171 | 21726.0289 | 161906.0593 | 29213.227 | 0.075821 | -225576.7953 | 225576.7953
C | Xist Rating 5930 | -44.14 | 1122.17 | 150.293 | 35.7 | 2235.87 | 8823.23 | 16015 | 0.55 | 2.12 | 19.218 | 26.929 | 1 | 1 | 2000 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2509026.2379 | 185372.5493 | 3895.7775 | 21835.2049 | 163537.3443 | 28913.3081 | 0.076202 | -223260.9008 | 223260.9008
C | Xist Rating 5931 | -43.82 | 1128.34 | 150.293 | 35.7 | 2236.81 | 8859.56 | 15953.9 | 0.54 | 2.11 | 19.222 | 26.74 | 1 | 1 | 2010 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2523882.1954 | 187121.1872 | 3934.8326 | 21944.381 | 165176.8062 | 28704.6494 | 0.076583 | -221649.6942 | 221649.6942
C | Xist Rating 5932 | -42.51 | 1160.25 | 150.293 | 35.7 | 2226.84 | 8825.47 | 15614.9 | 0.54 | 2.05 | 19.26 | 25.609 | 1 | 1 | 2020 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2583691.11 | 188878.002 | 3974.0826 | 22053.557 | 166824.445 | 27536.6185 | 0.076964 | -212630.4687 | 212630.4687
C | Xist Rating 5933 | -41.96 | 1171.84 | 150.293 | 35.7 | 2226.32 | 8859.91 | 15499.8 | 0.54 | 2.03 | 19.265 | 25.245 | 1 | 1 | 2030 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2608890.8288 | 190642.9936 | 4013.5273 | 22162.733 | 168480.2606 | 27163.5127 | 0.077345 | -209749.4446 | 209749.4446
C | Xist Rating 5934 | -41.66 | 1179.49 | 150.293 | 35.7 | 2223.76 | 8845.13 | 15431.7 | 0.53 | 2.02 | 19.259 | 25.047 | 1 | 1 | 2040 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2622902.6824 | 192416.1621 | 4053.1669 | 22271.909 | 170144.2531 | 26944.646 | 0.077726 | -208059.4142 | 208059.4142
C | Xist Rating 5935 | -41.24 | 1186.32 | 150.293 | 35.7 | 2227.7 | 8933.81 | 15364.2 | 0.52 | 2.01 | 19.28 | 24.837 | 1 | 1 | 2050 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2642765.064 | 194197.5075 | 4093.0012 | 22381.0851 | 171816.4224 | 26714.443 | 0.078107 | -206281.8473 | 206281.8473
C | Xist Rating 5936 | -40.85 | 1197.53 | 150.293 | 35.7 | 2221.97 | 8880.86 | 15264.2 | 0.51 | 1.99 | 19.261 | 24.542 | 1 | 1 | 2060 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2660875.7341 | 195987.0297 | 4133.0303 | 22490.2611 | 173496.7686 | 26393.8822 | 0.078488 | -203806.562 | 203806.562
C | Xist Rating 5937 | -39.46 | 1231.79 | 150.293 | 35.7 | 2211.79 | 8848.24 | 14936.1 | 0.51 | 1.94 | 19.299 | 23.51 | 1 | 1 | 2070 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2724460.8041 | 197784.7288 | 4173.2542 | 22599.4371 | 175185.2917 | 25328.3532 | 0.078869 | -195578.8296 | 195578.8296
C | Xist Rating 5938 | -39.14 | 1239.24 | 150.293 | 35.7 | 2210.57 | 8854.18 | 14873.4 | 0.51 | 1.93 | 19.295 | 23.334 | 1 | 1 | 2080 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2739426.7668 | 199590.6048 | 4213.6729 | 22708.6131 | 176881.9916 | 25149.7991 | 0.07925 | -194200.0825 | 194200.0825
C | Xist Rating 5939 | -38.74 | 1248.86 | 150.293 | 35.7 | 2208.72 | 8858.32 | 14790.7 | 0.5 | 1.91 | 19.293 | 23.096 | 1 | 1 | 2090 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2758382.0592 | 201404.6576 | 4254.2864 | 22817.7892 | 178586.8685 | 24888.8775 | 0.079631 | -192185.3151 | 192185.3151
C | Xist Rating 5940 | -38.29 | 1258.5 | 150.293 | 35.7 | 2208.29 | 8885.29 | 14709.1 | 0.49 | 1.9 | 19.295 | 22.862 | 1 | 1 | 2100 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2779132.965 | 203226.8873 | 4295.0947 | 22926.9652 | 180299.9221 | 24632.1243 | 0.080012 | -190202.7348 | 190202.7348
C | Xist Rating 5941 | -37.95 | 1267 | 150.293 | 35.7 | 2206.61 | 8887.81 | 14638.5 | 0.49 | 1.89 | 19.295 | 22.664 | 1 | 1 | 2110 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2795774.87 | 205057.2939 | 4336.0977 | 23036.1412 | 182021.1527 | 24430.7396 | 0.080393 | -188647.6954 | 188647.6954
C | Xist Rating 5942 | -36.66 | 1299.36 | 150.293 | 35.7 | 2196.39 | 8842.48 | 14358.9 | 0.49 | 1.84 | 19.332 | 21.835 | 1 | 1 | 2120 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2853901.3104 | 206895.8773 | 4377.2956 | 23145.3172 | 183750.5601 | 23575.7853 | 0.080774 | -182045.9645 | 182045.9645
C | Xist Rating 5943 | -36.2 | 1311.29 | 150.293 | 35.7 | 2192.9 | 8827.6 | 14263.7 | 0.48 | 1.83 | 19.331 | 21.571 | 1 | 1 | 2130 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2875527.841 | 208742.6376 | 4418.6882 | 23254.4933 | 185488.1444 | 23287.3644 | 0.081155 | -179818.8553 | 179818.8553
C | Xist Rating 5944 | -35.79 | 1323.25 | 150.293 | 35.7 | 2187.54 | 8782.37 | 14169.9 | 0.47 | 1.81 | 19.327 | 21.312 | 1 | 1 | 2140 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2894662.305 | 210597.5748 | 4460.2756 | 23363.6693 | 187233.9055 | 23003.829 | 0.081536 | -177629.4699 | 177629.4699
C | Xist Rating 5945 | -35.5 | 1329.57 | 150.293 | 35.7 | 2187.72 | 8805.87 | 14123.5 | 0.47 | 1.8 | 19.328 | 21.193 | 1 | 1 | 2150 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2908726.8804 | 212460.6889 | 4502.0578 | 23472.8453 | 188987.8436 | 22884.3647 | 0.081917 | -176706.9984 | 176706.9984
C | Xist Rating 5946 | -35.12 | 1338.02 | 150.293 | 35.7 | 2187.12 | 8825.15 | 14059.1 | 0.46 | 1.79 | 19.336 | 21.021 | 1 | 1 | 2160 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2926410.3024 | 214331.9798 | 4544.0348 | 23582.0213 | 190749.9584 | 22691.4576 | 0.082298 | -175217.421 | 175217.421
C | Xist Rating 5947 | -33.77 | 1372.92 | 150.293 | 35.7 | 2176.36 | 8775.64 | 13786 | 0.46 | 1.75 | 19.362 | 20.256 | 1 | 1 | 2170 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 2987968.1712 | 216211.4476 | 4586.2066 | 23691.1974 | 192520.2502 | 21902.1566 | 0.082679 | -169122.6479 | 169122.6479
C | Xist Rating 5948 | -33.27 | 1384.63 | 150.293 | 35.7 | 2175.23 | 8798.01 | 13699.1 | 0.46 | 1.74 | 19.364 | 20.025 | 1 | 1 | 2180 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3011888.7149 | 218099.0922 | 4628.5732 | 23800.3734 | 194298.7188 | 21666.3457 | 0.08306 | -167301.7785 | 167301.7785
C | Xist Rating 5949 | -32.91 | 1393.31 | 150.293 | 35.7 | 2174.04 | 8807.2 | 13638.9 | 0.45 | 1.73 | 19.361 | 19.873 | 1 | 1 | 2190 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3029111.6724 | 219994.9137 | 4671.1346 | 23909.5494 | 196085.3643 | 21493.3453 | 0.083441 | -165965.9152 | 165965.9152
C | Xist Rating 5950 | -32.58 | 1402.4 | 150.293 | 35.7 | 2171.11 | 8787.88 | 13579.4 | 0.44 | 1.72 | 19.351 | 19.729 | 1 | 1 | 2200 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3044764.664 | 221898.9121 | 4713.8907 | 24018.7254 | 197880.1867 | 21328.1803 | 0.083822 | -164690.5544 | 164690.5544
C | Xist Rating 5951 | -32.1 | 1414.37 | 150.293 | 35.7 | 2169.01 | 8794.17 | 13495.4 | 0.44 | 1.7 | 19.355 | 19.512 | 1 | 1 | 2210 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3067782.6737 | 223811.0873 | 4756.8417 | 24127.9015 | 199683.1859 | 21106.817 | 0.084203 | -162981.2462 | 162981.2462
C | Xist Rating 5952 | -30.74 | 1449.14 | 150.294 | 35.7 | 2159.98 | 8769.22 | 13246.1 | 0.44 | 1.66 | 19.387 | 18.849 | 1 | 1 | 2220 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3130113.4172 | 225731.4394 | 4799.9874 | 24237.0775 | 201494.362 | 20423.511 | 0.084584 | -157704.9385 | 157704.9385
C | Xist Rating 5953 | -30.34 | 1458.74 | 150.294 | 35.7 | 2158.76 | 8781.4 | 13182.4 | 0.43 | 1.65 | 19.393 | 18.691 | 1 | 1 | 2230 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3149069.5624 | 227659.9684 | 4843.3279 | 24346.2535 | 203313.7149 | 20244.1308 | 0.084965 | -156319.8119 | 156319.8119
C | Xist Rating 5954 | -29.94 | 1469.93 | 150.293 | 35.7 | 2155.36 | 8761.44 | 13111.6 | 0.43 | 1.64 | 19.388 | 18.521 | 1 | 1 | 2240 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3168228.3248 | 229596.6743 | 4886.8633 | 24455.4295 | 205141.2447 | 20071.1081 | 0.085346 | -154983.7766 | 154983.7766
C | Xist Rating 5955 | -29.46 | 1482.2 | 150.294 | 35.7 | 2152.8 | 8759.07 | 13034.1 | 0.42 | 1.63 | 19.385 | 18.333 | 1 | 1 | 2250 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3190880.16 | 231541.557 | 4930.5934 | 24564.6056 | 206976.9514 | 19859.9264 | 0.085727 | -153353.0876 | 153353.0876
C | Xist Rating 5956 | -29.16 | 1488.48 | 150.293 | 35.7 | 2153.54 | 8791.49 | 12995.6 | 0.42 | 1.62 | 19.39 | 18.245 | 1 | 1 | 2260 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3205501.2192 | 233494.6166 | 4974.5182 | 24673.7816 | 208820.835 | 19772.4008 | 0.086108 | -152677.2379 | 152677.2379
C | Xist Rating 5957 | -27.76 | 1525.91 | 150.294 | 35.7 | 2142.69 | 8740.73 | 12751.8 | 0.42 | 1.59 | 19.423 | 17.63 | 1 | 1 | 2270 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3269552.0979 | 235455.853 | 5018.6379 | 24782.9576 | 210672.8954 | 19138.785 | 0.086489 | -147784.6245 | 147784.6245
C | Xist Rating 5958 | -27.33 | 1537.04 | 150.294 | 35.7 | 2140.6 | 8741.65 | 12686.1 | 0.41 | 1.58 | 19.42 | 17.478 | 1 | 1 | 2280 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3290187.824 | 237425.2663 | 5062.9524 | 24892.1336 | 212533.1327 | 18964.6138 | 0.08687 | -146439.7209 | 146439.7209
C | Xist Rating 5959 | -26.81 | 1550.19 | 150.294 | 35.7 | 2138.18 | 8744.93 | 12606.8 | 0.41 | 1.56 | 19.418 | 17.291 | 1 | 1 | 2290 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3314585.2542 | 239402.8565 | 5107.4617 | 25001.3097 | 214401.5469 | 18773.8995 | 0.087251 | -144967.0753 | 144967.0753
C | Xist Rating 5960 | -26.48 | 1559.03 | 150.294 | 35.7 | 2136.41 | 8743.04 | 12556.9 | 0.4 | 1.56 | 19.415 | 17.18 | 1 | 1 | 2300 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3330727.2823 | 241388.6236 | 5152.1657 | 25110.4857 | 216278.1379 | 18642.0518 | 0.087632 | -143948.9823 | 143948.9823
| Xist Rating 5961 | -26.13 | 1568.15 | 150.294 | 35.7 | 2134.64 | 8740.93 | 12507.5 | 0.4 | 1.55 | 19.412 | 17.073 | 1 | 1 | 2310 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3347435.716 | 243382.5675 | 5197.0645 | 25219.6617 | 218162.9058 | 18534.2893 | 0.088013 | -143116.8688 | 143116.8688
| Xist Rating 5962 | -24.67 | 1606.54 | 150.294 | 35.7 | 2125.31 | 8715.89 | 12277 | 0.4 | 1.51 | 19.445 | 16.518 | 1 | 1 | 2320 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3414395.5274 | 245384.6883 | 5242.1582 | 25328.8377 | 220055.8505 | 17962.7759 | 0.088394 | -138703.7941 | 138703.7941
| Xist Rating 5963 | -24.24 | 1617.7 | 150.294 | 35.7 | 2123.34 | 8717.86 | 12216.6 | 0.39 | 1.5 | 19.442 | 16.386 | 1 | 1 | 2330 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3434927.118 | 247394.9859 | 5287.4466 | 25438.0138 | 221956.9722 | 17808.7497 | 0.088775 | -137514.4449 | 137514.4449
| Xist Rating 5964 | -23.84 | 1628.84 | 150.294 | 35.6 | 2120.75 | 8709.2 | 12157 | 0.39 | 1.49 | 19.435 | 16.255 | 1 | 1 | 2340 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3454362.43 | 249413.4605 | 5332.9298 | 25547.1898 | 223866.2707 | 17675.8189 | 0.089156 | -136487.988 | 136487.988
| Xist Rating 5965 | -23.52 | 1638.94 | 150.294 | 35.6 | 2117.18 | 8680.16 | 12104.6 | 0.38 | 1.49 | 19.438 | 16.144 | 1 | 1 | 2350 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3469930.9892 | 251440.1118 | 5378.6078 | 25656.3658 | 225783.746 | 17543.5908 | 0.089537 | -135466.9575 | 135466.9575
| Xist Rating 5966 | -23.07 | 1651.27 | 150.294 | 35.7 | 2114.12 | 8667.22 | 12039.8 | 0.38 | 1.48 | 19.434 | 16.003 | 1 | 1 | 2360 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3490982.9324 | 253474.9401 | 5424.4805 | 25765.5418 | 227709.3983 | 17400.3126 | 0.089918 | -134360.6018 | 134360.6018
| Xist Rating 5967 | -21.76 | 1686.47 | 150.294 | 35.7 | 2105.9 | 8645.4 | 11846.8 | 0.38 | 1.45 | 19.465 | 15.562 | 1 | 1 | 2370 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3551537.173 | 255517.9452 | 5470.5481 | 25874.7179 | 229643.2274 | 16946.8965 | 0.090299 | -130859.4429 | 130859.4429
| Xist Rating 5968 | -21.37 | 1697.85 | 150.294 | 35.7 | 2102.83 | 8627.9 | 11791.1 | 0.37 | 1.44 | 19.456 | 15.447 | 1 | 1 | 2380 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3570289.9155 | 257569.1272 | 5516.8105 | 25983.8939 | 231585.2333 | 16809.6637 | 0.09068 | -129799.7675 | 129799.7675
| Xist Rating 5969 | -20.91 | 1709.72 | 150.294 | 35.7 | 2101.15 | 8637.44 | 11730 | 0.37 | 1.43 | 19.454 | 15.315 | 1 | 1 | 2390 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 3592378.178 | 259628.4861 | 5563.2676 | 26093.0699 | 233535.4162 | 16675.7295 | 0.091061 | -128765.5626 | 128765.5626
C | Xist Rating 5973 | -11.69 | 1963.63 | 150.294 | 35.7 | 2044.76 | 8488.55 | 10537.8 | 0.39 | 1.25 | 19.476 | 12.818 | 1 | 1 | 2430 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4015152.0788 | 267947.6902 | 5751.0441 | 26529.774 | 241417.9162 | 14138.8195 | 0.092585 | -109176.2161 | 109176.2161
C | Xist Rating 5974 | -11.71 | 1965 | 150.294 | 35.7 | 2043.46 | 8466.25 | 10537.9 | 0.38 | 1.25 | 19.472 | 12.829 | 1 | 1 | 2440 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4015398.9 | 270047.9333 | 5798.4752 | 26638.95 | 243408.9833 | 14132.1801 | 0.092966 | -109124.9487 | 109124.9487
C | Xist Rating 5975 | -11.71 | 1966.32 | 150.294 | 35.7 | 2042.62 | 8451.77 | 10537.9 | 0.38 | 1.25 | 19.473 | 12.839 | 1 | 1 | 2450 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4016444.5584 | 272156.3534 | 5846.1011 | 26748.1261 | 245408.2274 | 14145.9236 | 0.093347 | -109231.072 | 109231.072
C | Xist Rating 5976 | -11.71 | 1967.8 | 150.294 | 35.7 | 2041.58 | 8433.95 | 10537.9 | 0.37 | 1.25 | 19.469 | 12.851 | 1 | 1 | 2460 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4017421.124 | 274272.9503 | 5893.9217 | 26857.3021 | 247415.6483 | 14140.0666 | 0.093728 | -109185.8464 | 109185.8464
C | Xist Rating 5977 | -11.63 | 1969.15 | 150.294 | 35.7 | 2042.76 | 8454.19 | 10537.9 | 0.37 | 1.25 | 19.495 | 12.861 | 1 | 1 | 2470 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4022500.854 | 276397.7241 | 5941.9372 | 26966.4781 | 249431.246 | 14154.7457 | 0.094109 | -109299.194 | 109299.194
C | Xist Rating 5978 | -11.63 | 1970.5 | 150.294 | 35.6 | 2042.23 | 8445.15 | 10537.9 | 0.36 | 1.25 | 19.491 | 12.872 | 1 | 1 | 2480 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4024214.215 | 278530.6748 | 5990.1474 | 27075.6541 | 251455.0207 | 14147.5707 | 0.09449 | -109243.7908 | 109243.7908
C | Xist Rating 5979 | -11.62 | 1971.89 | 150.294 | 35.6 | 2041.61 | 8434.52 | 10537.9 | 0.35 | 1.25 | 19.486 | 12.882 | 1 | 1 | 2490 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4025830.3429 | 280671.8023 | 6038.5525 | 27184.8302 | 253486.9722 | 14139.151 | 0.094871 | -109178.7764 | 109178.7764
C | Xist Rating 5980 | -11.59 | 1972.88 | 150.294 | 35.6 | 2041.84 | 8438.55 | 10537.9 | 0.35 | 1.25 | 19.483 | 12.891 | 1 | 1 | 2500 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4028305.2992 | 282821.1067 | 6087.1523 | 27294.0062 | 255527.1005 | 14151.4369 | 0.095252 | -109273.6449 | 109273.6449
C | Xist Rating 5981 | -11.6 | 1974.73 | 150.294 | 35.6 | 2040.27 | 8411.76 | 10537.8 | 0.34 | 1.25 | 19.477 | 12.904 | 1 | 1 | 2510 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4028982.3771 | 284978.588 | 6135.9469 | 27403.1822 | 257575.4058 | 14145.8442 | 0.095633 | -109230.4594 | 109230.4594
C | Xist Rating 5982 | -11.59 | 1976.18 | 150.294 | 35.6 | 2039.67 | 8401.57 | 10537.8 | 0.34 | 1.25 | 19.514 | 12.915 | 1 | 1 | 2520 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4030755.0606 | 287144.2461 | 6184.9363 | 27512.3582 | 259631.8879 | 14161.6571 | 0.096014 | -109352.5622 | 109352.5622
C | Xist Rating 5983 | -11.57 | 1977.52 | 150.294 | 35.6 | 2039.17 | 8393.1 | 10537.8 | 0.33 | 1.25 | 19.508 | 12.925 | 1 | 1 | 2530 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4032499.4584 | 289318.0811 | 6234.1205 | 27621.5343 | 261696.5468 | 14152.6614 | 0.096395 | -109283.1 | 109283.1
C | Xist Rating 5984 | -11.56 | 1978.67 | 150.294 | 35.6 | 2039.05 | 8391.13 | 10537.8 | 0.33 | 1.25 | 19.504 | 12.934 | 1 | 1 | 2540 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4034607.0635 | 291500.093 | 6283.4995 | 27730.7103 | 263769.3827 | 14164.7433 | 0.096776 | -109376.3928 | 109376.3928
C | Xist Rating 5985 | -11.52 | 1980.22 | 150.294 | 35.6 | 2038.78 | 8386.46 | 10537.8 | 0.32 | 1.25 | 19.498 | 12.946 | 1 | 1 | 2550 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4037232.9316 | 293690.2817 | 6333.0732 | 27839.8863 | 265850.3954 | 14157.5772 | 0.097157 | -109321.0584 | 109321.0584
C | Xist Rating 5986 | -11.51 | 1981.67 | 150.294 | 35.6 | 2038.46 | 8381.11 | 10537.7 | 0.32 | 1.25 | 19.491 | 12.956 | 1 | 1 | 2560 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4039555.0282 | 295888.6473 | 6382.8418 | 27949.0623 | 267939.585 | 14170.5019 | 0.097538 | -109420.8597 | 109420.8597
C | Xist Rating 5987 | -11.49 | 1983.06 | 150.294 | 35.6 | 2038.05 | 8374.26 | 10537.7 | 0.31 | 1.25 | 19.488 | 12.966 | 1 | 1 | 2570 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4041575.433 | 298095.1898 | 6432.8051 | 28058.2384 | 270036.9514 | 14161.122 | 0.097919 | -109348.4306 | 109348.4306
C | Xist Rating 5988 | -11.46 | 1984.42 | 150.294 | 35.6 | 2038.13 | 8375.56 | 10537.7 | 0.31 | 1.25 | 19.539 | 12.977 | 1 | 1 | 2580 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4044505.9346 | 300309.9091 | 6482.9633 | 28167.4144 | 272142.4947 | 14177.0819 | 0.0983 | -109471.6684 | 109471.6684
C | Xist Rating 5989 | -11.43 | 1985.78 | 150.294 | 35.6 | 2038.04 | 8374.06 | 10537.7 | 0.3 | 1.25 | 19.539 | 12.987 | 1 | 1 | 2590 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4047099.0712 | 302532.8053 | 6533.3162 | 28276.5904 | 274256.2149 | 14167.498 | 0.098681 | -109397.664 | 109397.664
C | Xist Rating 5990 | -11.41 | 1986.96 | 150.294 | 35.6 | 2037.96 | 8372.74 | 10537.6 | 0.3 | 1.25 | 19.536 | 12.996 | 1 | 1 | 2600 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4049345.0016 | 304763.8784 | 6583.8639 | 28385.7664 | 276378.1119 | 14179.3671 | 0.099062 | -109489.3139 | 109489.3139
C | Xist Rating 5991 | -11.42 | 1988.65 | 150.294 | 35.6 | 2036.85 | 8354.16 | 10537.6 | 0.3 | 1.25 | 19.529 | 13.007 | 1 | 1 | 2610 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4050581.7525 | 307003.1283 | 6634.6064 | 28494.9424 | 278508.1858 | 14193.1719 | 0.099443 | -109595.9115 | 109595.9115
C | Xist Rating 5992 | -11.35 | 1990.04 | 150.294 | 35.6 | 2037.25 | 8360.81 | 10537.7 | 0.29 | 1.25 | 19.538 | 13.018 | 1 | 1 | 2620 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4054208.99 | 309250.5551 | 6685.5437 | 28604.1185 | 280646.4366 | 14184.5931 | 0.099824 | -109529.6681 | 109529.6681
C | Xist Rating 5993 | -11.33 | 1991.47 | 150.294 | 35.6 | 2036.92 | 8355.2 | 10537.6 | 0.29 | 1.25 | 19.574 | 13.028 | 1 | 1 | 2630 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4056465.0724 | 311506.1588 | 6736.6758 | 28713.2945 | 282792.8643 | 14198.7486 | 0.10021 | -109638.9732 | 109638.9732
C | Xist Rating 5994 | -11.31 | 1992.71 | 150.294 | 35.6 | 2036.85 | 8354.14 | 10537.6 | 0.28 | 1.25 | 19.571 | 13.037 | 1 | 1 | 2640 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4058851.3635 | 313769.9393 | 6788.0027 | 28822.4705 | 284947.4688 | 14187.3769 | 0.10059 | -109551.1635 | 109551.1635
C | Xist Rating 5995 | -11.27 | 1994.22 | 150.294 | 35.6 | 2036.84 | 8353.9 | 10537.6 | 0.28 | 1.25 | 19.57 | 13.048 | 1 | 1 | 2650 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4061907.0648 | 316041.8967 | 6839.5243 | 28931.6465 | 287110.2502 | 14201.2234 | 0.10097 | -109658.0829 | 109658.0829
C | Xist Rating 5996 | -11.23 | 1995.56 | 150.294 | 35.6 | 2036.92 | 8355.34 | 10537.6 | 0.28 | 1.25 | 19.568 | 13.058 | 1 | 1 | 2660 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4064796.0752 | 318322.031 | 6891.2408 | 29040.8226 | 289281.2084 | 14213.9978 | 0.10135 | -109756.7237 | 109756.7237
C | Xist Rating 5997 | -11.21 | 1996.95 | 150.294 | 35.6 | 2036.75 | 8352.42 | 10537.6 | 0.27 | 1.25 | 19.566 | 13.068 | 1 | 1 | 2670 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4067287.9125 | 320610.3421 | 6943.152 | 29149.9986 | 291460.3435 | 14203.3548 | 0.10173 | -109674.5411 | 109674.5411
C | Xist Rating 5998 | -11.13 | 1998.36 | 150.294 | 35.6 | 2037.73 | 8368.82 | 10537.6 | 0.27 | 1.25 | 19.608 | 13.078 | 1 | 1 | 2680 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4072118.1228 | 322906.8301 | 6995.258 | 29259.1746 | 293647.6555 | 14217.4701 | 0.10211 | -109783.5354 | 109783.5354
C | Xist Rating 5999 | -11.09 | 1999.74 | 150.294 | 35.6 | 2038.07 | 8374.62 | 10537.6 | 0.26 | 1.25 | 19.606 | 13.088 | 1 | 1 | 2690 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4075610.1018 | 325211.495 | 7047.5588 | 29368.3506 | 295843.1443 | 14206.5225 | 0.10249 | -109699.0008 | 109699.0008
C | Xist Rating 6000 | -11.03 | 2000.94 | 150.294 | 35.6 | 2038.77 | 8386.49 | 10537.5 | 0.26 | 1.25 | 19.604 | 13.097 | 1 | 1 | 2700 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4079456.4438 | 327524.3367 | 7100.0544 | 29477.5267 | 298046.8101 | 14218.091 | 0.10287 | -109788.3298 | 109788.3298
C | Xist Rating 6001 | -11 | 2002.6 | 150.294 | 35.6 | 2038.69 | 8385.29 | 10537.5 | 0.26 | 1.25 | 19.603 | 13.108 | 1 | 1 | 2710 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4082680.594 | 329845.3553 | 7152.7448 | 29586.7027 | 300258.6526 | 14231.7676 | 0.10325 | -109893.9371 | 109893.9371
C | Xist Rating 6002 | -10.97 | 2003.94 | 150.294 | 35.6 | 2038.49 | 8381.87 | 10537.5 | 0.25 | 1.25 | 19.597 | 13.117 | 1 | 1 | 2720 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4085011.6506 | 332174.5508 | 7205.63 | 29695.8787 | 302478.6721 | 14219.3153 | 0.10363 | -109797.7833 | 109797.7833
C | Xist Rating 6003 | -10.97 | 2005.26 | 150.294 | 35.6 | 2037.72 | 8368.88 | 10537.5 | 0.25 | 1.25 | 19.63 | 13.127 | 1 | 1 | 2730 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4086158.4072 | 334511.9232 | 7258.71 | 29805.0547 | 304706.8684 | 14232.9059 | 0.10402 | -109902.7264 | 109902.7264
C | Xist Rating 6004 | -10.99 | 2006.55 | 150.294 | 35.6 | 2036.5 | 8348.28 | 10537.5 | 0.25 | 1.25 | 19.621 | 13.136 | 1 | 1 | 2740 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4086339.075 | 336857.4724 | 7311.9847 | 29914.2308 | 306943.2416 | 14244.1758 | 0.1044 | -109989.7497 | 109989.7497
C | Xist Rating 6005 | -10.98 | 2008.09 | 150.294 | 35.6 | 2035.84 | 8337.25 | 10537.5 | 0.25 | 1.25 | 19.621 | 13.146 | 1 | 1 | 2750 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 23 | E | Rod | 4088149.9456 | 339211.1984 | 7365.4543 | 30023.4068 | 309187.7916 | 14256.7595 | 0.10478 | -110086.918 | 110086.918
C | Xist Rating 6006 | -10.97 | 2009.52 | 150.294 | 35.6 | 2035.14 | 8325.43 | 10537.5 | 0.24 | 1.25 | 19.617 | 13.156 | 1 | 1 | 2760 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4089654.5328 | 341573.1014 | 7419.1186 | 30132.5828 | 311440.5186 | 14244.9502 | 0.10516 | -109995.7294 | 109995.7294
C | Xist Rating 6007 | -10.99 | 2010.75 | 150.294 | 35.6 | 2034.1 | 8308.15 | 10537.5 | 0.24 | 1.25 | 19.61 | 13.165 | 1 | 1 | 2770 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4090066.575 | 343943.1812 | 7472.9777 | 30241.7588 | 313701.4223 | 14256.1985 | 0.10554 | -110082.5856 | 110082.5856
C | Xist Rating 6008 | -10.97 | 2012.3 | 150.295 | 35.6 | 2033.57 | 8299.26 | 10537.5 | 0.24 | 1.25 | 19.653 | 13.176 | 1 | 1 | 2780 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4092152.911 | 346321.4379 | 7527.0316 | 30350.9349 | 315970.503 | 14271.0176 | 0.10592 | -110197.0148 | 110197.0148
C | Xist Rating 6009 | -10.94 | 2013.71 | 150.295 | 35.6 | 2033.48 | 8297.7 | 10537.5 | 0.23 | 1.25 | 19.656 | 13.185 | 1 | 1 | 2790 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4094839.0108 | 348707.8714 | 7581.2803 | 30460.1109 | 318247.7605 | 14257.9864 | 0.1063 | -110096.3916 | 110096.3916
C | Xist Rating 6010 | -10.96 | 2014.68 | 150.295 | 35.6 | 2032.79 | 8286.27 | 10537.4 | 0.23 | 1.25 | 19.655 | 13.193 | 1 | 1 | 2800 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4095421.3572 | 351102.4818 | 7635.7238 | 30569.2869 | 320533.1949 | 14268.292 | 0.10668 | -110175.9687 | 110175.9687
C | Xist Rating 6011 | -10.96 | 2016.43 | 150.295 | 35.6 | 2031.72 | 8268.63 | 10537.4 | 0.23 | 1.25 | 19.657 | 13.204 | 1 | 1 | 2810 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4096821.1596 | 353505.2691 | 7690.3621 | 30678.4629 | 322826.8062 | 14281.7998 | 0.10706 | -110280.2722 | 110280.2722
C | Xist Rating 6012 | -10.87 | 2017.91 | 150.295 | 35.6 | 2032.71 | 8284.82 | 10537.6 | 0.23 | 1.25 | 19.668 | 13.214 | 1 | 1 | 2820 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4101825.8361 | 355916.2333 | 7745.1952 | 30787.639 | 325128.5943 | 14294.5311 | 0.10744 | -110378.5804 | 110378.5804
C | Xist Rating 6013 | -10.87 | 2019.28 | 150.295 | 35.6 | 2031.72 | 8268.43 | 10537.6 | 0.22 | 1.25 | 19.706 | 13.223 | 1 | 1 | 2830 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4102611.5616 | 358335.3743 | 7800.223 | 30896.815 | 327438.5593 | 14282.0162 | 0.10783 | -110281.9436 | 110281.9436
C | Xist Rating 6014 | -10.84 | 2020.59 | 150.295 | 35.6 | 2031.93 | 8272.06 | 10537.5 | 0.22 | 1.25 | 19.717 | 13.233 | 1 | 1 | 2840 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4105697.4387 | 360762.6921 | 7855.4457 | 31005.991 | 329756.7011 | 14294.6526 | 0.10821 | -110379.5181 | 110379.5181
C | Xist Rating 6015 | -10.76 | 2022.04 | 150.295 | 35.6 | 2033.05 | 8290.48 | 10537.6 | 0.22 | 1.25 | 19.732 | 13.242 | 1 | 1 | 2850 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4110908.422 | 363198.1869 | 7910.8631 | 31115.167 | 332083.0199 | 14306.365 | 0.10859 | -110469.9585 | 110469.9585
C | Xist Rating 6016 | -10.7 | 2023.44 | 150.295 | 35.6 | 2033.28 | 8294.28 | 10537.7 | 0.22 | 1.25 | 19.733 | 13.252 | 1 | 1 | 2860 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4114220.0832 | 365641.8585 | 7966.4753 | 31224.3431 | 334417.5154 | 14318.7241 | 0.10897 | -110565.3917 | 110565.3917
C | Xist Rating 6017 | -10.25 | 2024.63 | 150.295 | 35.6 | 2043.23 | 8462.34 | 10537.9 | 0.21 | 1.25 | 19.809 | 13.261 | 1 | 1 | 2870 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4136784.7549 | 368093.707 | 8022.2824 | 31333.5191 | 336760.1879 | 14306.6838 | 0.10935 | -110472.4204 | 110472.4204
C | Xist Rating 6018 | -9.76 | 2026.14 | 150.295 | 35.6 | 2053.65 | 8643.72 | 10538 | 0.21 | 1.25 | 19.907 | 13.272 | 1 | 1 | 2880 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4160982.411 | 370553.7323 | 8078.2842 | 31442.6951 | 339111.0372 | 14322.6288 | 0.10973 | -110595.5428 | 110595.5428
C | Xist Rating 6019 | -10.24 | 2027.48 | 150.295 | 35.6 | 2041.84 | 8438.42 | 10537.8 | 0.21 | 1.25 | 19.838 | 13.28 | 1 | 1 | 2890 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4139789.7632 | 373021.9346 | 8134.4807 | 31551.8711 | 341470.0634 | 14330.9335 | 0.11011 | -110659.6701 | 110659.6701
C | Xist Rating 6020 | -9.46 | 2028.87 | 150.295 | 35.6 | 2059.21 | 8743.08 | 10538.1 | 0.2 | 1.25 | 19.927 | 13.29 | 1 | 1 | 2900 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4177869.3927 | 375498.3136 | 8190.8721 | 31661.0472 | 343837.2665 | 14319.7121 | 0.11049 | -110573.0207 | 110573.0207
C | Xist Rating 6021 | -9.11 | 2030.41 | 150.295 | 35.6 | 2066.33 | 8872.92 | 10538.1 | 0.2 | 1.25 | 19.964 | 13.301 | 1 | 1 | 2910 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4195497.0953 | 377982.8696 | 8247.4583 | 31770.2232 | 346212.6464 | 14333.8872 | 0.11087 | -110682.4777 | 110682.4777
C | Xist Rating 6022 | -8.81 | 2031.8 | 150.295 | 35.6 | 2072.48 | 8987.42 | 10538.1 | 0.2 | 1.25 | 19.993 | 13.311 | 1 | 1 | 2920 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4210864.864 | 380475.6024 | 8304.2393 | 31879.3992 | 348596.2032 | 14346.8211 | 0.11125 | -110782.3498 | 110782.3498
C | Xist Rating 6023 | -8.58 | 2033.19 | 150.295 | 35.6 | 2077.06 | 9074.14 | 10538 | 0.19 | 1.25 | 20.055 | 13.32 | 1 | 1 | 2930 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4223057.6214 | 382976.5121 | 8361.215 | 31988.5752 | 350987.9369 | 14333.2491 | 0.11164 | -110677.5499 | 110677.5499
C | Xist Rating 6024 | -8.35 | 2034.55 | 150.295 | 35.6 | 2081.6 | 9161.61 | 10538 | 0.19 | 1.25 | 20.075 | 13.33 | 1 | 1 | 2940 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4235119.28 | 385485.5987 | 8418.3855 | 32097.7513 | 353387.8474 | 14345.8428 | 0.11202 | -110774.7958 | 110774.7958
C | Xist Rating 6025 | -8.16 | 2035.96 | 150.295 | 35.6 | 2085.42 | 9236.12 | 10537.9 | 0.19 | 1.25 | 20.097 | 13.339 | 1 | 1 | 2950 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4245831.7032 | 388002.8621 | 8475.7509 | 32206.9273 | 355795.9348 | 14357.4518 | 0.1124 | -110864.4369 | 110864.4369
C | Xist Rating 6026 | -7.68 | 2037.33 | 150.295 | 35.5 | 2095.8 | 9443.31 | 10537.8 | 0.19 | 1.25 | 20.117 | 13.349 | 1 | 1 | 2960 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4269836.214 | 390528.3024 | 8533.311 | 32316.1033 | 358212.199 | 14370.0526 | 0.11278 | -110961.7368 | 110961.7368
C | Xist Rating 6027 | -7.66 | 2038.72 | 150.295 | 35.5 | 2095.37 | 9434.54 | 10537.9 | 0.18 | 1.25 | 20.124 | 13.358 | 1 | 1 | 2970 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4271872.7264 | 393061.9195 | 8591.0659 | 32425.2793 | 360636.6402 | 14354.4985 | 0.11316 | -110841.6323 | 110841.6323
C | Xist Rating 6028 | -7.66 | 2039.94 | 150.295 | 35.5 | 2094.78 | 9422.61 | 10537.9 | 0.18 | 1.25 | 20.16 | 13.366 | 1 | 1 | 2980 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4273225.5132 | 395603.7135 | 8649.0156 | 32534.4554 | 363069.2582 | 14365.2957 | 0.11354 | -110925.0059 | 110925.0059
C | Xist Rating 6029 | -7.64 | 2041.5 | 150.295 | 35.5 | 2094.12 | 9409.34 | 10537.9 | 0.18 | 1.25 | 20.154 | 13.376 | 1 | 1 | 2990 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4275145.98 | 398153.6844 | 8707.16 | 32643.6314 | 365510.053 | 14377.1626 | 0.11392 | -111016.6385 | 111016.6385
C | Xist Rating 6030 | -7.62 | 2042.93 | 150.295 | 35.5 | 2093.63 | 9399.36 | 10537.8 | 0.18 | 1.25 | 20.138 | 13.385 | 1 | 1 | 3000 | 152.4 | 2 | 3.9 | 19.05 | 1.3333 | 22 | E | Rod | 4277139.5359 | 400711.8322 | 8765.4993 | 32752.8074 | 367959.0248 | 14387.7479 | 0.1143 | -111098.3754 | 111098.3754
C | Xist Rating 6031 | -88.7 | 206.178 | 150.299 | 35.9 | 2371.56 | 7143.29 | 58745.9 | 2.47 | 10.95 | 21.778 | 522.2 | 1 | 1 | 1000 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 488963.4977 | 53130.1934 | 973.9444 | 11197.541 | 41932.6524 | 544715.0667 | 0.038101 | -4206145.3569 | 4206145.3569
C | Xist Rating 6032 | -88.6 | 208.317 | 150.299 | 35.9 | 2369.47 | 7132.26 | 58284.2 | 2.45 | 10.85 | 21.843 | 512.393 | 1 | 1 | 1010 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 493600.882 | 54085.0151 | 993.5206 | 11309.5164 | 42775.4987 | 534542.1153 | 0.038482 | -4127592.5225 | 4127592.5225
C | Xist Rating 6033 | -87.74 | 224.512 | 150.299 | 35.9 | 2363.36 | 7137.29 | 54967.7 | 2.46 | 10.07 | 21.895 | 444.043 | 1 | 1 | 1020 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 530602.6803 | 55048.2234 | 1013.2917 | 11421.4918 | 43626.7316 | 463600.5719 | 0.038863 | -3579800.7294 | 3579800.7294
C | Xist Rating 6034 | -87.6 | 228.934 | 150.298 | 35.9 | 2345.5 | 6991.74 | 54179.1 | 2.37 | 9.89 | 21.396 | 429.141 | 1 | 1 | 1030 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 536964.697 | 56019.8182 | 1033.2576 | 11533.4672 | 44486.3509 | 448003.4314 | 0.039244 | -3459363.7446 | 3459363.7446
C | Xist Rating 6035 | -87.52 | 231.147 | 150.298 | 35.9 | 2339.7 | 6947.74 | 53793.6 | 2.33 | 9.8 | 21.274 | 421.996 | 1 | 1 | 1040 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 540814.6359 | 56999.7995 | 1053.4182 | 11645.4426 | 45354.3568 | 440552.9413 | 0.039625 | -3401833.0354 | 3401833.0354
C | Xist Rating 6036 | -87.33 | 235.448 | 150.298 | 35.9 | 2333.45 | 6907.37 | 53042.7 | 2.29 | 9.63 | 21.195 | 407.998 | 1 | 1 | 1050 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 549406.1356 | 57988.1673 | 1073.7737 | 11757.418 | 46230.7493 | 425989.6935 | 0.040006 | -3289379.4956 | 3289379.4956
C | Xist Rating 6037 | -87.18 | 237.641 | 150.298 | 35.9 | 2339.88 | 6971.32 | 52676.7 | 2.25 | 9.54 | 21.179 | 401.378 | 1 | 1 | 1060 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 556051.4231 | 58984.9217 | 1094.3239 | 11869.3935 | 47115.5282 | 419094.5973 | 0.040387 | -3236137.3906 | 3236137.3906
C | Xist Rating 6038 | -86.34 | 255.06 | 150.297 | 35.9 | 2323.08 | 6882.24 | 49857.2 | 2.23 | 8.9 | 20.99 | 351.193 | 1 | 1 | 1070 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 592524.7848 | 59990.0626 | 1115.0689 | 11981.3689 | 48008.6937 | 366958.3837 | 0.040768 | -2833555.3691 | 2833555.3691
C | Xist Rating 6039 | -86.13 | 258.354 | 150.297 | 35.9 | 2330.13 | 6955.32 | 49380.6 | 2.18 | 8.79 | 20.894 | 343.318 | 1 | 1 | 1080 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 601998.406 | 61003.59 | 1136.0087 | 12093.3443 | 48910.2458 | 358740.2517 | 0.041149 | -2770097.1323 | 2770097.1323
C | Xist Rating 6040 | -85.88 | 262.735 | 150.297 | 35.9 | 2332.66 | 6992.33 | 48761.3 | 2.12 | 8.65 | 20.742 | 333.198 | 1 | 1 | 1090 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 612871.4251 | 62025.504 | 1157.1433 | 12205.3197 | 49820.1843 | 348174.0692 | 0.04153 | -2688507.8713 | 2688507.8713
C | Xist Rating 6041 | -85.66 | 265.996 | 150.297 | 35.8 | 2341.54 | 7083.81 | 48308.1 | 2.08 | 8.55 | 20.743 | 325.897 | 1 | 1 | 1100 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 622840.2738 | 63055.8045 | 1178.4727 | 12317.2951 | 50738.5094 | 340570.8964 | 0.041911 | -2629798.1866 | 2629798.1866
C | Xist Rating 6042 | -85.55 | 268.377 | 150.296 | 35.8 | 2338.79 | 7066.08 | 48010.9 | 2 | 8.49 | 20.434 | 321.421 | 1 | 1 | 1110 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 627677.4438 | 64094.4915 | 1199.9969 | 12429.2705 | 51665.221 | 335828.6024 | 0.042292 | -2593179.4495 | 2593179.4495
C | Xist Rating 6043 | -84.54 | 287.76 | 150.297 | 35.8 | 2334.9 | 7098.04 | 45447.7 | 2.04 | 7.92 | 20.698 | 281.235 | 1 | 1 | 1120 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 671890.824 | 65141.5651 | 1221.7158 | 12541.2459 | 52600.3192 | 294181.896 | 0.042673 | -2271594.6217 | 2271594.6217
C | Xist Rating 6044 | -84.42 | 290.094 | 150.296 | 35.8 | 2335.06 | 7106.84 | 45189.3 | 1.98 | 7.86 | 20.505 | 277.63 | 1 | 1 | 1130 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 677386.8956 | 66197.0252 | 1243.6296 | 12653.2213 | 53543.8038 | 290374.7763 | 0.043054 | -2242197.0525 | 2242197.0525
C | Xist Rating 6045 | -84.21 | 294.546 | 150.296 | 35.8 | 2332.17 | 7094.7 | 44681.5 | 1.92 | 7.75 | 20.323 | 270.378 | 1 | 1 | 1140 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 686931.3448 | 67260.8718 | 1265.7381 | 12765.1967 | 54495.6751 | 282781.0596 | 0.043435 | -2183560.3854 | 2183560.3854
C | Xist Rating 6046 | -83.97 | 298.934 | 150.295 | 35.8 | 2332.59 | 7113.17 | 44186.2 | 1.88 | 7.64 | 20.134 | 263.36 | 1 | 1 | 1150 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 697290.4591 | 68333.1049 | 1288.0414 | 12877.1721 | 55455.9328 | 275450.1475 | 0.043816 | -2126953.0254 | 2126953.0254
C | Xist Rating 6047 | -83.77 | 303.402 | 150.295 | 35.8 | 2329.04 | 7094.73 | 43703.3 | 1.83 | 7.53 | 19.974 | 256.685 | 1 | 1 | 1160 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 706635.3941 | 69413.7246 | 1310.5395 | 12989.1476 | 56424.5771 | 268467.568 | 0.044197 | -2073035.3972 | 2073035.3972
C | Xist Rating 6048 | -82.86 | 320.807 | 150.295 | 35.8 | 2326.73 | 7132.7 | 41832.4 | 1.85 | 7.13 | 20.124 | 230.893 | 1 | 1 | 1170 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 746431.2711 | 70502.7308 | 1333.2324 | 13101.123 | 57401.6079 | 241734.5054 | 0.044578 | -1866609.7738 | 1866609.7738
C | Xist Rating 6049 | -82.72 | 322.067 | 150.295 | 35.8 | 2337.26 | 7236.32 | 41724.7 | 1.8 | 7.11 | 20.047 | 229.647 | 1 | 1 | 1180 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 752754.3164 | 71600.1236 | 1356.1201 | 13213.0984 | 58387.0252 | 240396.6723 | 0.044959 | -1856279.3813 | 1856279.3813
C | Xist Rating 6050 | -82.33 | 330.829 | 150.295 | 35.8 | 2328.3 | 7180.11 | 40885.5 | 1.75 | 6.93 | 19.879 | 218.877 | 1 | 1 | 1190 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 770269.1607 | 72705.9028 | 1379.2026 | 13325.0738 | 59380.8291 | 229159.0701 | 0.04534 | -1769505.5958 | 1769505.5958
C | Xist Rating 6051 | -82.12 | 333.056 | 150.295 | 35.8 | 2339.71 | 7297.23 | 40682.7 | 1.72 | 6.88 | 19.926 | 216.368 | 1 | 1 | 1200 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 779254.4538 | 73820.0686 | 1402.4799 | 13437.0492 | 60383.0194 | 226541.3411 | 0.045721 | -1749292.1866 | 1749292.1866
C | Xist Rating 6052 | -81.9 | 337.593 | 150.295 | 35.8 | 2338.95 | 7304.82 | 40281.4 | 1.67 | 6.8 | 19.775 | 211.476 | 1 | 1 | 1210 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 789613.1473 | 74942.621 | 1425.9519 | 13549.0246 | 61393.5964 | 221408.6552 | 0.046102 | -1709658.9463 | 1709658.9463
C | Xist Rating 6053 | -80.96 | 357.329 | 150.295 | 35.8 | 2325.08 | 7238.32 | 38537.9 | 1.67 | 6.43 | 19.781 | 190.164 | 1 | 1 | 1220 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 830818.5113 | 76073.5598 | 1449.6188 | 13661 | 62412.5598 | 199291.5278 | 0.046483 | -1538876.3516 | 1538876.3516
C | Xist Rating 6054 | -80.67 | 361.716 | 150.295 | 35.8 | 2332.59 | 7326.42 | 38183.2 | 1.64 | 6.35 | 19.794 | 186.087 | 1 | 1 | 1230 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 843735.1244 | 77212.8852 | 1473.4804 | 13772.9754 | 63439.9098 | 195040.8344 | 0.046864 | -1506053.6235 | 1506053.6235
C | Xist Rating 6055 | -80.44 | 366.242 | 150.294 | 35.8 | 2332.74 | 7342.84 | 37835.8 | 1.6 | 6.28 | 19.695 | 182.207 | 1 | 1 | 1240 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 854347.3631 | 78360.5972 | 1497.5369 | 13884.9508 | 64475.6463 | 190973.1992 | 0.047245 | -1474644.4231 | 1474644.4231
C | Xist Rating 6056 | -80.28 | 368.613 | 150.294 | 35.8 | 2336.83 | 7390.98 | 37664.6 | 1.56 | 6.24 | 19.629 | 180.384 | 1 | 1 | 1250 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 861385.9168 | 79516.6956 | 1521.7881 | 13996.9262 | 65519.7694 | 189044.2318 | 0.047626 | -1459749.4475 | 1459749.4475
C | Xist Rating 6057 | -79.95 | 375.216 | 150.294 | 35.8 | 2336.08 | 7406.16 | 37161.6 | 1.53 | 6.14 | 19.585 | 174.782 | 1 | 1 | 1260 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 876534.5933 | 80681.1806 | 1546.2341 | 14108.9017 | 66572.2789 | 183203.2285 | 0.048007 | -1414646.7685 | 1414646.7685
C | Xist Rating 6058 | -79.02 | 393.909 | 150.294 | 35.8 | 2329.27 | 7403.15 | 35777.7 | 1.54 | 5.85 | 19.65 | 159.621 | 1 | 1 | 1270 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 917520.4164 | 81854.0521 | 1570.8749 | 14220.8771 | 67633.175 | 167488.8333 | 0.048388 | -1293304.3745 | 1293304.3745
C | Xist Rating 6059 | -78.81 | 398.503 | 150.294 | 35.8 | 2326.32 | 7388.29 | 35477.4 | 1.5 | 5.79 | 19.542 | 156.59 | 1 | 1 | 1280 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 927045.499 | 83035.3102 | 1595.7105 | 14332.8525 | 68702.4577 | 164300.317 | 0.048769 | -1268683.4965 | 1268683.4965
C | Xist Rating 6060 | -78.58 | 403.047 | 150.294 | 35.8 | 2325.36 | 7393.41 | 35182.8 | 1.46 | 5.73 | 19.501 | 153.629 | 1 | 1 | 1290 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 937229.3719 | 84224.9547 | 1620.7408 | 14444.8279 | 69780.1269 | 161189.8016 | 0.04915 | -1244664.921 | 1244664.921
C | Xist Rating 6061 | -78.22 | 409.628 | 150.294 | 35.8 | 2327.58 | 7438.29 | 34751.2 | 1.44 | 5.64 | 19.539 | 149.252 | 1 | 1 | 1300 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 953441.9402 | 85422.9858 | 1645.966 | 14556.8033 | 70866.1825 | 156637.5176 | 0.049531 | -1209513.3909 | 1209513.3909
C | Xist Rating 6062 | -77.99 | 413.114 | 150.294 | 35.8 | 2333.27 | 7508.07 | 34540.1 | 1.4 | 5.59 | 19.489 | 147.221 | 1 | 1 | 1310 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 963906.5028 | 86629.4035 | 1671.3859 | 14668.7787 | 71960.6248 | 154490.9354 | 0.049912 | -1192938.0521 | 1192938.0521
C | Xist Rating 6063 | -77.06 | 431.904 | 150.294 | 35.8 | 2327.21 | 7511.4 | 33363.1 | 1.41 | 5.35 | 19.541 | 135.578 | 1 | 1 | 1320 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 25 | E | Rod | 1005131.3078 | 87844.2076 | 1697.0007 | 14780.7541 | 73063.4535 | 142427.7981 | 0.050293 | -1099789.7037 | 1099789.7037
C | Xist Rating 6064 | -76.74 | 438.703 | 150.293 | 35.8 | 2324.27 | 7503.34 | 32979.9 | 1.37 | 5.28 | 19.399 | 132.039 | 1 | 1 | 1330 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1019664.2218 | 89067.3983 | 1722.8102 | 14892.7295 | 74174.6688 | 138706.706 | 0.050674 | -1071056.4163 | 1071056.4163
C | Xist Rating 6065 | -76.36 | 445.399 | 150.293 | 35.8 | 2326.95 | 7554.05 | 32606.7 | 1.34 | 5.2 | 19.319 | 128.615 | 1 | 1 | 1340 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1036421.203 | 90298.9756 | 1748.8145 | 15004.7049 | 75294.2706 | 135121.4052 | 0.051055 | -1043371.6745 | 1043371.6745
C | Xist Rating 6066 | -76.14 | 448.903 | 150.293 | 35.8 | 2331.7 | 7615.88 | 32423.8 | 1.31 | 5.16 | 19.285 | 127.012 | 1 | 1 | 1350 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1046707.1251 | 91538.9393 | 1775.0136 | 15116.6803 | 76422.259 | 133430.5293 | 0.051436 | -1030315.1787 | 1030315.1787
C | Xist Rating 6067 | -75.88 | 451.076 | 150.293 | 35.8 | 2346.51 | 7784.16 | 32303.4 | 1.3 | 5.14 | 19.358 | 125.926 | 1 | 1 | 1360 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1058454.3448 | 92787.2896 | 1801.4075 | 15228.6558 | 77558.6339 | 132308.073 | 0.051817 | -1021647.869 | 1021647.869
C | Xist Rating 6068 | -74.73 | 477.755 | 150.293 | 35.8 | 2321.42 | 7607.11 | 30902.5 | 1.29 | 4.86 | 19.291 | 113.468 | 1 | 1 | 1370 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1109070.0121 | 94044.0264 | 1827.9962 | 15340.6312 | 78703.3953 | 119364.5447 | 0.052198 | -921701.374 | 921701.374
C | Xist Rating 6069 | -74.62 | 480.189 | 150.293 | 35.8 | 2320.86 | 7608.61 | 30794.1 | 1.26 | 4.84 | 19.252 | 112.618 | 1 | 1 | 1380 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1114451.4425 | 95309.1498 | 1854.7797 | 15452.6066 | 79856.5432 | 118454.137 | 0.052579 | -914671.4474 | 914671.4474
C | Xist Rating 6070 | -74.32 | 485.888 | 150.293 | 35.7 | 2321.93 | 7639.16 | 30526.9 | 1.24 | 4.78 | 19.217 | 110.418 | 1 | 1 | 1390 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1128197.9238 | 96582.6597 | 1881.7579 | 15564.582 | 81018.0777 | 116153.6194 | 0.05296 | -896907.4597 | 896907.4597
C | Xist Rating 6071 | -74.02 | 491.584 | 150.293 | 35.7 | 2323.17 | 7671.7 | 30265 | 1.21 | 4.73 | 19.187 | 108.284 | 1 | 1 | 1400 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1142033.2013 | 97864.5561 | 1908.931 | 15676.5574 | 82187.9987 | 113909.6884 | 0.053341 | -879580.42 | 879580.42
C | Xist Rating 6072 | -73.66 | 498.342 | 150.293 | 35.7 | 2323.93 | 7703.15 | 29957.4 | 1.19 | 4.67 | 19.166 | 105.788 | 1 | 1 | 1410 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1158111.9241 | 99154.839 | 1936.2988 | 15788.5328 | 83366.3062 | 111302.1701 | 0.053722 | -859445.8548 | 859445.8548
C | Xist Rating 6073 | -72.67 | 518.321 | 150.293 | 35.7 | 2319.32 | 7723.42 | 29051.8 | 1.2 | 4.49 | 19.238 | 98.435 | 1 | 1 | 1420 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1202152.2617 | 100453.5085 | 1963.8614 | 15900.5082 | 84553.0003 | 103694.0135 | 0.054103 | -800697.6857 | 800697.6857
C | Xist Rating 6074 | -72.5 | 522.064 | 150.293 | 35.7 | 2318.1 | 7721.49 | 28910.7 | 1.16 | 4.47 | 19.157 | 97.43 | 1 | 1 | 1430 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1210196.5584 | 101760.5645 | 1991.6188 | 16012.4836 | 85748.0809 | 102605.3222 | 0.054484 | -792291.1001 | 792291.1001
C | Xist Rating 6075 | -72.06 | 530.996 | 150.293 | 35.7 | 2316.83 | 7737.98 | 28541.9 | 1.14 | 4.39 | 19.141 | 94.608 | 1 | 1 | 1440 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1230227.4627 | 103076.007 | 2019.571 | 16124.459 | 86951.548 | 99658.7325 | 0.054865 | -769538.3161 | 769538.3161
C | Xist Rating 6076 | -71.76 | 536.729 | 150.293 | 35.7 | 2317 | 7759.22 | 28316.8 | 1.12 | 4.35 | 19.118 | 92.944 | 1 | 1 | 1450 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1243601.093 | 104399.8361 | 2047.718 | 16236.4344 | 88163.4017 | 97913.8963 | 0.055246 | -756065.153 | 756065.153
C | Xist Rating 6077 | -71.49 | 540.114 | 150.293 | 35.7 | 2325.54 | 7867.62 | 28183.7 | 1.11 | 4.32 | 19.146 | 91.968 | 1 | 1 | 1460 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1256056.7116 | 105732.0517 | 2076.0598 | 16348.4099 | 89383.6418 | 96899.4422 | 0.055627 | -748231.8072 | 748231.8072
C | Xist Rating 6078 | -70.52 | 562.695 | 150.293 | 35.7 | 2308.84 | 7757.42 | 27310.3 | 1.1 | 4.16 | 19.124 | 85.517 | 1 | 1 | 1470 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1299172.7238 | 107072.6538 | 2104.5964 | 16460.3853 | 90612.2686 | 90195.4047 | 0.056008 | -696465.007 | 696465.007
C | Xist Rating 6079 | -70.16 | 569.496 | 150.293 | 35.7 | 2310.37 | 7797.78 | 27066.3 | 1.08 | 4.11 | 19.11 | 83.807 | 1 | 1 | 1480 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1315746.4735 | 108421.6425 | 2133.3277 | 16572.3607 | 91849.2818 | 88402.6249 | 0.056389 | -682621.6368 | 682621.6368
C | Xist Rating 6080 | -69.85 | 575.232 | 150.293 | 35.7 | 2311.78 | 7833.27 | 26866.5 | 1.07 | 4.07 | 19.098 | 82.436 | 1 | 1 | 1490 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1329809.833 | 109779.0177 | 2162.2539 | 16684.3361 | 93094.6816 | 86974.474 | 0.05677 | -671593.8337 | 671593.8337
C | Xist Rating 6081 | -69.55 | 581.059 | 150.293 | 35.7 | 2312.21 | 7857.58 | 26670 | 1.04 | 4.03 | 19.072 | 81.114 | 1 | 1 | 1500 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1343530.4304 | 111144.7794 | 2191.3748 | 16796.3115 | 94348.4679 | 85570.3981 | 0.057151 | -660751.9318 | 660751.9318
C | Xist Rating 6082 | -69.15 | 587.888 | 150.293 | 35.7 | 2316.32 | 7928.84 | 26438.9 | 1.03 | 3.99 | 19.076 | 79.548 | 1 | 1 | 1510 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1361736.7322 | 112518.9276 | 2220.6906 | 16908.2869 | 95610.6407 | 83940.3704 | 0.057532 | -648165.2902 | 648165.2902
C | Xist Rating 6083 | -68.02 | 610.152 | 150.293 | 35.7 | 2313.78 | 7980.13 | 25681.2 | 1.03 | 3.84 | 19.155 | 74.375 | 1 | 1 | 1520 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1411757.4946 | 113901.4624 | 2250.2011 | 17020.2623 | 96881.2001 | 78582.5694 | 0.057913 | -606793.7708 | 606793.7708
C | Xist Rating 6084 | -67.72 | 617.324 | 150.293 | 35.7 | 2309.48 | 7952.79 | 25468.5 | 1 | 3.8 | 19.086 | 73.051 | 1 | 1 | 1530 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1425697.4315 | 115292.3837 | 2279.9064 | 17132.2377 | 98160.146 | 77172.2986 | 0.058294 | -595904.0337 | 595904.0337
C | Xist Rating 6085 | -67.48 | 620.983 | 150.293 | 35.7 | 2314.14 | 8020.38 | 25363.7 | 0.98 | 3.78 | 19.075 | 72.42 | 1 | 1 | 1540 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1437041.5996 | 116691.6916 | 2309.8065 | 17244.2131 | 99447.4784 | 76498.4671 | 0.058675 | -590700.8852 | 590700.8852
C | Xist Rating 6086 | -66.92 | 632.214 | 150.293 | 35.7 | 2312.66 | 8042.56 | 25021.2 | 0.97 | 3.72 | 19.068 | 70.237 | 1 | 1 | 1550 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1462096.0292 | 118099.3859 | 2339.9013 | 17356.1885 | 100743.1974 | 74226.0796 | 0.059056 | -573154.1115 | 573154.1115
C | Xist Rating 6087 | -66.6 | 635.648 | 150.293 | 35.7 | 2323.82 | 8191.58 | 24920.5 | 0.96 | 3.7 | 19.107 | 69.622 | 1 | 1 | 1560 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1477131.5354 | 119515.4668 | 2370.191 | 17468.164 | 102047.3029 | 73584.9783 | 0.059437 | -568203.6971 | 568203.6971
C | Xist Rating 6088 | -65.52 | 661.796 | 150.293 | 35.7 | 2304.56 | 8049.94 | 24162.1 | 0.95 | 3.56 | 19.056 | 64.912 | 1 | 1 | 1570 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1525148.5898 | 120939.9343 | 2400.6755 | 17580.1394 | 103359.7949 | 68685.0166 | 0.059818 | -530367.4922 | 530367.4922
C | Xist Rating 6089 | -65.18 | 667.652 | 150.293 | 35.7 | 2307.39 | 8104.69 | 24007.5 | 0.93 | 3.53 | 19.049 | 64.017 | 1 | 1 | 1580 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1540533.5483 | 122372.7882 | 2431.3547 | 17692.1148 | 104680.6734 | 67736.2222 | 0.0602 | -523041.1526 | 523041.1526
C | Xist Rating 6090 | -64.89 | 673.543 | 150.293 | 35.7 | 2308.24 | 8135.47 | 23854.4 | 0.92 | 3.5 | 19.022 | 63.144 | 1 | 1 | 1590 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1554698.8943 | 123814.0287 | 2462.2288 | 17804.0902 | 106009.9385 | 66822.2072 | 0.060581 | -515983.371 | 515983.371
C | Xist Rating 6091 | -64.43 | 681.465 | 150.293 | 35.7 | 2312.19 | 8213.58 | 23644.6 | 0.91 | 3.46 | 19.036 | 61.92 | 1 | 1 | 1600 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1575676.5584 | 125263.6557 | 2493.2976 | 17916.0656 | 107347.5901 | 65546.2007 | 0.060962 | -506130.3878 | 506130.3878
C | Xist Rating 6092 | -64.22 | 685.32 | 150.292 | 35.7 | 2313.82 | 8246.63 | 23555.9 | 0.89 | 3.45 | 19.01 | 61.457 | 1 | 1 | 1610 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1585707.1224 | 126721.6693 | 2524.5612 | 18028.041 | 108693.6283 | 65043.9952 | 0.061343 | -502252.4897 | 502252.4897
C | Xist Rating 6093 | -62.93 | 714.566 | 150.293 | 35.7 | 2299.83 | 8177.86 | 22804.4 | 0.89 | 3.31 | 19.038 | 57.114 | 1 | 1 | 1620 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1643380.3238 | 128188.0694 | 2556.0196 | 18140.0164 | 110048.0529 | 60543.19 | 0.061724 | -467498.4649 | 467498.4649
C | Xist Rating 6094 | -62.6 | 718.076 | 150.293 | 35.7 | 2309.65 | 8315.82 | 22722.8 | 0.88 | 3.29 | 19.061 | 56.683 | 1 | 1 | 1630 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1658504.2334 | 129662.856 | 2587.6728 | 18251.9918 | 111410.8641 | 60090.761 | 0.062105 | -464004.9285 | 464004.9285
C | Xist Rating 6095 | -62.29 | 724.114 | 150.293 | 35.7 | 2310.02 | 8341.58 | 22588 | 0.86 | 3.27 | 19.039 | 55.98 | 1 | 1 | 1640 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1672717.8223 | 131146.0291 | 2619.5208 | 18363.9672 | 112782.0619 | 59338.8001 | 0.062486 | -458198.4857 | 458198.4857
C | Xist Rating 6096 | -61.92 | 732.393 | 150.293 | 35.7 | 2307.26 | 8334.88 | 22402.4 | 0.84 | 3.23 | 19.013 | 55.001 | 1 | 1 | 1650 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1689821.0732 | 132637.5888 | 2651.5635 | 18475.9426 | 114161.6461 | 58299.6715 | 0.062867 | -450174.61 | 450174.61
C | Xist Rating 6097 | -61.49 | 740.428 | 150.293 | 35.7 | 2308.97 | 8386.77 | 22220.3 | 0.83 | 3.2 | 19.016 | 54.034 | 1 | 1 | 1660 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1709626.0392 | 134137.535 | 2683.8011 | 18587.9181 | 115549.6169 | 57288.6404 | 0.063248 | -442367.6954 | 442367.6954
C | Xist Rating 6098 | -60.35 | 766.62 | 150.293 | 35.7 | 2296.92 | 8326.37 | 21632.5 | 0.83 | 3.1 | 19.042 | 50.903 | 1 | 1 | 1670 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1760864.8104 | 135645.8677 | 2716.2334 | 18699.8935 | 116945.9743 | 54045.792 | 0.063629 | -417327.2802 | 417327.2802
C | Xist Rating 6099 | -60.07 | 770.242 | 150.293 | 35.7 | 2302.7 | 8415.39 | 21560 | 0.82 | 3.08 | 19.049 | 50.555 | 1 | 1 | 1680 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1773636.2534 | 137162.587 | 2748.8606 | 18811.8689 | 118350.7181 | 53677.5717 | 0.06401 | -414483.98 | 414483.98
C | Xist Rating 6100 | -59.62 | 780.81 | 150.293 | 35.7 | 2297.93 | 8389.63 | 21345.7 | 0.8 | 3.04 | 19.021 | 49.488 | 1 | 1 | 1690 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1794246.7233 | 138687.6928 | 2781.6825 | 18923.8443 | 119763.8485 | 52545.938 | 0.064391 | -405745.805 | 405745.805
C | Xist Rating 6101 | -59.22 | 787.795 | 150.293 | 35.7 | 2300.95 | 8455.37 | 21205.6 | 0.79 | 3.02 | 19.023 | 48.798 | 1 | 1 | 1700 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1812676.9052 | 140221.1851 | 2814.6992 | 19035.8197 | 121185.3654 | 51821.821 | 0.064772 | -400154.3655 | 400154.3655
C | Xist Rating 6102 | -58.83 | 796.022 | 150.293 | 35.7 | 2299.81 | 8469.75 | 21044.5 | 0.78 | 2.99 | 19.012 | 48.016 | 1 | 1 | 1710 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1830699.3558 | 141763.064 | 2847.9107 | 19147.7951 | 122615.2689 | 51001.2128 | 0.065153 | -393817.8461 | 393817.8461
C | Xist Rating 6103 | -57.76 | 820.129 | 150.293 | 35.7 | 2290.8 | 8438.15 | 20567 | 0.78 | 2.9 | 19.043 | 45.654 | 1 | 1 | 1720 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1878751.5132 | 143313.3294 | 2881.317 | 19259.7705 | 124053.5588 | 48556.791 | 0.065534 | -374942.6688 | 374942.6688
C | Xist Rating 6104 | -57.28 | 830.567 | 150.293 | 35.7 | 2288.53 | 8445.08 | 20374.2 | 0.77 | 2.87 | 19.032 | 44.748 | 1 | 1 | 1730 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1900777.4965 | 144871.9813 | 2914.9181 | 19371.7459 | 125500.2354 | 47607.1454 | 0.065915 | -367609.7576 | 367609.7576
C | Xist Rating 6105 | -56.95 | 835.403 | 150.293 | 35.7 | 2293.74 | 8533.52 | 20289.9 | 0.76 | 2.85 | 19.037 | 44.372 | 1 | 1 | 1740 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1916197.2772 | 146439.0197 | 2948.714 | 19483.7213 | 126955.2984 | 47208.6913 | 0.066296 | -364533.0005 | 364533.0005
C | Xist Rating 6106 | -56.53 | 844.906 | 150.293 | 35.7 | 2290.95 | 8529.03 | 20123.5 | 0.74 | 2.82 | 19.018 | 43.615 | 1 | 1 | 1750 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1935637.4007 | 148014.4447 | 2982.7046 | 19595.6967 | 128418.748 | 46398.0639 | 0.066677 | -358273.5508 | 358273.5508
C | Xist Rating 6107 | -56.15 | 852.008 | 150.293 | 35.7 | 2291.82 | 8566.6 | 20001.1 | 0.73 | 2.8 | 19.024 | 43.064 | 1 | 1 | 1760 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 1952648.9746 | 149598.2562 | 3016.8901 | 19707.6722 | 129890.5841 | 45817.5016 | 0.067058 | -353790.6024 | 353790.6024
C | Xist Rating 6108 | -54.91 | 880.577 | 150.294 | 35.7 | 2280.82 | 8521.37 | 19497.8 | 0.73 | 2.71 | 19.06 | 40.74 | 1 | 1 | 1770 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2008437.6331 | 151190.4543 | 3051.2703 | 19819.6476 | 131370.8067 | 43412.3413 | 0.067439 | -335218.5925 | 335218.5925
C | Xist Rating 6109 | -54.79 | 887.788 | 150.294 | 35.6 | 2270.8 | 8407.64 | 19383.5 | 0.72 | 2.69 | 19.275 | 40.244 | 1 | 1 | 1780 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2015988.9904 | 152791.0388 | 3085.8453 | 19931.623 | 132859.4158 | 42900.6265 | 0.06782 | -331267.2663 | 331267.2663
C | Xist Rating 6110 | -54.58 | 891.669 | 150.293 | 35.6 | 2271.71 | 8432.54 | 19327 | 0.71 | 2.68 | 19.264 | 40.022 | 1 | 1 | 1790 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2025613.384 | 154400.0099 | 3120.6151 | 20043.5984 | 134356.4115 | 42660.2085 | 0.068201 | -329410.822 | 329410.822
C | Xist Rating 6111 | -53.84 | 904.435 | 150.293 | 35.6 | 2276.9 | 8550.95 | 19121.7 | 0.7 | 2.65 | 19.022 | 39.144 | 1 | 1 | 1800 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2059308.0515 | 156017.3676 | 3155.5797 | 20155.5738 | 135861.7938 | 41725.3268 | 0.068582 | -322191.9132 | 322191.9132
C | Xist Rating 6112 | -53.71 | 911.518 | 150.293 | 35.6 | 2265.8 | 8420.77 | 19013.2 | 0.69 | 2.63 | 19.251 | 38.678 | 1 | 1 | 1810 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2065317.4844 | 157643.1117 | 3190.7391 | 20267.5492 | 137375.5625 | 41244.7418 | 0.068963 | -318480.9635 | 318480.9635
C | Xist Rating 6113 | -52.26 | 940.347 | 150.293 | 35.6 | 2266.52 | 8536.35 | 18562.5 | 0.69 | 2.55 | 19.053 | 36.753 | 1 | 1 | 1820 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2131315.2824 | 159277.2424 | 3226.0933 | 20379.5246 | 138897.7178 | 39240.4409 | 0.069344 | -303004.2833 | 303004.2833
C | Xist Rating 6114 | -52.47 | 935.766 | 150.294 | 35.6 | 2270.18 | 8571.69 | 18631.3 | 0.69 | 2.56 | 19.302 | 37.047 | 1 | 1 | 1830 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2124357.2579 | 160919.7596 | 3261.6423 | 20491.5 | 140428.2596 | 39565.7458 | 0.069725 | -305516.2012 | 305516.2012
C | Xist Rating 6115 | -52.02 | 941.583 | 150.294 | 35.6 | 2277.71 | 8701.69 | 18545.1 | 0.68 | 2.55 | 19.324 | 36.698 | 1 | 1 | 1840 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2144653.0149 | 162570.6634 | 3297.386 | 20603.4754 | 141967.1879 | 39194.5938 | 0.070106 | -302650.2642 | 302650.2642
C | Xist Rating 6116 | -51.6 | 951.203 | 150.294 | 35.6 | 2274.6 | 8690.86 | 18409.3 | 0.67 | 2.52 | 19.314 | 36.155 | 1 | 1 | 1850 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2163606.3438 | 164229.9537 | 3333.3246 | 20715.4508 | 143514.5028 | 38619.9991 | 0.070487 | -298213.3964 | 298213.3964
C | Xist Rating 6117 | -51.14 | 961.983 | 150.293 | 35.6 | 2271.1 | 8678.6 | 18259 | 0.66 | 2.5 | 19.301 | 35.558 | 1 | 1 | 1860 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2184759.5913 | 165897.6305 | 3369.4579 | 20827.4263 | 145070.2042 | 37988.9979 | 0.070868 | -293340.972 | 293340.972
C | Xist Rating 6118 | -49.95 | 988.454 | 150.294 | 35.6 | 2264.65 | 8684.89 | 17879.6 | 0.66 | 2.43 | 19.35 | 34.01 | 1 | 1 | 1870 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2238502.3511 | 167573.6938 | 3405.7861 | 20939.4017 | 146634.2922 | 36389.8232 | 0.071249 | -280992.5689 | 280992.5689
C | Xist Rating 6119 | -49.47 | 999.22 | 150.294 | 35.6 | 2262.16 | 8686.7 | 17738.8 | 0.65 | 2.41 | 19.341 | 33.472 | 1 | 1 | 1880 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2260395.5152 | 169258.1437 | 3442.309 | 21051.3771 | 148206.7666 | 35820.0363 | 0.07163 | -276592.8256 | 276592.8256
C | Xist Rating 6120 | -49.05 | 1006.35 | 150.294 | 35.6 | 2265.36 | 8760.04 | 17646.5 | 0.64 | 2.39 | 19.357 | 33.125 | 1 | 1 | 1890 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2279745.036 | 170950.9801 | 3479.0267 | 21163.3525 | 149787.6276 | 35449.7947 | 0.072011 | -273733.9177 | 273733.9177
C | Xist Rating 6121 | -48.75 | 1013.94 | 150.294 | 35.6 | 2262.17 | 8738.37 | 17555 | 0.62 | 2.38 | 19.341 | 32.797 | 1 | 1 | 1900 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2293704.6498 | 172652.203 | 3515.9392 | 21275.3279 | 151376.8751 | 35080.9039 | 0.072392 | -270885.4413 | 270885.4413
C | Xist Rating 6122 | -48.37 | 1021.25 | 150.294 | 35.6 | 2263.04 | 8777.42 | 17464.8 | 0.61 | 2.36 | 19.343 | 32.467 | 1 | 1 | 1910 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2311129.6 | 174361.8125 | 3553.0464 | 21387.3033 | 152974.5092 | 34727.1202 | 0.072773 | -268153.6171 | 268153.6171
C | Xist Rating 6123 | -46.96 | 1053.4 | 150.294 | 35.6 | 2254 | 8764.28 | 17050.3 | 0.62 | 2.29 | 19.395 | 30.874 | 1 | 1 | 1920 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2374363.6 | 176079.8085 | 3590.3485 | 21499.2787 | 154580.5298 | 33097.5031 | 0.073154 | -255570.1457 | 255570.1457
C | Xist Rating 6124 | -46.54 | 1064.24 | 150.294 | 35.6 | 2249.39 | 8733.24 | 16923.9 | 0.61 | 2.27 | 19.389 | 30.423 | 1 | 1 | 1930 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2393890.8136 | 177806.191 | 3627.8454 | 21611.2541 | 156194.9369 | 32617.4349 | 0.073535 | -251863.1862 | 251863.1862
C | Xist Rating 6125 | -46.18 | 1067.76 | 150.294 | 35.6 | 2257.55 | 8870.78 | 16882.2 | 0.6 | 2.26 | 19.419 | 30.28 | 1 | 1 | 1940 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2410521.588 | 179540.9601 | 3665.537 | 21723.2295 | 157817.7306 | 32458.9358 | 0.073916 | -250639.2982 | 250639.2982
C | Xist Rating 6126 | -45.85 | 1077.95 | 150.294 | 35.6 | 2250.34 | 8794.87 | 16772.2 | 0.59 | 2.24 | 19.394 | 29.907 | 1 | 1 | 1950 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2425754.003 | 181284.1157 | 3703.4235 | 21835.2049 | 159448.9107 | 32058.5355 | 0.074297 | -247547.5136 | 247547.5136
C | Xist Rating 6127 | -45.33 | 1089.84 | 150.294 | 35.6 | 2247.61 | 8796.2 | 16637.2 | 0.58 | 2.22 | 19.42 | 29.43 | 1 | 1 | 1960 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2449535.2824 | 183035.6578 | 3741.5047 | 21947.1804 | 161088.4774 | 31552.5868 | 0.074678 | -243640.712 | 243640.712
C | Xist Rating 6128 | -44.08 | 1118.79 | 150.294 | 35.7 | 2240.22 | 8792.15 | 16303.3 | 0.58 | 2.16 | 19.485 | 28.23 | 1 | 1 | 1970 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2506335.7338 | 184795.5864 | 3779.7807 | 22059.1558 | 162736.4307 | 30314.7667 | 0.075059 | -234082.5929 | 234082.5929
C | Xist Rating 6129 | -43.68 | 1127.25 | 150.294 | 35.7 | 2239.9 | 8817.2 | 16214.2 | 0.57 | 2.15 | 19.508 | 27.933 | 1 | 1 | 1980 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2524927.275 | 186563.9016 | 3818.2515 | 22171.1312 | 164392.7705 | 29995.2685 | 0.07544 | -231615.5125 | 231615.5125
C | Xist Rating 6130 | -43.25 | 1138.28 | 150.294 | 35.7 | 2235.73 | 8791.28 | 16101.4 | 0.56 | 2.13 | 19.508 | 27.561 | 1 | 1 | 1990 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2544886.7444 | 188340.6033 | 3856.9171 | 22283.1066 | 166057.4968 | 29596.53 | 0.075821 | -228536.5599 | 228536.5599
C | Xist Rating 6131 | -42.86 | 1146.86 | 150.294 | 35.7 | 2234.42 | 8800.76 | 16015 | 0.55 | 2.12 | 19.51 | 27.279 | 1 | 1 | 2000 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2562566.9212 | 190125.6916 | 3895.7775 | 22395.082 | 167730.6096 | 29291.1802 | 0.076202 | -226178.7291 | 226178.7291
C | Xist Rating 6132 | -42.53 | 1153.15 | 150.294 | 35.7 | 2235.37 | 8836.95 | 15953.8 | 0.54 | 2.11 | 19.514 | 27.087 | 1 | 1 | 2010 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2577716.9155 | 191919.1663 | 3934.8326 | 22507.0574 | 169412.1089 | 29079.215 | 0.076583 | -224541.99 | 224541.99
C | Xist Rating 6133 | -41.19 | 1185.75 | 150.294 | 35.7 | 2225.66 | 8806.84 | 15614.9 | 0.54 | 2.05 | 19.551 | 25.938 | 1 | 1 | 2020 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2639076.345 | 193721.0276 | 3974.0826 | 22619.0328 | 171101.9948 | 27892.5128 | 0.076964 | -215378.5905 | 215378.5905
C | Xist Rating 6134 | -40.64 | 1197.57 | 150.294 | 35.7 | 2224.65 | 8833.62 | 15499.8 | 0.54 | 2.03 | 19.556 | 25.569 | 1 | 1 | 2030 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2664174.1005 | 195531.2755 | 4013.5273 | 22731.0082 | 172800.2673 | 27514.285 | 0.077345 | -212458.0153 | 212458.0153
C | Xist Rating 6135 | -40.34 | 1205.36 | 150.294 | 35.7 | 2222.01 | 8817.51 | 15431.7 | 0.53 | 2.02 | 19.549 | 25.368 | 1 | 1 | 2040 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2678321.9736 | 197349.9098 | 4053.1669 | 22842.9836 | 174506.9262 | 27292.0587 | 0.077726 | -210742.0427 | 210742.0427
C | Xist Rating 6136 | -39.89 | 1212.34 | 150.294 | 35.7 | 2226.5 | 8914.52 | 15364.2 | 0.52 | 2.01 | 19.572 | 25.155 | 1 | 1 | 2050 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2699275.01 | 199176.9307 | 4093.0012 | 22954.959 | 176221.9717 | 27058.6381 | 0.078107 | -208939.631 | 208939.631
C | Xist Rating 6137 | -39.51 | 1223.77 | 150.294 | 35.7 | 2220.4 | 8855.93 | 15264.2 | 0.51 | 1.99 | 19.554 | 24.855 | 1 | 1 | 2060 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2717258.908 | 201012.3382 | 4133.0303 | 23066.9345 | 177945.4037 | 26732.7304 | 0.078488 | -206423.0578 | 206423.0578
C | Xist Rating 6138 | -38.08 | 1258.76 | 150.294 | 35.7 | 2210.23 | 8823.37 | 14936 | 0.51 | 1.94 | 19.592 | 23.807 | 1 | 1 | 2070 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2782149.1148 | 202856.1321 | 4173.2542 | 23178.9099 | 179677.2222 | 25650.6524 | 0.078869 | -198067.5386 | 198067.5386
C | Xist Rating 6139 | -37.79 | 1266.35 | 150.294 | 35.7 | 2207.99 | 8812.89 | 14873.4 | 0.51 | 1.93 | 19.595 | 23.628 | 1 | 1 | 2080 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2796088.1365 | 204708.3126 | 4213.6729 | 23290.8853 | 181417.4273 | 25469.3827 | 0.07925 | -196667.8218 | 196667.8218
C | Xist Rating 6140 | -37.36 | 1276.17 | 150.294 | 35.7 | 2206.67 | 8825.34 | 14790.8 | 0.5 | 1.91 | 19.595 | 23.386 | 1 | 1 | 2090 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2816086.0539 | 206568.8796 | 4254.2864 | 23402.8607 | 183166.0189 | 25204.1883 | 0.079631 | -194620.0611 | 194620.0611
C | Xist Rating 6141 | -36.93 | 1285.99 | 150.294 | 35.7 | 2205.14 | 8834.48 | 14709.3 | 0.49 | 1.9 | 19.593 | 23.149 | 1 | 1 | 2100 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2835787.9886 | 208437.8332 | 4295.0947 | 23514.8361 | 184922.9971 | 24943.9185 | 0.080012 | -192610.3267 | 192610.3267
C | Xist Rating 6142 | -36.54 | 1294.67 | 150.294 | 35.7 | 2204.19 | 8848.63 | 14638.7 | 0.49 | 1.89 | 19.594 | 22.948 | 1 | 1 | 2110 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2853698.6673 | 210315.1732 | 4336.0977 | 23626.8115 | 186688.3617 | 24739.5301 | 0.080393 | -191032.0936 | 191032.0936
C | Xist Rating 6143 | -35.23 | 1327.7 | 150.294 | 35.7 | 2194.55 | 8812.6 | 14359.1 | 0.49 | 1.84 | 19.627 | 22.106 | 1 | 1 | 2120 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2913704.035 | 212200.8998 | 4377.2956 | 23738.7869 | 188462.1129 | 23870.9547 | 0.080774 | -184325.1844 | 184325.1844
C | Xist Rating 6144 | -34.73 | 1339.87 | 150.294 | 35.7 | 2192.07 | 8814.09 | 14263.8 | 0.48 | 1.83 | 19.623 | 21.837 | 1 | 1 | 2130 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2937088.8309 | 214095.013 | 4418.6882 | 23850.7623 | 190244.2507 | 23576.987 | 0.081155 | -182055.244 | 182055.244
C | Xist Rating 6145 | -34.31 | 1352.07 | 150.294 | 35.7 | 2186.8 | 8770.4 | 14170 | 0.47 | 1.81 | 19.618 | 21.574 | 1 | 1 | 2140 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2956706.676 | 215997.5126 | 4460.2756 | 23962.7377 | 192034.7749 | 23289.0352 | 0.081536 | -179831.7567 | 179831.7567
C | Xist Rating 6146 | -34.01 | 1358.51 | 150.294 | 35.7 | 2186.79 | 8790.86 | 14123.5 | 0.47 | 1.8 | 19.62 | 21.453 | 1 | 1 | 2150 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2970776.0829 | 217908.3988 | 4502.0578 | 24074.7131 | 193833.6857 | 23167.6005 | 0.081917 | -178894.0703 | 178894.0703
C | Xist Rating 6147 | -33.63 | 1367.13 | 150.294 | 35.7 | 2186.53 | 8815.59 | 14059 | 0.46 | 1.79 | 19.622 | 21.278 | 1 | 1 | 2160 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 2989270.7589 | 219827.6716 | 4544.0348 | 24186.6886 | 195640.983 | 22971.0895 | 0.082298 | -177376.6643 | 177376.6643
C | Xist Rating 6148 | -32.25 | 1402.76 | 150.294 | 35.7 | 2175.74 | 8765.55 | 13786 | 0.46 | 1.75 | 19.651 | 20.502 | 1 | 1 | 2170 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3052041.0424 | 221755.3308 | 4586.2066 | 24298.664 | 197456.6669 | 22170.5583 | 0.082679 | -171195.1741 | 171195.1741
C | Xist Rating 6149 | -31.73 | 1414.71 | 150.294 | 35.7 | 2174.58 | 8787.45 | 13699.1 | 0.46 | 1.74 | 19.654 | 20.267 | 1 | 1 | 2180 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3076400.0718 | 223691.3766 | 4628.5732 | 24410.6394 | 199280.7372 | 21930.6979 | 0.08306 | -169343.0359 | 169343.0359
C | Xist Rating 6150 | -31.36 | 1423.56 | 150.294 | 35.7 | 2173.45 | 8797.6 | 13638.9 | 0.45 | 1.73 | 19.651 | 20.113 | 1 | 1 | 2190 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3094036.482 | 225635.8089 | 4671.1346 | 24522.6148 | 201113.1942 | 21755.3956 | 0.083441 | -167989.398 | 167989.398
C | Xist Rating 6151 | -31.07 | 1432.82 | 150.294 | 35.7 | 2169.43 | 8760.44 | 13579.3 | 0.44 | 1.72 | 19.648 | 19.966 | 1 | 1 | 2200 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3108402.6926 | 227588.6278 | 4713.8907 | 24634.5902 | 202954.0376 | 21587.1913 | 0.083822 | -166690.569 | 166690.569
C | Xist Rating 6152 | -30.57 | 1445.02 | 150.294 | 35.7 | 2167.32 | 8766.42 | 13495.3 | 0.44 | 1.7 | 19.648 | 19.746 | 1 | 1 | 2210 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3131820.7464 | 229549.8332 | 4756.8417 | 24746.5656 | 204803.2676 | 21362.5968 | 0.084203 | -164956.3097 | 164956.3097
C | Xist Rating 6153 | -29.19 | 1480.53 | 150.294 | 35.7 | 2158.08 | 8737.96 | 13246.1 | 0.44 | 1.66 | 19.686 | 19.072 | 1 | 1 | 2220 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3195102.1824 | 231519.4251 | 4799.9874 | 24858.541 | 206660.8841 | 20668.1878 | 0.084584 | -159594.2677 | 159594.2677
C | Xist Rating 6154 | -28.76 | 1490.32 | 150.294 | 35.7 | 2157.49 | 8760.38 | 13182.5 | 0.43 | 1.65 | 19.687 | 18.912 | 1 | 1 | 2230 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3215350.4968 | 233497.4035 | 4843.3279 | 24970.5164 | 208526.8871 | 20486.2758 | 0.084965 | -158189.5911 | 158189.5911
C | Xist Rating 6155 | -28.33 | 1501.72 | 150.294 | 35.7 | 2154.6 | 8748.85 | 13111.6 | 0.43 | 1.64 | 19.682 | 18.739 | 1 | 1 | 2240 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3235605.912 | 235483.7685 | 4886.8633 | 25082.4918 | 210401.2767 | 20310.1942 | 0.085346 | -156829.9363 | 156829.9363
C | Xist Rating 6156 | -27.86 | 1514.23 | 150.294 | 35.7 | 2151.61 | 8739.38 | 13034 | 0.42 | 1.63 | 19.677 | 18.548 | 1 | 1 | 2250 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3258032.4103 | 237478.52 | 4930.5934 | 25194.4672 | 212284.0528 | 20095.5725 | 0.085727 | -155172.6842 | 155172.6842
C | Xist Rating 6157 | -27.54 | 1520.63 | 150.294 | 35.7 | 2152.49 | 8773.97 | 12995.5 | 0.42 | 1.62 | 19.683 | 18.458 | 1 | 1 | 2260 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3273140.8687 | 239481.658 | 4974.5182 | 25306.4427 | 214175.2154 | 20006.0674 | 0.086108 | -154481.5494 | 154481.5494
C | Xist Rating 6158 | -26.12 | 1558.83 | 150.294 | 35.7 | 2141.51 | 8721.22 | 12751.8 | 0.42 | 1.59 | 19.716 | 17.834 | 1 | 1 | 2270 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3338250.0333 | 241493.1826 | 5018.6379 | 25418.4181 | 216074.7645 | 19363.1603 | 0.086489 | -149517.1909 | 149517.1909
C | Xist Rating 6159 | -25.68 | 1570.18 | 150.294 | 35.7 | 2139.55 | 8724.24 | 12686 | 0.41 | 1.58 | 19.713 | 17.68 | 1 | 1 | 2280 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3359478.619 | 243513.0937 | 5062.9524 | 25530.3935 | 217982.7002 | 19186.6678 | 0.08687 | -148154.363 | 148154.363
C | Xist Rating 6160 | -25.14 | 1583.59 | 150.294 | 35.7 | 2137.27 | 8729.75 | 12606.8 | 0.41 | 1.56 | 19.711 | 17.49 | 1 | 1 | 2290 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3384559.3993 | 245541.3913 | 5107.4617 | 25642.3689 | 219899.0224 | 18992.8918 | 0.087251 | -146658.0761 | 146658.0761
C | Xist Rating 6161 | -24.8 | 1592.61 | 150.294 | 35.7 | 2135.59 | 8729.28 | 12556.9 | 0.4 | 1.56 | 19.708 | 17.377 | 1 | 1 | 2300 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3401161.9899 | 247578.0755 | 5152.1657 | 25754.3443 | 221823.7312 | 18858.7189 | 0.087632 | -145622.0284 | 145622.0284
| Xist Rating 6162 | -24.45 | 1601.89 | 150.294 | 35.7 | 2133.65 | 8724.35 | 12507.5 | 0.4 | 1.55 | 19.705 | 17.268 | 1 | 1 | 2310 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3417872.5985 | 249623.1461 | 5197.0645 | 25866.3197 | 223756.8264 | 18748.9319 | 0.088013 | -144774.2825 | 144774.2825
| Xist Rating 6163 | -22.98 | 1641.09 | 150.294 | 35.7 | 2123.84 | 8691.14 | 12277 | 0.4 | 1.51 | 19.736 | 16.705 | 1 | 1 | 2320 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3485412.5856 | 251676.6034 | 5242.1582 | 25978.2951 | 225698.3083 | 18169.0799 | 0.088394 | -140296.819 | 140296.819
| Xist Rating 6164 | -22.58 | 1652.46 | 150.294 | 35.7 | 2120.64 | 8672.5 | 12216.8 | 0.39 | 1.5 | 19.747 | 16.571 | 1 | 1 | 2330 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3504272.7744 | 253738.4471 | 5287.4466 | 26090.2705 | 227648.1766 | 18013.2953 | 0.088775 | -139093.8911 | 139093.8911
| Xist Rating 6165 | -22.14 | 1663.82 | 150.294 | 35.7 | 2118.55 | 8672.11 | 12157.1 | 0.39 | 1.49 | 19.741 | 16.438 | 1 | 1 | 2340 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3524885.861 | 255808.6774 | 5332.9298 | 26202.2459 | 229606.4315 | 17878.3816 | 0.089156 | -138052.1238 | 138052.1238
| Xist Rating 6166 | -21.78 | 1674.11 | 150.294 | 35.7 | 2116.08 | 8661.61 | 12104.6 | 0.38 | 1.49 | 19.734 | 16.324 | 1 | 1 | 2350 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3542550.6888 | 257887.2942 | 5378.6078 | 26314.2213 | 231573.0729 | 17742.3689 | 0.089537 | -137001.8695 | 137001.8695
| Xist Rating 6167 | -21.33 | 1686.67 | 150.294 | 35.7 | 2112.9 | 8646.77 | 12039.8 | 0.38 | 1.48 | 19.729 | 16.181 | 1 | 1 | 2360 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3563765.043 | 259974.2975 | 5424.4805 | 26426.1968 | 233548.1008 | 17597.024 | 0.089918 | -135879.5547 | 135879.5547
| Xist Rating 6168 | -19.98 | 1722.6 | 150.294 | 35.7 | 2104.91 | 8628.73 | 11846.8 | 0.38 | 1.45 | 19.759 | 15.733 | 1 | 1 | 2370 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3625917.966 | 262069.6874 | 5470.5481 | 26538.1722 | 235531.5152 | 17136.3483 | 0.090299 | -132322.339 | 132322.339
| Xist Rating 6169 | -19.58 | 1734.2 | 150.294 | 35.7 | 2102.08 | 8615.29 | 11791.2 | 0.37 | 1.44 | 19.749 | 15.616 | 1 | 1 | 2380 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 24 | E | Rod | 3645427.136 | 264173.4638 | 5516.8105 | 26650.1476 | 237523.3162 | 16996.7354 | 0.09068 | -131244.2856 | 131244.2856
| Xist Rating 6170 | -19.1 | 1746.31 | 150.294 | 35.7 | 2100.45 | 8625.72 | 11730 | 0.37 | 1.43 | 19.743 | 15.483 | 1 | 1 | 2390 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 3668036.8395 | 266285.6267 | 5563.2676 | 26762.123 | 239523.5037 | 16861.6527 | 0.091061 | -130201.2126 | 130201.2126
C | Xist Rating 6174 | -9.73 | 2005.52 | 150.294 | 35.7 | 2043 | 8458.34 | 10537.8 | 0.39 | 1.25 | 19.769 | 12.948 | 1 | 1 | 2430 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4097277.36 | 274818.1437 | 5751.0441 | 27210.0246 | 247608.1191 | 14286.271 | 0.092585 | -110314.7977 | 110314.7977
C | Xist Rating 6175 | -9.73 | 2006.89 | 150.294 | 35.7 | 2042.18 | 8444.34 | 10537.9 | 0.38 | 1.25 | 19.764 | 12.959 | 1 | 1 | 2440 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4098430.6202 | 276972.2393 | 5798.4752 | 27322 | 249650.2393 | 14279.3208 | 0.092966 | -110261.1304 | 110261.1304
C | Xist Rating 6176 | -9.69 | 2008.22 | 150.294 | 35.7 | 2042.1 | 8442.85 | 10537.9 | 0.38 | 1.25 | 19.759 | 12.97 | 1 | 1 | 2450 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4100986.062 | 279134.7214 | 5846.1011 | 27433.9754 | 251700.746 | 14293.9021 | 0.093347 | -110373.7233 | 110373.7233
C | Xist Rating 6177 | -9.65 | 2009.69 | 150.294 | 35.7 | 2042.25 | 8445.49 | 10537.9 | 0.37 | 1.25 | 19.748 | 12.981 | 1 | 1 | 2460 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4104289.4025 | 281305.5901 | 5893.9217 | 27545.9509 | 253759.6392 | 14286.4545 | 0.093728 | -110316.2144 | 110316.2144
C | Xist Rating 6178 | -9.63 | 2011.04 | 150.294 | 35.7 | 2041.9 | 8439.47 | 10537.9 | 0.37 | 1.25 | 19.784 | 12.991 | 1 | 1 | 2470 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4106342.576 | 283484.8453 | 5941.9372 | 27657.9263 | 255826.919 | 14301.5894 | 0.094109 | -110433.0826 | 110433.0826
C | Xist Rating 6179 | -9.63 | 2012.39 | 150.294 | 35.6 | 2041.23 | 8428.01 | 10537.9 | 0.36 | 1.25 | 19.782 | 13.002 | 1 | 1 | 2480 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4107750.8397 | 285672.487 | 5990.1474 | 27769.9017 | 257902.5853 | 14294.2212 | 0.09449 | -110376.1868 | 110376.1868
C | Xist Rating 6180 | -9.63 | 2013.79 | 150.294 | 35.6 | 2040.6 | 8417.36 | 10537.9 | 0.35 | 1.25 | 19.777 | 13.013 | 1 | 1 | 2490 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4109339.874 | 287868.5152 | 6038.5525 | 27881.8771 | 259986.6381 | 14286.5622 | 0.094871 | -110317.046 | 110317.046
C | Xist Rating 6181 | -9.6 | 2014.77 | 150.294 | 35.6 | 2040.83 | 8421.3 | 10537.9 | 0.35 | 1.25 | 19.773 | 13.021 | 1 | 1 | 2500 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4111803.0591 | 290072.93 | 6087.1523 | 27993.8525 | 262079.0775 | 14297.816 | 0.095252 | -110403.9452 | 110403.9452
C | Xist Rating 6182 | -9.61 | 2016.62 | 150.294 | 35.6 | 2039.28 | 8394.88 | 10537.8 | 0.34 | 1.25 | 19.768 | 13.034 | 1 | 1 | 2510 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4112452.8336 | 292285.7313 | 6135.9469 | 28105.8279 | 264179.9034 | 14291.9807 | 0.095633 | -110358.8869 | 110358.8869
C | Xist Rating 6183 | -9.59 | 2018.08 | 150.294 | 35.6 | 2038.7 | 8385.06 | 10537.8 | 0.34 | 1.25 | 19.805 | 13.045 | 1 | 1 | 2520 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4114259.696 | 294506.9191 | 6184.9363 | 28217.8033 | 266289.1158 | 14307.838 | 0.096014 | -110481.3321 | 110481.3321
C | Xist Rating 6184 | -9.58 | 2019.41 | 150.294 | 35.6 | 2038.17 | 8376.22 | 10537.8 | 0.33 | 1.25 | 19.8 | 13.055 | 1 | 1 | 2530 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4115900.8797 | 296736.4934 | 6234.1205 | 28329.7787 | 268406.7147 | 14298.594 | 0.096395 | -110409.9531 | 110409.9531
C | Xist Rating 6185 | -9.57 | 2020.56 | 150.294 | 35.6 | 2038.06 | 8374.26 | 10537.8 | 0.33 | 1.25 | 19.795 | 13.065 | 1 | 1 | 2540 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4118022.5136 | 298974.4543 | 6283.4995 | 28441.7541 | 270532.7002 | 14311.72 | 0.096776 | -110511.3083 | 110511.3083
C | Xist Rating 6186 | -9.54 | 2022.11 | 150.294 | 35.6 | 2037.67 | 8367.69 | 10537.8 | 0.32 | 1.25 | 19.794 | 13.076 | 1 | 1 | 2550 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4120392.8837 | 301220.8017 | 6333.0732 | 28553.7295 | 272667.0722 | 14303.4088 | 0.097157 | -110447.1311 | 110447.1311
C | Xist Rating 6187 | -9.52 | 2023.56 | 150.294 | 35.6 | 2037.44 | 8363.9 | 10537.7 | 0.32 | 1.25 | 19.783 | 13.086 | 1 | 1 | 2560 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4122882.0864 | 303475.5357 | 6382.8418 | 28665.7049 | 274809.8307 | 14316.2291 | 0.097538 | -110546.126 | 110546.126
C | Xist Rating 6188 | -9.51 | 2024.95 | 150.294 | 35.6 | 2037 | 8356.54 | 10537.7 | 0.31 | 1.25 | 19.779 | 13.097 | 1 | 1 | 2570 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4124823.15 | 305738.6562 | 6432.8051 | 28777.6804 | 276960.9758 | 14307.5575 | 0.097919 | -110479.1662 | 110479.1662
C | Xist Rating 6189 | -9.46 | 2026.31 | 150.295 | 35.6 | 2037.28 | 8361.31 | 10537.7 | 0.31 | 1.25 | 19.832 | 13.107 | 1 | 1 | 2580 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4128160.8368 | 308010.1632 | 6482.9633 | 28889.6558 | 279120.5074 | 14322.591 | 0.0983 | -110595.2508 | 110595.2508
C | Xist Rating 6190 | -9.45 | 2027.67 | 150.295 | 35.6 | 2037.01 | 8356.66 | 10537.7 | 0.3 | 1.25 | 19.831 | 13.117 | 1 | 1 | 2590 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4130384.0667 | 310290.0567 | 6533.3162 | 29001.6312 | 281288.4255 | 14312.6728 | 0.098681 | -110518.6652 | 110518.6652
C | Xist Rating 6191 | -9.43 | 2028.85 | 150.295 | 35.6 | 2036.94 | 8355.53 | 10537.6 | 0.3 | 1.25 | 19.828 | 13.126 | 1 | 1 | 2600 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4132645.719 | 312578.3368 | 6583.8639 | 29113.6066 | 283464.7302 | 14324.5811 | 0.099062 | -110610.6183 | 110610.6183
C | Xist Rating 6192 | -9.42 | 2030.54 | 150.295 | 35.6 | 2035.99 | 8339.69 | 10537.6 | 0.29 | 1.25 | 19.824 | 13.138 | 1 | 1 | 2610 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4134159.1346 | 314875.0034 | 6634.6064 | 29225.582 | 285649.4214 | 14316.3765 | 0.099443 | -110547.2644 | 110547.2644
C | Xist Rating 6193 | -9.41 | 2031.93 | 150.295 | 35.6 | 2035.55 | 8332.18 | 10537.6 | 0.29 | 1.25 | 19.82 | 13.148 | 1 | 1 | 2620 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4136095.1115 | 317180.0565 | 6685.5437 | 29337.5574 | 287842.4991 | 14329.2022 | 0.099824 | -110646.3011 | 110646.3011
C | Xist Rating 6194 | -9.38 | 2033.36 | 150.295 | 35.6 | 2035.31 | 8328.32 | 10537.6 | 0.29 | 1.25 | 19.858 | 13.158 | 1 | 1 | 2630 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4138517.9416 | 319493.4962 | 6736.6758 | 29449.5328 | 290043.9634 | 14343.4627 | 0.10021 | -110756.4173 | 110756.4173
C | Xist Rating 6195 | -9.33 | 2034.61 | 150.295 | 35.6 | 2035.71 | 8334.9 | 10537.6 | 0.28 | 1.25 | 19.863 | 13.168 | 1 | 1 | 2640 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4141875.9231 | 321815.3224 | 6788.0027 | 29561.5082 | 292253.8141 | 14333.0954 | 0.10059 | -110676.3634 | 110676.3634
C | Xist Rating 6196 | -9.29 | 2036.11 | 150.295 | 35.6 | 2035.7 | 8334.72 | 10537.6 | 0.28 | 1.25 | 19.861 | 13.178 | 1 | 1 | 2650 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4144909.127 | 324145.5351 | 6839.5243 | 29673.4836 | 294472.0514 | 14345.9068 | 0.10097 | -110775.29 | 110775.29
C | Xist Rating 6197 | -9.26 | 2037.45 | 150.295 | 35.6 | 2035.78 | 8336.13 | 10537.6 | 0.28 | 1.25 | 19.86 | 13.188 | 1 | 1 | 2660 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4147799.961 | 326484.1343 | 6891.2408 | 29785.459 | 296698.6753 | 14358.7512 | 0.10135 | -110874.4705 | 110874.4705
C | Xist Rating 6198 | -9.21 | 2038.84 | 150.295 | 35.6 | 2036.1 | 8341.46 | 10537.6 | 0.27 | 1.25 | 19.862 | 13.198 | 1 | 1 | 2670 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4151282.124 | 328831.1201 | 6943.152 | 29897.4345 | 298933.6857 | 14347.9246 | 0.10173 | -110790.8705 | 110790.8705
C | Xist Rating 6199 | -9.15 | 2040.26 | 150.295 | 35.6 | 2036.71 | 8351.76 | 10537.7 | 0.27 | 1.25 | 19.902 | 13.208 | 1 | 1 | 2680 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4155417.9446 | 331186.4924 | 6995.258 | 30009.4099 | 301177.0826 | 14362.0108 | 0.10211 | -110899.6405 | 110899.6405
C | Xist Rating 6200 | -9.11 | 2041.63 | 150.295 | 35.6 | 2036.77 | 8352.73 | 10537.6 | 0.26 | 1.25 | 19.898 | 13.218 | 1 | 1 | 2690 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4158330.7351 | 333550.2513 | 7047.5588 | 30121.3853 | 303428.866 | 14350.6816 | 0.10249 | -110812.1591 | 110812.1591
C | Xist Rating 6201 | -9.05 | 2042.83 | 150.295 | 35.6 | 2037.75 | 8369.27 | 10537.5 | 0.26 | 1.25 | 19.897 | 13.227 | 1 | 1 | 2700 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4162776.8325 | 335922.3967 | 7100.0544 | 30233.3607 | 305689.036 | 14362.3156 | 0.10287 | -110901.9939 | 110901.9939
C | Xist Rating 6202 | -9.02 | 2044.49 | 150.295 | 35.6 | 2037.38 | 8363.15 | 10537.5 | 0.26 | 1.25 | 19.896 | 13.238 | 1 | 1 | 2710 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4165403.0362 | 338302.9286 | 7152.7448 | 30345.3361 | 307957.5925 | 14376.0264 | 0.10325 | -111007.8649 | 111007.8649
C | Xist Rating 6203 | -9.01 | 2045.83 | 150.295 | 35.6 | 2036.92 | 8355.34 | 10537.4 | 0.25 | 1.25 | 19.889 | 13.248 | 1 | 1 | 2720 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4167192.0436 | 340691.847 | 7205.63 | 30457.3115 | 310234.5355 | 14364.2589 | 0.10363 | -110916.9999 | 110916.9999
C | Xist Rating 6204 | -9 | 2047.16 | 150.295 | 35.6 | 2036.36 | 8345.89 | 10537.5 | 0.25 | 1.25 | 19.924 | 13.257 | 1 | 1 | 2730 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4168754.7376 | 343089.152 | 7258.71 | 30569.2869 | 312519.865 | 14376.905 | 0.10402 | -111014.6492 | 111014.6492
C | Xist Rating 6205 | -8.99 | 2048.44 | 150.295 | 35.6 | 2035.83 | 8337.07 | 10537.5 | 0.25 | 1.25 | 19.921 | 13.266 | 1 | 1 | 2740 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4170275.6052 | 345494.8435 | 7311.9847 | 30681.2623 | 314813.5811 | 14388.392 | 0.1044 | -111103.3494 | 111103.3494
C | Xist Rating 6206 | -9.02 | 2049.99 | 150.295 | 35.6 | 2034.39 | 8312.95 | 10537.5 | 0.25 | 1.25 | 19.912 | 13.277 | 1 | 1 | 2750 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4170479.1561 | 347908.9215 | 7365.4543 | 30793.2377 | 317115.6837 | 14401.7706 | 0.10478 | -111206.6547 | 111206.6547
C | Xist Rating 6207 | -9.01 | 2051.41 | 150.295 | 35.6 | 2033.77 | 8302.63 | 10537.5 | 0.24 | 1.25 | 19.911 | 13.287 | 1 | 1 | 2760 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4172096.1157 | 350331.386 | 7419.1186 | 30905.2131 | 319426.1729 | 14389.7229 | 0.10516 | -111113.6258 | 111113.6258
C | Xist Rating 6208 | -9.02 | 2052.65 | 150.295 | 35.6 | 2032.96 | 8289.12 | 10537.5 | 0.24 | 1.25 | 19.907 | 13.295 | 1 | 1 | 2770 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4172955.344 | 352762.2371 | 7472.9777 | 31017.1886 | 321745.0486 | 14400.0537 | 0.10554 | -111193.3975 | 111193.3975
C | Xist Rating 6209 | -9.01 | 2054.19 | 150.295 | 35.6 | 2032.17 | 8276.04 | 10537.5 | 0.24 | 1.25 | 19.949 | 13.306 | 1 | 1 | 2780 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4174463.2923 | 355201.4747 | 7527.0316 | 31129.164 | 324072.3108 | 14414.8748 | 0.10592 | -111307.8425 | 111307.8425
C | Xist Rating 6210 | -8.97 | 2055.6 | 150.295 | 35.6 | 2032.15 | 8275.64 | 10537.5 | 0.23 | 1.25 | 19.953 | 13.316 | 1 | 1 | 2790 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4177287.54 | 357649.0989 | 7581.2803 | 31241.1394 | 326407.9595 | 14402.5726 | 0.1063 | -111212.8479 | 111212.8479
C | Xist Rating 6211 | -8.98 | 2056.58 | 150.295 | 35.6 | 2031.71 | 8268.32 | 10537.5 | 0.23 | 1.25 | 19.948 | 13.323 | 1 | 1 | 2800 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4178374.1518 | 360105.1096 | 7635.7238 | 31353.1148 | 328751.9948 | 14411.7548 | 0.10668 | -111283.7507 | 111283.7507
C | Xist Rating 6212 | -8.97 | 2058.32 | 150.295 | 35.6 | 2030.77 | 8252.78 | 10537.5 | 0.23 | 1.25 | 19.952 | 13.334 | 1 | 1 | 2810 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4179974.5064 | 362569.5068 | 7690.3621 | 31465.0902 | 331104.4166 | 14425.3508 | 0.10706 | -111388.735 | 111388.735
C | Xist Rating 6213 | -8.93 | 2059.8 | 150.295 | 35.6 | 2030.83 | 8253.83 | 10537.6 | 0.23 | 1.25 | 19.961 | 13.344 | 1 | 1 | 2820 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4183103.634 | 365042.2905 | 7745.1952 | 31577.0656 | 333465.2249 | 14438.0544 | 0.10744 | -111486.829 | 111486.829
C | Xist Rating 6214 | -8.87 | 2061.17 | 150.295 | 35.6 | 2031.35 | 8262.29 | 10537.6 | 0.22 | 1.25 | 20.012 | 13.354 | 1 | 1 | 2830 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4186957.6795 | 367523.4608 | 7800.223 | 31689.041 | 335834.4198 | 14426.5993 | 0.10783 | -111398.3759 | 111398.3759
C | Xist Rating 6215 | -8.88 | 2062.49 | 150.295 | 35.6 | 2030.43 | 8247.1 | 10537.6 | 0.22 | 1.25 | 20.006 | 13.363 | 1 | 1 | 2840 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4187741.5707 | 370013.0176 | 7855.4457 | 31801.0164 | 338212.0012 | 14437.7512 | 0.10821 | -111484.488 | 111484.488
C | Xist Rating 6216 | -8.8 | 2063.93 | 150.295 | 35.6 | 2031.38 | 8262.86 | 10537.6 | 0.22 | 1.25 | 20.022 | 13.373 | 1 | 1 | 2850 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4192626.1234 | 372510.9609 | 7910.8631 | 31912.9918 | 340597.9691 | 14450.5588 | 0.10859 | -111583.3845 | 111583.3845
C | Xist Rating 6217 | -8.6 | 2065.34 | 150.295 | 35.6 | 2034.97 | 8322.49 | 10537.7 | 0.21 | 1.25 | 20.057 | 13.382 | 1 | 1 | 2860 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4202904.9398 | 375017.2908 | 7966.4753 | 32024.9672 | 342992.3235 | 14437.1541 | 0.10897 | -111479.8769 | 111479.8769
C | Xist Rating 6218 | -8.44 | 2066.53 | 150.295 | 35.6 | 2038.12 | 8375.32 | 10537.8 | 0.21 | 1.25 | 20.082 | 13.391 | 1 | 1 | 2870 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4211836.1236 | 377532.0072 | 8022.2824 | 32136.9427 | 345395.0645 | 14449.064 | 0.10935 | -111571.8418 | 111571.8418
C | Xist Rating 6219 | -8.01 | 2068.03 | 150.295 | 35.6 | 2047.01 | 8527.37 | 10538 | 0.21 | 1.25 | 20.178 | 13.402 | 1 | 1 | 2880 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4233278.0903 | 380055.1101 | 8078.2842 | 32248.9181 | 347806.192 | 14464.9803 | 0.10973 | -111694.744 | 111694.744
C | Xist Rating 6220 | -8.51 | 2069.38 | 150.295 | 35.6 | 2034.98 | 8322.56 | 10537.7 | 0.21 | 1.25 | 20.098 | 13.41 | 1 | 1 | 2890 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4211146.9124 | 382586.5995 | 8134.4807 | 32360.8935 | 350225.7061 | 14473.0114 | 0.11011 | -111756.7577 | 111756.7577
C | Xist Rating 6221 | -7.74 | 2070.76 | 150.295 | 35.6 | 2051.69 | 8609.24 | 10538 | 0.2 | 1.25 | 20.192 | 13.42 | 1 | 1 | 2900 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4248557.5844 | 385126.4755 | 8190.8721 | 32472.8689 | 352653.6066 | 14461.6064 | 0.11049 | -111668.6912 | 111668.6912
C | Xist Rating 6222 | -7.27 | 2072.3 | 150.295 | 35.6 | 2061.43 | 8783.39 | 10538 | 0.2 | 1.25 | 20.242 | 13.431 | 1 | 1 | 2910 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4271901.389 | 387674.738 | 8247.4583 | 32584.8443 | 355089.8937 | 14476.1445 | 0.11087 | -111780.9504 | 111780.9504
C | Xist Rating 6223 | -6.89 | 2073.69 | 150.295 | 35.6 | 2069.27 | 8927.43 | 10538.1 | 0.2 | 1.25 | 20.282 | 13.441 | 1 | 1 | 2920 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4291024.5063 | 390231.3871 | 8304.2393 | 32696.8197 | 357534.5674 | 14489.3912 | 0.11125 | -111883.2385 | 111883.2385
C | Xist Rating 6224 | -6.62 | 2075.08 | 150.295 | 35.6 | 2074.72 | 9029.75 | 10538 | 0.19 | 1.25 | 20.351 | 13.451 | 1 | 1 | 2930 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4305209.9776 | 392796.4227 | 8361.215 | 32808.7951 | 359987.6275 | 14476.6787 | 0.11164 | -111785.0756 | 111785.0756
C | Xist Rating 6225 | -6.35 | 2076.45 | 150.295 | 35.6 | 2080.11 | 9132.9 | 10538 | 0.19 | 1.25 | 20.377 | 13.46 | 1 | 1 | 2940 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4319244.4095 | 395369.8448 | 8418.3855 | 32920.7705 | 362449.0742 | 14488.4094 | 0.11202 | -111875.6572 | 111875.6572
C | Xist Rating 6226 | -6.2 | 2077.86 | 150.295 | 35.6 | 2082.85 | 9185.78 | 10538 | 0.19 | 1.25 | 20.392 | 13.469 | 1 | 1 | 2950 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4327870.701 | 397951.6534 | 8475.7509 | 33032.7459 | 364918.9075 | 14499.8682 | 0.1124 | -111964.1389 | 111964.1389
C | Xist Rating 6227 | -5.63 | 2079.23 | 150.295 | 35.5 | 2095.13 | 9429.77 | 10537.8 | 0.19 | 1.25 | 20.422 | 13.479 | 1 | 1 | 2960 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4356257.1499 | 400541.8486 | 8533.311 | 33144.7213 | 367397.1272 | 14512.7462 | 0.11278 | -112063.5793 | 112063.5793
C | Xist Rating 6228 | -5.62 | 2080.61 | 150.295 | 35.5 | 2094.45 | 9415.94 | 10537.8 | 0.18 | 1.25 | 20.419 | 13.488 | 1 | 1 | 2970 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4357733.6145 | 403140.4303 | 8591.0659 | 33256.6968 | 369883.7335 | 14496.5724 | 0.11316 | -111938.6897 | 111938.6897
C | Xist Rating 6229 | -5.6 | 2081.83 | 150.295 | 35.5 | 2094.14 | 9409.58 | 10537.9 | 0.18 | 1.25 | 20.465 | 13.497 | 1 | 1 | 2980 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4359643.4762 | 405747.3985 | 8649.0156 | 33368.6722 | 372378.7263 | 14508.6724 | 0.11354 | -112032.1227 | 112032.1227
C | Xist Rating 6230 | -5.59 | 2083.39 | 150.295 | 35.5 | 2093.48 | 9396.37 | 10537.9 | 0.18 | 1.25 | 20.46 | 13.506 | 1 | 1 | 2990 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4361535.2972 | 408362.7533 | 8707.16 | 33480.6476 | 374882.1057 | 14519.5495 | 0.11392 | -112116.1126 | 112116.1126
C | Xist Rating 6231 | -5.57 | 2084.82 | 150.295 | 35.5 | 2092.94 | 9385.62 | 10537.8 | 0.18 | 1.25 | 20.443 | 13.516 | 1 | 1 | 3000 | 152.4 | 2 | 4 | 19.05 | 1.3333 | 23 | E | Rod | 4363403.1708 | 410986.4945 | 8765.4993 | 33592.623 | 377393.8716 | 14531.1738 | 0.1143 | -112205.8723 | 112205.8723
C | Xist Rating 6232 | -88.44 | 210.954 | 150.3 | 35.9 | 2369.66 | 7126.05 | 58745.9 | 2.47 | 10.95 | 22.043 | 530.269 | 1 | 1 | 1000 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 499889.2556 | 54458.4482 | 973.9444 | 11477.4795 | 42980.9687 | 553124.0504 | 0.038101 | -4271077.3002 | 4271077.3002
C | Xist Rating 6233 | -88.33 | 213.141 | 150.3 | 35.9 | 2367.53 | 7114.68 | 58284.2 | 2.45 | 10.85 | 22.107 | 520.308 | 1 | 1 | 1010 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 504617.7117 | 55437.1405 | 993.5206 | 11592.2543 | 43844.8862 | 542791.1128 | 0.038482 | -4191289.0946 | 4191289.0946
C | Xist Rating 6234 | -87.46 | 229.707 | 150.3 | 35.9 | 2361.34 | 7118.88 | 54967.6 | 2.46 | 10.07 | 22.161 | 450.903 | 1 | 1 | 1020 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 542416.3274 | 56424.429 | 1013.2917 | 11707.0291 | 44717.3998 | 470754.5892 | 0.038863 | -3635042.1542 | 3635042.1542
C | Xist Rating 6235 | -87.31 | 234.224 | 150.299 | 35.9 | 2344.16 | 6979.82 | 54178.5 | 2.37 | 9.89 | 21.658 | 435.754 | 1 | 1 | 1030 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 549058.5318 | 57420.3136 | 1033.2576 | 11821.8039 | 45598.5097 | 454899.6899 | 0.039244 | -3512614.8245 | 3512614.8245
C | Xist Rating 6236 | -87.23 | 236.485 | 150.299 | 35.9 | 2337.9 | 6931.87 | 53793.6 | 2.33 | 9.8 | 21.537 | 428.503 | 1 | 1 | 1040 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 552878.2815 | 58424.7945 | 1053.4182 | 11936.5787 | 46488.2158 | 447339.0174 | 0.039625 | -3454233.3157 | 3454233.3157
C | Xist Rating 6237 | -87.03 | 240.882 | 150.298 | 35.9 | 2331.52 | 6890.48 | 53042.7 | 2.3 | 9.63 | 21.457 | 414.286 | 1 | 1 | 1050 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 561621.2006 | 59437.8715 | 1073.7737 | 12051.3535 | 47386.518 | 432558.1091 | 0.040006 | -3340099.0596 | 3340099.0596
C | Xist Rating 6238 | -86.89 | 243.123 | 150.298 | 35.9 | 2336.89 | 6944.82 | 52676.7 | 2.25 | 9.54 | 21.439 | 407.56 | 1 | 1 | 1060 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 568151.7075 | 60459.5447 | 1094.3239 | 12166.1283 | 48293.4164 | 425542.3903 | 0.040387 | -3285925.5389 | 3285925.5389
C | Xist Rating 6239 | -86.03 | 260.937 | 150.298 | 35.9 | 2319.71 | 6852.81 | 49857.3 | 2.24 | 8.9 | 21.249 | 356.598 | 1 | 1 | 1070 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 605298.1683 | 61489.8142 | 1115.0689 | 12280.9031 | 49208.9111 | 372609.3608 | 0.040768 | -2877190.7164 | 2877190.7164
C | Xist Rating 6240 | -85.81 | 264.303 | 150.298 | 35.9 | 2327.33 | 6930.37 | 49380.5 | 2.18 | 8.79 | 21.155 | 348.599 | 1 | 1 | 1080 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 615120.301 | 62528.6798 | 1136.0087 | 12395.6779 | 50133.0019 | 364252.1066 | 0.041149 | -2812658.2142 | 2812658.2142
C | Xist Rating 6241 | -85.56 | 268.779 | 150.298 | 35.9 | 2329.9 | 6967.52 | 48761.3 | 2.12 | 8.65 | 21.002 | 338.319 | 1 | 1 | 1090 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 626228.1921 | 63576.1416 | 1157.1433 | 12510.4527 | 51065.6889 | 353519.1506 | 0.04153 | -2729781.1731 | 2729781.1731
C | Xist Rating 6242 | -85.33 | 272.113 | 150.298 | 35.9 | 2338.24 | 7053.65 | 48308.1 | 2.08 | 8.55 | 21.003 | 330.901 | 1 | 1 | 1100 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 636265.5011 | 64632.1996 | 1178.4727 | 12625.2275 | 52006.9721 | 345794.2078 | 0.041911 | -2670131.2125 | 2670131.2125
C | Xist Rating 6243 | -85.22 | 274.541 | 150.297 | 35.8 | 2335.92 | 7039.92 | 48011 | 2 | 8.49 | 20.693 | 326.351 | 1 | 1 | 1110 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 641305.8127 | 65696.8538 | 1199.9969 | 12740.0023 | 52956.8515 | 340974.1729 | 0.042292 | -2632912.1808 | 2632912.1808
C | Xist Rating 6244 | -84.19 | 294.367 | 150.297 | 35.8 | 2331.75 | 7069.05 | 45447.6 | 2.04 | 7.92 | 20.959 | 285.548 | 1 | 1 | 1120 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 686390.2523 | 66770.1042 | 1221.7158 | 12854.7771 | 53915.3271 | 298687.6701 | 0.042673 | -2306387.0148 | 2306387.0148
C | Xist Rating 6245 | -84.06 | 296.749 | 150.297 | 35.8 | 2332.42 | 7082.5 | 45189.3 | 1.98 | 7.86 | 20.766 | 281.885 | 1 | 1 | 1130 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 692143.3026 | 67851.9508 | 1243.6296 | 12969.5519 | 54882.3989 | 294819.7629 | 0.043054 | -2276520.0611 | 2276520.0611
C | Xist Rating 6246 | -83.85 | 301.296 | 150.297 | 35.8 | 2329.53 | 7070.33 | 44681.5 | 1.92 | 7.75 | 20.584 | 274.517 | 1 | 1 | 1140 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 701878.0709 | 68942.3936 | 1265.7381 | 13084.3267 | 55858.0669 | 287105.0119 | 0.043435 | -2216948.7985 | 2216948.7985
C | Xist Rating 6247 | -83.61 | 305.781 | 150.296 | 35.8 | 2330.07 | 7089.81 | 44186.2 | 1.89 | 7.64 | 20.394 | 267.389 | 1 | 1 | 1150 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 712491.1347 | 70041.4326 | 1288.0414 | 13199.1014 | 56842.3311 | 279669.9673 | 0.043816 | -2159537.3549 | 2159537.3549
C | Xist Rating 6248 | -83.4 | 310.344 | 150.296 | 35.8 | 2326.72 | 7073.24 | 43703.4 | 1.83 | 7.53 | 20.236 | 260.608 | 1 | 1 | 1160 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 722083.5917 | 71149.0677 | 1310.5395 | 13313.8762 | 57835.1915 | 272566.5276 | 0.044197 | -2104686.4766 | 2104686.4766
C | Xist Rating 6249 | -82.47 | 328.144 | 150.296 | 35.8 | 2323.44 | 7101.9 | 41832.4 | 1.85 | 7.13 | 20.383 | 234.419 | 1 | 1 | 1170 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 762422.8954 | 72265.2991 | 1333.2324 | 13428.651 | 58836.6481 | 245421.3798 | 0.044578 | -1895078.8404 | 1895078.8404
C | Xist Rating 6250 | -82.33 | 329.428 | 150.296 | 35.8 | 2334.19 | 7206.96 | 41724.7 | 1.8 | 7.11 | 20.307 | 233.151 | 1 | 1 | 1180 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 768947.5433 | 73390.1267 | 1356.1201 | 13543.4258 | 59846.7008 | 244060.3247 | 0.044959 | -1884569.1342 | 1884569.1342
C | Xist Rating 6251 | -81.93 | 338.382 | 150.295 | 35.8 | 2325.42 | 7152.85 | 40885.5 | 1.75 | 6.92 | 20.139 | 222.214 | 1 | 1 | 1190 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 786880.2704 | 74523.5504 | 1379.2026 | 13658.2006 | 60865.3498 | 232648.8096 | 0.04534 | -1796452.4394 | 1796452.4394
C | Xist Rating 6252 | -81.72 | 340.657 | 150.296 | 35.8 | 2337 | 7270.93 | 40682.1 | 1.72 | 6.88 | 20.18 | 219.659 | 1 | 1 | 1200 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 796115.409 | 75665.5704 | 1402.4799 | 13772.9754 | 61892.5949 | 229982.539 | 0.045721 | -1775864.2045 | 1775864.2045
C | Xist Rating 6253 | -81.49 | 345.289 | 150.295 | 35.8 | 2336.17 | 7277.77 | 40281.4 | 1.67 | 6.8 | 20.036 | 214.694 | 1 | 1 | 1210 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 806653.8031 | 76816.1865 | 1425.9519 | 13887.7502 | 62928.4363 | 224774.1837 | 0.046102 | -1735646.6657 | 1735646.6657
C | Xist Rating 6254 | -80.53 | 365.468 | 150.295 | 35.8 | 2322.83 | 7216.53 | 38537.6 | 1.67 | 6.43 | 20.043 | 193.056 | 1 | 1 | 1220 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 848920.0344 | 77975.3988 | 1449.6188 | 14002.525 | 63972.8738 | 202318.7926 | 0.046483 | -1562252.0877 | 1562252.0877
C | Xist Rating 6255 | -80.24 | 369.951 | 150.295 | 35.8 | 2328.95 | 7290.67 | 38183.2 | 1.64 | 6.35 | 20.053 | 188.91 | 1 | 1 | 1230 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 861597.3814 | 79143.2074 | 1473.4804 | 14117.2998 | 65025.9076 | 197995.9343 | 0.046864 | -1528872.1215 | 1528872.1215
C | Xist Rating 6256 | -80 | 374.573 | 150.295 | 35.8 | 2330.01 | 7315.81 | 37835.7 | 1.6 | 6.28 | 19.957 | 184.971 | 1 | 1 | 1240 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 872758.8357 | 80319.6121 | 1497.5369 | 14232.0746 | 66087.5375 | 193866.9091 | 0.047245 | -1496988.8834 | 1496988.8834
C | Xist Rating 6257 | -79.84 | 376.992 | 150.295 | 35.8 | 2334.37 | 7366.46 | 37664.5 | 1.56 | 6.24 | 19.891 | 183.119 | 1 | 1 | 1250 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 880038.815 | 81504.613 | 1521.7881 | 14346.8494 | 67157.7636 | 191907.4258 | 0.047626 | -1481858.2733 | 1481858.2733
C | Xist Rating 6258 | -79.49 | 383.738 | 150.295 | 35.8 | 2333.95 | 7384.77 | 37161.6 | 1.53 | 6.14 | 19.848 | 177.429 | 1 | 1 | 1260 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 895625.3051 | 82698.2101 | 1546.2341 | 14461.6242 | 68236.5859 | 185974.8604 | 0.048007 | -1436048.5755 | 1436048.5755
C | Xist Rating 6259 | -78.54 | 402.85 | 150.295 | 35.8 | 2326.74 | 7377.66 | 35777.7 | 1.54 | 5.85 | 19.913 | 162.035 | 1 | 1 | 1270 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 937327.209 | 83900.4034 | 1570.8749 | 14576.399 | 69324.0044 | 170018.8252 | 0.048388 | -1312840.3011 | 1312840.3011
C | Xist Rating 6260 | -78.32 | 407.54 | 150.295 | 35.8 | 2324.36 | 7368.52 | 35477.4 | 1.5 | 5.79 | 19.806 | 158.955 | 1 | 1 | 1280 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 947269.6744 | 85111.1929 | 1595.7105 | 14691.1738 | 70420.0191 | 166779.0865 | 0.048769 | -1287823.8973 | 1287823.8973
C | Xist Rating 6261 | -78.09 | 412.179 | 150.294 | 35.8 | 2323.33 | 7372.91 | 35182.7 | 1.46 | 5.73 | 19.765 | 155.947 | 1 | 1 | 1290 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 957627.8361 | 86330.5786 | 1620.7408 | 14805.9486 | 71524.63 | 163619.3285 | 0.04915 | -1263425.084 | 1263425.084
C | Xist Rating 6262 | -77.73 | 418.904 | 150.294 | 35.8 | 2325.05 | 7412.55 | 34751.2 | 1.44 | 5.64 | 19.803 | 151.501 | 1 | 1 | 1300 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 973972.7452 | 87558.5605 | 1645.966 | 14920.7234 | 72637.8371 | 158995.2532 | 0.049531 | -1227719.2006 | 1227719.2006
C | Xist Rating 6263 | -77.5 | 422.462 | 150.294 | 35.8 | 2330.05 | 7474.91 | 34540.1 | 1.41 | 5.59 | 19.752 | 149.437 | 1 | 1 | 1310 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 984357.5831 | 88795.1386 | 1671.3859 | 15035.4982 | 73759.6404 | 156825.4671 | 0.049912 | -1210964.6874 | 1210964.6874
C | Xist Rating 6264 | -76.54 | 441.671 | 150.294 | 35.8 | 2324.56 | 7483.91 | 33363.1 | 1.41 | 5.35 | 19.805 | 137.617 | 1 | 1 | 1320 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1026690.7398 | 90040.3128 | 1697.0007 | 15150.273 | 74890.0399 | 144567.3213 | 0.050293 | -1116310.5345 | 1116310.5345
C | Xist Rating 6265 | -76.21 | 448.613 | 150.294 | 35.8 | 2321.69 | 7476.54 | 32979.9 | 1.37 | 5.28 | 19.706 | 134.021 | 1 | 1 | 1330 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1041540.316 | 91294.0833 | 1722.8102 | 15265.0478 | 76029.0355 | 140790.084 | 0.050674 | -1087143.7097 | 1087143.7097
C | Xist Rating 6266 | -75.84 | 455.454 | 150.294 | 35.8 | 2323.61 | 7518.98 | 32606.7 | 1.34 | 5.2 | 19.621 | 130.543 | 1 | 1 | 1340 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1058297.4689 | 92556.45 | 1748.8145 | 15379.8226 | 77176.6274 | 137147.9373 | 0.051055 | -1059020.018 | 1059020.018
C | Xist Rating 6267 | -75.6 | 459.029 | 150.294 | 35.8 | 2329.12 | 7588.44 | 32423.8 | 1.31 | 5.16 | 19.587 | 128.914 | 1 | 1 | 1350 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1069133.6245 | 93827.4128 | 1775.0136 | 15494.5974 | 78332.8155 | 135429.6935 | 0.051436 | -1045752.1951 | 1045752.1951
C | Xist Rating 6268 | -75.34 | 461.25 | 150.294 | 35.8 | 2343.94 | 7755.99 | 32303.3 | 1.3 | 5.14 | 19.664 | 127.812 | 1 | 1 | 1360 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1081142.325 | 95106.9719 | 1801.4075 | 15609.3721 | 79497.5997 | 134290.9315 | 0.051817 | -1036958.9768 | 1036958.9768
C | Xist Rating 6269 | -74.17 | 488.515 | 150.294 | 35.8 | 2318.33 | 7573.95 | 30902.5 | 1.29 | 4.86 | 19.592 | 115.162 | 1 | 1 | 1370 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1132538.9799 | 96395.1271 | 1827.9962 | 15724.1469 | 80670.9802 | 121147.6058 | 0.052198 | -935469.6994 | 935469.6994
C | Xist Rating 6270 | -74.05 | 490.998 | 150.294 | 35.8 | 2318.3 | 7581.22 | 30794.1 | 1.27 | 4.84 | 19.552 | 114.298 | 1 | 1 | 1380 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1138280.6634 | 97691.8785 | 1854.7797 | 15838.9217 | 81852.9568 | 120234.2912 | 0.052579 | -928417.3259 | 928417.3259
C | Xist Rating 6271 | -73.75 | 496.816 | 150.294 | 35.7 | 2319.26 | 7610.37 | 30526.9 | 1.24 | 4.78 | 19.516 | 112.062 | 1 | 1 | 1390 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1152245.4762 | 98997.2262 | 1881.7579 | 15953.6965 | 83043.5296 | 117884.0114 | 0.05296 | -910269.0886 | 910269.0886
C | Xist Rating 6272 | -73.43 | 502.631 | 150.294 | 35.7 | 2320.71 | 7644.93 | 30264.9 | 1.21 | 4.73 | 19.486 | 109.894 | 1 | 1 | 1400 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1166460.788 | 100311.17 | 1908.931 | 16068.4713 | 84242.6987 | 115604.3749 | 0.053341 | -892666.3392 | 892666.3392
C | Xist Rating 6273 | -73.07 | 509.533 | 150.294 | 35.7 | 2321.39 | 7675.36 | 29957.2 | 1.19 | 4.67 | 19.464 | 107.359 | 1 | 1 | 1410 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1182824.8109 | 101633.71 | 1936.2988 | 16183.2461 | 85450.4639 | 112956.0641 | 0.053722 | -872216.7857 | 872216.7857
C | Xist Rating 6274 | -72.06 | 529.955 | 150.294 | 35.7 | 2316.86 | 7696.22 | 29051.8 | 1.2 | 4.49 | 19.536 | 99.895 | 1 | 1 | 1420 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1227831.5413 | 102964.8462 | 1963.8614 | 16298.0209 | 86666.8253 | 105232.9828 | 0.054103 | -812581.1986 | 812581.1986
C | Xist Rating 6275 | -71.89 | 533.77 | 150.294 | 35.7 | 2315.32 | 7690.72 | 28910.6 | 1.16 | 4.47 | 19.452 | 98.872 | 1 | 1 | 1430 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1235848.3564 | 104304.5786 | 1991.6188 | 16412.7957 | 87891.7829 | 104124.7717 | 0.054484 | -804023.8863 | 804023.8863
C | Xist Rating 6276 | -71.43 | 542.893 | 150.294 | 35.7 | 2314.42 | 7711.15 | 28541.9 | 1.15 | 4.39 | 19.437 | 96.007 | 1 | 1 | 1440 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1256482.4171 | 105652.9072 | 2019.571 | 16527.5705 | 89125.3367 | 101145.9188 | 0.054865 | -781021.9744 | 781021.9744
C | Xist Rating 6277 | -71.12 | 548.746 | 150.294 | 35.7 | 2315.19 | 7738.94 | 28316.7 | 1.12 | 4.35 | 19.414 | 94.316 | 1 | 1 | 1450 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1270451.2517 | 107009.832 | 2047.718 | 16642.3453 | 90367.4867 | 99360.2635 | 0.055246 | -767233.6173 | 767233.6173
C | Xist Rating 6278 | -70.85 | 552.203 | 150.294 | 35.7 | 2323.21 | 7841.04 | 28183.7 | 1.11 | 4.32 | 19.443 | 93.325 | 1 | 1 | 1460 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1282883.5316 | 108375.353 | 2076.0598 | 16757.1201 | 91618.2329 | 98330.2594 | 0.055627 | -759280.199 | 759280.199
C | Xist Rating 6279 | -69.85 | 575.275 | 150.294 | 35.7 | 2307.05 | 7737.26 | 27310.2 | 1.1 | 4.16 | 19.418 | 86.775 | 1 | 1 | 1470 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1327188.1887 | 109749.4702 | 2104.5964 | 16871.8949 | 92877.5753 | 91523.1453 | 0.056008 | -706717.4677 | 706717.4677
C | Xist Rating 6280 | -69.5 | 582.22 | 150.294 | 35.7 | 2306.8 | 7757.35 | 27066 | 1.09 | 4.11 | 19.402 | 85.037 | 1 | 1 | 1480 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1343065.096 | 111132.1835 | 2133.3277 | 16986.6697 | 94145.5139 | 89713.7705 | 0.056389 | -692745.9553 | 692745.9553
C | Xist Rating 6281 | -69.17 | 588.075 | 150.293 | 35.7 | 2309.53 | 7807.43 | 26866.5 | 1.07 | 4.07 | 19.391 | 83.645 | 1 | 1 | 1490 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1358176.8548 | 112523.4931 | 2162.2539 | 17101.4445 | 95422.0486 | 88250.9575 | 0.05677 | -681450.5011 | 681450.5011
C | Xist Rating 6282 | -68.87 | 594.022 | 150.293 | 35.7 | 2309.46 | 7825.93 | 26670.3 | 1.05 | 4.03 | 19.366 | 82.303 | 1 | 1 | 1500 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1371870.0481 | 113923.3989 | 2191.3748 | 17216.2193 | 96707.1796 | 86838.7522 | 0.057151 | -670545.826 | 670545.826
C | Xist Rating 6283 | -68.45 | 600.994 | 150.293 | 35.7 | 2313.99 | 7901.69 | 26438.9 | 1.03 | 3.99 | 19.368 | 80.711 | 1 | 1 | 1510 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1390694.1061 | 115331.9008 | 2220.6906 | 17330.9941 | 98000.9067 | 85168.5011 | 0.057532 | -657648.5897 | 657648.5897
C | Xist Rating 6284 | -67.31 | 623.749 | 150.294 | 35.7 | 2311.63 | 7954.62 | 25681 | 1.03 | 3.84 | 19.447 | 75.458 | 1 | 1 | 1520 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1441876.9009 | 116748.999 | 2250.2011 | 17445.7689 | 99303.2301 | 79727.755 | 0.057913 | -615636.5906 | 615636.5906
C | Xist Rating 6285 | -67 | 631.065 | 150.294 | 35.7 | 2306.9 | 7922.24 | 25468.6 | 1.01 | 3.8 | 19.377 | 74.113 | 1 | 1 | 1530 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1455803.8485 | 118174.6933 | 2279.9064 | 17560.5437 | 100614.1496 | 78308.4303 | 0.058294 | -604676.9414 | 604676.9414
C | Xist Rating 6286 | -66.75 | 634.796 | 150.293 | 35.7 | 2312.05 | 7995.27 | 25363.7 | 0.98 | 3.78 | 19.366 | 73.473 | 1 | 1 | 1540 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1467680.0918 | 119608.9838 | 2309.8065 | 17675.3185 | 101933.6654 | 77611.6919 | 0.058675 | -599296.9121 | 599296.9121
C | Xist Rating 6287 | -66.18 | 646.265 | 150.293 | 35.7 | 2310.56 | 8017.19 | 25021.1 | 0.97 | 3.72 | 19.359 | 71.255 | 1 | 1 | 1550 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1493234.0584 | 121051.8706 | 2339.9013 | 17790.0933 | 103261.7773 | 75302.8826 | 0.059056 | -581468.8988 | 581468.8988
C | Xist Rating 6288 | -65.85 | 649.772 | 150.294 | 35.7 | 2320.9 | 8155.47 | 24920.5 | 0.96 | 3.7 | 19.398 | 70.631 | 1 | 1 | 1560 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1508055.8348 | 122503.3535 | 2370.191 | 17904.8681 | 104598.4854 | 74652.3578 | 0.059437 | -576445.7191 | 576445.7191
C | Xist Rating 6289 | -64.8 | 676.482 | 150.293 | 35.7 | 2300.04 | 7995.15 | 24161.2 | 0.95 | 3.56 | 19.32 | 65.845 | 1 | 1 | 1570 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1555935.6593 | 123963.4326 | 2400.6755 | 18019.6428 | 105943.7898 | 69671.5856 | 0.059818 | -537985.5165 | 537985.5165
C | Xist Rating 6290 | -64.46 | 682.458 | 150.293 | 35.7 | 2302.96 | 8050.44 | 24006.5 | 0.94 | 3.53 | 19.313 | 64.936 | 1 | 1 | 1580 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1571673.4757 | 125432.1079 | 2431.3547 | 18134.4176 | 107297.6903 | 68721.6687 | 0.0602 | -530650.5095 | 530650.5095
C | Xist Rating 6291 | -64.13 | 688.469 | 150.293 | 35.7 | 2305.15 | 8097.28 | 23854 | 0.92 | 3.5 | 19.302 | 64.05 | 1 | 1 | 1590 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1587024.3154 | 126909.3794 | 2462.2288 | 18249.1924 | 108660.187 | 67781.4462 | 0.060581 | -523390.3605 | 523390.3605
C | Xist Rating 6292 | -63.63 | 696.558 | 150.293 | 35.7 | 2310.01 | 8186.11 | 23644.6 | 0.91 | 3.46 | 19.324 | 62.81 | 1 | 1 | 1600 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1609055.9456 | 128395.2471 | 2493.2976 | 18363.9672 | 110031.2799 | 66489.2606 | 0.060962 | -513412.4458 | 513412.4458
C | Xist Rating 6293 | -63.42 | 700.485 | 150.293 | 35.7 | 2311.47 | 8216.78 | 23555.9 | 0.89 | 3.45 | 19.297 | 62.338 | 1 | 1 | 1610 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1619150.0629 | 129889.711 | 2524.5612 | 18478.742 | 111410.969 | 65977.3461 | 0.061343 | -509459.5779 | 509459.5779
C | Xist Rating 6294 | -62.1 | 730.365 | 150.293 | 35.7 | 2297.72 | 8151.17 | 22804.4 | 0.89 | 3.31 | 19.326 | 57.929 | 1 | 1 | 1620 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1678174.2678 | 131392.7711 | 2556.0196 | 18593.5168 | 112799.2543 | 61408.1791 | 0.061724 | -474177.6817 | 474177.6817
C | Xist Rating 6295 | -61.76 | 733.947 | 150.293 | 35.7 | 2307.38 | 8286.57 | 22722.7 | 0.88 | 3.29 | 19.349 | 57.491 | 1 | 1 | 1630 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1693494.6289 | 132904.4274 | 2587.6728 | 18708.2916 | 114196.1358 | 60948.3852 | 0.062105 | -470627.2745 | 470627.2745
C | Xist Rating 6296 | -61.45 | 740.105 | 150.293 | 35.7 | 2307.99 | 8315.26 | 22588 | 0.86 | 3.27 | 19.327 | 56.777 | 1 | 1 | 1640 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1708154.9389 | 134424.6798 | 2619.5208 | 18823.0664 | 115601.6134 | 60184.6909 | 0.062486 | -464730.2302 | 464730.2302
C | Xist Rating 6297 | -61.07 | 748.551 | 150.293 | 35.7 | 2305.25 | 8308.72 | 22402.4 | 0.84 | 3.23 | 19.3 | 55.783 | 1 | 1 | 1650 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1725597.1928 | 135953.5285 | 2651.5635 | 18937.8412 | 117015.6873 | 59129.6077 | 0.062867 | -456583.1573 | 456583.1573
C | Xist Rating 6298 | -60.63 | 756.754 | 150.293 | 35.7 | 2306.95 | 8360.22 | 22220.3 | 0.83 | 3.2 | 19.303 | 54.8 | 1 | 1 | 1660 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1745793.6403 | 137490.9734 | 2683.8011 | 19052.616 | 118438.3574 | 58101.8551 | 0.063248 | -448647.124 | 448647.124
C | Xist Rating 6299 | -59.46 | 783.509 | 150.293 | 35.7 | 2294.93 | 8300.31 | 21632.5 | 0.83 | 3.1 | 19.329 | 51.622 | 1 | 1 | 1670 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1798098.3094 | 139037.0144 | 2716.2334 | 19167.3908 | 119869.6236 | 54810.3041 | 0.063629 | -423230.6399 | 423230.6399
C | Xist Rating 6300 | -59.18 | 787.202 | 150.293 | 35.7 | 2300.76 | 8389.62 | 21560 | 0.82 | 3.08 | 19.336 | 51.267 | 1 | 1 | 1680 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1811162.8735 | 140591.6517 | 2748.8606 | 19282.1656 | 121309.4861 | 54434.7049 | 0.06401 | -420330.3623 | 420330.3623
C | Xist Rating 6301 | -58.72 | 797.986 | 150.293 | 35.7 | 2295.98 | 8363.75 | 21345.7 | 0.8 | 3.04 | 19.307 | 50.183 | 1 | 1 | 1690 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1832159.8963 | 142154.8851 | 2781.6825 | 19396.9404 | 122757.9447 | 53285.0269 | 0.064391 | -411452.8531 | 411452.8531
C | Xist Rating 6302 | -58.31 | 805.114 | 150.293 | 35.7 | 2298.99 | 8428.94 | 21205.6 | 0.79 | 3.02 | 19.31 | 49.483 | 1 | 1 | 1700 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1850949.0349 | 143726.7147 | 2814.6992 | 19511.7152 | 124214.9996 | 52550.4697 | 0.064772 | -405780.7975 | 405780.7975
C | Xist Rating 6303 | -57.9 | 813.51 | 150.293 | 35.7 | 2298.49 | 8451.82 | 21044.5 | 0.78 | 2.99 | 19.299 | 48.688 | 1 | 1 | 1710 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1869844.5999 | 145307.1406 | 2847.9107 | 19626.49 | 125680.6506 | 51716.2426 | 0.065153 | -399339.117 | 399339.117
C | Xist Rating 6304 | -56.82 | 838.131 | 150.293 | 35.7 | 2288.86 | 8411.86 | 20567 | 0.78 | 2.9 | 19.328 | 46.291 | 1 | 1 | 1720 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1918364.5207 | 146896.1626 | 2881.317 | 19741.2648 | 127154.8978 | 49235.4534 | 0.065534 | -380183.1204 | 380183.1204
C | Xist Rating 6305 | -56.31 | 848.784 | 150.293 | 35.7 | 2287.38 | 8429.46 | 20374.2 | 0.77 | 2.87 | 19.319 | 45.37 | 1 | 1 | 1730 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1941491.5459 | 148493.7808 | 2914.9181 | 19856.0396 | 128637.7412 | 48270.2285 | 0.065915 | -372729.9091 | 372729.9091
C | Xist Rating 6306 | -56.01 | 853.716 | 150.293 | 35.7 | 2290.53 | 8489.23 | 20289.8 | 0.76 | 2.85 | 19.32 | 44.988 | 1 | 1 | 1740 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1955462.1095 | 150099.9952 | 2948.714 | 19970.8144 | 130129.1809 | 47865.1815 | 0.066296 | -369602.2435 | 369602.2435
C | Xist Rating 6307 | -55.55 | 863.41 | 150.294 | 35.7 | 2289.19 | 8504.63 | 20123.5 | 0.74 | 2.82 | 19.304 | 44.219 | 1 | 1 | 1750 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1976509.5379 | 151714.8058 | 2982.7046 | 20085.5892 | 131629.2167 | 47041.9187 | 0.066677 | -363245.2265 | 363245.2265
C | Xist Rating 6308 | -55.16 | 870.656 | 150.294 | 35.7 | 2290.05 | 8541.97 | 20001.1 | 0.73 | 2.8 | 19.309 | 43.66 | 1 | 1 | 1760 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 1993845.7728 | 153338.2126 | 3016.8901 | 20200.364 | 133137.8487 | 46452.86 | 0.067058 | -358696.6716 | 358696.6716
C | Xist Rating 6309 | -53.94 | 899.836 | 150.294 | 35.7 | 2277.05 | 8468.95 | 19497.7 | 0.73 | 2.71 | 19.342 | 41.3 | 1 | 1 | 1770 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2048971.5638 | 154970.2156 | 3051.2703 | 20315.1388 | 134655.0769 | 44010.2333 | 0.067439 | -339835.3558 | 339835.3558
C | Xist Rating 6310 | -53.59 | 907.191 | 150.294 | 35.6 | 2277.21 | 8496.35 | 19382.9 | 0.72 | 2.69 | 19.325 | 40.805 | 1 | 1 | 1780 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2065864.4171 | 156610.8148 | 3085.8453 | 20429.9135 | 136180.9012 | 43486.0965 | 0.06782 | -335788.1103 | 335788.1103
C | Xist Rating 6311 | -53.37 | 911.143 | 150.294 | 35.6 | 2279.18 | 8536.45 | 19326.3 | 0.71 | 2.68 | 19.316 | 40.579 | 1 | 1 | 1790 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2076658.9027 | 158260.0102 | 3120.6151 | 20544.6883 | 137715.3218 | 43241.6144 | 0.068201 | -333900.2845 | 333900.2845
C | Xist Rating 6312 | -52.8 | 924.172 | 150.294 | 35.6 | 2275.73 | 8534.41 | 19121.6 | 0.7 | 2.65 | 19.308 | 39.679 | 1 | 1 | 1800 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2103165.9456 | 159917.8017 | 3155.5797 | 20659.4631 | 139258.3386 | 42297.0764 | 0.068582 | -326606.8125 | 326606.8125
C | Xist Rating 6313 | -52.67 | 931.399 | 150.294 | 35.6 | 2264.43 | 8401.82 | 19013 | 0.69 | 2.63 | 19.538 | 39.205 | 1 | 1 | 1810 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2109087.8376 | 161584.1895 | 3190.7391 | 20774.2379 | 140809.9516 | 41808.0972 | 0.068963 | -322831.0442 | 322831.0442
C | Xist Rating 6314 | -51.18 | 960.838 | 150.294 | 35.6 | 2265.23 | 8518.15 | 18562.5 | 0.69 | 2.55 | 19.339 | 37.251 | 1 | 1 | 1820 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2176519.0627 | 163259.1735 | 3226.0933 | 20889.0127 | 142370.1607 | 39773.7123 | 0.069344 | -307122.0635 | 307122.0635
C | Xist Rating 6315 | -51.41 | 956.161 | 150.294 | 35.6 | 2268.17 | 8543.15 | 18631.3 | 0.69 | 2.56 | 19.592 | 37.549 | 1 | 1 | 1830 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2168735.6954 | 164942.7536 | 3261.6423 | 21003.7875 | 143938.9661 | 40103.486 | 0.069725 | -309668.4887 | 309668.4887
C | Xist Rating 6316 | -50.95 | 962.098 | 150.294 | 35.6 | 2275.94 | 8675.89 | 18545.1 | 0.68 | 2.55 | 19.615 | 37.195 | 1 | 1 | 1840 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2189677.3221 | 166634.93 | 3297.386 | 21118.5623 | 145516.3676 | 39727.0482 | 0.070106 | -306761.7354 | 306761.7354
C | Xist Rating 6317 | -50.52 | 971.909 | 150.294 | 35.6 | 2272.82 | 8665.03 | 18409.3 | 0.67 | 2.52 | 19.604 | 36.643 | 1 | 1 | 1850 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2208974.2134 | 168335.7025 | 3333.3246 | 21233.3371 | 147102.3654 | 39142.8988 | 0.070487 | -302251.089 | 302251.089
C | Xist Rating 6318 | -50.06 | 982.905 | 150.294 | 35.6 | 2269.01 | 8648.21 | 18258.9 | 0.66 | 2.5 | 19.59 | 36.037 | 1 | 1 | 1860 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2230221.2741 | 170045.0712 | 3369.4579 | 21348.1119 | 148696.9593 | 38502.3414 | 0.070868 | -297304.8742 | 297304.8742
C | Xist Rating 6319 | -48.83 | 1009.94 | 150.294 | 35.6 | 2262.89 | 8659.04 | 17879.6 | 0.66 | 2.43 | 19.639 | 34.465 | 1 | 1 | 1870 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2285383.1266 | 171763.0362 | 3405.7861 | 21462.8867 | 150300.1495 | 36878.3282 | 0.071249 | -284764.6751 | 284764.6751
C | Xist Rating 6320 | -48.35 | 1020.92 | 150.294 | 35.6 | 2260.34 | 8659.93 | 17738.8 | 0.65 | 2.41 | 19.63 | 33.919 | 1 | 1 | 1880 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2307626.3128 | 173489.5973 | 3442.309 | 21577.6615 | 151911.9358 | 36300.0753 | 0.07163 | -280299.5594 | 280299.5594
C | Xist Rating 6321 | -47.91 | 1028.2 | 150.294 | 35.6 | 2263.62 | 8734.1 | 17646.5 | 0.64 | 2.39 | 19.647 | 33.567 | 1 | 1 | 1890 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2327454.084 | 175224.7546 | 3479.0267 | 21692.4363 | 153532.3183 | 35924.5347 | 0.072011 | -277399.7347 | 277399.7347
C | Xist Rating 6322 | -47.61 | 1035.93 | 150.294 | 35.6 | 2260.4 | 8712.11 | 17555 | 0.62 | 2.38 | 19.631 | 33.233 | 1 | 1 | 1900 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2341616.172 | 176968.5081 | 3515.9392 | 21807.2111 | 155161.297 | 35549.0022 | 0.072392 | -274499.9723 | 274499.9723
C | Xist Rating 6323 | -47.22 | 1043.38 | 150.294 | 35.6 | 2261.34 | 8751.8 | 17464.8 | 0.61 | 2.36 | 19.632 | 32.898 | 1 | 1 | 1910 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2359436.9292 | 178720.8578 | 3553.0464 | 21921.9859 | 156798.8719 | 35189.8061 | 0.072773 | -271726.355 | 271726.355
C | Xist Rating 6324 | -45.78 | 1076.21 | 150.294 | 35.6 | 2252.22 | 8737.36 | 17050.3 | 0.62 | 2.29 | 19.685 | 31.281 | 1 | 1 | 1920 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2423861.6862 | 180481.8037 | 3590.3485 | 22036.7607 | 158445.043 | 33535.6461 | 0.073154 | -258953.3702 | 258953.3702
C | Xist Rating 6325 | -45.35 | 1087.27 | 150.294 | 35.6 | 2247.74 | 8708.35 | 16923.9 | 0.61 | 2.27 | 19.679 | 30.823 | 1 | 1 | 1930 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2443900.2698 | 182251.3458 | 3627.8454 | 22151.5355 | 160099.8103 | 33048.1381 | 0.073535 | -255188.9627 | 255188.9627
C | Xist Rating 6326 | -45 | 1090.86 | 150.294 | 35.6 | 2254.66 | 8826.23 | 16882.1 | 0.6 | 2.26 | 19.709 | 30.677 | 1 | 1 | 1940 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2459518.4076 | 184029.4841 | 3665.537 | 22266.3103 | 161763.1738 | 32886.3507 | 0.073916 | -253939.6826 | 253939.6826
C | Xist Rating 6327 | -44.67 | 1101.24 | 150.294 | 35.6 | 2247.49 | 8751.54 | 16772.1 | 0.59 | 2.24 | 19.681 | 30.298 | 1 | 1 | 1950 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2475025.8876 | 185816.2186 | 3703.4235 | 22381.0851 | 163435.1335 | 32479.3892 | 0.074297 | -250797.2342 | 250797.2342
C | Xist Rating 6328 | -44.11 | 1113.37 | 150.294 | 35.7 | 2245.86 | 8769.34 | 16637.2 | 0.58 | 2.22 | 19.71 | 29.814 | 1 | 1 | 1960 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2500473.1482 | 187611.5492 | 3741.5047 | 22495.8599 | 165115.6894 | 31966.1477 | 0.074678 | -246834.119 | 246834.119
C | Xist Rating 6329 | -42.83 | 1142.93 | 150.295 | 35.7 | 2238.45 | 8764.97 | 16303.3 | 0.58 | 2.16 | 19.776 | 28.595 | 1 | 1 | 1970 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2558391.6585 | 189415.4761 | 3779.7807 | 22610.6347 | 166804.8414 | 30708.7227 | 0.075059 | -237124.6164 | 237124.6164
C | Xist Rating 6330 | -42.42 | 1151.56 | 150.295 | 35.7 | 2238.2 | 8790.91 | 16214.2 | 0.57 | 2.15 | 19.8 | 28.294 | 1 | 1 | 1980 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2577421.592 | 191227.9992 | 3818.2515 | 22725.4095 | 168502.5897 | 30384.9384 | 0.07544 | -234624.4405 | 234624.4405
C | Xist Rating 6331 | -41.97 | 1162.81 | 150.295 | 35.7 | 2234.46 | 8771.66 | 16101.4 | 0.56 | 2.13 | 19.799 | 27.916 | 1 | 1 | 1990 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2598252.4326 | 193049.1184 | 3856.9171 | 22840.1842 | 170208.9342 | 29979.7332 | 0.075821 | -231495.553 | 231495.553
C | Xist Rating 6332 | -41.58 | 1171.55 | 150.295 | 35.7 | 2233.12 | 8780.66 | 16015 | 0.55 | 2.12 | 19.802 | 27.63 | 1 | 1 | 2000 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2616211.736 | 194878.8339 | 3895.7775 | 22954.959 | 171923.8748 | 29670.0908 | 0.076202 | -229104.5765 | 229104.5765
C | Xist Rating 6333 | -41.27 | 1177.96 | 150.295 | 35.7 | 2233.38 | 8805.93 | 15953.8 | 0.55 | 2.11 | 19.805 | 27.434 | 1 | 1 | 2010 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2630832.3048 | 196717.1455 | 3934.8326 | 23069.7338 | 173647.4117 | 29471.5757 | 0.076583 | -227571.6953 | 227571.6953
C | Xist Rating 6334 | -39.89 | 1211.24 | 150.295 | 35.7 | 2223.66 | 8775.72 | 15614.8 | 0.55 | 2.05 | 19.842 | 26.268 | 1 | 1 | 2020 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 25 | E | Rod | 2693385.9384 | 198564.0533 | 3974.0826 | 23184.5086 | 175379.5447 | 28267.4118 | 0.076964 | -218273.4608 | 218273.4608
C | Xist Rating 6335 | -39.33 | 1223.31 | 150.295 | 35.7 | 2222.92 | 8806.43 | 15499.7 | 0.54 | 2.03 | 19.84 | 25.893 | 1 | 1 | 2030 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 2719320.2652 | 200419.5574 | 4013.5273 | 23299.2834 | 177120.2739 | 27864.7133 | 0.077345 | -215163.93 | 215163.93
C | Xist Rating 6336 | -39.02 | 1231.24 | 150.295 | 35.7 | 2220.5 | 8793.75 | 15431.6 | 0.53 | 2.02 | 19.836 | 25.688 | 1 | 1 | 2040 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 2733968.42 | 202283.6576 | 4053.1669 | 23414.0582 | 178869.5994 | 27638.2875 | 0.077726 | -213415.5296 | 213415.5296
C | Xist Rating 6337 | -38.56 | 1238.36 | 150.295 | 35.7 | 2224.92 | 8889.32 | 15364.1 | 0.53 | 2.01 | 19.858 | 25.472 | 1 | 1 | 2050 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 2755251.9312 | 204156.354 | 4093.0012 | 23528.833 | 180627.521 | 27419.7557 | 0.078107 | -211728.0853 | 211728.0853
C | Xist Rating 6338 | -38.21 | 1250.01 | 150.295 | 35.7 | 2216.92 | 8800.65 | 15264.3 | 0.51 | 1.99 | 19.85 | 25.168 | 1 | 1 | 2060 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 2771172.1692 | 206037.6466 | 4133.0303 | 23643.6078 | 182394.0388 | 27071.7198 | 0.078488 | -209040.6447 | 209040.6447
C | Xist Rating 6339 | -36.75 | 1285.72 | 150.295 | 35.7 | 2206.94 | 8770.97 | 14936.3 | 0.51 | 1.94 | 19.888 | 24.104 | 1 | 1 | 2070 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 2837506.8968 | 207927.5354 | 4173.2542 | 23758.3826 | 184169.1528 | 25973.0936 | 0.078869 | -200557.3437 | 200557.3437
C | Xist Rating 6340 | -36.38 | 1293.46 | 150.295 | 35.7 | 2207.26 | 8801.13 | 14873.5 | 0.51 | 1.93 | 19.884 | 23.922 | 1 | 1 | 2080 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 2855002.5196 | 209826.0204 | 4213.6729 | 23873.1574 | 185952.863 | 25788.4432 | 0.07925 | -199131.5223 | 199131.5223
C | Xist Rating 6341 | -35.94 | 1303.47 | 150.295 | 35.7 | 2205.8 | 8811.42 | 14790.9 | 0.5 | 1.91 | 19.881 | 23.677 | 1 | 1 | 2090 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 2875194.126 | 211733.1016 | 4254.2864 | 23987.9322 | 187745.1694 | 25519.7881 | 0.079631 | -197057.039 | 197057.039
C | Xist Rating 6342 | -35.5 | 1313.49 | 150.295 | 35.7 | 2204.33 | 8821.47 | 14709.3 | 0.49 | 1.9 | 19.878 | 23.436 | 1 | 1 | 2100 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 2895365.4117 | 213648.779 | 4295.0947 | 24102.707 | 189546.072 | 25255.113 | 0.080012 | -195013.2885 | 195013.2885
C | Xist Rating 6343 | -35.11 | 1322.33 | 150.295 | 35.7 | 2203.41 | 8836.04 | 14638.8 | 0.49 | 1.89 | 19.878 | 23.231 | 1 | 1 | 2110 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 2913635.1453 | 215573.0526 | 4336.0977 | 24217.4818 | 191355.5708 | 25046.5869 | 0.080393 | -193403.1048 | 193403.1048
C | Xist Rating 6344 | -33.77 | 1356.04 | 150.295 | 35.7 | 2193.86 | 8801.46 | 14359.1 | 0.49 | 1.84 | 19.911 | 22.376 | 1 | 1 | 2120 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 2974961.9144 | 217505.9223 | 4377.2956 | 24332.2566 | 193173.6657 | 24164.5734 | 0.080774 | -186592.4302 | 186592.4302
C | Xist Rating 6345 | -33.26 | 1368.45 | 150.295 | 35.7 | 2191.34 | 8802.34 | 14263.8 | 0.48 | 1.83 | 19.908 | 22.103 | 1 | 1 | 2130 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 2998739.223 | 219447.3883 | 4418.6882 | 24447.0314 | 195000.3569 | 23866.2888 | 0.081155 | -184289.1555 | 184289.1555
C | Xist Rating 6346 | -32.83 | 1380.89 | 150.295 | 35.7 | 2186.19 | 8760.59 | 14169.9 | 0.48 | 1.81 | 19.901 | 21.836 | 1 | 1 | 2140 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3018887.9091 | 221397.4505 | 4460.2756 | 24561.8062 | 196835.6443 | 23592.9707 | 0.081536 | -182178.6663 | 182178.6663
C | Xist Rating 6347 | -32.53 | 1387.45 | 150.295 | 35.7 | 2186.15 | 8780.47 | 14123.5 | 0.47 | 1.8 | 19.903 | 21.713 | 1 | 1 | 2150 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3033173.8175 | 223356.1088 | 4502.0578 | 24676.581 | 198679.5278 | 23450.4287 | 0.081917 | -181077.9944 | 181077.9944
C | Xist Rating 6348 | -32.14 | 1396.23 | 150.295 | 35.7 | 2185.75 | 8802.91 | 14059 | 0.46 | 1.79 | 19.906 | 21.535 | 1 | 1 | 2160 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3051809.7225 | 225323.3634 | 4544.0348 | 24791.3558 | 200532.0076 | 23250.6323 | 0.082298 | -179535.2199 | 179535.2199
C | Xist Rating 6349 | -30.76 | 1432.6 | 150.295 | 35.7 | 2174.01 | 8737.63 | 13785.9 | 0.46 | 1.75 | 19.939 | 20.747 | 1 | 1 | 2170 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3114486.726 | 227299.2141 | 4586.2066 | 24906.1306 | 202393.0835 | 22437.8766 | 0.082679 | -173259.3357 | 173259.3357
C | Xist Rating 6350 | -30.24 | 1444.79 | 150.295 | 35.7 | 2172.78 | 8758.22 | 13699 | 0.46 | 1.74 | 19.947 | 20.508 | 1 | 1 | 2180 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3139210.8162 | 229283.661 | 4628.5732 | 25020.9054 | 204262.7557 | 22194.1464 | 0.08306 | -171377.3155 | 171377.3155
C | Xist Rating 6351 | -29.86 | 1453.81 | 150.295 | 35.7 | 2171.45 | 8764.88 | 13638.9 | 0.45 | 1.73 | 19.945 | 20.352 | 1 | 1 | 2190 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3156875.7245 | 231276.7042 | 4671.1346 | 25135.6802 | 206141.024 | 22016.5841 | 0.083441 | -170006.2262 | 170006.2262
C | Xist Rating 6352 | -29.54 | 1463.23 | 150.295 | 35.7 | 2168.22 | 8740.71 | 13579.3 | 0.44 | 1.72 | 19.935 | 20.203 | 1 | 1 | 2200 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3172604.5506 | 233278.3435 | 4713.8907 | 25250.4549 | 208027.8885 | 21845.7684 | 0.083822 | -168687.233 | 168687.233
C | Xist Rating 6353 | -29.03 | 1475.67 | 150.295 | 35.7 | 2166.13 | 8746.99 | 13495.2 | 0.44 | 1.7 | 19.936 | 19.979 | 1 | 1 | 2210 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3196493.0571 | 235288.579 | 4756.8417 | 25365.2297 | 209923.3493 | 21617.1201 | 0.084203 | -166921.6714 | 166921.6714
C | Xist Rating 6354 | -27.61 | 1511.91 | 150.295 | 35.7 | 2156.86 | 8717.95 | 13246 | 0.44 | 1.66 | 19.973 | 19.295 | 1 | 1 | 2220 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3260978.2026 | 237307.4107 | 4799.9874 | 25480.0045 | 211827.4062 | 20912.3392 | 0.084584 | -161479.5398 | 161479.5398
C | Xist Rating 6355 | -27.18 | 1521.89 | 150.295 | 35.7 | 2156.28 | 8740.43 | 13182.4 | 0.44 | 1.65 | 19.975 | 19.133 | 1 | 1 | 2230 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3281620.9692 | 239334.8386 | 4843.3279 | 25594.7793 | 213740.0593 | 20748.1296 | 0.084965 | -160211.5573 | 160211.5573
C | Xist Rating 6356 | -26.74 | 1533.51 | 150.295 | 35.7 | 2153.41 | 8729.31 | 13111.6 | 0.43 | 1.64 | 19.969 | 18.957 | 1 | 1 | 2240 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3302275.7691 | 241370.8627 | 4886.8633 | 25709.5541 | 215661.3086 | 20548.9782 | 0.085346 | -158673.7624 | 158673.7624
C | Xist Rating 6357 | -26.26 | 1546.26 | 150.295 | 35.7 | 2150.41 | 8719.64 | 13033.9 | 0.42 | 1.63 | 19.965 | 18.763 | 1 | 1 | 2250 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3325092.9666 | 243415.483 | 4930.5934 | 25824.3289 | 217591.1541 | 20331.0491 | 0.085727 | -156990.9723 | 156990.9723
C | Xist Rating 6358 | -25.95 | 1552.78 | 150.295 | 35.7 | 2151.08 | 8750.73 | 12995.5 | 0.42 | 1.62 | 19.97 | 18.672 | 1 | 1 | 2260 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3340154.0024 | 245468.6995 | 4974.5182 | 25939.1037 | 219529.5958 | 20240.5172 | 0.086108 | -156291.9087 | 156291.9087
C | Xist Rating 6359 | -24.49 | 1591.76 | 150.295 | 35.7 | 2140.37 | 8702.29 | 12751.8 | 0.42 | 1.59 | 20.003 | 18.038 | 1 | 1 | 2270 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3406955.3512 | 247530.5122 | 5018.6379 | 26053.8785 | 221476.6336 | 19587.2791 | 0.086489 | -151247.7773 | 151247.7773
C | Xist Rating 6360 | -24.04 | 1603.32 | 150.295 | 35.7 | 2138.19 | 8701.61 | 12686.1 | 0.41 | 1.58 | 19.999 | 17.881 | 1 | 1 | 2280 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3428202.7908 | 249600.921 | 5062.9524 | 26168.6533 | 223432.2677 | 19407.39 | 0.08687 | -149858.7211 | 149858.7211
C | Xist Rating 6361 | -23.48 | 1617 | 150.295 | 35.7 | 2136.31 | 8713.69 | 12606.8 | 0.41 | 1.56 | 19.999 | 17.688 | 1 | 1 | 2290 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3454413.27 | 251679.9261 | 5107.4617 | 26283.4281 | 225396.498 | 19210.6352 | 0.087251 | -148339.433 | 148339.433
C | Xist Rating 6362 | -23.18 | 1626.18 | 150.295 | 35.7 | 2132.9 | 8684.51 | 12557 | 0.4 | 1.56 | 20.009 | 17.574 | 1 | 1 | 2300 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3468479.322 | 253767.5273 | 5152.1657 | 26398.2029 | 227369.3245 | 19075.7159 | 0.087632 | -147297.6219 | 147297.6219
| Xist Rating 6363 | -22.83 | 1635.63 | 150.295 | 35.7 | 2130.87 | 8678.15 | 12507.6 | 0.4 | 1.55 | 19.999 | 17.463 | 1 | 1 | 2310 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3485314.8981 | 255863.7248 | 5197.0645 | 26512.9777 | 229350.7471 | 18963.616 | 0.088013 | -146432.0161 | 146432.0161
| Xist Rating 6364 | -21.33 | 1675.63 | 150.295 | 35.7 | 2120.82 | 8640.82 | 12277.1 | 0.4 | 1.51 | 20.04 | 16.892 | 1 | 1 | 2320 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3553709.6166 | 257968.5184 | 5242.1582 | 26627.7525 | 231340.766 | 18375.9247 | 0.088394 | -141894.0195 | 141894.0195
| Xist Rating 6365 | -20.84 | 1687.22 | 150.295 | 35.7 | 2120.04 | 8662.46 | 12216.8 | 0.39 | 1.5 | 20.037 | 16.755 | 1 | 1 | 2330 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3576973.8888 | 260081.9083 | 5287.4466 | 26742.5273 | 233339.381 | 18216.1913 | 0.088775 | -140660.6005 | 140660.6005
| Xist Rating 6366 | -20.42 | 1698.79 | 150.295 | 35.7 | 2117.49 | 8654.51 | 12157.1 | 0.39 | 1.49 | 20.03 | 16.621 | 1 | 1 | 2340 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3597170.8371 | 262203.8943 | 5332.9298 | 26857.3021 | 235346.5922 | 18080.2489 | 0.089156 | -139610.8898 | 139610.8898
| Xist Rating 6367 | -20.04 | 1709.27 | 150.295 | 35.7 | 2115.28 | 8648.28 | 12104.7 | 0.38 | 1.49 | 20.023 | 16.505 | 1 | 1 | 2350 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3615584.6456 | 264334.4765 | 5378.6078 | 26972.0769 | 237362.3997 | 17941.9053 | 0.089537 | -138542.6369 | 138542.6369
| Xist Rating 6368 | -19.58 | 1722.08 | 150.295 | 35.7 | 2112.2 | 8634.94 | 12039.8 | 0.38 | 1.48 | 20.017 | 16.359 | 1 | 1 | 2360 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3637377.376 | 266473.655 | 5424.4805 | 27086.8517 | 239386.8033 | 17793.4539 | 0.089918 | -137396.3348 | 137396.3348
| Xist Rating 6369 | -18.2 | 1758.74 | 150.295 | 35.7 | 2104.35 | 8619.32 | 11846.8 | 0.38 | 1.45 | 20.046 | 15.905 | 1 | 1 | 2370 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3701004.519 | 268621.4296 | 5470.5481 | 27201.6265 | 241419.8031 | 17326.5559 | 0.090299 | -133791.0721 | 133791.0721
| Xist Rating 6370 | -17.79 | 1770.55 | 150.295 | 35.7 | 2101.21 | 8600.66 | 11791.2 | 0.37 | 1.44 | 20.038 | 15.786 | 1 | 1 | 2380 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3720297.3655 | 270777.8004 | 5516.8105 | 27316.4013 | 243461.3991 | 17184.6877 | 0.09068 | -132695.6035 | 132695.6035
| Xist Rating 6371 | -17.31 | 1782.9 | 150.295 | 35.7 | 2099.57 | 8610.85 | 11730 | 0.37 | 1.43 | 20.036 | 15.651 | 1 | 1 | 2390 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 3743323.353 | 272942.7674 | 5563.2676 | 27431.1761 | 245511.5913 | 17047.7345 | 0.091061 | -131638.0869 | 131638.0869
C | Xist Rating 6374 | -7.67 | 2046.05 | 150.295 | 35.7 | 2043.18 | 8460.84 | 10538.7 | 0.39 | 1.25 | 20.081 | 13.069 | 1 | 1 | 2420 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4180448.439 | 279489.2456 | 5703.8078 | 27775.5004 | 251713.7451 | 14421.6727 | 0.092204 | -111360.3336 | 111360.3336
C | Xist Rating 6375 | -7.73 | 2047.41 | 150.295 | 35.7 | 2041.97 | 8440.65 | 10537.9 | 0.39 | 1.25 | 20.066 | 13.078 | 1 | 1 | 2430 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4180749.7977 | 281688.5973 | 5751.0441 | 27890.2752 | 253798.3221 | 14433.8924 | 0.092585 | -111454.6914 | 111454.6914
C | Xist Rating 6376 | -7.7 | 2048.78 | 150.295 | 35.7 | 2041.8 | 8437.79 | 10537.9 | 0.38 | 1.25 | 20.059 | 13.089 | 1 | 1 | 2440 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4183199.004 | 283896.5453 | 5798.4752 | 28005.05 | 255891.4953 | 14426.5862 | 0.092966 | -111398.2749 | 111398.2749
C | Xist Rating 6377 | -7.69 | 2050.11 | 150.295 | 35.7 | 2041.36 | 8430.25 | 10537.9 | 0.38 | 1.25 | 20.057 | 13.1 | 1 | 1 | 2450 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4185012.5496 | 286113.0895 | 5846.1011 | 28119.8248 | 257993.2647 | 14441.343 | 0.093347 | -111512.2225 | 111512.2225
C | Xist Rating 6378 | -7.66 | 2051.58 | 150.295 | 35.7 | 2041.36 | 8430.32 | 10537.9 | 0.37 | 1.25 | 20.048 | 13.111 | 1 | 1 | 2460 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4188013.3488 | 288338.2298 | 5893.9217 | 28234.5996 | 260103.6302 | 14433.6991 | 0.093728 | -111453.1983 | 111453.1983
C | Xist Rating 6379 | -7.64 | 2052.93 | 150.295 | 35.7 | 2040.99 | 8423.98 | 10537.9 | 0.36 | 1.25 | 20.083 | 13.122 | 1 | 1 | 2470 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4190009.6007 | 290571.9664 | 5941.9372 | 28349.3744 | 262222.592 | 14427.646 | 0.094109 | -111406.4584 | 111406.4584
C | Xist Rating 6380 | -7.63 | 2054.28 | 150.295 | 35.7 | 2040.46 | 8414.9 | 10537.9 | 0.36 | 1.25 | 20.077 | 13.132 | 1 | 1 | 2480 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4191676.1688 | 292814.2991 | 5990.1474 | 28464.1492 | 264350.1499 | 14441.0317 | 0.09449 | -111509.8188 | 111509.8188
C | Xist Rating 6381 | -7.62 | 2055.68 | 150.295 | 35.6 | 2039.82 | 8404.01 | 10537.9 | 0.35 | 1.25 | 20.071 | 13.143 | 1 | 1 | 2490 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4193217.1776 | 295065.2281 | 6038.5525 | 28578.924 | 266486.3041 | 14433.052 | 0.094871 | -111448.2015 | 111448.2015
C | Xist Rating 6382 | -7.6 | 2056.66 | 150.295 | 35.6 | 2040.04 | 8407.86 | 10537.9 | 0.35 | 1.25 | 20.068 | 13.152 | 1 | 1 | 2500 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4195668.6664 | 297324.7532 | 6087.1523 | 28693.6988 | 268631.0544 | 14445.4296 | 0.095252 | -111543.7787 | 111543.7787
C | Xist Rating 6383 | -7.61 | 2058.51 | 150.295 | 35.6 | 2038.49 | 8381.52 | 10537.9 | 0.34 | 1.25 | 20.062 | 13.164 | 1 | 1 | 2510 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4196252.0499 | 299592.8745 | 6135.9469 | 28808.4736 | 270784.4009 | 14438.232 | 0.095633 | -111488.2005 | 111488.2005
C | Xist Rating 6384 | -7.6 | 2059.97 | 150.295 | 35.6 | 2037.86 | 8370.89 | 10537.9 | 0.34 | 1.25 | 20.099 | 13.175 | 1 | 1 | 2520 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4197930.4642 | 301869.5921 | 6184.9363 | 28923.2484 | 272946.3437 | 14454.134 | 0.096014 | -111610.9917 | 111610.9917
C | Xist Rating 6385 | -7.59 | 2061.31 | 150.295 | 35.6 | 2037.39 | 8363.01 | 10537.8 | 0.33 | 1.25 | 20.094 | 13.186 | 1 | 1 | 2530 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4199692.3809 | 304154.9058 | 6234.1205 | 29038.0232 | 275116.8826 | 14445.64 | 0.096395 | -111545.4031 | 111545.4031
C | Xist Rating 6386 | -7.57 | 2062.46 | 150.295 | 35.6 | 2037.28 | 8361.08 | 10537.8 | 0.33 | 1.25 | 20.09 | 13.195 | 1 | 1 | 2540 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4201808.5088 | 306448.8157 | 6283.4995 | 29152.798 | 277296.0177 | 14457.8086 | 0.096776 | -111639.3653 | 111639.3653
C | Xist Rating 6387 | -7.57 | 2064 | 150.295 | 35.6 | 2036.36 | 8345.76 | 10537.8 | 0.32 | 1.25 | 20.085 | 13.206 | 1 | 1 | 2550 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4203047.04 | 308751.3218 | 6333.0732 | 29267.5728 | 279483.749 | 14449.0574 | 0.097157 | -111571.7916 | 111571.7916
C | Xist Rating 6388 | -7.52 | 2065.45 | 150.295 | 35.6 | 2036.65 | 8350.59 | 10537.7 | 0.32 | 1.25 | 20.077 | 13.217 | 1 | 1 | 2560 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4206598.7425 | 311062.4241 | 6382.8418 | 29382.3476 | 281680.0765 | 14463.0681 | 0.097538 | -111679.9784 | 111679.9784
C | Xist Rating 6389 | -7.51 | 2066.84 | 150.295 | 35.6 | 2036.27 | 8344.21 | 10537.7 | 0.31 | 1.25 | 20.073 | 13.227 | 1 | 1 | 2570 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4208644.2868 | 313382.1226 | 6432.8051 | 29497.1224 | 283885.0002 | 14453.0615 | 0.097919 | -111602.71 | 111602.71
C | Xist Rating 6390 | -7.48 | 2068.21 | 150.295 | 35.6 | 2036.35 | 8345.6 | 10537.7 | 0.31 | 1.25 | 20.125 | 13.237 | 1 | 1 | 2580 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4211599.4335 | 315710.4173 | 6482.9633 | 29611.8972 | 286098.5201 | 14468.1 | 0.0983 | -111718.8333 | 111718.8333
C | Xist Rating 6391 | -7.46 | 2069.57 | 150.296 | 35.6 | 2036.04 | 8340.43 | 10537.7 | 0.3 | 1.25 | 20.123 | 13.247 | 1 | 1 | 2590 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4213727.3028 | 318047.3081 | 6533.3162 | 29726.672 | 288320.6362 | 14457.8476 | 0.098681 | -111639.6665 | 111639.6665
C | Xist Rating 6392 | -7.42 | 2070.74 | 150.296 | 35.6 | 2036.36 | 8345.85 | 10537.7 | 0.3 | 1.25 | 20.124 | 13.257 | 1 | 1 | 2600 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4216772.1064 | 320392.7952 | 6583.8639 | 29841.4468 | 290551.3484 | 14470.9735 | 0.099062 | -111741.0217 | 111741.0217
C | Xist Rating 6393 | -7.43 | 2072.43 | 150.296 | 35.6 | 2035.23 | 8326.95 | 10537.6 | 0.29 | 1.25 | 20.117 | 13.268 | 1 | 1 | 2610 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4217871.7089 | 322746.8785 | 6634.6064 | 29956.2215 | 292790.6569 | 14461.3221 | 0.099443 | -111666.4962 | 111666.4962
C | Xist Rating 6394 | -7.4 | 2073.83 | 150.296 | 35.6 | 2034.97 | 8322.52 | 10537.6 | 0.29 | 1.25 | 20.116 | 13.278 | 1 | 1 | 2620 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4220181.8351 | 325109.5579 | 6685.5437 | 30070.9963 | 295038.5616 | 14474.2881 | 0.099824 | -111766.6159 | 111766.6159
C | Xist Rating 6395 | -7.38 | 2075.25 | 150.296 | 35.6 | 2034.74 | 8318.65 | 10537.6 | 0.29 | 1.25 | 20.154 | 13.288 | 1 | 1 | 2630 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4222594.185 | 327480.8336 | 6736.6758 | 30185.7711 | 297295.0624 | 14488.5871 | 0.10021 | -111877.0292 | 111877.0292
C | Xist Rating 6396 | -7.33 | 2076.5 | 150.296 | 35.6 | 2035 | 8323.04 | 10537.6 | 0.28 | 1.25 | 20.156 | 13.298 | 1 | 1 | 2640 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4225677.5 | 329860.7054 | 6788.0027 | 30300.5459 | 299560.1595 | 14477.8086 | 0.10059 | -111793.8001 | 111793.8001
C | Xist Rating 6397 | -7.3 | 2078 | 150.296 | 35.6 | 2034.87 | 8320.9 | 10537.6 | 0.28 | 1.25 | 20.155 | 13.309 | 1 | 1 | 2650 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4228459.86 | 332249.1735 | 6839.5243 | 30415.3207 | 301833.8527 | 14491.7285 | 0.10097 | -111901.2865 | 111901.2865
C | Xist Rating 6398 | -7.26 | 2079.34 | 150.296 | 35.6 | 2034.96 | 8322.43 | 10537.6 | 0.28 | 1.25 | 20.153 | 13.318 | 1 | 1 | 2660 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4231373.7264 | 334646.2377 | 6891.2408 | 30530.0955 | 304116.1422 | 14503.5379 | 0.10135 | -111992.4752 | 111992.4752
C | Xist Rating 6399 | -7.21 | 2080.73 | 150.296 | 35.6 | 2035.27 | 8327.62 | 10537.6 | 0.27 | 1.25 | 20.156 | 13.328 | 1 | 1 | 2670 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4234847.3471 | 337051.8981 | 6943.152 | 30644.8703 | 306407.0278 | 14492.4297 | 0.10173 | -111906.7009 | 111906.7009
C | Xist Rating 6400 | -7.16 | 2082.15 | 150.296 | 35.6 | 2035.77 | 8335.97 | 10537.7 | 0.27 | 1.25 | 20.196 | 13.338 | 1 | 1 | 2680 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4238778.5055 | 339466.1547 | 6995.258 | 30759.6451 | 308706.5096 | 14506.5515 | 0.10211 | -112015.7456 | 112015.7456
C | Xist Rating 6401 | -7.1 | 2083.52 | 150.296 | 35.6 | 2036.44 | 8347.15 | 10537.7 | 0.26 | 1.25 | 20.197 | 13.348 | 1 | 1 | 2690 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4242963.4688 | 341889.0076 | 7047.5588 | 30874.4199 | 311014.5876 | 14495.0601 | 0.10249 | -111927.012 | 111927.012
C | Xist Rating 6402 | -7.03 | 2084.72 | 150.296 | 35.6 | 2037.55 | 8365.87 | 10537.5 | 0.26 | 1.25 | 20.195 | 13.357 | 1 | 1 | 2700 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4247721.236 | 344320.4566 | 7100.0544 | 30989.1947 | 313331.2619 | 14506.6975 | 0.10287 | -112016.8729 | 112016.8729
C | Xist Rating 6403 | -7 | 2086.38 | 150.296 | 35.6 | 2037.22 | 8360.49 | 10537.5 | 0.26 | 1.25 | 20.189 | 13.368 | 1 | 1 | 2710 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4250415.0636 | 346760.5018 | 7152.7448 | 31103.9695 | 315656.5323 | 14520.2851 | 0.10325 | -112121.7927 | 112121.7927
C | Xist Rating 6404 | -6.99 | 2087.72 | 150.296 | 35.6 | 2036.8 | 8353.33 | 10537.5 | 0.25 | 1.25 | 20.186 | 13.378 | 1 | 1 | 2720 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4252268.096 | 349209.1432 | 7205.63 | 31218.7443 | 317990.3989 | 14508.3165 | 0.10363 | -112029.3744 | 112029.3744
C | Xist Rating 6405 | -6.99 | 2089.05 | 150.296 | 35.6 | 2035.92 | 8338.55 | 10537.5 | 0.25 | 1.25 | 20.219 | 13.387 | 1 | 1 | 2730 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4253138.676 | 351666.3808 | 7258.71 | 31333.5191 | 320332.8617 | 14520.9346 | 0.10402 | -112126.8082 | 112126.8082
C | Xist Rating 6406 | -6.99 | 2090.33 | 150.296 | 35.6 | 2035.33 | 8328.56 | 10537.5 | 0.25 | 1.25 | 20.216 | 13.397 | 1 | 1 | 2740 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4254511.3589 | 354132.2145 | 7311.9847 | 31448.2939 | 322683.9207 | 14533.4933 | 0.1044 | -112223.7827 | 112223.7827
C | Xist Rating 6407 | -7.01 | 2091.88 | 150.296 | 35.6 | 2033.9 | 8304.79 | 10537.5 | 0.25 | 1.25 | 20.208 | 13.407 | 1 | 1 | 2750 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4254674.732 | 356606.6445 | 7365.4543 | 31563.0687 | 325043.5758 | 14545.8972 | 0.10478 | -112319.5622 | 112319.5622
C | Xist Rating 6408 | -7.01 | 2093.3 | 150.296 | 35.6 | 2033.23 | 8293.52 | 10537.5 | 0.24 | 1.25 | 20.206 | 13.417 | 1 | 1 | 2760 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4256160.359 | 359089.6707 | 7419.1186 | 31677.8435 | 327411.8272 | 14533.4868 | 0.10516 | -112223.7324 | 112223.7324
C | Xist Rating 6409 | -6.98 | 2094.54 | 150.296 | 35.6 | 2033.16 | 8292.33 | 10537.5 | 0.24 | 1.25 | 20.213 | 13.426 | 1 | 1 | 2770 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4258534.9464 | 361581.2931 | 7472.9777 | 31792.6183 | 329788.6748 | 14545.2156 | 0.10554 | -112314.2993 | 112314.2993
C | Xist Rating 6410 | -7.01 | 2096.09 | 150.296 | 35.6 | 2031.69 | 8267.96 | 10537.5 | 0.24 | 1.25 | 20.246 | 13.436 | 1 | 1 | 2780 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4258605.0921 | 364081.5116 | 7527.0316 | 31907.3931 | 332174.1185 | 14558.762 | 0.10592 | -112418.9011 | 112418.9011
C | Xist Rating 6411 | -6.98 | 2097.49 | 150.296 | 35.6 | 2031.37 | 8262.65 | 10537.5 | 0.23 | 1.25 | 20.25 | 13.446 | 1 | 1 | 2790 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4260778.2613 | 366590.3264 | 7581.2803 | 32022.1679 | 334568.1585 | 14546.1203 | 0.1063 | -112321.2852 | 112321.2852
C | Xist Rating 6412 | -6.99 | 2098.47 | 150.296 | 35.6 | 2030.9 | 8254.92 | 10537.5 | 0.23 | 1.25 | 20.244 | 13.453 | 1 | 1 | 2800 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4261782.723 | 369107.7373 | 7635.7238 | 32136.9427 | 336970.7946 | 14555.3043 | 0.10668 | -112392.2015 | 112392.2015
C | Xist Rating 6413 | -6.97 | 2100.21 | 150.296 | 35.6 | 2030.28 | 8244.63 | 10537.5 | 0.23 | 1.25 | 20.251 | 13.465 | 1 | 1 | 2810 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4264014.3588 | 371633.7444 | 7690.3621 | 32251.7175 | 339382.027 | 14570.0561 | 0.10706 | -112506.1115 | 112506.1115
C | Xist Rating 6414 | -6.95 | 2101.69 | 150.296 | 35.6 | 2029.88 | 8238.08 | 10537.5 | 0.23 | 1.25 | 20.257 | 13.474 | 1 | 1 | 2820 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4266178.4972 | 374168.3478 | 7745.1952 | 32366.4922 | 341801.8555 | 14581.6649 | 0.10744 | -112595.7511 | 112595.7511
C | Xist Rating 6415 | -6.89 | 2103.06 | 150.296 | 35.6 | 2030.4 | 8246.67 | 10537.6 | 0.22 | 1.25 | 20.309 | 13.484 | 1 | 1 | 2830 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4270053.024 | 376711.5473 | 7800.223 | 32481.267 | 344230.2803 | 14569.8927 | 0.10783 | -112504.8497 | 112504.8497
C | Xist Rating 6416 | -6.88 | 2104.38 | 150.296 | 35.6 | 2029.98 | 8239.77 | 10537.6 | 0.22 | 1.25 | 20.309 | 13.493 | 1 | 1 | 2840 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4271849.3124 | 379263.343 | 7855.4457 | 32596.0418 | 346667.3012 | 14581.242 | 0.10821 | -112592.4855 | 112592.4855
C | Xist Rating 6417 | -6.8 | 2105.82 | 150.296 | 35.6 | 2030.69 | 8251.38 | 10537.7 | 0.22 | 1.25 | 20.32 | 13.503 | 1 | 1 | 2850 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4276267.6158 | 381823.7349 | 7910.8631 | 32710.8166 | 349112.9183 | 14593.9389 | 0.10859 | -112690.5276 | 112690.5276
C | Xist Rating 6418 | -6.72 | 2107.23 | 150.296 | 35.6 | 2031.83 | 8270.2 | 10537.7 | 0.22 | 1.25 | 20.339 | 13.512 | 1 | 1 | 2860 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4281533.1309 | 384392.7231 | 7966.4753 | 32825.5914 | 351567.1316 | 14605.8251 | 0.10897 | -112782.3097 | 112782.3097
C | Xist Rating 6419 | -6.3 | 2108.42 | 150.296 | 35.6 | 2040.58 | 8416.93 | 10537.9 | 0.21 | 1.25 | 20.409 | 13.522 | 1 | 1 | 2870 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4302399.6836 | 386970.3074 | 8022.2824 | 32940.3662 | 354029.9411 | 14593.9414 | 0.10935 | -112690.5472 | 112690.5472
C | Xist Rating 6420 | -6.15 | 2109.93 | 150.296 | 35.6 | 2042.97 | 8457.81 | 10537.9 | 0.21 | 1.25 | 20.46 | 13.532 | 1 | 1 | 2880 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4310523.6921 | 389556.4878 | 8078.2842 | 33055.141 | 356501.3468 | 14607.6301 | 0.10973 | -112796.2479 | 112796.2479
C | Xist Rating 6421 | -6.66 | 2111.27 | 150.296 | 35.6 | 2031.03 | 8257.01 | 10537.7 | 0.21 | 1.25 | 20.379 | 13.54 | 1 | 1 | 2890 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4288052.7081 | 392151.2645 | 8134.4807 | 33169.9158 | 358981.3487 | 14615.6605 | 0.11011 | -112858.2565 | 112858.2565
C | Xist Rating 6422 | -6.25 | 2112.66 | 150.296 | 35.6 | 2039.59 | 8400.28 | 10537.8 | 0.21 | 1.25 | 20.433 | 13.55 | 1 | 1 | 2900 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4308960.2094 | 394754.6374 | 8190.8721 | 33284.6906 | 361469.9468 | 14629.4379 | 0.11049 | -112964.6419 | 112964.6419
C | Xist Rating 6423 | -5.54 | 2114.2 | 150.296 | 35.6 | 2054.39 | 8656.88 | 10538 | 0.2 | 1.25 | 20.509 | 13.561 | 1 | 1 | 2910 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4343391.338 | 397366.6065 | 8247.4583 | 33399.4654 | 363967.1411 | 14618.1147 | 0.11087 | -112877.2073 | 112877.2073
C | Xist Rating 6424 | -4.95 | 2115.59 | 150.296 | 35.6 | 2066.66 | 8878.94 | 10538.1 | 0.2 | 1.25 | 20.575 | 13.571 | 1 | 1 | 2920 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4372205.2294 | 399987.1718 | 8304.2393 | 33514.2402 | 366472.9316 | 14632.0661 | 0.11125 | -112984.9357 | 112984.9357
C | Xist Rating 6425 | -4.65 | 2116.97 | 150.296 | 35.6 | 2072.6 | 8989.7 | 10538.1 | 0.19 | 1.25 | 20.644 | 13.581 | 1 | 1 | 2930 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4387632.022 | 402616.3332 | 8361.215 | 33629.015 | 368987.3182 | 14618.995 | 0.11164 | -112884.0042 | 112884.0042
C | Xist Rating 6426 | -4.37 | 2118.34 | 150.296 | 35.6 | 2078.13 | 9094.73 | 10538 | 0.19 | 1.25 | 20.671 | 13.59 | 1 | 1 | 2940 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4402185.9042 | 405254.0909 | 8418.3855 | 33743.7898 | 371510.3011 | 14630.7757 | 0.11202 | -112974.9718 | 112974.9718
C | Xist Rating 6427 | -4.19 | 2119.75 | 150.296 | 35.6 | 2081.51 | 9159.71 | 10538 | 0.19 | 1.25 | 20.691 | 13.6 | 1 | 1 | 2950 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4412280.8225 | 407900.4447 | 8475.7509 | 33858.5646 | 374041.8802 | 14643.4237 | 0.1124 | -113072.6359 | 113072.6359
C | Xist Rating 6428 | -3.55 | 2121.12 | 150.296 | 35.5 | 2094.94 | 9425.91 | 10537.8 | 0.19 | 1.25 | 20.728 | 13.61 | 1 | 1 | 2960 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4443619.1328 | 410555.3948 | 8533.311 | 33973.3394 | 376582.0554 | 14656.5036 | 0.11278 | -113173.6356 | 113173.6356
C | Xist Rating 6429 | -3.55 | 2122.5 | 150.296 | 35.5 | 2094.28 | 9412.59 | 10537.8 | 0.18 | 1.25 | 20.724 | 13.619 | 1 | 1 | 2970 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4445109.3 | 413218.941 | 8591.0659 | 34088.1142 | 379130.8269 | 14639.9245 | 0.11316 | -113045.6166 | 113045.6166
C | Xist Rating 6430 | -3.54 | 2123.73 | 150.296 | 35.5 | 2093.69 | 9400.57 | 10537.8 | 0.18 | 1.25 | 20.76 | 13.627 | 1 | 1 | 2980 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4446432.2637 | 415891.0835 | 8649.0156 | 34202.889 | 381688.1945 | 14650.7702 | 0.11354 | -113129.364 | 113129.364
C | Xist Rating 6431 | -3.52 | 2125.28 | 150.296 | 35.5 | 2093.28 | 9392.33 | 10537.9 | 0.18 | 1.25 | 20.764 | 13.637 | 1 | 1 | 2990 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4448806.1184 | 418571.8221 | 8707.16 | 34317.6638 | 384254.1583 | 14662.9267 | 0.11392 | -113223.2332 | 113223.2332
C | Xist Rating 6432 | -3.52 | 2126.72 | 150.296 | 35.5 | 2092.35 | 9373.74 | 10537.9 | 0.18 | 1.25 | 20.748 | 13.646 | 1 | 1 | 3000 | 152.4 | 2 | 4.1 | 19.05 | 1.3333 | 24 | E | Rod | 4449842.592 | 421261.1569 | 8765.4993 | 34432.4386 | 386828.7183 | 14673.5612 | 0.1143 | -113305.3502 | 113305.3502
C | Xist Rating 6433 | -88.18 | 215.73 | 150.301 | 35.9 | 2367.62 | 7107.64 | 58745.8 | 2.47 | 10.95 | 22.439 | 538.338 | 1 | 1 | 1000 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 510766.6626 | 55786.7031 | 973.9444 | 11757.418 | 44029.285 | 561547.538 | 0.038101 | -4336121.2388 | 4336121.2388
C | Xist Rating 6434 | -88.07 | 217.964 | 150.301 | 35.9 | 2365.53 | 7096.65 | 58284.2 | 2.45 | 10.85 | 22.507 | 528.223 | 1 | 1 | 1010 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 515600.3809 | 56789.2659 | 993.5206 | 11874.9922 | 44914.2736 | 551055.1952 | 0.038482 | -4255102.1485 | 4255102.1485
C | Xist Rating 6435 | -87.18 | 234.901 | 150.301 | 35.9 | 2359.42 | 7101.45 | 54967 | 2.46 | 10.07 | 22.558 | 457.753 | 1 | 1 | 1020 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 554230.1174 | 57800.6345 | 1013.2917 | 11992.5664 | 45808.0681 | 477912.9555 | 0.038863 | -3690317.1617 | 3690317.1617
C | Xist Rating 6436 | -87.03 | 239.515 | 150.3 | 35.9 | 2341.97 | 6960.48 | 54178.4 | 2.37 | 9.89 | 22.04 | 442.375 | 1 | 1 | 1030 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 560936.9445 | 58820.8091 | 1033.2576 | 12110.1406 | 46710.6685 | 461817.3869 | 0.039244 | -3566031.4473 | 3566031.4473
C | Xist Rating 6437 | -86.94 | 241.824 | 150.3 | 35.9 | 2336 | 6915.2 | 53793.7 | 2.33 | 9.8 | 21.918 | 435.01 | 1 | 1 | 1040 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 564900.864 | 59849.7894 | 1053.4182 | 12227.7148 | 47622.0747 | 454137.9105 | 0.039625 | -3506732.5659 | 3506732.5659
C | Xist Rating 6438 | -86.74 | 246.316 | 150.299 | 35.9 | 2329.47 | 6872.55 | 53042.8 | 2.3 | 9.63 | 21.835 | 420.574 | 1 | 1 | 1050 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 573785.7325 | 60887.5757 | 1073.7737 | 12345.2889 | 48542.2867 | 439129.1062 | 0.040006 | -3390838.5577 | 3390838.5577
C | Xist Rating 6439 | -86.6 | 248.605 | 150.299 | 35.9 | 2333.74 | 6917.07 | 52676.7 | 2.25 | 9.54 | 21.814 | 413.741 | 1 | 1 | 1060 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 580179.4327 | 61934.1678 | 1094.3239 | 12462.8631 | 49471.3046 | 432001.4391 | 0.040387 | -3335800.6015 | 3335800.6015
C | Xist Rating 6440 | -85.73 | 266.814 | 150.299 | 35.9 | 2315.27 | 6814.19 | 49857 | 2.24 | 8.9 | 21.613 | 361.999 | 1 | 1 | 1070 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 617746.4498 | 62989.5657 | 1115.0689 | 12580.4373 | 50409.1284 | 378257.3974 | 0.040768 | -2920803.3576 | 2920803.3576
C | Xist Rating 6441 | -85.5 | 270.251 | 150.299 | 35.9 | 2324.46 | 6905 | 49380.4 | 2.18 | 8.79 | 21.518 | 353.879 | 1 | 1 | 1080 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 628187.6395 | 64053.7695 | 1136.0087 | 12698.0115 | 51355.758 | 369773.6875 | 0.041149 | -2855294.3984 | 2855294.3984
C | Xist Rating 6442 | -85.24 | 274.824 | 150.298 | 35.9 | 2327.18 | 6943.28 | 48761.3 | 2.12 | 8.65 | 21.361 | 343.439 | 1 | 1 | 1090 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 639564.9163 | 65126.7792 | 1157.1433 | 12815.5857 | 52311.1935 | 358873.448 | 0.04153 | -2771125.6385 | 2771125.6385
C | Xist Rating 6443 | -85.01 | 278.229 | 150.298 | 35.9 | 2335.52 | 7029.02 | 48308 | 2.08 | 8.55 | 21.362 | 335.905 | 1 | 1 | 1100 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 649809.3941 | 66208.5947 | 1178.4727 | 12933.1599 | 53275.4349 | 351027.6725 | 0.041911 | -2710542.6396 | 2710542.6396
C | Xist Rating 6444 | -84.9 | 280.705 | 150.298 | 35.8 | 2333.22 | 7015.43 | 48010.9 | 2 | 8.49 | 21.042 | 331.281 | 1 | 1 | 1110 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 654946.5201 | 67299.2161 | 1199.9969 | 13050.734 | 54248.4821 | 346128.6993 | 0.042292 | -2672714.0678 | 2672714.0678
C | Xist Rating 6445 | -83.84 | 300.974 | 150.298 | 35.8 | 2329.12 | 7044.94 | 45447.6 | 2.05 | 7.92 | 21.315 | 289.862 | 1 | 1 | 1120 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 701004.5629 | 68398.6433 | 1221.7158 | 13168.3082 | 55230.3351 | 303214.913 | 0.042673 | -2341345.1848 | 2341345.1848
C | Xist Rating 6446 | -83.71 | 303.404 | 150.298 | 35.8 | 2329.22 | 7053.06 | 45189.3 | 1.98 | 7.86 | 21.115 | 286.138 | 1 | 1 | 1130 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 706694.6649 | 69506.8764 | 1243.6296 | 13285.8824 | 56220.994 | 299271.4981 | 0.043054 | -2310895.1804 | 2310895.1804
C | Xist Rating 6447 | -83.49 | 308.047 | 150.297 | 35.8 | 2327.02 | 7047.28 | 44681.5 | 1.93 | 7.75 | 20.928 | 278.657 | 1 | 1 | 1140 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 716831.5299 | 70623.9154 | 1265.7381 | 13403.4566 | 57220.4588 | 291448.8401 | 0.043435 | -2250490.689 | 2250490.689
C | Xist Rating 6448 | -83.25 | 312.627 | 150.297 | 35.8 | 2327.39 | 7065.04 | 44186.2 | 1.89 | 7.64 | 20.731 | 271.418 | 1 | 1 | 1150 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 727604.9535 | 71749.7602 | 1288.0414 | 13521.0308 | 58228.7294 | 283886.9101 | 0.043816 | -2192099.4695 | 2192099.4695
C | Xist Rating 6449 | -83.03 | 317.286 | 150.296 | 35.8 | 2324.31 | 7050.97 | 43703.3 | 1.84 | 7.53 | 20.567 | 264.531 | 1 | 1 | 1160 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 737471.0227 | 72884.4108 | 1310.5395 | 13638.6049 | 59245.8059 | 276682.7469 | 0.044197 | -2136470.8312 | 2136470.8312
C | Xist Rating 6450 | -82.09 | 335.481 | 150.297 | 35.8 | 2320.37 | 7073.24 | 41832.4 | 1.86 | 7.13 | 20.717 | 237.946 | 1 | 1 | 1170 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 778440.048 | 74027.8674 | 1333.2324 | 13756.1791 | 60271.6883 | 249127.4343 | 0.044578 | -1923696.0116 | 1923696.0116
C | Xist Rating 6451 | -81.95 | 336.79 | 150.297 | 35.8 | 2330.73 | 7174.08 | 41724.3 | 1.81 | 7.11 | 20.638 | 236.656 | 1 | 1 | 1180 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 784966.5567 | 75180.1297 | 1356.1201 | 13873.7533 | 61306.3765 | 247742.6915 | 0.044959 | -1913003.3941 | 1913003.3941
C | Xist Rating 6452 | -81.53 | 345.935 | 150.296 | 35.8 | 2322.64 | 7126.56 | 40885.5 | 1.76 | 6.93 | 20.465 | 225.55 | 1 | 1 | 1190 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 803482.4684 | 76341.198 | 1379.2026 | 13991.3275 | 62349.8705 | 236154.5879 | 0.04534 | -1823523.1299 | 1823523.1299
C | Xist Rating 6453 | -81.32 | 348.257 | 150.296 | 35.8 | 2334.57 | 7247.5 | 40681.9 | 1.72 | 6.88 | 20.508 | 222.956 | 1 | 1 | 1200 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 813030.3445 | 77511.0721 | 1402.4799 | 14108.9017 | 63402.1704 | 233436.8142 | 0.045721 | -1802537.2021 | 1802537.2021
C | Xist Rating 6454 | -81.09 | 352.985 | 150.296 | 35.8 | 2332.01 | 7237.64 | 40281.2 | 1.67 | 6.8 | 20.355 | 217.909 | 1 | 1 | 1210 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 823164.5499 | 78689.752 | 1425.9519 | 14226.4758 | 64463.2762 | 228141.8503 | 0.046102 | -1761650.894 | 1761650.894
C | Xist Rating 6455 | -80.1 | 373.608 | 150.296 | 35.8 | 2320 | 7189.3 | 38537.6 | 1.67 | 6.43 | 20.363 | 195.946 | 1 | 1 | 1220 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 866770.56 | 79877.2378 | 1449.6188 | 14344.05 | 65533.1878 | 205349.2773 | 0.046483 | -1585652.687 | 1585652.687
C | Xist Rating 6456 | -79.81 | 378.185 | 150.296 | 35.8 | 2325.98 | 7261.64 | 38183.1 | 1.65 | 6.35 | 20.374 | 191.735 | 1 | 1 | 1230 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 879650.7463 | 81073.5295 | 1473.4804 | 14461.6242 | 66611.9053 | 200969.9503 | 0.046864 | -1551836.6848 | 1551836.6848
C | Xist Rating 6457 | -79.56 | 382.903 | 150.296 | 35.8 | 2326.13 | 7277.72 | 37835.7 | 1.6 | 6.28 | 20.274 | 187.735 | 1 | 1 | 1240 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 890682.1554 | 82278.627 | 1497.5369 | 14579.1984 | 67699.4286 | 196765.5102 | 0.047245 | -1519371.1128 | 1519371.1128
C | Xist Rating 6458 | -79.39 | 385.37 | 150.296 | 35.8 | 2331.59 | 7338.86 | 37664.5 | 1.56 | 6.24 | 20.208 | 185.853 | 1 | 1 | 1250 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 898524.8383 | 83492.5304 | 1521.7881 | 14696.7726 | 68795.7578 | 194774.3889 | 0.047626 | -1503996.2019 | 1503996.2019
C | Xist Rating 6459 | -79.03 | 392.261 | 150.295 | 35.8 | 2331.58 | 7361.09 | 37161.5 | 1.53 | 6.14 | 20.164 | 180.076 | 1 | 1 | 1260 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 914587.9024 | 84715.2396 | 1546.2341 | 14814.3467 | 69900.8929 | 188751.0722 | 0.048007 | -1457485.7472 | 1457485.7472
C | Xist Rating 6460 | -78.07 | 411.791 | 150.296 | 35.8 | 2324.21 | 7352.29 | 35777.7 | 1.54 | 5.85 | 20.229 | 164.449 | 1 | 1 | 1270 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 957088.7601 | 85946.7547 | 1570.8749 | 14931.9209 | 71014.8338 | 172553.4635 | 0.048388 | -1332412.1061 | 1332412.1061
C | Xist Rating 6461 | -77.84 | 416.577 | 150.295 | 35.8 | 2321.89 | 7343.75 | 35477.4 | 1.5 | 5.79 | 20.118 | 161.321 | 1 | 1 | 1280 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 967245.9705 | 87187.0757 | 1595.7105 | 15049.4951 | 72137.5806 | 169263.0255 | 0.048769 | -1307004.216 | 1307004.216
C | Xist Rating 6462 | -77.61 | 421.312 | 150.295 | 35.8 | 2321.3 | 7352.51 | 35182.7 | 1.46 | 5.73 | 20.076 | 158.265 | 1 | 1 | 1290 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 977991.5456 | 88436.2025 | 1620.7408 | 15167.0693 | 73269.1332 | 166052.8233 | 0.04915 | -1282215.8859 | 1282215.8859
C | Xist Rating 6463 | -77.24 | 428.18 | 150.295 | 35.8 | 2322.57 | 7387.39 | 34751.1 | 1.44 | 5.64 | 20.113 | 153.751 | 1 | 1 | 1300 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 994478.0226 | 89694.1351 | 1645.966 | 15284.6435 | 74409.4917 | 161357.8873 | 0.049531 | -1245962.8347 | 1245962.8347
C | Xist Rating 6464 | -77.01 | 431.81 | 150.295 | 35.8 | 2327.53 | 7448.99 | 34540 | 1.41 | 5.59 | 20.062 | 151.654 | 1 | 1 | 1310 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1005050.7293 | 90960.8737 | 1671.3859 | 15402.2176 | 75558.656 | 159153.4848 | 0.049912 | -1228941.0225 | 1228941.0225
C | Xist Rating 6465 | -76.02 | 451.438 | 150.295 | 35.8 | 2322.03 | 7457.73 | 33363.1 | 1.41 | 5.35 | 20.116 | 139.655 | 1 | 1 | 1320 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1048252.5791 | 92236.418 | 1697.0007 | 15519.7918 | 76716.6262 | 146709.7271 | 0.050293 | -1132853.624 | 1132853.624
C | Xist Rating 6466 | -75.69 | 458.524 | 150.295 | 35.8 | 2319.23 | 7451.06 | 32979.9 | 1.37 | 5.28 | 20.013 | 136.003 | 1 | 1 | 1330 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1063422.6165 | 93520.7683 | 1722.8102 | 15637.366 | 77883.4023 | 142873.4621 | 0.050674 | -1103231.003 | 1103231.003
C | Xist Rating 6467 | -75.31 | 465.508 | 150.295 | 35.8 | 2321.25 | 7494.32 | 32606.7 | 1.35 | 5.2 | 19.926 | 132.471 | 1 | 1 | 1340 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1080560.445 | 94813.9244 | 1748.8145 | 15754.9402 | 79058.9842 | 139186.6794 | 0.051055 | -1074762.6439 | 1074762.6439
C | Xist Rating 6468 | -75.07 | 469.155 | 150.295 | 35.8 | 2326 | 7555.39 | 32423.8 | 1.31 | 5.16 | 19.889 | 130.816 | 1 | 1 | 1350 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1091254.53 | 96115.8863 | 1775.0136 | 15872.5144 | 80243.3719 | 137428.8578 | 0.051436 | -1061189.2116 | 1061189.2116
C | Xist Rating 6469 | -74.8 | 471.424 | 150.295 | 35.8 | 2341.18 | 7725.82 | 32303.3 | 1.3 | 5.14 | 19.969 | 129.697 | 1 | 1 | 1360 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1103688.4403 | 97426.6541 | 1801.4075 | 15990.0885 | 81436.5656 | 136272.6723 | 0.051817 | -1052261.4537 | 1052261.4537
C | Xist Rating 6470 | -73.6 | 499.275 | 150.295 | 35.8 | 2315.97 | 7548.83 | 30902.5 | 1.29 | 4.86 | 19.893 | 116.855 | 1 | 1 | 1370 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1156305.9217 | 98746.2278 | 1827.9962 | 16107.6627 | 82638.565 | 122929.6284 | 0.052198 | -949230.0057 | 949230.0057
C | Xist Rating 6471 | -73.48 | 501.806 | 150.295 | 35.8 | 2315.82 | 7554.79 | 30794 | 1.27 | 4.84 | 19.853 | 115.977 | 1 | 1 | 1380 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1162092.3709 | 100074.6073 | 1854.7797 | 16225.2369 | 83849.3704 | 122001.5765 | 0.052579 | -942063.8346 | 942063.8346
C | Xist Rating 6472 | -73.17 | 507.744 | 150.295 | 35.8 | 2317.13 | 7587.47 | 30526.9 | 1.24 | 4.78 | 19.816 | 113.707 | 1 | 1 | 1390 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1176508.8547 | 101411.7927 | 1881.7579 | 16342.8111 | 85068.9816 | 119615.5193 | 0.05296 | -923639.3331 | 923639.3331
C | Xist Rating 6473 | -72.85 | 513.679 | 150.295 | 35.7 | 2318.09 | 7616.67 | 30264.9 | 1.22 | 4.73 | 19.784 | 111.505 | 1 | 1 | 1400 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1190754.1531 | 102757.7839 | 1908.931 | 16460.3853 | 86297.3986 | 117312.4392 | 0.053341 | -905855.5592 | 905855.5592
C | Xist Rating 6474 | -72.48 | 520.724 | 150.294 | 35.7 | 2319 | 7649.28 | 29957.2 | 1.19 | 4.67 | 19.761 | 108.931 | 1 | 1 | 1410 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1207558.956 | 104112.581 | 1936.2988 | 16577.9594 | 87534.6215 | 114610.9214 | 0.053722 | -884995.1549 | 884995.1549
C | Xist Rating 6475 | -71.44 | 541.589 | 150.295 | 35.7 | 2314.23 | 7667.26 | 29051.8 | 1.2 | 4.49 | 19.835 | 101.354 | 1 | 1 | 1420 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1253361.5115 | 105476.1839 | 1963.8614 | 16695.5336 | 88780.6503 | 106770.9899 | 0.054103 | -824457.2823 | 824457.2823
C | Xist Rating 6476 | -71.26 | 545.476 | 150.294 | 35.7 | 2313.25 | 7667.92 | 28910.6 | 1.16 | 4.47 | 19.751 | 100.314 | 1 | 1 | 1430 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1261822.357 | 106848.5927 | 1991.6188 | 16813.1078 | 90035.4849 | 105644.5186 | 0.054484 | -815758.969 | 815758.969
C | Xist Rating 6477 | -70.8 | 554.791 | 150.294 | 35.7 | 2312.1 | 7685.55 | 28541.8 | 1.15 | 4.39 | 19.732 | 97.405 | 1 | 1 | 1440 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1282732.2711 | 108229.8074 | 2019.571 | 16930.682 | 91299.1254 | 102619.6374 | 0.054865 | -792401.6383 | 792401.6383
C | Xist Rating 6478 | -70.49 | 560.764 | 150.294 | 35.7 | 2312.83 | 7712.66 | 28316.8 | 1.13 | 4.35 | 19.709 | 95.688 | 1 | 1 | 1450 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1296951.8021 | 109619.8279 | 2047.718 | 17048.2562 | 92571.5717 | 100819.3679 | 0.055246 | -778500.435 | 778500.435
C | Xist Rating 6479 | -70.22 | 564.292 | 150.294 | 35.7 | 2319.76 | 7801.87 | 28183.6 | 1.11 | 4.32 | 19.738 | 94.68 | 1 | 1 | 1460 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1309022.0099 | 111018.6543 | 2076.0598 | 17165.8303 | 93852.8239 | 99758.8544 | 0.055627 | -770311.4308 | 770311.4308
C | Xist Rating 6480 | -69.19 | 587.854 | 150.294 | 35.7 | 2304.76 | 7711.59 | 27310.2 | 1.1 | 4.16 | 19.711 | 88.032 | 1 | 1 | 1470 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1354862.385 | 112426.2865 | 2104.5964 | 17283.4045 | 95142.882 | 92849.7749 | 0.056008 | -716961.3497 | 716961.3497
C | Xist Rating 6481 | -68.82 | 594.943 | 150.294 | 35.7 | 2305.44 | 7741.93 | 27066 | 1.09 | 4.11 | 19.698 | 86.268 | 1 | 1 | 1480 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1371605.3899 | 113842.7246 | 2133.3277 | 17400.9787 | 96441.7459 | 91013.5662 | 0.056389 | -702782.6328 | 702782.6328
C | Xist Rating 6482 | -68.51 | 600.918 | 150.294 | 35.7 | 2306.09 | 7768.3 | 26866.5 | 1.07 | 4.07 | 19.684 | 84.854 | 1 | 1 | 1490 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1385770.9906 | 115267.9686 | 2162.2539 | 17518.5529 | 97749.4157 | 89527.441 | 0.05677 | -691307.1685 | 691307.1685
C | Xist Rating 6483 | -68.19 | 606.985 | 150.294 | 35.7 | 2307.38 | 7802.12 | 26670 | 1.05 | 4.03 | 19.656 | 83.489 | 1 | 1 | 1500 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1400545.0493 | 116702.0184 | 2191.3748 | 17636.1271 | 99065.8913 | 88090.885 | 0.057151 | -680214.4635 | 680214.4635
C | Xist Rating 6484 | -67.77 | 614.1 | 150.294 | 35.7 | 2311.48 | 7872.53 | 26438.8 | 1.03 | 3.99 | 19.66 | 81.874 | 1 | 1 | 1510 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1419479.868 | 118144.874 | 2220.6906 | 17753.7012 | 100391.1728 | 86396.6317 | 0.057532 | -667131.8891 | 667131.8891
C | Xist Rating 6485 | -66.6 | 637.346 | 150.294 | 35.7 | 2308.97 | 7923.28 | 25681 | 1.04 | 3.84 | 19.739 | 76.542 | 1 | 1 | 1520 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1471612.7936 | 119596.5355 | 2250.2011 | 17871.2754 | 101725.2601 | 80887.428 | 0.057913 | -624591.2779 | 624591.2779
C | Xist Rating 6486 | -66.28 | 644.806 | 150.294 | 35.7 | 2304.15 | 7889.96 | 25468.5 | 1.01 | 3.8 | 19.667 | 75.176 | 1 | 1 | 1530 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1485729.7449 | 121057.0029 | 2279.9064 | 17988.8496 | 103068.1533 | 79432.4417 | 0.058294 | -613356.2595 | 613356.2595
C | Xist Rating 6487 | -66.01 | 648.608 | 150.294 | 35.7 | 2310.02 | 7971.09 | 25363.7 | 0.99 | 3.78 | 19.657 | 74.525 | 1 | 1 | 1540 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1498297.4522 | 122526.2761 | 2309.8065 | 18106.4238 | 104419.8523 | 78737.4474 | 0.058675 | -607989.6978 | 607989.6978
C | Xist Rating 6488 | -65.43 | 660.317 | 150.294 | 35.7 | 2308.55 | 7993.08 | 25021.2 | 0.97 | 3.72 | 19.649 | 72.274 | 1 | 1 | 1550 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1524374.8104 | 124004.3552 | 2339.9013 | 18223.998 | 105780.3572 | 76380.6567 | 0.059056 | -589791.1848 | 589791.1848
C | Xist Rating 6489 | -65.17 | 663.896 | 150.294 | 35.7 | 2316.34 | 8099.49 | 24919.5 | 0.96 | 3.7 | 19.665 | 71.636 | 1 | 1 | 1560 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1537808.8606 | 125491.2402 | 2370.191 | 18341.5722 | 107149.668 | 75713.9723 | 0.059437 | -584643.2246 | 584643.2246
C | Xist Rating 6490 | -64.03 | 691.169 | 150.294 | 35.7 | 2298.08 | 7971.56 | 24161.2 | 0.96 | 3.56 | 19.608 | 66.782 | 1 | 1 | 1570 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1588361.6555 | 126986.931 | 2400.6755 | 18459.1463 | 108527.7846 | 70677.7123 | 0.059818 | -545754.5594 | 545754.5594
C | Xist Rating 6491 | -63.68 | 697.264 | 150.294 | 35.7 | 2300.98 | 8026.25 | 24006.5 | 0.94 | 3.53 | 19.601 | 65.858 | 1 | 1 | 1580 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1604390.5187 | 128491.4276 | 2431.3547 | 18576.7205 | 109914.7071 | 69698.3374 | 0.0602 | -538192.0866 | 538192.0866
C | Xist Rating 6492 | -63.34 | 703.395 | 150.294 | 35.7 | 2303.17 | 8072.93 | 23854 | 0.92 | 3.5 | 19.59 | 64.958 | 1 | 1 | 1590 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1620038.2622 | 130004.7301 | 2462.2288 | 18694.2947 | 111310.4354 | 68743.2868 | 0.060581 | -530817.4385 | 530817.4385
C | Xist Rating 6493 | -62.85 | 711.651 | 150.294 | 35.7 | 2307.2 | 8150.93 | 23644.6 | 0.91 | 3.46 | 19.61 | 63.698 | 1 | 1 | 1600 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1641921.1872 | 131526.8385 | 2493.2976 | 18811.8689 | 112714.9696 | 67430.1129 | 0.060962 | -520677.4578 | 520677.4578
C | Xist Rating 6494 | -62.62 | 715.65 | 150.294 | 35.7 | 2309.29 | 8189.33 | 23555.9 | 0.89 | 3.45 | 19.583 | 63.219 | 1 | 1 | 1610 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1652643.3885 | 133057.7527 | 2524.5612 | 18929.4431 | 114128.3097 | 66910.6328 | 0.061343 | -516666.1702 | 516666.1702
C | Xist Rating 6495 | -61.28 | 746.165 | 150.294 | 35.7 | 2295.05 | 8117.68 | 22804.4 | 0.89 | 3.31 | 19.612 | 58.744 | 1 | 1 | 1620 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1712485.9833 | 134597.4728 | 2556.0196 | 19047.0172 | 115550.4556 | 62273.039 | 0.061724 | -480855.9004 | 480855.9004
C | Xist Rating 6496 | -60.94 | 749.818 | 150.294 | 35.7 | 2304.83 | 8253.76 | 22722.7 | 0.88 | 3.29 | 19.637 | 58.299 | 1 | 1 | 1630 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1728203.0209 | 136145.9988 | 2587.6728 | 19164.5914 | 116981.4074 | 61806.0093 | 0.062105 | -477249.6206 | 477249.6206
C | Xist Rating 6497 | -60.6 | 756.096 | 150.294 | 35.7 | 2305.95 | 8288.73 | 22588 | 0.86 | 3.27 | 19.615 | 57.574 | 1 | 1 | 1640 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1743519.5712 | 137703.3306 | 2619.5208 | 19282.1656 | 118421.165 | 61030.5817 | 0.062486 | -471261.9747 | 471261.9747
C | Xist Rating 6498 | -60.21 | 764.71 | 150.294 | 35.7 | 2303.24 | 8282.69 | 22402.4 | 0.84 | 3.23 | 19.587 | 56.564 | 1 | 1 | 1650 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1761310.6604 | 139269.4682 | 2651.5635 | 19399.7398 | 119869.7285 | 59958.5054 | 0.062867 | -462983.6857 | 462983.6857
C | Xist Rating 6499 | -59.76 | 773.081 | 150.294 | 35.7 | 2304.91 | 8333.47 | 22220.3 | 0.83 | 3.2 | 19.59 | 55.566 | 1 | 1 | 1660 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 26 | E | Rod | 1781882.1277 | 140844.4117 | 2683.8011 | 19517.314 | 121327.0978 | 58915.0698 | 0.063248 | -454926.5527 | 454926.5527
C | Xist Rating 6500 | -58.57 | 800.397 | 150.294 | 35.7 | 2292.97 | 8274.67 | 21632.5 | 0.83 | 3.1 | 19.6 | 52.34 | 1 | 1 | 1670 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 1835286.3091 | 142428.1611 | 2716.2334 | 19634.8881 | 122793.273 | 55572.7836 | 0.063629 | -429118.3043 | 429118.3043
C | Xist Rating 6501 | -58.28 | 804.162 | 150.294 | 35.7 | 2298.82 | 8363.83 | 21560 | 0.82 | 3.08 | 19.608 | 51.98 | 1 | 1 | 1680 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 1848623.6888 | 144020.7163 | 2748.8606 | 19752.4623 | 124268.254 | 55191.9504 | 0.06401 | -426177.6112 | 426177.6112
C | Xist Rating 6502 | -57.82 | 815.162 | 150.294 | 35.7 | 2294.01 | 8337.7 | 21345.6 | 0.81 | 3.04 | 19.578 | 50.879 | 1 | 1 | 1690 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 1869989.7796 | 145622.0774 | 2781.6825 | 19870.0365 | 125752.0409 | 54039.0762 | 0.064391 | -417275.4223 | 417275.4223
C | Xist Rating 6503 | -57.4 | 822.434 | 150.294 | 35.7 | 2296.94 | 8401.55 | 21205.7 | 0.8 | 3.02 | 19.581 | 50.168 | 1 | 1 | 1700 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 1889081.552 | 147232.2444 | 2814.6992 | 19987.6107 | 127244.6337 | 53293.0763 | 0.064772 | -411515.0086 | 411515.0086
C | Xist Rating 6504 | -56.98 | 830.997 | 150.294 | 35.7 | 2296.52 | 8425.19 | 21044.6 | 0.78 | 2.99 | 19.571 | 49.361 | 1 | 1 | 1710 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 1908401.2304 | 148851.2172 | 2847.9107 | 20105.1849 | 128746.0323 | 52431.4141 | 0.065153 | -404861.482 | 404861.482
C | Xist Rating 6505 | -55.87 | 856.132 | 150.294 | 35.7 | 2286.89 | 8385.33 | 20567 | 0.78 | 2.9 | 19.6 | 46.927 | 1 | 1 | 1720 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 1957879.7095 | 150478.9958 | 2881.317 | 20222.759 | 130256.2368 | 49912.2956 | 0.065534 | -385409.5164 | 385409.5164
C | Xist Rating 6506 | -55.36 | 867.002 | 150.294 | 35.7 | 2285.43 | 8402.94 | 20374.2 | 0.77 | 2.87 | 19.591 | 45.993 | 1 | 1 | 1730 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 1981472.3809 | 152115.5803 | 2914.9181 | 20340.3332 | 131775.2471 | 48933.4543 | 0.065915 | -377851.1636 | 377851.1636
C | Xist Rating 6507 | -55.05 | 872.029 | 150.294 | 35.6 | 2289.39 | 8473.7 | 20289.5 | 0.76 | 2.85 | 19.592 | 45.603 | 1 | 1 | 1740 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 1996414.4723 | 153760.9707 | 2948.714 | 20457.9074 | 133303.0633 | 48519.9811 | 0.066296 | -374658.4327 | 374658.4327
C | Xist Rating 6508 | -54.61 | 881.915 | 150.294 | 35.7 | 2285.91 | 8459.55 | 20123.4 | 0.74 | 2.82 | 19.573 | 44.823 | 1 | 1 | 1750 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2015978.3176 | 155415.1669 | 2982.7046 | 20575.4816 | 134839.6854 | 47684.7866 | 0.066677 | -368209.2823 | 368209.2823
C | Xist Rating 6509 | -54.2 | 889.304 | 150.295 | 35.7 | 2287.49 | 8506.46 | 20001 | 0.73 | 2.8 | 19.578 | 44.255 | 1 | 1 | 1760 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2034274.007 | 157078.169 | 3016.8901 | 20693.0558 | 136385.1133 | 47086.2585 | 0.067058 | -363587.6066 | 363587.6066
C | Xist Rating 6510 | -52.98 | 919.094 | 150.294 | 35.7 | 2273.8 | 8424.29 | 19497.2 | 0.74 | 2.71 | 19.604 | 41.859 | 1 | 1 | 1770 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2089835.9372 | 158749.977 | 3051.2703 | 20810.6299 | 137939.347 | 44621.4822 | 0.067439 | -344555.2574 | 344555.2574
C | Xist Rating 6511 | -52.61 | 926.593 | 150.294 | 35.7 | 2274.11 | 8453.47 | 19382.8 | 0.72 | 2.69 | 19.594 | 41.357 | 1 | 1 | 1780 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2107174.4072 | 160430.5908 | 3085.8453 | 20928.2041 | 139502.3866 | 44074.8009 | 0.06782 | -340333.93 | 340333.93
C | Xist Rating 6512 | -52.34 | 930.617 | 150.294 | 35.6 | 2277.59 | 8514.25 | 19326.3 | 0.71 | 2.68 | 19.589 | 41.128 | 1 | 1 | 1790 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2119563.973 | 162120.0104 | 3120.6151 | 21045.7783 | 141074.2321 | 43827.3022 | 0.068201 | -338422.8104 | 338422.8104
C | Xist Rating 6513 | -51.76 | 943.909 | 150.295 | 35.6 | 2274.2 | 8513 | 19121.6 | 0.7 | 2.65 | 19.582 | 40.213 | 1 | 1 | 1800 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2146637.8478 | 163818.2359 | 3155.5797 | 21163.3525 | 142654.8834 | 42867.1099 | 0.068582 | -331008.4595 | 331008.4595
C | Xist Rating 6514 | -51.62 | 951.28 | 150.295 | 35.6 | 2263.08 | 8383.36 | 19013 | 0.69 | 2.63 | 19.816 | 39.732 | 1 | 1 | 1810 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2152822.7424 | 165525.2673 | 3190.7391 | 21280.9267 | 144244.3406 | 42370.9487 | 0.068963 | -327177.2345 | 327177.2345
C | Xist Rating 6515 | -50.1 | 981.329 | 150.295 | 35.6 | 2263.9 | 8499.36 | 18562.6 | 0.69 | 2.55 | 19.613 | 37.75 | 1 | 1 | 1820 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2221630.7231 | 167241.1045 | 3226.0933 | 21398.5008 | 145842.6037 | 40307.3467 | 0.069344 | -311242.6468 | 311242.6468
C | Xist Rating 6516 | -50.35 | 976.557 | 150.295 | 35.6 | 2266.63 | 8521.3 | 18631.3 | 0.69 | 2.56 | 19.869 | 38.051 | 1 | 1 | 1830 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2213493.3929 | 168965.7476 | 3261.6423 | 21516.075 | 147449.6726 | 40640.4904 | 0.069725 | -313815.0946 | 313815.0946
C | Xist Rating 6517 | -49.88 | 982.614 | 150.295 | 35.6 | 2274.16 | 8650.09 | 18545.1 | 0.68 | 2.55 | 19.893 | 37.692 | 1 | 1 | 1840 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2234621.4542 | 170699.1966 | 3297.386 | 21633.6492 | 149065.5473 | 40258.7734 | 0.070106 | -310867.5767 | 310867.5767
C | Xist Rating 6518 | -49.44 | 992.616 | 150.295 | 35.6 | 2271.05 | 8639.39 | 18409.3 | 0.67 | 2.52 | 19.882 | 37.132 | 1 | 1 | 1850 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2254280.5668 | 172441.4513 | 3333.3246 | 21751.2234 | 150690.228 | 39666.1703 | 0.070487 | -306291.6525 | 306291.6525
C | Xist Rating 6519 | -48.97 | 1003.83 | 150.295 | 35.6 | 2267.33 | 8623.78 | 18259 | 0.66 | 2.5 | 19.869 | 36.516 | 1 | 1 | 1860 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2276013.8739 | 174192.512 | 3369.4579 | 21868.7976 | 152323.7144 | 39015.1346 | 0.070868 | -301264.5274 | 301264.5274
C | Xist Rating 6520 | -47.72 | 1031.42 | 150.295 | 35.6 | 2261.16 | 8633.8 | 17879.6 | 0.66 | 2.43 | 19.918 | 34.92 | 1 | 1 | 1870 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2332205.6472 | 175952.3785 | 3405.7861 | 21986.3717 | 153966.0068 | 37366.28 | 0.071249 | -288532.5094 | 288532.5094
C | Xist Rating 6521 | -47.22 | 1042.62 | 150.295 | 35.6 | 2258.56 | 8633.84 | 17738.8 | 0.65 | 2.41 | 19.908 | 34.366 | 1 | 1 | 1880 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2354819.8272 | 177721.0509 | 3442.309 | 22103.9459 | 155617.105 | 36779.5117 | 0.07163 | -284001.6405 | 284001.6405
C | Xist Rating 6522 | -46.78 | 1050.04 | 150.295 | 35.6 | 2261.86 | 8707.94 | 17646.4 | 0.64 | 2.39 | 19.926 | 34.008 | 1 | 1 | 1890 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2375043.4744 | 179498.5291 | 3479.0267 | 22221.5201 | 157277.009 | 36397.6399 | 0.072011 | -281052.9273 | 281052.9273
C | Xist Rating 6523 | -46.47 | 1057.92 | 150.295 | 35.6 | 2258.58 | 8685.14 | 17554.9 | 0.62 | 2.38 | 19.91 | 33.669 | 1 | 1 | 1900 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2389396.9536 | 181284.8132 | 3515.9392 | 22339.0943 | 158945.7189 | 36016.5197 | 0.072392 | -278110.0183 | 278110.0183
C | Xist Rating 6524 | -46.09 | 1065.52 | 150.295 | 35.6 | 2258.11 | 8703.57 | 17465 | 0.61 | 2.36 | 19.919 | 33.329 | 1 | 1 | 1910 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2406061.3672 | 183079.9031 | 3553.0464 | 22456.6685 | 160623.2347 | 35652.3876 | 0.072773 | -275298.2863 | 275298.2863
C | Xist Rating 6525 | -44.6 | 1099.03 | 150.295 | 35.6 | 2250.51 | 8711.67 | 17050.3 | 0.62 | 2.29 | 19.965 | 31.688 | 1 | 1 | 1920 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2473378.0053 | 184883.7989 | 3590.3485 | 22574.2426 | 162309.5563 | 33973.2556 | 0.073154 | -262332.4744 | 262332.4744
C | Xist Rating 6526 | -44.16 | 1110.3 | 150.295 | 35.6 | 2245.97 | 8681.9 | 16923.9 | 0.61 | 2.27 | 19.959 | 31.222 | 1 | 1 | 1930 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2493700.491 | 186696.5006 | 3627.8454 | 22691.8168 | 164004.6838 | 33477.2752 | 0.073535 | -258502.6452 | 258502.6452
C | Xist Rating 6527 | -43.8 | 1113.96 | 150.295 | 35.6 | 2253.37 | 8806.51 | 16882.1 | 0.6 | 2.26 | 19.988 | 31.074 | 1 | 1 | 1940 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2510164.0452 | 188518.0081 | 3665.537 | 22809.391 | 165708.6171 | 33313.1916 | 0.073916 | -257235.6353 | 257235.6353
C | Xist Rating 6528 | -43.46 | 1124.54 | 150.295 | 35.6 | 2246.37 | 8734.58 | 16772.1 | 0.59 | 2.24 | 19.956 | 30.689 | 1 | 1 | 1950 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2526132.9198 | 190348.3215 | 3703.4235 | 22926.9652 | 167421.3563 | 32899.6241 | 0.074297 | -254042.1763 | 254042.1763
C | Xist Rating 6529 | -42.89 | 1136.9 | 150.295 | 35.7 | 2244.44 | 8747.78 | 16637.2 | 0.58 | 2.22 | 19.989 | 30.197 | 1 | 1 | 1960 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2551703.836 | 192187.4407 | 3741.5047 | 23044.5394 | 169142.9013 | 32378.1095 | 0.074678 | -250015.1789 | 250015.1789
C | Xist Rating 6530 | -41.58 | 1167.08 | 150.295 | 35.7 | 2237.06 | 8743.59 | 16303.3 | 0.58 | 2.16 | 20.055 | 28.961 | 1 | 1 | 1970 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2610827.9848 | 194035.3658 | 3779.7807 | 23162.1136 | 170873.2522 | 31103.1025 | 0.075059 | -240169.9132 | 240169.9132
C | Xist Rating 6531 | -41.16 | 1175.87 | 150.295 | 35.7 | 2236.74 | 8768.47 | 16214.3 | 0.57 | 2.15 | 20.079 | 28.655 | 1 | 1 | 1980 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2630115.4638 | 195892.0967 | 3818.2515 | 23279.6877 | 172612.409 | 30773.9507 | 0.07544 | -237628.2903 | 237628.2903
C | Xist Rating 6532 | -40.71 | 1187.33 | 150.295 | 35.7 | 2232.73 | 8744.98 | 16101.3 | 0.56 | 2.13 | 20.083 | 28.27 | 1 | 1 | 1990 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2650987.3109 | 197757.6335 | 3856.9171 | 23397.2619 | 174360.3716 | 30361.5482 | 0.075821 | -234443.827 | 234443.827
C | Xist Rating 6533 | -40.31 | 1196.25 | 150.295 | 35.7 | 2231.61 | 8757.39 | 16014.9 | 0.55 | 2.12 | 20.086 | 27.98 | 1 | 1 | 2000 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2669563.4625 | 199631.9762 | 3895.7775 | 23514.8361 | 176117.1401 | 30047.5685 | 0.076202 | -232019.359 | 232019.359
C | Xist Rating 6534 | -39.99 | 1202.78 | 150.295 | 35.7 | 2231.88 | 8782.74 | 15953.7 | 0.55 | 2.11 | 20.089 | 27.781 | 1 | 1 | 2010 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2684460.6264 | 201515.1247 | 3934.8326 | 23632.4103 | 177882.7144 | 29846.0079 | 0.076583 | -230462.9614 | 230462.9614
C | Xist Rating 6535 | -38.63 | 1236.73 | 150.295 | 35.6 | 2221.49 | 8741.96 | 15614.6 | 0.55 | 2.05 | 20.128 | 26.598 | 1 | 1 | 2020 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2747383.3277 | 203407.079 | 3974.0826 | 23749.9845 | 179657.0946 | 28624.3591 | 0.076964 | -221029.7134 | 221029.7134
C | Xist Rating 6536 | -38.06 | 1249.04 | 150.295 | 35.7 | 2219.84 | 8758.19 | 15499.8 | 0.54 | 2.03 | 20.141 | 26.218 | 1 | 1 | 2030 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2772668.9536 | 205307.8393 | 4013.5273 | 23867.5586 | 181440.2806 | 28217.0155 | 0.077345 | -217884.3139 | 217884.3139
C | Xist Rating 6537 | -37.74 | 1257.12 | 150.295 | 35.7 | 2217.1 | 8740.69 | 15431.8 | 0.53 | 2.02 | 20.133 | 26.01 | 1 | 1 | 2040 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2787160.752 | 207217.4053 | 4053.1669 | 23985.1328 | 183232.2725 | 27987.0779 | 0.077726 | -216108.7968 | 216108.7968
C | Xist Rating 6538 | -37.26 | 1264.38 | 150.295 | 35.7 | 2221.65 | 8837.25 | 15364.3 | 0.52 | 2.01 | 20.161 | 25.79 | 1 | 1 | 2050 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2809009.827 | 209135.7773 | 4093.0012 | 24102.707 | 185033.0703 | 27746.2288 | 0.078107 | -214249.0244 | 214249.0244
C | Xist Rating 6539 | -36.85 | 1276.24 | 150.295 | 35.7 | 2216.11 | 8788.03 | 15264.3 | 0.51 | 1.99 | 20.138 | 25.481 | 1 | 1 | 2060 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2828288.2264 | 211062.9551 | 4133.0303 | 24220.2812 | 186842.6739 | 27410.3326 | 0.078488 | -211655.3224 | 211655.3224
C | Xist Rating 6540 | -35.35 | 1312.69 | 150.296 | 35.7 | 2206.29 | 8760.85 | 14936.2 | 0.51 | 1.94 | 20.175 | 24.401 | 1 | 1 | 2070 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2896174.8201 | 212998.9387 | 4173.2542 | 24337.8554 | 188661.0834 | 26295.1088 | 0.078869 | -203043.8603 | 203043.8603
C | Xist Rating 6541 | -34.97 | 1320.57 | 150.295 | 35.7 | 2206.49 | 8788.96 | 14873.5 | 0.51 | 1.93 | 20.175 | 24.216 | 1 | 1 | 2080 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2913824.4993 | 214943.7282 | 4213.6729 | 24455.4295 | 190488.2987 | 26107.5987 | 0.07925 | -201595.9571 | 201595.9571
C | Xist Rating 6542 | -34.53 | 1330.77 | 150.295 | 35.7 | 2205.09 | 8800.16 | 14790.9 | 0.5 | 1.91 | 20.168 | 23.967 | 1 | 1 | 2090 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2934467.6193 | 216897.3236 | 4254.2864 | 24573.0037 | 192324.3199 | 25834.3962 | 0.079631 | -199486.3596 | 199486.3596
C | Xist Rating 6543 | -34.08 | 1340.98 | 150.295 | 35.7 | 2203.61 | 8809.92 | 14709.4 | 0.49 | 1.9 | 20.169 | 23.722 | 1 | 1 | 2100 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2954996.9378 | 218859.7248 | 4295.0947 | 24690.5779 | 194169.1469 | 25565.5458 | 0.080012 | -197410.3683 | 197410.3683
C | Xist Rating 6544 | -33.68 | 1349.99 | 150.295 | 35.7 | 2202.74 | 8825.27 | 14638.8 | 0.49 | 1.89 | 20.169 | 23.513 | 1 | 1 | 2110 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 2973676.9726 | 220830.9319 | 4336.0977 | 24808.1521 | 196022.7798 | 25352.9296 | 0.080393 | -195768.6021 | 195768.6021
C | Xist Rating 6545 | -32.31 | 1384.39 | 150.296 | 35.7 | 2193.22 | 8791.13 | 14359.1 | 0.49 | 1.84 | 20.202 | 22.647 | 1 | 1 | 2120 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3036271.8358 | 222810.9448 | 4377.2956 | 24925.7263 | 197885.2186 | 24459.5565 | 0.080774 | -188870.2119 | 188870.2119
C | Xist Rating 6546 | -31.81 | 1397.04 | 150.296 | 35.7 | 2190.04 | 8781.47 | 14263.7 | 0.48 | 1.83 | 20.199 | 22.369 | 1 | 1 | 2130 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3059573.4816 | 224799.7636 | 4418.6882 | 25043.3004 | 199756.4632 | 24155.8655 | 0.081155 | -186525.1903 | 186525.1903
C | Xist Rating 6547 | -31.39 | 1409.71 | 150.296 | 35.7 | 2184.43 | 8732.53 | 14169.8 | 0.48 | 1.81 | 20.195 | 22.098 | 1 | 1 | 2140 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3079412.8153 | 226797.3883 | 4460.2756 | 25160.8746 | 201636.5137 | 23878.5942 | 0.081536 | -184384.1751 | 184384.1751
C | Xist Rating 6548 | -31.08 | 1416.39 | 150.296 | 35.7 | 2184.42 | 8752.69 | 14123.4 | 0.47 | 1.8 | 20.197 | 21.973 | 1 | 1 | 2150 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3093990.6438 | 228803.8188 | 4502.0578 | 25278.4488 | 203525.37 | 23733.7551 | 0.081917 | -183265.7658 | 183265.7658
C | Xist Rating 6549 | -30.68 | 1425.34 | 150.296 | 35.7 | 2183.94 | 8773.57 | 14059 | 0.46 | 1.79 | 20.201 | 21.792 | 1 | 1 | 2160 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3112857.0396 | 230819.0551 | 4544.0348 | 25396.023 | 205423.0322 | 23530.6651 | 0.082298 | -181697.5585 | 181697.5585
C | Xist Rating 6550 | -29.26 | 1462.44 | 150.296 | 35.7 | 2172.65 | 8715.56 | 13785.9 | 0.46 | 1.75 | 20.231 | 20.993 | 1 | 1 | 2170 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3177370.266 | 232843.0974 | 4586.2066 | 25513.5972 | 207329.5002 | 22706.4125 | 0.082679 | -175332.8983 | 175332.8983
C | Xist Rating 6551 | -28.71 | 1474.87 | 150.296 | 35.7 | 2171.7 | 8740.64 | 13698.9 | 0.46 | 1.74 | 20.235 | 20.75 | 1 | 1 | 2180 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3202975.179 | 234875.9454 | 4628.5732 | 25631.1713 | 209244.7741 | 22458.4087 | 0.08306 | -173417.8786 | 173417.8786
C | Xist Rating 6552 | -28.34 | 1484.05 | 150.296 | 35.7 | 2170.23 | 8745.07 | 13638.9 | 0.45 | 1.73 | 20.238 | 20.591 | 1 | 1 | 2190 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3220729.8315 | 236917.5994 | 4671.1346 | 25748.7455 | 211168.8539 | 22277.7284 | 0.083441 | -172022.7133 | 172022.7133
C | Xist Rating 6553 | -28 | 1493.65 | 150.296 | 35.7 | 2167.06 | 8721.86 | 13579.3 | 0.44 | 1.72 | 20.228 | 20.44 | 1 | 1 | 2200 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3236829.169 | 238968.0592 | 4713.8907 | 25866.3197 | 213101.7395 | 22104.6059 | 0.083822 | -170685.9074 | 170685.9074
C | Xist Rating 6554 | -27.49 | 1506.33 | 150.296 | 35.7 | 2164.96 | 8728.07 | 13495.2 | 0.44 | 1.7 | 20.228 | 20.212 | 1 | 1 | 2210 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3261144.1968 | 241027.3248 | 4756.8417 | 25983.8939 | 215043.4309 | 21871.8178 | 0.084203 | -168888.3794 | 168888.3794
C | Xist Rating 6555 | -26.04 | 1543.29 | 150.296 | 35.7 | 2155.72 | 8699.48 | 13246 | 0.44 | 1.66 | 20.266 | 19.519 | 1 | 1 | 2220 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3326901.1188 | 243095.3963 | 4799.9874 | 26101.4681 | 216993.9283 | 21157.7917 | 0.084584 | -163374.8595 | 163374.8595
C | Xist Rating 6556 | -25.59 | 1553.46 | 150.296 | 35.7 | 2155.21 | 8722.86 | 13182.3 | 0.44 | 1.65 | 20.268 | 19.354 | 1 | 1 | 2230 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3348032.5266 | 245172.2737 | 4843.3279 | 26219.0422 | 218953.2315 | 20990.5245 | 0.084965 | -162083.2662 | 162083.2662
C | Xist Rating 6557 | -25.15 | 1565.3 | 150.296 | 35.7 | 2152.25 | 8710.3 | 13111.6 | 0.43 | 1.64 | 20.261 | 19.175 | 1 | 1 | 2240 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3368916.925 | 247257.9569 | 4886.8633 | 26336.6164 | 220921.3405 | 20787.9779 | 0.085346 | -160519.2554 | 160519.2554
C | Xist Rating 6558 | -24.66 | 1578.29 | 150.296 | 35.7 | 2149.27 | 8700.97 | 13033.9 | 0.42 | 1.63 | 20.257 | 18.978 | 1 | 1 | 2250 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3392171.3483 | 249352.446 | 4930.5934 | 26454.1906 | 222898.2554 | 20566.6952 | 0.085727 | -158810.5688 | 158810.5688
C | Xist Rating 6559 | -24.34 | 1584.93 | 150.296 | 35.7 | 2149.97 | 8732.25 | 12995.5 | 0.42 | 1.62 | 20.262 | 18.885 | 1 | 1 | 2260 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3407551.9521 | 251455.7409 | 4974.5182 | 26571.7648 | 224883.9761 | 20474.1413 | 0.086108 | -158095.8917 | 158095.8917
C | Xist Rating 6560 | -22.92 | 1624.69 | 150.296 | 35.7 | 2137.3 | 8651.8 | 12751.7 | 0.42 | 1.59 | 20.298 | 18.243 | 1 | 1 | 2270 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3472449.937 | 253567.8417 | 5018.6379 | 26689.339 | 226878.5028 | 19812.7784 | 0.086489 | -152989.0227 | 152989.0227
C | Xist Rating 6561 | -22.45 | 1636.46 | 150.296 | 35.7 | 2135.33 | 8654.42 | 12686.2 | 0.41 | 1.58 | 20.299 | 18.084 | 1 | 1 | 2280 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3494382.1318 | 255688.7484 | 5062.9524 | 26806.9131 | 228881.8352 | 19630.7758 | 0.08687 | -151583.6471 | 151583.6471
C | Xist Rating 6562 | -21.88 | 1650.41 | 150.296 | 35.7 | 2133.27 | 8663.22 | 12607 | 0.41 | 1.56 | 20.307 | 17.888 | 1 | 1 | 2290 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3520770.1407 | 257818.4609 | 5107.4617 | 26924.4873 | 230893.9735 | 19431.2974 | 0.087251 | -150043.3275 | 150043.3275
C | Xist Rating 6563 | -21.52 | 1659.76 | 150.296 | 35.7 | 2131.61 | 8663 | 12557.1 | 0.4 | 1.56 | 20.307 | 17.771 | 1 | 1 | 2300 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3537961.0136 | 259956.9792 | 5152.1657 | 27042.0615 | 232914.9177 | 19292.5892 | 0.087632 | -148972.2602 | 148972.2602
| Xist Rating 6564 | -21.15 | 1669.37 | 150.296 | 35.7 | 2129.96 | 8663.06 | 12507.5 | 0.4 | 1.55 | 20.293 | 17.658 | 1 | 1 | 2310 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3555691.3252 | 262104.3035 | 5197.0645 | 27159.6357 | 234944.6678 | 19178.3001 | 0.088013 | -148089.7496 | 148089.7496
| Xist Rating 6565 | -19.59 | 1710.17 | 150.296 | 35.7 | 2120.7 | 8638.73 | 12277.1 | 0.4 | 1.51 | 20.327 | 17.078 | 1 | 1 | 2320 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3626757.519 | 264260.4335 | 5242.1582 | 27277.2099 | 236983.2237 | 18581.0238 | 0.088394 | -143477.7406 | 143477.7406
| Xist Rating 6566 | -19.09 | 1721.98 | 150.296 | 35.7 | 2119.8 | 8658.45 | 12216.8 | 0.39 | 1.5 | 20.323 | 16.94 | 1 | 1 | 2330 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3650253.204 | 266425.3695 | 5287.4466 | 27394.784 | 239030.5854 | 18419.9629 | 0.088775 | -142234.0709 | 142234.0709
| Xist Rating 6567 | -18.67 | 1733.77 | 150.296 | 35.7 | 2117.2 | 8649.69 | 12157.1 | 0.39 | 1.49 | 20.316 | 16.803 | 1 | 1 | 2340 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3670737.844 | 268599.1113 | 5332.9298 | 27512.3582 | 241086.753 | 18280.955 | 0.089156 | -141160.6891 | 141160.6891
| Xist Rating 6568 | -18.3 | 1744.44 | 150.296 | 35.7 | 2114.46 | 8634.48 | 12104.7 | 0.38 | 1.49 | 20.316 | 16.685 | 1 | 1 | 2350 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3688548.6024 | 270781.6589 | 5378.6078 | 27629.9324 | 243151.7265 | 18140.5633 | 0.089537 | -140076.6216 | 140076.6216
| Xist Rating 6569 | -17.83 | 1757.48 | 150.296 | 35.7 | 2111.38 | 8621.36 | 12039.9 | 0.38 | 1.48 | 20.311 | 16.538 | 1 | 1 | 2360 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3710708.1224 | 272973.0124 | 5424.4805 | 27747.5066 | 245225.5058 | 17991.1636 | 0.089918 | -138922.9963 | 138922.9963
| Xist Rating 6570 | -16.42 | 1794.87 | 150.296 | 35.7 | 2103.56 | 8606.18 | 11846.8 | 0.38 | 1.45 | 20.34 | 16.076 | 1 | 1 | 2370 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3775616.7372 | 275173.1718 | 5470.5481 | 27865.0808 | 247308.091 | 17516.0077 | 0.090299 | -135253.9682 | 135253.9682
| Xist Rating 6571 | -16 | 1806.9 | 150.296 | 35.7 | 2100.41 | 8587.32 | 11791.2 | 0.37 | 1.44 | 20.332 | 15.956 | 1 | 1 | 2380 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3795230.829 | 277382.137 | 5516.8105 | 27982.6549 | 249399.482 | 17372.8374 | 0.09068 | -134148.4454 | 134148.4454
| Xist Rating 6572 | -15.51 | 1819.49 | 150.296 | 35.7 | 2098.76 | 8597.15 | 11730 | 0.37 | 1.43 | 20.33 | 15.818 | 1 | 1 | 2390 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 3818672.8324 | 279599.9081 | 5563.2676 | 28100.2291 | 251499.6789 | 17232.8174 | 0.091061 | -133067.2483 | 133067.2483
C | Xist Rating 6576 | -5.73 | 2089.3 | 150.296 | 35.7 | 2041.21 | 8427.77 | 10537.9 | 0.39 | 1.25 | 20.36 | 13.209 | 1 | 1 | 2430 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4264700.053 | 288559.0509 | 5751.0441 | 28570.5259 | 259988.5251 | 14582.4249 | 0.092585 | -112601.6201 | 112601.6201
C | Xist Rating 6577 | -5.71 | 2090.67 | 150.296 | 35.7 | 2040.81 | 8420.84 | 10537.9 | 0.38 | 1.25 | 20.353 | 13.22 | 1 | 1 | 2440 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4266660.2427 | 290820.8513 | 5798.4752 | 28688.1 | 262132.7513 | 14574.8486 | 0.092966 | -112543.1174 | 112543.1174
C | Xist Rating 6578 | -5.69 | 2092 | 150.296 | 35.7 | 2040.49 | 8415.5 | 10537.9 | 0.38 | 1.25 | 20.346 | 13.23 | 1 | 1 | 2450 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4268705.08 | 293091.4575 | 5846.1011 | 28805.6742 | 264285.7833 | 14588.4083 | 0.093347 | -112647.8216 | 112647.8216
C | Xist Rating 6579 | -5.66 | 2093.47 | 150.296 | 35.7 | 2040.48 | 8415.32 | 10537.9 | 0.37 | 1.25 | 20.338 | 13.241 | 1 | 1 | 2460 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4271683.6656 | 295370.8696 | 5893.9217 | 28923.2484 | 266447.6212 | 14580.5357 | 0.093728 | -112587.0317 | 112587.0317
C | Xist Rating 6580 | -5.65 | 2094.83 | 150.296 | 35.7 | 2040.03 | 8407.66 | 10537.9 | 0.36 | 1.25 | 20.378 | 13.252 | 1 | 1 | 2470 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4273516.0449 | 297659.0875 | 5941.9372 | 29040.8226 | 268618.2649 | 14574.409 | 0.094109 | -112539.7229 | 112539.7229
C | Xist Rating 6581 | -5.64 | 2096.17 | 150.296 | 35.7 | 2039.5 | 8398.59 | 10537.9 | 0.36 | 1.25 | 20.371 | 13.262 | 1 | 1 | 2480 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4275138.715 | 299956.1113 | 5990.1474 | 29158.3968 | 270797.7146 | 14587.8022 | 0.09449 | -112643.1418 | 112643.1418
C | Xist Rating 6582 | -5.63 | 2097.57 | 150.296 | 35.6 | 2038.9 | 8388.43 | 10537.9 | 0.35 | 1.25 | 20.366 | 13.273 | 1 | 1 | 2490 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4276735.473 | 302261.941 | 6038.5525 | 29275.9709 | 272985.97 | 14579.5808 | 0.094871 | -112579.6586 | 112579.6586
C | Xist Rating 6583 | -5.61 | 2098.56 | 150.296 | 35.6 | 2039.15 | 8392.7 | 10537.9 | 0.35 | 1.25 | 20.363 | 13.282 | 1 | 1 | 2500 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4279278.624 | 304576.5765 | 6087.1523 | 29393.5451 | 275183.0313 | 14592.0048 | 0.095252 | -112675.5932 | 112675.5932
C | Xist Rating 6584 | -5.62 | 2100.41 | 150.296 | 35.6 | 2037.58 | 8366.27 | 10537.8 | 0.34 | 1.25 | 20.357 | 13.295 | 1 | 1 | 2510 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4279753.4078 | 306900.0178 | 6135.9469 | 29511.1193 | 277388.8985 | 14585.5601 | 0.095633 | -112625.8285 | 112625.8285
C | Xist Rating 6585 | -5.61 | 2101.86 | 150.296 | 35.6 | 2036.99 | 8356.21 | 10537.8 | 0.34 | 1.25 | 20.394 | 13.306 | 1 | 1 | 2520 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4281467.8014 | 309232.265 | 6184.9363 | 29628.6935 | 279603.5716 | 14601.507 | 0.096014 | -112748.9669 | 112748.9669
C | Xist Rating 6586 | -5.6 | 2103.2 | 150.296 | 35.6 | 2036.51 | 8348.16 | 10537.8 | 0.33 | 1.25 | 20.388 | 13.316 | 1 | 1 | 2530 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4283187.832 | 311573.3181 | 6234.1205 | 29746.2677 | 281827.0505 | 14591.6475 | 0.096395 | -112672.8342 | 112672.8342
C | Xist Rating 6587 | -5.58 | 2104.35 | 150.296 | 35.6 | 2036.41 | 8346.48 | 10537.8 | 0.33 | 1.25 | 20.384 | 13.325 | 1 | 1 | 2540 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4285319.3835 | 313923.177 | 6283.4995 | 29863.8418 | 284059.3352 | 14603.8595 | 0.096776 | -112767.1322 | 112767.1322
C | Xist Rating 6588 | -5.58 | 2105.9 | 150.296 | 35.6 | 2035.47 | 8330.81 | 10537.8 | 0.32 | 1.25 | 20.38 | 13.336 | 1 | 1 | 2550 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4286496.273 | 316281.8418 | 6333.0732 | 29981.416 | 286300.4258 | 14594.8524 | 0.097157 | -112697.5818 | 112697.5818
C | Xist Rating 6589 | -5.53 | 2107.34 | 150.296 | 35.6 | 2035.75 | 8335.55 | 10537.7 | 0.32 | 1.25 | 20.371 | 13.347 | 1 | 1 | 2560 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4290017.405 | 318649.3125 | 6382.8418 | 30098.9902 | 288550.3223 | 14608.8687 | 0.097538 | -112805.8118 | 112805.8118
C | Xist Rating 6590 | -5.52 | 2108.73 | 150.296 | 35.6 | 2035.37 | 8329.17 | 10537.7 | 0.31 | 1.25 | 20.367 | 13.357 | 1 | 1 | 2570 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4292045.7801 | 321025.589 | 6432.8051 | 30216.5644 | 290809.0246 | 14598.5656 | 0.097919 | -112726.2538 | 112726.2538
C | Xist Rating 6591 | -5.49 | 2110.1 | 150.296 | 35.6 | 2035.39 | 8329.53 | 10537.7 | 0.31 | 1.25 | 20.413 | 13.367 | 1 | 1 | 2580 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4294876.439 | 323410.6713 | 6482.9633 | 30334.1386 | 293076.5328 | 14613.4298 | 0.0983 | -112841.0315 | 112841.0315
C | Xist Rating 6592 | -5.46 | 2111.46 | 150.296 | 35.6 | 2035.34 | 8328.68 | 10537.7 | 0.3 | 1.25 | 20.419 | 13.378 | 1 | 1 | 2590 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4297538.9964 | 325804.5595 | 6533.3162 | 30451.7127 | 295352.8468 | 14604.2002 | 0.098681 | -112769.7625 | 112769.7625
C | Xist Rating 6593 | -5.45 | 2112.64 | 150.296 | 35.6 | 2035.15 | 8325.51 | 10537.6 | 0.3 | 1.25 | 20.414 | 13.387 | 1 | 1 | 2600 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4299539.296 | 328207.2536 | 6583.8639 | 30569.2869 | 297637.9667 | 14616.1177 | 0.099062 | -112861.7862 | 112861.7862
C | Xist Rating 6594 | -5.44 | 2114.32 | 150.296 | 35.6 | 2034.38 | 8312.67 | 10537.6 | 0.29 | 1.25 | 20.412 | 13.398 | 1 | 1 | 2610 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4301330.3216 | 330618.7536 | 6634.6064 | 30686.8611 | 299931.8925 | 14606.3356 | 0.099443 | -112786.2519 | 112786.2519
C | Xist Rating 6595 | -5.41 | 2115.72 | 150.296 | 35.6 | 2034.25 | 8310.53 | 10537.6 | 0.29 | 1.25 | 20.413 | 13.409 | 1 | 1 | 2620 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4303903.41 | 333039.0593 | 6685.5437 | 30804.4353 | 302234.6241 | 14620.4465 | 0.099824 | -112895.2127 | 112895.2127
C | Xist Rating 6596 | -5.38 | 2117.15 | 150.296 | 35.6 | 2034.07 | 8307.54 | 10537.6 | 0.29 | 1.25 | 20.451 | 13.419 | 1 | 1 | 2630 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4306431.3005 | 335468.171 | 6736.6758 | 30922.0095 | 304546.1615 | 14634.7842 | 0.10021 | -113005.9241 | 113005.9241
C | Xist Rating 6597 | -5.34 | 2118.39 | 150.296 | 35.6 | 2034.31 | 8311.56 | 10537.6 | 0.28 | 1.25 | 20.453 | 13.428 | 1 | 1 | 2640 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4309461.9609 | 337906.0885 | 6788.0027 | 31039.5836 | 306866.5048 | 14622.6543 | 0.10059 | -112912.2602 | 112912.2602
C | Xist Rating 6598 | -5.31 | 2119.9 | 150.296 | 35.6 | 2034.07 | 8307.55 | 10537.6 | 0.28 | 1.25 | 20.451 | 13.439 | 1 | 1 | 2650 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4312024.993 | 340352.8118 | 6839.5243 | 31157.1578 | 309195.654 | 14636.5783 | 0.10097 | -113019.7777 | 113019.7777
C | Xist Rating 6599 | -5.26 | 2121.24 | 150.296 | 35.6 | 2034.45 | 8313.83 | 10537.6 | 0.27 | 1.25 | 20.451 | 13.449 | 1 | 1 | 2660 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4315556.718 | 342808.3411 | 6891.2408 | 31274.732 | 311533.6091 | 14625.1456 | 0.10135 | -112931.4975 | 112931.4975
C | Xist Rating 6600 | -5.22 | 2122.62 | 150.296 | 35.6 | 2034.51 | 8314.85 | 10537.6 | 0.27 | 1.25 | 20.453 | 13.459 | 1 | 1 | 2670 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4318491.6162 | 345272.6761 | 6943.152 | 31392.3062 | 313880.3699 | 14638.0703 | 0.10173 | -113031.2988 | 113031.2988
C | Xist Rating 6601 | -5.18 | 2124.04 | 150.296 | 35.6 | 2034.73 | 8318.42 | 10537.7 | 0.27 | 1.25 | 20.491 | 13.469 | 1 | 1 | 2680 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4321847.9092 | 347745.8171 | 6995.258 | 31509.8804 | 316235.9367 | 14652.1632 | 0.10211 | -113140.1202 | 113140.1202
C | Xist Rating 6602 | -5.13 | 2125.42 | 150.296 | 35.6 | 2035.14 | 8325.35 | 10537.6 | 0.26 | 1.25 | 20.492 | 13.479 | 1 | 1 | 2690 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4325527.2588 | 350227.7638 | 7047.5588 | 31627.4545 | 318600.3093 | 14640.3518 | 0.10249 | -113048.9156 | 113048.9156
C | Xist Rating 6603 | -5.04 | 2126.62 | 150.296 | 35.6 | 2036.63 | 8350.36 | 10537.5 | 0.26 | 1.25 | 20.494 | 13.488 | 1 | 1 | 2700 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4331138.0906 | 352718.5165 | 7100.0544 | 31745.0287 | 320973.4878 | 14652.1494 | 0.10287 | -113140.0139 | 113140.0139
C | Xist Rating 6604 | -5.02 | 2128.27 | 150.296 | 35.6 | 2036.16 | 8342.59 | 10537.5 | 0.26 | 1.25 | 20.488 | 13.499 | 1 | 1 | 2710 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 25 | E | Rod | 4333498.2432 | 355218.075 | 7152.7448 | 31862.6029 | 323355.4721 | 14665.7718 | 0.10325 | -113245.2027 | 113245.2027
C | Xist Rating 6605 | -4.99 | 2129.62 | 150.296 | 35.6 | 2036.12 | 8341.92 | 10537.5 | 0.25 | 1.25 | 20.483 | 13.508 | 1 | 1 | 2720 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4336161.8744 | 357726.4393 | 7205.63 | 31980.1771 | 325746.2623 | 14652.3741 | 0.10363 | -113141.7488 | 113141.7488
C | Xist Rating 6606 | -5 | 2130.94 | 150.297 | 35.6 | 2035.14 | 8325.43 | 10537.5 | 0.25 | 1.25 | 20.514 | 13.518 | 1 | 1 | 2730 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4336761.2316 | 360243.6096 | 7258.71 | 32097.7513 | 328145.8583 | 14666.0028 | 0.10402 | -113246.9862 | 113246.9862
C | Xist Rating 6607 | -4.99 | 2132.22 | 150.297 | 35.6 | 2034.59 | 8316.3 | 10537.5 | 0.25 | 1.25 | 20.51 | 13.527 | 1 | 1 | 2740 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4338193.4898 | 362769.5856 | 7311.9847 | 32215.3254 | 330554.2602 | 14677.5253 | 0.1044 | -113335.9599 | 113335.9599
C | Xist Rating 6608 | -5.02 | 2133.77 | 150.297 | 35.6 | 2033.17 | 8292.64 | 10537.5 | 0.25 | 1.25 | 20.503 | 13.537 | 1 | 1 | 2750 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4338317.1509 | 365304.3676 | 7365.4543 | 32332.8996 | 332971.4679 | 14689.993 | 0.10478 | -113432.2317 | 113432.2317
C | Xist Rating 6609 | -5 | 2135.2 | 150.297 | 35.6 | 2032.73 | 8285.3 | 10537.5 | 0.24 | 1.25 | 20.508 | 13.547 | 1 | 1 | 2760 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4340285.096 | 367847.9553 | 7419.1186 | 32450.4738 | 335397.4815 | 14677.4585 | 0.10516 | -113335.444 | 113335.444
C | Xist Rating 6610 | -4.99 | 2136.43 | 150.297 | 35.6 | 2032.34 | 8278.75 | 10537.5 | 0.24 | 1.25 | 20.51 | 13.556 | 1 | 1 | 2770 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4341952.1462 | 370400.349 | 7472.9777 | 32568.048 | 337832.301 | 14689.0708 | 0.10554 | -113425.1112 | 113425.1112
C | Xist Rating 6611 | -5 | 2137.98 | 150.297 | 35.6 | 2031.21 | 8260.08 | 10537.5 | 0.24 | 1.25 | 20.548 | 13.566 | 1 | 1 | 2780 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4342686.3558 | 372961.5485 | 7527.0316 | 32685.6222 | 340275.9263 | 14702.7987 | 0.10592 | -113531.1144 | 113531.1144
C | Xist Rating 6612 | -5 | 2139.39 | 150.297 | 35.6 | 2030.56 | 8249.34 | 10537.5 | 0.23 | 1.25 | 20.548 | 13.576 | 1 | 1 | 2790 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4344159.7584 | 375531.5538 | 7581.2803 | 32803.1963 | 342728.3575 | 14689.6968 | 0.1063 | -113429.9445 | 113429.9445
C | Xist Rating 6613 | -5 | 2140.36 | 150.297 | 35.6 | 2030.22 | 8243.75 | 10537.5 | 0.23 | 1.25 | 20.544 | 13.584 | 1 | 1 | 2800 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4345401.6792 | 378110.365 | 7635.7238 | 32920.7705 | 345189.5945 | 14700.0077 | 0.10668 | -113509.5629 | 113509.5629
C | Xist Rating 6614 | -4.99 | 2142.11 | 150.297 | 35.6 | 2029.34 | 8229.27 | 10537.5 | 0.23 | 1.25 | 20.549 | 13.595 | 1 | 1 | 2810 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4347069.5074 | 380697.9821 | 7690.3621 | 33038.3447 | 347659.6374 | 14713.6941 | 0.10706 | -113615.2453 | 113615.2453
C | Xist Rating 6615 | -4.97 | 2143.58 | 150.297 | 35.6 | 2029.04 | 8224.34 | 10537.5 | 0.23 | 1.25 | 20.555 | 13.605 | 1 | 1 | 2820 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4349409.5632 | 383294.405 | 7745.1952 | 33155.9189 | 350138.4862 | 14726.372 | 0.10744 | -113713.1412 | 113713.1412
C | Xist Rating 6616 | -4.9 | 2144.95 | 150.297 | 35.6 | 2029.7 | 8235.11 | 10537.6 | 0.22 | 1.25 | 20.608 | 13.614 | 1 | 1 | 2830 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4353605.015 | 385899.6338 | 7800.223 | 33273.4931 | 352626.1408 | 14713.242 | 0.10783 | -113611.7545 | 113611.7545
C | Xist Rating 6617 | -4.92 | 2146.27 | 150.297 | 35.6 | 2028.71 | 8218.88 | 10537.6 | 0.22 | 1.25 | 20.602 | 13.623 | 1 | 1 | 2840 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4354159.4117 | 388513.6685 | 7855.4457 | 33391.0673 | 355122.6012 | 14724.4527 | 0.10821 | -113698.3205 | 113698.3205
C | Xist Rating 6618 | -4.85 | 2147.72 | 150.297 | 35.6 | 2029.43 | 8230.68 | 10537.6 | 0.22 | 1.25 | 20.611 | 13.633 | 1 | 1 | 2850 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4358647.3996 | 391136.509 | 7910.8631 | 33508.6414 | 357627.8675 | 14737.1222 | 0.10859 | -113796.1516 | 113796.1516
C | Xist Rating 6619 | -4.74 | 2149.12 | 150.297 | 35.6 | 2030.97 | 8255.99 | 10537.7 | 0.22 | 1.25 | 20.632 | 13.643 | 1 | 1 | 2860 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4364798.2464 | 393768.1553 | 7966.4753 | 33626.2156 | 360141.9397 | 14750.132 | 0.10897 | -113896.6098 | 113896.6098
C | Xist Rating 6620 | -4.73 | 2150.31 | 150.297 | 35.6 | 2030.76 | 8252.51 | 10537.6 | 0.21 | 1.25 | 20.631 | 13.651 | 1 | 1 | 2870 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4366763.5356 | 396408.6075 | 8022.2824 | 33743.7898 | 362664.8177 | 14733.9052 | 0.10935 | -113771.3106 | 113771.3106
C | Xist Rating 6621 | -4.38 | 2151.82 | 150.297 | 35.6 | 2037.34 | 8362.14 | 10537.8 | 0.21 | 1.25 | 20.727 | 13.661 | 1 | 1 | 2880 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4383988.9588 | 399057.8656 | 8078.2842 | 33861.364 | 365196.5016 | 14748.8348 | 0.10973 | -113886.5928 | 113886.5928
C | Xist Rating 6622 | -3.81 | 2153.16 | 150.297 | 35.6 | 2049.04 | 8562.68 | 10538 | 0.21 | 1.25 | 20.788 | 13.671 | 1 | 1 | 2890 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4411910.9664 | 401715.9295 | 8134.4807 | 33978.9382 | 367736.9914 | 14762.8303 | 0.11011 | -113994.6624 | 113994.6624
C | Xist Rating 6623 | -3.33 | 2154.55 | 150.297 | 35.6 | 2058.79 | 8735.53 | 10538.1 | 0.2 | 1.25 | 20.839 | 13.682 | 1 | 1 | 2900 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4435765.9945 | 404382.7993 | 8190.8721 | 34096.5123 | 370286.287 | 14750.5139 | 0.11049 | -113899.5582 | 113899.5582
C | Xist Rating 6624 | -3.78 | 2156.09 | 150.297 | 35.6 | 2048.14 | 8546.98 | 10538 | 0.2 | 1.25 | 20.778 | 13.691 | 1 | 1 | 2910 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4415974.1726 | 407058.4749 | 8247.4583 | 34214.0865 | 372844.3884 | 14760.1372 | 0.11087 | -113973.867 | 113973.867
C | Xist Rating 6625 | -3.1 | 2157.48 | 150.297 | 35.6 | 2062.15 | 8796.43 | 10538 | 0.2 | 1.25 | 20.85 | 13.701 | 1 | 1 | 2920 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4449047.382 | 409742.9564 | 8304.2393 | 34331.6607 | 375411.2958 | 14774.2697 | 0.11125 | -114082.9944 | 114082.9944
C | Xist Rating 6626 | -2.68 | 2158.86 | 150.297 | 35.6 | 2070.63 | 8952.7 | 10538.1 | 0.19 | 1.25 | 20.936 | 13.711 | 1 | 1 | 2930 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4470200.2818 | 412436.2438 | 8361.215 | 34449.2349 | 377987.0089 | 14761.2863 | 0.11164 | -113982.7401 | 113982.7401
C | Xist Rating 6627 | -2.39 | 2160.23 | 150.297 | 35.6 | 2076.19 | 9057.69 | 10538 | 0.19 | 1.25 | 20.964 | 13.72 | 1 | 1 | 2940 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4485047.9237 | 415138.337 | 8418.3855 | 34566.8091 | 380571.528 | 14773.1169 | 0.11202 | -114074.0931 | 114074.0931
C | Xist Rating 6628 | -2.21 | 2161.64 | 150.297 | 35.6 | 2079.47 | 9120.41 | 10538 | 0.19 | 1.25 | 20.983 | 13.73 | 1 | 1 | 2950 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4495065.5308 | 417849.2361 | 8475.7509 | 34684.3832 | 383164.8528 | 14785.7647 | 0.1124 | -114171.7559 | 114171.7559
C | Xist Rating 6629 | -1.48 | 2163.01 | 150.297 | 35.5 | 2094.73 | 9421.59 | 10537.8 | 0.19 | 1.25 | 21.031 | 13.74 | 1 | 1 | 2960 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4530921.9373 | 420568.941 | 8533.311 | 34801.9574 | 385766.9836 | 14799.1468 | 0.11278 | -114275.0889 | 114275.0889
C | Xist Rating 6630 | -1.48 | 2164.4 | 150.297 | 35.5 | 2094.07 | 9408.25 | 10537.8 | 0.18 | 1.25 | 21.028 | 13.749 | 1 | 1 | 2970 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4532405.108 | 423297.4518 | 8591.0659 | 34919.5316 | 388377.9202 | 14782.2141 | 0.11316 | -114144.3393 | 114144.3393
C | Xist Rating 6631 | -1.47 | 2165.62 | 150.297 | 35.5 | 2093.57 | 9398.25 | 10537.8 | 0.18 | 1.25 | 21.063 | 13.757 | 1 | 1 | 2980 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4533877.0634 | 426034.7684 | 8649.0156 | 35037.1058 | 390997.6626 | 14793.0603 | 0.11354 | -114228.0905 | 114228.0905
C | Xist Rating 6632 | -1.46 | 2167.18 | 150.297 | 35.5 | 2092.81 | 9382.96 | 10537.8 | 0.18 | 1.25 | 21.057 | 13.767 | 1 | 1 | 2990 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4535495.9758 | 428780.8909 | 8707.16 | 35154.68 | 393626.211 | 14805 | 0.11392 | -114320.2856 | 114320.2856
C | Xist Rating 6633 | -1.45 | 2168.61 | 150.297 | 35.5 | 2092.12 | 9369.12 | 10537.9 | 0.18 | 1.25 | 21.051 | 13.776 | 1 | 1 | 3000 | 152.4 | 2 | 4.2 | 19.05 | 1.3333 | 24 | E | Rod | 4536992.3532 | 431535.8193 | 8765.4993 | 35272.2541 | 396263.5651 | 14815.9002 | 0.1143 | -114404.4542 | 114404.4542
C | Xist Rating 6634 | -87.92 | 220.506 | 150.302 | 35.9 | 2365.34 | 7087.12 | 58745.8 | 2.47 | 10.95 | 22.836 | 546.406 | 1 | 1 | 1000 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 521571.662 | 57114.9579 | 973.9444 | 12037.3566 | 45077.6013 | 569970.0979 | 0.038101 | -4401158.0134 | 4401158.0134
C | Xist Rating 6635 | -87.81 | 222.788 | 150.302 | 35.9 | 2363.18 | 7075.52 | 58284.2 | 2.45 | 10.85 | 22.908 | 536.137 | 1 | 1 | 1010 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 526488.1458 | 58141.3912 | 993.5206 | 12157.7301 | 45983.6611 | 559318.35 | 0.038482 | -4318908.0399 | 4318908.0399
C | Xist Rating 6636 | -86.9 | 240.096 | 150.302 | 35.9 | 2356.72 | 7077.11 | 54967 | 2.46 | 10.07 | 22.957 | 464.612 | 1 | 1 | 1020 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 565839.0451 | 59176.8401 | 1013.2917 | 12278.1037 | 46898.7364 | 485080.8933 | 0.038863 | -3745666.0772 | 3745666.0772
C | Xist Rating 6637 | -86.74 | 244.805 | 150.301 | 35.9 | 2339.9 | 6942.19 | 54178.4 | 2.38 | 9.89 | 22.423 | 448.996 | 1 | 1 | 1030 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 572819.2195 | 60221.3045 | 1033.2576 | 12398.4773 | 47822.8272 | 468745.5459 | 0.039244 | -3619528.8547 | 3619528.8547
C | Xist Rating 6638 | -86.66 | 247.162 | 150.301 | 35.9 | 2333.82 | 6896.19 | 53793.6 | 2.33 | 9.8 | 22.297 | 441.517 | 1 | 1 | 1040 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 576831.6188 | 61274.7844 | 1053.4182 | 12518.8508 | 48755.9336 | 460936.5863 | 0.039625 | -3559230.1387 | 3559230.1387
C | Xist Rating 6639 | -86.46 | 251.75 | 150.3 | 35.9 | 2326.11 | 6843.42 | 53042.6 | 2.3 | 9.63 | 22.212 | 426.857 | 1 | 1 | 1050 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 585598.1925 | 62337.2799 | 1073.7737 | 12639.2244 | 49698.0555 | 445694.8026 | 0.040006 | -3441537.1248 | 3441537.1248
C | Xist Rating 6640 | -86.31 | 254.087 | 150.3 | 35.9 | 2330.32 | 6887.13 | 52676.7 | 2.26 | 9.54 | 22.189 | 419.922 | 1 | 1 | 1060 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 592104.0178 | 63408.7908 | 1094.3239 | 12759.598 | 50649.1928 | 438471.0307 | 0.040387 | -3385757.0735 | 3385757.0735
C | Xist Rating 6641 | -85.43 | 272.691 | 150.3 | 35.9 | 2311.95 | 6785.49 | 49856.9 | 2.24 | 8.9 | 21.979 | 367.402 | 1 | 1 | 1070 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 630447.9574 | 64489.3173 | 1115.0689 | 12879.9715 | 51609.3458 | 383907.7258 | 0.040768 | -2964433.696 | 2964433.696
C | Xist Rating 6642 | -85.19 | 276.2 | 150.299 | 35.9 | 2321.11 | 6875.55 | 49380.5 | 2.18 | 8.79 | 21.881 | 359.159 | 1 | 1 | 1080 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 641090.582 | 65578.8593 | 1136.0087 | 13000.3451 | 52578.5142 | 375295.2684 | 0.041149 | -2897930.5826 | 2897930.5826
C | Xist Rating 6643 | -84.92 | 280.868 | 150.299 | 35.9 | 2324.46 | 6919.15 | 48761.2 | 2.12 | 8.65 | 21.719 | 348.56 | 1 | 1 | 1090 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 652866.4313 | 66677.4168 | 1157.1433 | 13120.7187 | 53556.6981 | 364228.6803 | 0.04153 | -2812477.323 | 2812477.323
C | Xist Rating 6644 | -84.69 | 284.345 | 150.299 | 35.9 | 2332.62 | 7002.79 | 48308 | 2.09 | 8.55 | 21.721 | 340.911 | 1 | 1 | 1100 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 663268.8339 | 67784.9898 | 1178.4727 | 13241.0922 | 54543.8976 | 356273.9242 | 0.041911 | -2751052.8046 | 2751052.8046
C | Xist Rating 6645 | -84.57 | 286.87 | 150.298 | 35.8 | 2330.13 | 6987.58 | 48010.9 | 2 | 8.49 | 21.389 | 336.21 | 1 | 1 | 1110 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 668444.3931 | 68901.5784 | 1199.9969 | 13361.4658 | 55540.1126 | 351281.9883 | 0.042292 | -2712506.3989 | 2712506.3989
C | Xist Rating 6646 | -83.49 | 307.581 | 150.299 | 35.9 | 2326.46 | 7020.64 | 45448.3 | 2.05 | 7.92 | 21.677 | 294.183 | 1 | 1 | 1120 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 715574.8933 | 70027.1825 | 1221.7158 | 13481.8394 | 56545.3431 | 307739.5208 | 0.042673 | -2376283.0066 | 2376283.0066
C | Xist Rating 6647 | -83.36 | 310.059 | 150.298 | 35.8 | 2326.7 | 7030.01 | 45189.2 | 1.99 | 7.86 | 21.464 | 290.392 | 1 | 1 | 1130 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 721414.2753 | 71161.8021 | 1243.6296 | 13602.2129 | 57559.5891 | 303735.1438 | 0.043054 | -2345362.2688 | 2345362.2688
C | Xist Rating 6648 | -83.13 | 314.798 | 150.298 | 35.8 | 2323.91 | 7018.75 | 44681.5 | 1.93 | 7.75 | 21.271 | 282.795 | 1 | 1 | 1140 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 731562.2202 | 72305.4372 | 1265.7381 | 13722.5865 | 58582.8507 | 295779.9744 | 0.043435 | -2283934.5593 | 2283934.5593
C | Xist Rating 6649 | -82.88 | 319.474 | 150.298 | 35.8 | 2325.11 | 7044.05 | 44186.3 | 1.89 | 7.64 | 21.069 | 275.447 | 1 | 1 | 1150 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 742812.1921 | 73458.0878 | 1288.0414 | 13842.9601 | 59615.1278 | 288103.9503 | 0.043816 | -2224662.3365 | 2224662.3365
C | Xist Rating 6650 | -82.66 | 324.228 | 150.297 | 35.8 | 2321.7 | 7027.02 | 43703.3 | 1.84 | 7.53 | 20.899 | 268.453 | 1 | 1 | 1160 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 752760.1476 | 74619.754 | 1310.5395 | 13963.3336 | 60656.4203 | 280787.5014 | 0.044197 | -2168166.6572 | 2168166.6572
C | Xist Rating 6651 | -81.7 | 342.819 | 150.298 | 35.8 | 2317.7 | 7048.54 | 41832.4 | 1.86 | 7.13 | 21.052 | 241.472 | 1 | 1 | 1170 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 794551.5963 | 75790.4356 | 1333.2324 | 14083.7072 | 61706.7285 | 252821.8581 | 0.044578 | -1952223.3729 | 1952223.3729
C | Xist Rating 6652 | -81.57 | 344.151 | 150.297 | 35.8 | 2327.27 | 7141.37 | 41724.4 | 1.81 | 7.11 | 20.968 | 240.161 | 1 | 1 | 1180 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 800932.2978 | 76970.1328 | 1356.1201 | 14204.0808 | 62766.0521 | 251414.2215 | 0.044959 | -1941353.9755 | 1941353.9755
C | Xist Rating 6653 | -81.13 | 353.487 | 150.297 | 35.8 | 2319.93 | 7101.15 | 40885.6 | 1.76 | 6.92 | 20.793 | 228.886 | 1 | 1 | 1190 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 820065.0959 | 78158.8456 | 1379.2026 | 14324.4543 | 63834.3912 | 239649.8115 | 0.04534 | -1850512.3201 | 1850512.3201
C | Xist Rating 6654 | -80.92 | 355.858 | 150.297 | 35.8 | 2331.62 | 7219.15 | 40681.8 | 1.72 | 6.88 | 20.835 | 226.252 | 1 | 1 | 1200 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 829725.63 | 79356.5738 | 1402.4799 | 14444.8279 | 64911.7459 | 236889.9584 | 0.045721 | -1829201.4663 | 1829201.4663
C | Xist Rating 6655 | -80.68 | 360.681 | 150.297 | 35.8 | 2329.73 | 7215.65 | 40280.9 | 1.67 | 6.8 | 20.678 | 221.128 | 1 | 1 | 1210 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 840289.3461 | 80563.3176 | 1425.9519 | 14565.2015 | 65998.1161 | 231514.0331 | 0.046102 | -1787689.996 | 1787689.996
C | Xist Rating 6656 | -79.67 | 381.747 | 150.297 | 35.8 | 2317.68 | 7167.04 | 38537.8 | 1.67 | 6.43 | 20.684 | 198.835 | 1 | 1 | 1220 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 884767.387 | 81779.0768 | 1449.6188 | 14685.575 | 67093.5018 | 208378.8148 | 0.046483 | -1609045.9725 | 1609045.9725
C | Xist Rating 6657 | -79.37 | 386.42 | 150.297 | 35.8 | 2323.66 | 7239.03 | 38183.3 | 1.65 | 6.35 | 20.704 | 194.566 | 1 | 1 | 1230 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 897908.6972 | 83003.8516 | 1473.4804 | 14805.9486 | 68197.903 | 203939.9599 | 0.046864 | -1574770.3122 | 1574770.3122
C | Xist Rating 6658 | -79.12 | 391.234 | 150.296 | 35.8 | 2323.58 | 7252.86 | 37835.6 | 1.6 | 6.28 | 20.594 | 190.497 | 1 | 1 | 1240 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 909063.4977 | 84237.6419 | 1497.5369 | 14926.3221 | 69311.3198 | 199662.3011 | 0.047245 | -1541739.3644 | 1541739.3644
C | Xist Rating 6659 | -78.95 | 393.749 | 150.296 | 35.8 | 2328.88 | 7312.12 | 37664.5 | 1.56 | 6.24 | 20.524 | 188.587 | 1 | 1 | 1250 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 916994.1711 | 85480.4478 | 1521.7881 | 15046.6957 | 70433.7521 | 197641.2645 | 0.047626 | -1526133.4556 | 1526133.4556
C | Xist Rating 6660 | -78.58 | 400.783 | 150.296 | 35.8 | 2329.02 | 7335.65 | 37161.5 | 1.53 | 6.14 | 20.48 | 182.723 | 1 | 1 | 1260 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 933431.6227 | 86732.2691 | 1546.2341 | 15167.0693 | 71565.1999 | 191527.284 | 0.048007 | -1478922.919 | 1478922.919
C | Xist Rating 6661 | -77.59 | 420.732 | 150.296 | 35.8 | 2321.68 | 7327.02 | 35777.7 | 1.54 | 5.85 | 20.545 | 166.863 | 1 | 1 | 1270 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 976805.0698 | 87993.106 | 1570.8749 | 15287.4428 | 72705.6632 | 175088.1018 | 0.048388 | -1351983.9111 | 1351983.9111
C | Xist Rating 6662 | -77.37 | 425.614 | 150.296 | 35.8 | 2319.41 | 7319.04 | 35477.4 | 1.5 | 5.79 | 20.429 | 163.686 | 1 | 1 | 1280 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 987173.3677 | 89262.9584 | 1595.7105 | 15407.8164 | 73855.142 | 171745.8399 | 0.048769 | -1326175.8511 | 1326175.8511
C | Xist Rating 6663 | -77.12 | 430.444 | 150.296 | 35.8 | 2319.16 | 7331.05 | 35182.8 | 1.47 | 5.73 | 20.39 | 160.583 | 1 | 1 | 1290 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 27 | E | Rod | 998268.507 | 90541.8263 | 1620.7408 | 15528.19 | 75013.6364 | 168498.3617 | 0.04915 | -1301099.6848 | 1301099.6848
C | Xist Rating 6664 | -76.75 | 437.456 | 150.296 | 35.8 | 2320.16 | 7363.05 | 34751.1 | 1.45 | 5.64 | 20.376 | 156.001 | 1 | 1 | 1300 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1014967.913 | 91829.7098 | 1645.966 | 15648.5635 | 76181.1462 | 163728.4511 | 0.049531 | -1264267.6996 | 1264267.6996
C | Xist Rating 6665 | -76.51 | 441.158 | 150.296 | 35.8 | 2325.01 | 7423.24 | 34539.8 | 1.41 | 5.59 | 20.326 | 153.871 | 1 | 1 | 1310 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1025696.7616 | 93126.6087 | 1671.3859 | 15768.9371 | 77357.6716 | 161477.6938 | 0.049912 | -1246887.9485 | 1246887.9485
C | Xist Rating 6666 | -75.51 | 461.205 | 150.296 | 35.8 | 2319.55 | 7432.19 | 33363 | 1.41 | 5.35 | 20.38 | 141.694 | 1 | 1 | 1320 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1069788.0578 | 94432.5232 | 1697.0007 | 15889.3107 | 78543.2125 | 148849.2502 | 0.050293 | -1149374.4548 | 1149374.4548
C | Xist Rating 6667 | -75.16 | 468.434 | 150.296 | 35.8 | 2316.81 | 7426.14 | 32979.9 | 1.37 | 5.28 | 20.277 | 137.986 | 1 | 1 | 1330 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1085272.5755 | 95747.4532 | 1722.8102 | 16009.6842 | 79737.769 | 144954.3667 | 0.050674 | -1119299.1965 | 1119299.1965
C | Xist Rating 6668 | -74.77 | 475.562 | 150.295 | 35.8 | 2318.79 | 7468.73 | 32606.7 | 1.35 | 5.2 | 20.19 | 134.4 | 1 | 1 | 1340 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1102728.41 | 97071.3987 | 1748.8145 | 16130.0578 | 80941.3409 | 141211.35 | 0.051055 | -1090396.6138 | 1090396.6138
C | Xist Rating 6669 | -74.53 | 479.281 | 150.295 | 35.8 | 2323.66 | 7530.76 | 32423.7 | 1.32 | 5.16 | 20.153 | 132.718 | 1 | 1 | 1350 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1113686.0885 | 98404.3598 | 1775.0136 | 16250.4314 | 82153.9284 | 139437.2049 | 0.051436 | -1076697.1359 | 1076697.1359
C | Xist Rating 6670 | -74.25 | 481.598 | 150.296 | 35.8 | 2338.91 | 7701.26 | 32303.4 | 1.3 | 5.14 | 20.236 | 131.583 | 1 | 1 | 1360 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1126414.3782 | 99746.3363 | 1801.4075 | 16370.8049 | 83375.5314 | 138252.4401 | 0.051817 | -1067548.6956 | 1067548.6956
C | Xist Rating 6671 | -73.03 | 510.036 | 150.295 | 35.8 | 2313.68 | 7524.59 | 30902.5 | 1.29 | 4.86 | 20.158 | 118.549 | 1 | 1 | 1370 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1180060.0925 | 101097.3284 | 1827.9962 | 16491.1785 | 84606.1499 | 124709.8377 | 0.052198 | -962976.3096 | 962976.3096
C | Xist Rating 6672 | -72.92 | 512.614 | 150.295 | 35.8 | 2312.77 | 7522.33 | 30794 | 1.27 | 4.84 | 20.116 | 117.656 | 1 | 1 | 1380 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1185558.2808 | 102457.336 | 1854.7797 | 16611.5521 | 85845.784 | 123765.8765 | 0.052579 | -955687.2918 | 955687.2918
C | Xist Rating 6673 | -72.59 | 518.672 | 150.295 | 35.8 | 2314.36 | 7557.8 | 30526.9 | 1.24 | 4.78 | 20.08 | 115.351 | 1 | 1 | 1390 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1200393.7299 | 103826.3592 | 1881.7579 | 16731.9256 | 87094.4335 | 121343.2072 | 0.05296 | -936980.0817 | 936980.0817
C | Xist Rating 6674 | -72.26 | 524.727 | 150.295 | 35.7 | 2316.03 | 7594.47 | 30265 | 1.22 | 4.73 | 20.051 | 113.116 | 1 | 1 | 1400 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1215283.4738 | 105204.3978 | 1908.931 | 16852.2992 | 88352.0986 | 119005.9018 | 0.053341 | -918932.0286 | 918932.0286
C | Xist Rating 6675 | -71.89 | 531.915 | 150.295 | 35.7 | 2316.81 | 7625.5 | 29957.3 | 1.19 | 4.67 | 20.029 | 110.502 | 1 | 1 | 1410 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1232345.9911 | 106591.452 | 1936.2988 | 16972.6728 | 89618.7792 | 116262.559 | 0.053722 | -897748.6629 | 897748.6629
C | Xist Rating 6676 | -70.83 | 553.223 | 150.295 | 35.7 | 2311.76 | 7640.28 | 29051.8 | 1.2 | 4.49 | 20.1 | 102.813 | 1 | 1 | 1420 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1278918.8025 | 107987.5216 | 1963.8614 | 17093.0463 | 90894.4753 | 108306.4001 | 0.054103 | -836313.313 | 836313.313
C | Xist Rating 6677 | -70.65 | 557.182 | 150.295 | 35.7 | 2310.66 | 7639.56 | 28910.6 | 1.16 | 4.47 | 20.016 | 101.756 | 1 | 1 | 1430 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1287458.1601 | 109392.6068 | 1991.6188 | 17213.4199 | 92179.1869 | 107161.7374 | 0.054484 | -827474.5306 | 827474.5306
C | Xist Rating 6678 | -70.17 | 566.688 | 150.295 | 35.7 | 2310.3 | 7665.71 | 28541.8 | 1.15 | 4.39 | 20.001 | 98.803 | 1 | 1 | 1440 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1309219.2864 | 110806.7076 | 2019.571 | 17333.7935 | 93472.9141 | 104091.4259 | 0.054865 | -803766.3994 | 803766.3994
C | Xist Rating 6679 | -69.85 | 572.781 | 150.295 | 35.7 | 2310.59 | 7687.74 | 28316.6 | 1.13 | 4.35 | 19.974 | 97.06 | 1 | 1 | 1450 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1323462.0508 | 112229.8238 | 2047.718 | 17454.167 | 94775.6568 | 102263.6507 | 0.055246 | -789652.8039 | 789652.8039
C | Xist Rating 6680 | -69.58 | 576.381 | 150.295 | 35.7 | 2318.01 | 7782.13 | 28183.5 | 1.11 | 4.32 | 20.004 | 96.037 | 1 | 1 | 1460 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1336056.9218 | 113661.9556 | 2076.0598 | 17574.5406 | 96087.415 | 101187.4198 | 0.055627 | -781342.4337 | 781342.4337
C | Xist Rating 6681 | -68.53 | 600.434 | 150.295 | 35.7 | 2302.54 | 7686.82 | 27310 | 1.1 | 4.16 | 19.978 | 89.289 | 1 | 1 | 1470 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1382523.3024 | 115103.1029 | 2104.5964 | 17694.9142 | 97408.1887 | 94174.5199 | 0.056008 | -727190.6799 | 727190.6799
C | Xist Rating 6682 | -68.16 | 607.666 | 150.295 | 35.7 | 2303.07 | 7715.29 | 27065.9 | 1.09 | 4.11 | 19.963 | 87.498 | 1 | 1 | 1480 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1399497.3346 | 116553.2657 | 2133.3277 | 17815.2877 | 98737.9779 | 92310.0817 | 0.056389 | -712793.9818 | 712793.9818
C | Xist Rating 6683 | -67.83 | 613.761 | 150.295 | 35.7 | 2304.55 | 7750.83 | 26866.2 | 1.07 | 4.07 | 19.95 | 86.062 | 1 | 1 | 1490 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1414442.9126 | 118012.444 | 2162.2539 | 17935.6613 | 100076.7827 | 90800.9565 | 0.05677 | -701140.9176 | 701140.9176
C | Xist Rating 6684 | -67.51 | 619.947 | 150.295 | 35.7 | 2305.18 | 7777 | 26669.9 | 1.05 | 4.03 | 19.923 | 84.676 | 1 | 1 | 1500 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1429089.4255 | 119480.6378 | 2191.3748 | 18056.0349 | 101424.603 | 89342.4325 | 0.057151 | -689878.5816 | 689878.5816
C | Xist Rating 6685 | -67.08 | 627.207 | 150.295 | 35.7 | 2309.32 | 7847.56 | 26438.4 | 1.03 | 3.99 | 19.924 | 83.035 | 1 | 1 | 1510 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1448421.6692 | 120957.8472 | 2220.6906 | 18176.4084 | 102781.4388 | 87620.7334 | 0.057532 | -676584.0775 | 676584.0775
C | Xist Rating 6686 | -65.89 | 650.943 | 150.295 | 35.7 | 2306.4 | 7892.97 | 25681 | 1.04 | 3.84 | 20.005 | 77.627 | 1 | 1 | 1520 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1501334.9352 | 122444.0721 | 2250.2011 | 18296.782 | 104147.2901 | 82033.0472 | 0.057913 | -633437.4459 | 633437.4459
C | Xist Rating 6687 | -65.57 | 658.546 | 150.295 | 35.7 | 2301.62 | 7860.35 | 25468.6 | 1.01 | 3.8 | 19.933 | 76.239 | 1 | 1 | 1530 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1515722.6445 | 123939.3125 | 2279.9064 | 18417.1556 | 105522.1569 | 80554.7907 | 0.058294 | -622022.7408 | 622022.7408
C | Xist Rating 6688 | -65.28 | 662.421 | 150.295 | 35.7 | 2307.92 | 7946.1 | 25363.6 | 0.99 | 3.78 | 19.925 | 75.577 | 1 | 1 | 1540 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1528814.6743 | 125443.5684 | 2309.8065 | 18537.5291 | 106906.0393 | 79848.2628 | 0.058675 | -616567.1196 | 616567.1196
C | Xist Rating 6689 | -64.69 | 674.369 | 150.295 | 35.7 | 2306.6 | 7969.73 | 25021.1 | 0.97 | 3.72 | 19.918 | 73.292 | 1 | 1 | 1550 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1555499.5354 | 126956.8399 | 2339.9013 | 18657.9027 | 108298.9372 | 77455.977 | 0.059056 | -598094.5234 | 598094.5234
C | Xist Rating 6690 | -64.42 | 678.019 | 150.295 | 35.7 | 2314.3 | 8074.65 | 24919.5 | 0.96 | 3.7 | 19.933 | 72.645 | 1 | 1 | 1560 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1569139.3717 | 128479.1268 | 2370.191 | 18778.2763 | 109700.8506 | 76779.8079 | 0.059437 | -592873.3244 | 592873.3244
C | Xist Rating 6691 | -63.26 | 705.855 | 150.295 | 35.7 | 2296.07 | 7947.38 | 24161.1 | 0.96 | 3.56 | 19.876 | 67.718 | 1 | 1 | 1570 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1620692.4899 | 130010.4293 | 2400.6755 | 18898.6498 | 111111.7795 | 71667.8528 | 0.059818 | -553400.1621 | 553400.1621
C | Xist Rating 6692 | -62.9 | 712.07 | 150.295 | 35.7 | 2299.07 | 8003.11 | 24006.5 | 0.94 | 3.53 | 19.869 | 66.78 | 1 | 1 | 1580 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1637098.7749 | 131550.7473 | 2431.3547 | 19019.0234 | 112531.7239 | 70673.6747 | 0.0602 | -545723.3824 | 545723.3824
C | Xist Rating 6693 | -62.55 | 718.32 | 150.295 | 35.7 | 2301.25 | 8049.34 | 23854 | 0.92 | 3.5 | 19.858 | 65.866 | 1 | 1 | 1590 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1653033.9 | 133100.0809 | 2462.2288 | 19139.3969 | 113960.6839 | 69703.816 | 0.060581 | -538234.3903 | 538234.3903
C | Xist Rating 6694 | -62.05 | 726.744 | 150.295 | 35.7 | 2305.23 | 8126.34 | 23644.6 | 0.91 | 3.46 | 19.878 | 64.587 | 1 | 1 | 1600 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1675312.0711 | 134658.4299 | 2493.2976 | 19259.7705 | 115398.6594 | 68370.8289 | 0.060962 | -527941.4176 | 527941.4176
C | Xist Rating 6695 | -61.82 | 730.815 | 150.295 | 35.7 | 2307.2 | 8163.04 | 23555.9 | 0.89 | 3.45 | 19.852 | 64.1 | 1 | 1 | 1610 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1686136.368 | 136225.7945 | 2524.5612 | 19380.1441 | 116845.6504 | 67842.8275 | 0.061343 | -523864.3311 | 523864.3311
C | Xist Rating 6696 | -60.44 | 761.964 | 150.295 | 35.7 | 2293.14 | 8093.9 | 22804.4 | 0.89 | 3.31 | 19.881 | 59.559 | 1 | 1 | 1620 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1747290.127 | 137802.1746 | 2556.0196 | 19500.5176 | 118301.6569 | 63136.8002 | 0.061724 | -487525.6353 | 487525.6353
C | Xist Rating 6697 | -60.1 | 765.689 | 150.295 | 35.7 | 2302.67 | 8226.01 | 22722.7 | 0.88 | 3.29 | 19.906 | 59.108 | 1 | 1 | 1630 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1763129.0896 | 139387.5702 | 2587.6728 | 19620.8912 | 119766.679 | 62663.4502 | 0.062105 | -483870.5525 | 483870.5525
C | Xist Rating 6698 | -59.76 | 772.087 | 150.295 | 35.7 | 2303.76 | 8260.59 | 22588 | 0.86 | 3.27 | 19.884 | 58.37 | 1 | 1 | 1640 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1778703.1471 | 140981.9813 | 2619.5208 | 19741.2648 | 121240.7165 | 61874.2328 | 0.062486 | -477776.4249 | 477776.4249
C | Xist Rating 6699 | -59.37 | 780.869 | 150.295 | 35.7 | 2301.13 | 8255.44 | 22402.4 | 0.85 | 3.23 | 19.857 | 57.345 | 1 | 1 | 1650 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1796881.082 | 142585.4079 | 2651.5635 | 19861.6383 | 122723.7696 | 60801.0333 | 0.062867 | -469489.4629 | 469489.4629
C | Xist Rating 6700 | -58.9 | 789.407 | 150.295 | 35.7 | 2302.95 | 8307.91 | 22220.3 | 0.83 | 3.2 | 19.861 | 56.332 | 1 | 1 | 1660 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1817964.8506 | 144197.8501 | 2683.8011 | 19982.0119 | 124215.8382 | 59727.2964 | 0.063248 | -461198.3511 | 461198.3511
C | Xist Rating 6701 | -57.68 | 817.286 | 150.295 | 35.7 | 2290.97 | 8248.75 | 21632.5 | 0.83 | 3.09 | 19.886 | 53.058 | 1 | 1 | 1670 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1872377.7074 | 145819.3078 | 2716.2334 | 20102.3855 | 125716.9223 | 56336.1951 | 0.063629 | -435013.1653 | 435013.1653
C | Xist Rating 6702 | -57.39 | 821.123 | 150.295 | 35.7 | 2296.82 | 8337.47 | 21560 | 0.82 | 3.08 | 19.894 | 52.692 | 1 | 1 | 1680 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1885971.7289 | 147449.781 | 2748.8606 | 20222.759 | 127227.022 | 55949.0219 | 0.06401 | -432023.5167 | 432023.5167
C | Xist Rating 6703 | -56.91 | 832.338 | 150.295 | 35.7 | 2292.18 | 8313.54 | 21345.6 | 0.81 | 3.04 | 19.864 | 51.575 | 1 | 1 | 1690 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1907868.5168 | 149089.2697 | 2781.6825 | 20343.1326 | 128746.1371 | 54779.4202 | 0.064391 | -422992.1624 | 422992.1624
C | Xist Rating 6704 | -56.5 | 839.753 | 150.295 | 35.7 | 2294.6 | 8370.4 | 21205.4 | 0.8 | 3.02 | 19.867 | 50.853 | 1 | 1 | 1700 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1926897.2338 | 150737.774 | 2814.6992 | 20463.5062 | 130274.2678 | 54021.8827 | 0.064772 | -417142.6585 | 417142.6585
C | Xist Rating 6705 | -56.06 | 848.484 | 150.295 | 35.7 | 2294.62 | 8399.7 | 21044.6 | 0.78 | 2.99 | 19.857 | 50.033 | 1 | 1 | 1710 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1946948.3561 | 152395.2938 | 2847.9107 | 20583.8797 | 131811.414 | 53146.3842 | 0.065153 | -410382.2912 | 410382.2912
C | Xist Rating 6706 | -54.93 | 874.134 | 150.295 | 35.7 | 2285.12 | 8361.56 | 20567 | 0.78 | 2.9 | 19.886 | 47.564 | 1 | 1 | 1720 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 1997501.0861 | 154061.8291 | 2881.317 | 20704.2533 | 133357.5758 | 50591.0182 | 0.065534 | -390650.4325 | 390650.4325
C | Xist Rating 6707 | -54.41 | 885.219 | 150.295 | 35.7 | 2283.41 | 8375.69 | 20374.2 | 0.77 | 2.87 | 19.876 | 46.615 | 1 | 1 | 1730 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2021317.9168 | 155737.3799 | 2914.9181 | 20824.6269 | 134912.753 | 49596.418 | 0.065915 | -382970.393 | 382970.393
C | Xist Rating 6708 | -54.09 | 890.342 | 150.295 | 35.7 | 2287.51 | 8447.97 | 20289.5 | 0.76 | 2.85 | 19.878 | 46.219 | 1 | 1 | 1740 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2036666.2284 | 157421.9462 | 2948.714 | 20945.0004 | 136476.9458 | 49176.6491 | 0.066296 | -379729.0489 | 379729.0489
C | Xist Rating 6709 | -53.63 | 900.419 | 150.295 | 35.7 | 2284.52 | 8440.61 | 20123.4 | 0.75 | 2.82 | 19.858 | 45.427 | 1 | 1 | 1750 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2057025.2139 | 159115.5281 | 2982.7046 | 21065.374 | 138050.1541 | 48344.1605 | 0.066677 | -373300.7931 | 373300.7931
C | Xist Rating 6710 | -53.32 | 907.952 | 150.295 | 35.6 | 2282.5 | 8438.11 | 20000.2 | 0.74 | 2.8 | 19.852 | 44.847 | 1 | 1 | 1760 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2072400.44 | 160818.1254 | 3016.8901 | 21185.7476 | 139632.3779 | 47732.4909 | 0.067058 | -368577.6422 | 368577.6422
C | Xist Rating 6711 | -51.98 | 938.353 | 150.295 | 35.7 | 2271.76 | 8396.45 | 19497.1 | 0.74 | 2.71 | 19.888 | 42.419 | 1 | 1 | 1770 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2131712.8113 | 162529.7383 | 3051.2703 | 21306.1211 | 141223.6172 | 45219.7153 | 0.067439 | -349174.6551 | 349174.6551
C | Xist Rating 6712 | -51.58 | 945.995 | 150.295 | 35.7 | 2272.96 | 8437.51 | 19382.8 | 0.72 | 2.69 | 19.88 | 41.91 | 1 | 1 | 1780 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2150208.7952 | 164250.3667 | 3085.8453 | 21426.4947 | 142823.872 | 44665.5205 | 0.06782 | -344895.3097 | 344895.3097
C | Xist Rating 6713 | -51.32 | 950.091 | 150.295 | 35.6 | 2275.93 | 8491.07 | 19326.3 | 0.71 | 2.68 | 19.874 | 41.676 | 1 | 1 | 1790 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2162340.6096 | 165980.0107 | 3120.6151 | 21546.8683 | 144433.1424 | 44412.6351 | 0.068201 | -342942.596 | 342942.596
C | Xist Rating 6714 | -50.73 | 963.647 | 150.295 | 35.6 | 2272.6 | 8490.66 | 19121.6 | 0.7 | 2.65 | 19.866 | 40.748 | 1 | 1 | 1800 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2189984.1722 | 167718.6701 | 3155.5797 | 21667.2418 | 146051.4283 | 43438.7466 | 0.068582 | -335422.4866 | 335422.4866
C | Xist Rating 6715 | -50.58 | 971.161 | 150.295 | 35.6 | 2261.97 | 8368.04 | 19013 | 0.69 | 2.63 | 20.106 | 40.26 | 1 | 1 | 1810 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2196737.0472 | 169466.3451 | 3190.7391 | 21787.6154 | 147678.7297 | 42935.5105 | 0.068963 | -331536.6311 | 331536.6311
C | Xist Rating 6716 | -49.03 | 1001.82 | 150.296 | 35.6 | 2262.42 | 8478.53 | 18562.6 | 0.69 | 2.55 | 19.898 | 38.248 | 1 | 1 | 1820 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2266537.6044 | 171223.0356 | 3226.0933 | 21907.989 | 149315.0466 | 40840.5618 | 0.069344 | -315359.9924 | 315359.9924
C | Xist Rating 6717 | -49.28 | 996.953 | 150.296 | 35.6 | 2265.64 | 8507.41 | 18631.2 | 0.69 | 2.56 | 20.158 | 38.554 | 1 | 1 | 1830 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2258736.5949 | 172988.7416 | 3261.6423 | 22028.3625 | 150960.3791 | 41179.2126 | 0.069725 | -317974.964 | 317974.964
C | Xist Rating 6718 | -48.81 | 1003.13 | 150.296 | 35.6 | 2272.45 | 8625.41 | 18545.1 | 0.68 | 2.55 | 20.183 | 38.188 | 1 | 1 | 1840 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2279562.7685 | 174763.4631 | 3297.386 | 22148.7361 | 152614.727 | 40790.1331 | 0.070106 | -314970.5959 | 314970.5959
C | Xist Rating 6719 | -48.36 | 1013.32 | 150.296 | 35.6 | 2269.34 | 8614.57 | 18409.3 | 0.67 | 2.52 | 20.171 | 37.62 | 1 | 1 | 1850 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2299567.6088 | 176547.2002 | 3333.3246 | 22269.1097 | 154278.0905 | 40189.0144 | 0.070487 | -310328.9161 | 310328.9161
C | Xist Rating 6720 | -47.88 | 1024.75 | 150.296 | 35.6 | 2265.63 | 8599.31 | 18259 | 0.66 | 2.5 | 20.158 | 36.995 | 1 | 1 | 1860 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2321704.3425 | 178339.9528 | 3369.4579 | 22389.4832 | 155950.4695 | 39528.478 | 0.070868 | -305228.4296 | 305228.4296
C | Xist Rating 6721 | -46.6 | 1052.91 | 150.296 | 35.6 | 2259.47 | 8609.19 | 17879.6 | 0.66 | 2.43 | 20.207 | 35.376 | 1 | 1 | 1870 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2379018.5577 | 180141.7209 | 3405.7861 | 22509.8568 | 157631.8641 | 37855.8235 | 0.071249 | -292312.6346 | 292312.6346
C | Xist Rating 6722 | -46.1 | 1064.32 | 150.296 | 35.6 | 2256.83 | 8608.61 | 17738.8 | 0.65 | 2.41 | 20.198 | 34.813 | 1 | 1 | 1880 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2401989.3056 | 181952.5045 | 3442.309 | 22630.2304 | 159322.2741 | 37259.6055 | 0.07163 | -287708.7972 | 287708.7972
C | Xist Rating 6723 | -45.63 | 1071.88 | 150.296 | 35.6 | 2260.44 | 8686.96 | 17646.4 | 0.64 | 2.39 | 20.218 | 34.45 | 1 | 1 | 1890 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2422920.4272 | 183772.3036 | 3479.0267 | 22750.6039 | 161021.6997 | 36872.4884 | 0.072011 | -284719.5816 | 284719.5816
C | Xist Rating 6724 | -45.31 | 1079.9 | 150.296 | 35.6 | 2257.3 | 8666.14 | 17555.2 | 0.62 | 2.38 | 20.203 | 34.106 | 1 | 1 | 1900 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2437658.27 | 185601.1183 | 3515.9392 | 22870.9775 | 162730.1408 | 36485.8149 | 0.072392 | -281733.7915 | 281733.7915
C | Xist Rating 6725 | -44.91 | 1087.65 | 150.296 | 35.6 | 2257.99 | 8701.93 | 17464.9 | 0.61 | 2.36 | 20.207 | 33.76 | 1 | 1 | 1910 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2455902.8235 | 187438.9484 | 3553.0464 | 22991.3511 | 164447.5974 | 36115.0212 | 0.072773 | -278870.6209 | 278870.6209
C | Xist Rating 6726 | -43.42 | 1121.84 | 150.296 | 35.6 | 2249.07 | 8690.18 | 17050.3 | 0.62 | 2.29 | 20.254 | 32.094 | 1 | 1 | 1920 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2523096.6888 | 189285.7941 | 3590.3485 | 23111.7246 | 166174.0695 | 34410.3068 | 0.073154 | -265707.2678 | 265707.2678
C | Xist Rating 6727 | -42.96 | 1133.33 | 150.296 | 35.6 | 2244.62 | 8661.73 | 16923.8 | 0.61 | 2.27 | 20.247 | 31.622 | 1 | 1 | 1930 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2543895.1846 | 191141.6554 | 3627.8454 | 23232.0982 | 167909.5572 | 33907.8729 | 0.073535 | -261827.6066 | 261827.6066
C | Xist Rating 6728 | -42.61 | 1137.06 | 150.296 | 35.6 | 2251.53 | 8778.54 | 16882.1 | 0.6 | 2.26 | 20.279 | 31.472 | 1 | 1 | 1940 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2560124.7018 | 193006.5321 | 3665.537 | 23352.4717 | 169654.0603 | 33741.6972 | 0.073916 | -260544.4416 | 260544.4416
C | Xist Rating 6729 | -42.25 | 1147.83 | 150.296 | 35.6 | 2244.73 | 8709.83 | 16772.1 | 0.59 | 2.24 | 20.248 | 31.08 | 1 | 1 | 1950 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2576568.4359 | 194880.4244 | 3703.4235 | 23472.8453 | 171407.579 | 33320.7356 | 0.074297 | -257293.888 | 257293.888
C | Xist Rating 6730 | -41.7 | 1160.43 | 150.296 | 35.7 | 2242.23 | 8714.35 | 16637 | 0.58 | 2.22 | 20.273 | 30.581 | 1 | 1 | 1960 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2601950.9589 | 196763.3321 | 3741.5047 | 23593.2189 | 173170.1132 | 32791.3646 | 0.074678 | -253206.2251 | 253206.2251
C | Xist Rating 6731 | -40.36 | 1191.22 | 150.296 | 35.7 | 2234.78 | 8708.97 | 16303.2 | 0.58 | 2.16 | 20.341 | 29.326 | 1 | 1 | 1970 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2662114.6316 | 198655.2554 | 3779.7807 | 23713.5924 | 174941.663 | 31496.8024 | 0.075059 | -243209.9593 | 243209.9593
C | Xist Rating 6732 | -39.92 | 1200.17 | 150.296 | 35.7 | 2235.06 | 8742.79 | 16214.2 | 0.57 | 2.15 | 20.369 | 29.015 | 1 | 1 | 1980 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2682451.9602 | 200556.1942 | 3818.2515 | 23833.966 | 176722.2282 | 31162.481 | 0.07544 | -240628.418 | 240628.418
C | Xist Rating 6733 | -39.5 | 1211.86 | 150.296 | 35.7 | 2229.43 | 8694.66 | 16101.4 | 0.56 | 2.13 | 20.382 | 28.626 | 1 | 1 | 1990 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2701757.0398 | 202466.1486 | 3856.9171 | 23954.3396 | 178511.809 | 30746.1894 | 0.075821 | -237413.9249 | 237413.9249
C | Xist Rating 6734 | -39.07 | 1220.94 | 150.296 | 35.7 | 2228.9 | 8715.72 | 16015 | 0.55 | 2.12 | 20.384 | 28.331 | 1 | 1 | 2000 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2721353.166 | 204385.1184 | 3895.7775 | 24074.7131 | 180310.4053 | 30426.7749 | 0.076202 | -234947.4908 | 234947.4908
C | Xist Rating 6735 | -38.75 | 1227.59 | 150.296 | 35.7 | 2228.79 | 8734.97 | 15954 | 0.54 | 2.11 | 20.392 | 28.129 | 1 | 1 | 2010 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2736040.3161 | 206313.1038 | 3934.8326 | 24195.0867 | 182118.0171 | 30204.0474 | 0.076583 | -233227.6476 | 233227.6476
C | Xist Rating 6736 | -37.3 | 1262.23 | 150.296 | 35.7 | 2219.65 | 8713.5 | 15614.9 | 0.55 | 2.05 | 20.425 | 26.929 | 1 | 1 | 2020 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2801708.8195 | 208250.1047 | 3974.0826 | 24315.4603 | 183934.6444 | 28982.8927 | 0.076964 | -223798.2151 | 223798.2151
C | Xist Rating 6737 | -36.73 | 1274.78 | 150.296 | 35.7 | 2218.22 | 8733 | 15499.9 | 0.54 | 2.03 | 20.434 | 26.542 | 1 | 1 | 2030 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2827742.4916 | 210196.1211 | 4013.5273 | 24435.8338 | 185760.2873 | 28567.886 | 0.077345 | -220593.6434 | 220593.6434
C | Xist Rating 6738 | -36.39 | 1283 | 150.296 | 35.7 | 2216.19 | 8726.54 | 15431.8 | 0.53 | 2.02 | 20.424 | 26.33 | 1 | 1 | 2040 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2843371.77 | 212151.1531 | 4053.1669 | 24556.2074 | 187594.9457 | 28333.5005 | 0.077726 | -218783.7806 | 218783.7806
C | Xist Rating 6739 | -35.92 | 1290.4 | 150.296 | 35.7 | 2220.39 | 8817.41 | 15364.3 | 0.53 | 2.01 | 20.448 | 26.108 | 1 | 1 | 2050 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2865191.256 | 214115.2005 | 4093.0012 | 24676.581 | 189438.6196 | 28108.9749 | 0.078107 | -217050.053 | 217050.053
C | Xist Rating 6740 | -35.48 | 1302.48 | 150.296 | 35.7 | 2215.31 | 8775.45 | 15264.4 | 0.51 | 1.99 | 20.43 | 25.793 | 1 | 1 | 2060 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2885396.9688 | 216088.2635 | 4133.0303 | 24796.9545 | 191291.309 | 27748.0952 | 0.078488 | -214263.4356 | 214263.4356
C | Xist Rating 6741 | -33.97 | 1339.66 | 150.296 | 35.7 | 2205.11 | 8742.28 | 14936.3 | 0.52 | 1.94 | 20.465 | 24.698 | 1 | 1 | 2070 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2954097.6626 | 218070.342 | 4173.2542 | 24917.3281 | 193153.0139 | 26636.2549 | 0.078869 | -205678.1 | 205678.1
C | Xist Rating 6742 | -33.57 | 1347.68 | 150.296 | 35.7 | 2205.78 | 8777.73 | 14873.5 | 0.51 | 1.93 | 20.465 | 24.51 | 1 | 1 | 2080 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2972685.5904 | 220061.436 | 4213.6729 | 25037.7017 | 195023.7344 | 26426.7068 | 0.07925 | -204060.0247 | 204060.0247
C | Xist Rating 6743 | -33.12 | 1358.07 | 150.296 | 35.7 | 2204.41 | 8789.38 | 14790.9 | 0.5 | 1.91 | 20.457 | 24.256 | 1 | 1 | 2090 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 2993743.0887 | 222061.5456 | 4254.2864 | 25158.0752 | 196903.4703 | 26148.0595 | 0.079631 | -201908.3845 | 201908.3845
C | Xist Rating 6744 | -32.69 | 1368.47 | 150.296 | 35.7 | 2202.23 | 8787.96 | 14709.2 | 0.49 | 1.9 | 20.461 | 24.008 | 1 | 1 | 2100 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3013685.6881 | 224070.6706 | 4295.0947 | 25278.4488 | 198792.2218 | 25876.0248 | 0.080012 | -199807.8042 | 199807.8042
C | Xist Rating 6745 | -32.28 | 1377.65 | 150.296 | 35.7 | 2201.21 | 8800.92 | 14638.7 | 0.49 | 1.89 | 20.462 | 23.797 | 1 | 1 | 2110 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3032496.9565 | 226088.8112 | 4336.0977 | 25398.8224 | 200689.9889 | 25661.442 | 0.080393 | -198150.8531 | 198150.8531
C | Xist Rating 6746 | -30.89 | 1412.73 | 150.296 | 35.7 | 2191.43 | 8762.51 | 14359 | 0.49 | 1.84 | 20.495 | 22.917 | 1 | 1 | 2120 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3095898.9039 | 228115.9673 | 4377.2956 | 25519.1959 | 202596.7714 | 24753.5943 | 0.080774 | -191140.6937 | 191140.6937
C | Xist Rating 6747 | -30.37 | 1425.62 | 150.296 | 35.7 | 2188.28 | 8753.1 | 14263.8 | 0.48 | 1.83 | 20.491 | 22.635 | 1 | 1 | 2130 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3119655.7336 | 230152.1389 | 4418.6882 | 25639.5695 | 204512.5695 | 24445.4881 | 0.081155 | -188761.579 | 188761.579
C | Xist Rating 6748 | -29.93 | 1438.54 | 150.296 | 35.7 | 2183.19 | 8712.74 | 14169.8 | 0.48 | 1.81 | 20.488 | 22.36 | 1 | 1 | 2140 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3140606.1426 | 232197.3261 | 4460.2756 | 25759.9431 | 206437.383 | 24164.1717 | 0.081536 | -186589.3284 | 186589.3284
C | Xist Rating 6749 | -29.62 | 1445.33 | 150.296 | 35.7 | 2183.21 | 8733.3 | 14123.3 | 0.47 | 1.8 | 20.49 | 22.233 | 1 | 1 | 2150 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3155458.9093 | 234251.5288 | 4502.0578 | 25880.3166 | 208371.2121 | 24017.0362 | 0.081917 | -185453.1875 | 185453.1875
C | Xist Rating 6750 | -29.21 | 1454.45 | 150.296 | 35.7 | 2182.68 | 8753.4 | 14058.9 | 0.46 | 1.79 | 20.494 | 22.049 | 1 | 1 | 2160 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3174598.926 | 236314.7469 | 4544.0348 | 26000.6902 | 210314.0567 | 23810.6087 | 0.082298 | -183859.2092 | 183859.2092
C | Xist Rating 6751 | -27.76 | 1492.28 | 150.296 | 35.7 | 2171.44 | 8696.29 | 13785.9 | 0.46 | 1.75 | 20.524 | 21.238 | 1 | 1 | 2170 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3240396.4832 | 238386.9806 | 4586.2066 | 26121.0638 | 212265.9169 | 22973.9546 | 0.082679 | -177398.7875 | 177398.7875
C | Xist Rating 6752 | -27.2 | 1504.95 | 150.296 | 35.7 | 2170.53 | 8721.73 | 13698.9 | 0.46 | 1.74 | 20.528 | 20.992 | 1 | 1 | 2180 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3266539.1235 | 240468.2299 | 4628.5732 | 26241.4373 | 214226.7925 | 22722.8957 | 0.08306 | -175460.1772 | 175460.1772
C | Xist Rating 6753 | -26.82 | 1514.3 | 150.296 | 35.7 | 2169.07 | 8726.31 | 13638.8 | 0.45 | 1.73 | 20.53 | 20.831 | 1 | 1 | 2190 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3284622.701 | 242558.4946 | 4671.1346 | 26361.8109 | 216196.6837 | 22539.867 | 0.083441 | -174046.8783 | 174046.8783
C | Xist Rating 6754 | -26.48 | 1524.06 | 150.296 | 35.7 | 2165.9 | 8703.16 | 13579.3 | 0.44 | 1.72 | 20.52 | 20.676 | 1 | 1 | 2200 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3300961.554 | 244657.7749 | 4713.8907 | 26482.1845 | 218175.5904 | 22362.3615 | 0.083822 | -172676.2277 | 172676.2277
C | Xist Rating 6755 | -25.95 | 1536.98 | 150.296 | 35.7 | 2163.83 | 8709.67 | 13495.2 | 0.44 | 1.7 | 20.52 | 20.446 | 1 | 1 | 2210 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3325763.4334 | 246766.0707 | 4756.8417 | 26602.558 | 220163.5126 | 22127.554 | 0.084203 | -170863.1063 | 170863.1063
C | Xist Rating 6756 | -24.47 | 1574.68 | 150.296 | 35.7 | 2154.61 | 8681.37 | 13246 | 0.44 | 1.66 | 20.557 | 19.742 | 1 | 1 | 2220 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3392821.2748 | 248883.382 | 4799.9874 | 26722.9316 | 222160.4504 | 21402.1182 | 0.084584 | -165261.4839 | 165261.4839
C | Xist Rating 6757 | -24.02 | 1585.04 | 150.296 | 35.7 | 2154 | 8703.12 | 13182.3 | 0.44 | 1.65 | 20.56 | 19.575 | 1 | 1 | 2230 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3414176.16 | 251009.7088 | 4843.3279 | 26843.3052 | 224166.4036 | 21232.8754 | 0.084965 | -163954.6354 | 163954.6354
C | Xist Rating 6758 | -23.61 | 1597.09 | 150.296 | 35.7 | 2149.88 | 8671.59 | 13111.6 | 0.43 | 1.64 | 20.558 | 19.393 | 1 | 1 | 2240 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3433551.8492 | 253145.0511 | 4886.8633 | 26963.6787 | 226181.3724 | 21027.1936 | 0.085346 | -162366.4153 | 162366.4153
C | Xist Rating 6759 | -23.11 | 1610.32 | 150.296 | 35.7 | 2146.42 | 8654.49 | 13034 | 0.42 | 1.63 | 20.557 | 19.193 | 1 | 1 | 2250 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3456423.0544 | 255289.409 | 4930.5934 | 27084.0523 | 228205.3567 | 20802.6802 | 0.085727 | -160632.7821 | 160632.7821
C | Xist Rating 6760 | -22.79 | 1617.08 | 150.296 | 35.7 | 2147.04 | 8684.13 | 12995.6 | 0.42 | 1.62 | 20.562 | 19.099 | 1 | 1 | 2260 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3471935.4432 | 257442.7824 | 4974.5182 | 27204.4258 | 230238.3565 | 20709.1442 | 0.086108 | -159910.522 | 159910.522
C | Xist Rating 6761 | -21.28 | 1657.62 | 150.296 | 35.7 | 2136.1 | 8632.13 | 12751.8 | 0.42 | 1.59 | 20.595 | 18.447 | 1 | 1 | 2270 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3540842.082 | 259605.1713 | 5018.6379 | 27324.7994 | 232280.3719 | 20037.3246 | 0.086489 | -154722.9091 | 154722.9091
C | Xist Rating 6762 | -20.81 | 1669.61 | 150.296 | 35.7 | 2133.76 | 8628.68 | 12686.2 | 0.41 | 1.58 | 20.595 | 18.285 | 1 | 1 | 2280 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3562547.0336 | 261776.5757 | 5062.9524 | 27445.173 | 234331.4027 | 19851.917 | 0.08687 | -153291.2408 | 153291.2408
C | Xist Rating 6763 | -20.24 | 1683.81 | 150.296 | 35.7 | 2131.52 | 8634.38 | 12607 | 0.41 | 1.56 | 20.601 | 18.086 | 1 | 1 | 2290 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3589074.6912 | 263956.9957 | 5107.4617 | 27565.5465 | 236391.4491 | 19649.2933 | 0.087251 | -151726.6343 | 151726.6343
C | Xist Rating 6764 | -19.8 | 1693.33 | 150.296 | 35.7 | 2132.01 | 8669.76 | 12557.1 | 0.4 | 1.56 | 20.592 | 17.968 | 1 | 1 | 2300 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3610196.4933 | 266146.4311 | 5152.1657 | 27685.9201 | 238460.511 | 19508.9264 | 0.087632 | -150642.7588 | 150642.7588
| Xist Rating 6765 | -19.46 | 1703.11 | 150.296 | 35.7 | 2129.51 | 8655.46 | 12507.6 | 0.4 | 1.55 | 20.585 | 17.853 | 1 | 1 | 2310 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3626789.7761 | 268344.8821 | 5197.0645 | 27806.2937 | 240538.5884 | 19392.9013 | 0.088013 | -149746.8435 | 149746.8435
| Xist Rating 6766 | -17.86 | 1744.71 | 150.296 | 35.7 | 2120.52 | 8635.75 | 12277.1 | 0.4 | 1.51 | 20.616 | 17.265 | 1 | 1 | 2320 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3699692.4492 | 270552.3486 | 5242.1582 | 27926.6672 | 242625.6814 | 18787.2446 | 0.088394 | -145070.1231 | 145070.1231
| Xist Rating 6767 | -17.37 | 1756.74 | 150.296 | 35.7 | 2119.08 | 8646.52 | 12216.8 | 0.39 | 1.5 | 20.615 | 17.124 | 1 | 1 | 2330 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3722672.5992 | 272768.8306 | 5287.4466 | 28047.0408 | 244721.7898 | 18622.9404 | 0.088775 | -143801.4093 | 143801.4093
| Xist Rating 6768 | -16.94 | 1768.74 | 150.296 | 35.7 | 2116.23 | 8633.37 | 12157.2 | 0.39 | 1.49 | 20.615 | 16.985 | 1 | 1 | 2340 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3743060.6502 | 274994.3282 | 5332.9298 | 28167.4144 | 246826.9138 | 18482.1929 | 0.089156 | -142714.5949 | 142714.5949
| Xist Rating 6769 | -16.56 | 1779.61 | 150.296 | 35.7 | 2113.55 | 8619.41 | 12104.7 | 0.38 | 1.49 | 20.61 | 16.866 | 1 | 1 | 2350 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 26 | E | Rod | 3761294.7155 | 277228.8413 | 5378.6078 | 28287.7879 | 248941.0533 | 18340.2999 | 0.089537 | -141618.9345 | 141618.9345
| Xist Rating 6770 | -16.08 | 1792.89 | 150.296 | 35.7 | 2110.5 | 8606.68 | 12039.9 | 0.38 | 1.48 | 20.6 | 16.716 | 1 | 1 | 2360 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 3783894.345 | 279472.3698 | 5424.4805 | 28408.1615 | 251064.2083 | 18187.6337 | 0.089918 | -140440.0867 | 140440.0867
| Xist Rating 6771 | -14.64 | 1831.01 | 150.296 | 35.7 | 2102.68 | 8591.39 | 11846.8 | 0.38 | 1.45 | 20.629 | 16.248 | 1 | 1 | 2370 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 3850028.1068 | 281724.914 | 5470.5481 | 28528.5351 | 253196.3789 | 17706.2961 | 0.090299 | -136723.3247 | 136723.3247
| Xist Rating 6772 | -14.22 | 1843.25 | 150.296 | 35.7 | 2099.55 | 8572.93 | 11791.2 | 0.38 | 1.44 | 20.621 | 16.126 | 1 | 1 | 2380 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 3869995.5375 | 283986.4736 | 5516.8105 | 28648.9086 | 255337.5649 | 17582.7887 | 0.09068 | -135769.634 | 135769.634
| Xist Rating 6773 | -13.74 | 1856.08 | 150.296 | 35.7 | 2097.4 | 8574.47 | 11730 | 0.37 | 1.43 | 20.616 | 15.986 | 1 | 1 | 2390 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 3892942.192 | 286257.0487 | 5563.2676 | 28769.2822 | 257487.7665 | 17418.6218 | 0.091061 | -134501.9801 | 134501.9801
C | Xist Rating 6776 | -3.83 | 2129.84 | 150.297 | 35.7 | 2039.04 | 8390.82 | 10537.9 | 0.4 | 1.25 | 20.651 | 13.328 | 1 | 1 | 2420 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4342828.9536 | 293122.8673 | 5703.8078 | 29130.4029 | 263992.4644 | 14737.1592 | 0.092204 | -113796.437 | 113796.437
C | Xist Rating 6777 | -3.73 | 2131.2 | 150.296 | 35.7 | 2040.47 | 8415.12 | 10537.9 | 0.39 | 1.25 | 20.651 | 13.339 | 1 | 1 | 2430 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4348649.664 | 295429.5045 | 5751.0441 | 29250.7765 | 266178.7281 | 14729.7915 | 0.092585 | -113739.5456 | 113739.5456
C | Xist Rating 6778 | -3.71 | 2132.57 | 150.296 | 35.7 | 2040.09 | 8408.7 | 10537.9 | 0.38 | 1.25 | 20.643 | 13.35 | 1 | 1 | 2440 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4350634.7313 | 297745.1573 | 5798.4752 | 29371.15 | 268374.0072 | 14721.9062 | 0.092966 | -113678.6573 | 113678.6573
C | Xist Rating 6779 | -3.69 | 2133.89 | 150.296 | 35.7 | 2039.82 | 8404.09 | 10537.9 | 0.38 | 1.25 | 20.637 | 13.36 | 1 | 1 | 2450 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4352751.4998 | 300069.8256 | 5846.1011 | 29491.5236 | 270578.302 | 14735.557 | 0.093347 | -113784.0651 | 113784.0651
C | Xist Rating 6780 | -3.65 | 2135.36 | 150.296 | 35.7 | 2039.78 | 8403.32 | 10537.9 | 0.37 | 1.25 | 20.629 | 13.372 | 1 | 1 | 2460 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4355664.6208 | 302403.5093 | 5893.9217 | 29611.8972 | 272791.6122 | 14728.4516 | 0.093728 | -113729.1992 | 113729.1992
C | Xist Rating 6781 | -3.64 | 2136.72 | 150.296 | 35.7 | 2039.41 | 8397.19 | 10537.9 | 0.36 | 1.25 | 20.668 | 13.382 | 1 | 1 | 2470 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4357648.1352 | 304746.2087 | 5941.9372 | 29732.2707 | 275013.9379 | 14720.9726 | 0.094109 | -113671.4484 | 113671.4484
C | Xist Rating 6782 | -3.64 | 2138.07 | 150.296 | 35.7 | 2038.89 | 8388.24 | 10537.9 | 0.36 | 1.25 | 20.662 | 13.393 | 1 | 1 | 2480 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4359289.5423 | 307097.9235 | 5990.1474 | 29852.6443 | 277245.2792 | 14735.4911 | 0.09449 | -113783.5567 | 113783.5567
C | Xist Rating 6783 | -3.63 | 2139.46 | 150.296 | 35.7 | 2038.27 | 8377.78 | 10537.9 | 0.35 | 1.25 | 20.656 | 13.403 | 1 | 1 | 2490 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4360797.1342 | 309458.6538 | 6038.5525 | 29973.0179 | 279485.636 | 14725.9144 | 0.094871 | -113709.6075 | 113709.6075
C | Xist Rating 6784 | -3.6 | 2140.45 | 150.296 | 35.7 | 2038.54 | 8382.34 | 10537.9 | 0.35 | 1.25 | 20.653 | 13.412 | 1 | 1 | 2500 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4363392.943 | 311828.3997 | 6087.1523 | 30093.3914 | 281735.0083 | 14738.3839 | 0.095252 | -113805.8934 | 113805.8934
C | Xist Rating 6785 | -3.62 | 2142.3 | 150.296 | 35.6 | 2036.97 | 8355.97 | 10537.8 | 0.34 | 1.25 | 20.647 | 13.425 | 1 | 1 | 2510 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4363800.831 | 314207.1611 | 6135.9469 | 30213.765 | 283993.3961 | 14731.6583 | 0.095633 | -113753.9606 | 113753.9606
C | Xist Rating 6786 | -3.6 | 2143.75 | 150.296 | 35.6 | 2036.38 | 8346.02 | 10537.8 | 0.34 | 1.25 | 20.684 | 13.436 | 1 | 1 | 2520 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4365489.625 | 316594.938 | 6184.9363 | 30334.1386 | 286260.7995 | 14747.6495 | 0.096014 | -113877.4403 | 113877.4403
C | Xist Rating 6787 | -3.59 | 2145.09 | 150.296 | 35.6 | 2035.88 | 8337.56 | 10537.8 | 0.33 | 1.25 | 20.679 | 13.446 | 1 | 1 | 2530 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4367145.8292 | 318991.7304 | 6234.1205 | 30454.5121 | 288537.2183 | 14737.5427 | 0.096395 | -113799.3983 | 113799.3983
C | Xist Rating 6788 | -3.57 | 2146.24 | 150.296 | 35.6 | 2035.8 | 8336.31 | 10537.8 | 0.33 | 1.25 | 20.675 | 13.456 | 1 | 1 | 2540 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4369315.392 | 321397.5384 | 6283.4995 | 30574.8857 | 290822.6527 | 14750.8363 | 0.096776 | -113902.0477 | 113902.0477
C | Xist Rating 6789 | -3.58 | 2147.79 | 150.296 | 35.6 | 2034.91 | 8321.49 | 10537.8 | 0.32 | 1.25 | 20.671 | 13.467 | 1 | 1 | 2550 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4370559.3489 | 323812.3619 | 6333.0732 | 30695.2593 | 293117.1026 | 14741.5396 | 0.097157 | -113830.2613 | 113830.2613
C | Xist Rating 6790 | -3.53 | 2149.24 | 150.296 | 35.6 | 2035.14 | 8325.32 | 10537.7 | 0.32 | 1.25 | 20.663 | 13.477 | 1 | 1 | 2560 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4374004.2936 | 326236.2009 | 6382.8418 | 30815.6328 | 295420.568 | 14754.5959 | 0.097538 | -113931.0782 | 113931.0782
C | Xist Rating 6791 | -3.52 | 2150.63 | 150.296 | 35.6 | 2034.77 | 8319.11 | 10537.7 | 0.31 | 1.25 | 20.659 | 13.488 | 1 | 1 | 2570 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4376037.4051 | 328669.0554 | 6432.8051 | 30936.0064 | 297733.049 | 14745.0367 | 0.097919 | -113857.2651 | 113857.2651
C | Xist Rating 6792 | -3.48 | 2151.99 | 150.297 | 35.6 | 2034.83 | 8320.16 | 10537.7 | 0.31 | 1.25 | 20.705 | 13.498 | 1 | 1 | 2580 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4378933.8117 | 331110.9254 | 6482.9633 | 31056.38 | 300054.5455 | 14759.9415 | 0.0983 | -113972.3562 | 113972.3562
C | Xist Rating 6793 | -3.46 | 2153.35 | 150.297 | 35.6 | 2034.81 | 8319.81 | 10537.7 | 0.3 | 1.25 | 20.709 | 13.508 | 1 | 1 | 2590 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4381658.1135 | 333561.811 | 6533.3162 | 31176.7535 | 302385.0574 | 14749.3053 | 0.098681 | -113890.2258 | 113890.2258
C | Xist Rating 6794 | -3.43 | 2154.53 | 150.297 | 35.6 | 2034.86 | 8320.7 | 10537.7 | 0.3 | 1.25 | 20.708 | 13.517 | 1 | 1 | 2600 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4384166.9158 | 336021.712 | 6583.8639 | 31297.1271 | 304724.585 | 14761.4016 | 0.099062 | -113983.6306 | 113983.6306
C | Xist Rating 6795 | -3.42 | 2156.22 | 150.297 | 35.6 | 2034.06 | 8307.37 | 10537.7 | 0.29 | 1.25 | 20.705 | 13.529 | 1 | 1 | 2610 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4385880.8532 | 338490.6286 | 6634.6064 | 31417.5006 | 307073.128 | 14752.3197 | 0.099443 | -113913.5027 | 113913.5027
C | Xist Rating 6796 | -3.4 | 2157.61 | 150.297 | 35.6 | 2033.79 | 8302.86 | 10537.6 | 0.29 | 1.25 | 20.704 | 13.539 | 1 | 1 | 2620 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4388125.6419 | 340968.5608 | 6685.5437 | 31537.8742 | 309430.6865 | 14765.3621 | 0.099824 | -114014.2126 | 114014.2126
C | Xist Rating 6797 | -3.37 | 2159.04 | 150.297 | 35.6 | 2033.7 | 8301.27 | 10537.6 | 0.29 | 1.25 | 20.744 | 13.549 | 1 | 1 | 2630 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4390839.648 | 343455.5084 | 6736.6758 | 31658.2478 | 311797.2606 | 14779.806 | 0.10021 | -114125.7441 | 114125.7441
C | Xist Rating 6798 | -3.33 | 2160.28 | 150.297 | 35.6 | 2033.93 | 8305.18 | 10537.6 | 0.28 | 1.25 | 20.746 | 13.558 | 1 | 1 | 2640 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4393858.3004 | 345951.4715 | 6788.0027 | 31778.6213 | 314172.8502 | 14767.3674 | 0.10059 | -114029.697 | 114029.697
C | Xist Rating 6799 | -3.31 | 2161.79 | 150.297 | 35.6 | 2033.47 | 8297.56 | 10537.6 | 0.28 | 1.25 | 20.742 | 13.569 | 1 | 1 | 2650 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4395935.1113 | 348456.4502 | 6839.5243 | 31898.9949 | 316557.4553 | 14781.2617 | 0.10097 | -114136.9847 | 114136.9847
C | Xist Rating 6800 | -3.26 | 2163.13 | 150.297 | 35.6 | 2033.84 | 8303.66 | 10537.6 | 0.27 | 1.25 | 20.743 | 13.579 | 1 | 1 | 2660 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4399460.3192 | 350970.4444 | 6891.2408 | 32019.3685 | 318951.0759 | 14769.5507 | 0.10135 | -114046.5559 | 114046.5559
C | Xist Rating 6801 | -3.23 | 2164.52 | 150.297 | 35.6 | 2033.85 | 8303.81 | 10537.5 | 0.27 | 1.25 | 20.743 | 13.589 | 1 | 1 | 2670 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4402309.002 | 353493.4541 | 6943.152 | 32139.742 | 321353.7121 | 14782.4462 | 0.10173 | -114146.1311 | 114146.1311
C | Xist Rating 6802 | -3.17 | 2165.93 | 150.297 | 35.6 | 2034.41 | 8313.1 | 10537.6 | 0.27 | 1.25 | 20.788 | 13.599 | 1 | 1 | 2680 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4406389.6513 | 356025.4794 | 6995.258 | 32260.1156 | 323765.3638 | 14796.8012 | 0.10211 | -114256.9767 | 114256.9767
C | Xist Rating 6803 | -3.12 | 2167.31 | 150.297 | 35.6 | 2034.78 | 8319.34 | 10537.6 | 0.26 | 1.25 | 20.788 | 13.609 | 1 | 1 | 2690 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4409999.0418 | 358566.5201 | 7047.5588 | 32380.4892 | 326186.0309 | 14784.6363 | 0.10249 | -114163.0423 | 114163.0423
C | Xist Rating 6804 | -3.04 | 2168.51 | 150.297 | 35.6 | 2036.07 | 8341.07 | 10537.5 | 0.26 | 1.25 | 20.786 | 13.618 | 1 | 1 | 2700 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4415238.1557 | 361116.5764 | 7100.0544 | 32500.8627 | 328615.7137 | 14796.3425 | 0.10287 | -114253.435 | 114253.435
C | Xist Rating 6805 | -2.99 | 2170.17 | 150.297 | 35.6 | 2036.16 | 8342.55 | 10537.5 | 0.26 | 1.25 | 20.784 | 13.629 | 1 | 1 | 2710 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4418813.3472 | 363675.6482 | 7152.7448 | 32621.2363 | 331054.4119 | 14810.1253 | 0.10325 | -114359.8622 | 114359.8622
C | Xist Rating 6806 | -3 | 2171.51 | 150.297 | 35.6 | 2035.42 | 8330.14 | 10537.5 | 0.25 | 1.25 | 20.781 | 13.638 | 1 | 1 | 2720 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4419934.8842 | 366243.7355 | 7205.63 | 32741.6099 | 333502.1256 | 14796.4622 | 0.10363 | -114254.3586 | 114254.3586
C | Xist Rating 6807 | -2.98 | 2172.83 | 150.297 | 35.6 | 2035.14 | 8325.48 | 10537.5 | 0.25 | 1.25 | 20.814 | 13.648 | 1 | 1 | 2730 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4422013.2462 | 368820.8384 | 7258.71 | 32861.9834 | 335958.8549 | 14810.1855 | 0.10402 | -114360.3263 | 114360.3263
C | Xist Rating 6808 | -2.97 | 2174.12 | 150.297 | 35.6 | 2034.55 | 8315.54 | 10537.5 | 0.25 | 1.25 | 20.81 | 13.657 | 1 | 1 | 2740 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4423355.846 | 371406.9567 | 7311.9847 | 32982.357 | 338424.5997 | 14821.7416 | 0.1044 | -114449.5596 | 114449.5596
C | Xist Rating 6809 | -2.97 | 2175.66 | 150.297 | 35.6 | 2033.62 | 8300.12 | 10537.5 | 0.25 | 1.25 | 20.81 | 13.668 | 1 | 1 | 2750 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4424465.6892 | 374002.0906 | 7365.4543 | 33102.7306 | 340899.36 | 14835.4971 | 0.10478 | -114555.7758 | 114555.7758
C | Xist Rating 6810 | -2.99 | 2177.09 | 150.297 | 35.6 | 2032.4 | 8279.76 | 10537.5 | 0.24 | 1.25 | 20.805 | 13.677 | 1 | 1 | 2760 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4424717.716 | 376606.24 | 7419.1186 | 33223.1041 | 343383.1359 | 14821.2818 | 0.10516 | -114446.0092 | 114446.0092
C | Xist Rating 6811 | -2.98 | 2178.32 | 150.297 | 35.6 | 2032.1 | 8274.89 | 10537.5 | 0.24 | 1.25 | 20.809 | 13.686 | 1 | 1 | 2770 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4426564.072 | 379219.4049 | 7472.9777 | 33343.4777 | 345875.9272 | 14832.9856 | 0.10554 | -114536.3834 | 114536.3834
C | Xist Rating 6812 | -3 | 2179.87 | 150.297 | 35.6 | 2030.84 | 8253.92 | 10537.5 | 0.24 | 1.25 | 20.844 | 13.697 | 1 | 1 | 2780 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4426967.1908 | 381841.5853 | 7527.0316 | 33463.8513 | 348377.7341 | 14847.6945 | 0.10592 | -114649.9611 | 114649.9611
C | Xist Rating 6813 | -2.99 | 2181.28 | 150.297 | 35.6 | 2030.34 | 8245.65 | 10537.5 | 0.23 | 1.25 | 20.846 | 13.706 | 1 | 1 | 2790 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4428740.0352 | 384472.7813 | 7581.2803 | 33584.2248 | 350888.5565 | 14833.2732 | 0.1063 | -114538.6039 | 114538.6039
C | Xist Rating 6814 | -2.94 | 2182.26 | 150.297 | 35.6 | 2031.1 | 8258.23 | 10537.5 | 0.23 | 1.25 | 20.856 | 13.714 | 1 | 1 | 2800 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4432388.286 | 387112.9928 | 7635.7238 | 33704.5984 | 353408.3944 | 14844.019 | 0.10668 | -114621.5802 | 114621.5802
C | Xist Rating 6815 | -2.99 | 2184 | 150.297 | 35.6 | 2028.91 | 8222.16 | 10537.5 | 0.23 | 1.25 | 20.845 | 13.725 | 1 | 1 | 2810 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4431139.44 | 389762.2198 | 7690.3621 | 33824.972 | 355937.2478 | 14857.274 | 0.10706 | -114723.9318 | 114723.9318
C | Xist Rating 6816 | -2.95 | 2185.47 | 150.297 | 35.6 | 2028.92 | 8222.38 | 10537.5 | 0.23 | 1.25 | 20.855 | 13.735 | 1 | 1 | 2820 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4434143.7924 | 392420.4623 | 7745.1952 | 33945.3455 | 358475.1168 | 14870.0988 | 0.10744 | -114822.9612 | 114822.9612
C | Xist Rating 6817 | -2.91 | 2186.85 | 150.297 | 35.6 | 2029.08 | 8224.86 | 10537.6 | 0.22 | 1.25 | 20.903 | 13.744 | 1 | 1 | 2830 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4437293.598 | 395087.7203 | 7800.223 | 34065.7191 | 361022.0013 | 14856.4796 | 0.10783 | -114717.7973 | 114717.7973
C | Xist Rating 6818 | -2.91 | 2188.16 | 150.297 | 35.6 | 2028.23 | 8210.92 | 10537.6 | 0.22 | 1.25 | 20.897 | 13.753 | 1 | 1 | 2840 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4438091.7568 | 397763.9939 | 7855.4457 | 34186.0927 | 363577.9012 | 14867.7194 | 0.10821 | -114804.5879 | 114804.5879
C | Xist Rating 6819 | -2.84 | 2189.61 | 150.297 | 35.6 | 2029.13 | 8225.73 | 10537.6 | 0.22 | 1.25 | 20.909 | 13.763 | 1 | 1 | 2850 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4443003.3393 | 400449.283 | 7910.8631 | 34306.4662 | 366142.8168 | 14880.5023 | 0.10859 | -114903.2947 | 114903.2947
C | Xist Rating 6820 | -2.77 | 2191.01 | 150.297 | 35.6 | 2029.92 | 8238.69 | 10537.6 | 0.22 | 1.25 | 20.923 | 13.773 | 1 | 1 | 2860 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4447575.0192 | 403143.5876 | 7966.4753 | 34426.8398 | 368716.7478 | 14893.3441 | 0.10897 | -115002.4554 | 115002.4554
C | Xist Rating 6821 | -2.57 | 2192.2 | 150.297 | 35.6 | 2033.56 | 8298.94 | 10537.7 | 0.21 | 1.25 | 20.961 | 13.782 | 1 | 1 | 2870 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4457970.232 | 405846.9077 | 8022.2824 | 34547.2134 | 371299.6944 | 14878.8637 | 0.10935 | -114890.6419 | 114890.6419
C | Xist Rating 6822 | -2.59 | 2193.71 | 150.297 | 35.6 | 2032.18 | 8276.01 | 10537.7 | 0.21 | 1.25 | 20.995 | 13.791 | 1 | 1 | 2880 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4458013.5878 | 408559.2434 | 8078.2842 | 34667.5869 | 373891.6564 | 14891.1051 | 0.10973 | -114985.1661 | 114985.1661
C | Xist Rating 6823 | -2.04 | 2195.05 | 150.297 | 35.6 | 2043.28 | 8463.04 | 10537.9 | 0.21 | 1.25 | 21.057 | 13.801 | 1 | 1 | 2890 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4485101.764 | 411280.5945 | 8134.4807 | 34787.9605 | 376492.634 | 14905.153 | 0.11011 | -115093.6405 | 115093.6405
C | Xist Rating 6824 | -1.44 | 2196.44 | 150.297 | 35.6 | 2055.34 | 8673.73 | 10538.1 | 0.2 | 1.25 | 21.121 | 13.811 | 1 | 1 | 2900 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4514430.9896 | 414010.9612 | 8190.8721 | 34908.3341 | 379102.6271 | 14891.8117 | 0.11049 | -114990.6225 | 114990.6225
C | Xist Rating 6825 | -2.16 | 2197.98 | 150.297 | 35.6 | 2039.34 | 8395.87 | 10537.9 | 0.2 | 1.25 | 21.031 | 13.82 | 1 | 1 | 2910 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4482428.5332 | 416750.3434 | 8247.4583 | 35028.7076 | 381721.6358 | 14900.7037 | 0.11087 | -115059.2846 | 115059.2846
C | Xist Rating 6826 | -1.36 | 2199.37 | 150.297 | 35.6 | 2055.7 | 8680.23 | 10538 | 0.2 | 1.25 | 21.118 | 13.831 | 1 | 1 | 2920 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4521244.909 | 419498.7411 | 8304.2393 | 35149.0812 | 384349.6599 | 14916.2901 | 0.11125 | -115179.6382 | 115179.6382
C | Xist Rating 6827 | -0.76 | 2200.76 | 150.298 | 35.6 | 2067.5 | 8894.55 | 10538.1 | 0.19 | 1.25 | 21.222 | 13.841 | 1 | 1 | 2930 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4550071.3 | 422256.1544 | 8361.215 | 35269.4548 | 386986.6996 | 14903.4279 | 0.11164 | -115080.3199 | 115080.3199
C | Xist Rating 6828 | -0.44 | 2202.12 | 150.297 | 35.6 | 2073.75 | 9011.46 | 10538.1 | 0.19 | 1.25 | 21.254 | 13.85 | 1 | 1 | 2940 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4566646.35 | 425022.5831 | 8418.3855 | 35389.8283 | 389632.7548 | 14915.3831 | 0.11202 | -115172.6344 | 115172.6344
C | Xist Rating 6829 | -0.23 | 2203.53 | 150.297 | 35.6 | 2077.62 | 9084.85 | 10538 | 0.19 | 1.25 | 21.279 | 13.86 | 1 | 1 | 2950 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4578097.9986 | 427798.0274 | 8475.7509 | 35510.2019 | 392287.8255 | 14928.2063 | 0.1124 | -115271.6519 | 115271.6519
C | Xist Rating 6830 | 0.5 | 2204.9 | 150.297 | 35.6 | 2092.41 | 9374.78 | 10537.9 | 0.19 | 1.25 | 21.331 | 13.87 | 1 | 1 | 2960 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4613554.809 | 430582.4872 | 8533.311 | 35630.5754 | 394951.9118 | 14941.7144 | 0.11278 | -115375.9582 | 115375.9582
C | Xist Rating 6831 | 0.51 | 2206.29 | 150.297 | 35.6 | 2092.09 | 9368.41 | 10537.9 | 0.18 | 1.25 | 21.328 | 13.879 | 1 | 1 | 2970 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4615757.2461 | 433375.9625 | 8591.0659 | 35750.949 | 397625.0135 | 14924.4079 | 0.11316 | -115242.3219 | 115242.3219
C | Xist Rating 6832 | 0.52 | 2207.51 | 150.298 | 35.6 | 2091.56 | 9357.73 | 10537.9 | 0.18 | 1.25 | 21.361 | 13.887 | 1 | 1 | 2980 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4617139.6156 | 436178.4534 | 8649.0156 | 35871.3226 | 400307.1308 | 14935.2302 | 0.11354 | -115325.8887 | 115325.8887
C | Xist Rating 6833 | 0.53 | 2209.07 | 150.297 | 35.5 | 2090.82 | 9343.08 | 10537.9 | 0.18 | 1.25 | 21.357 | 13.897 | 1 | 1 | 2990 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4618767.7374 | 438989.9598 | 8707.16 | 35991.6961 | 402998.2636 | 14947.2422 | 0.11392 | -115418.642 | 115418.642
C | Xist Rating 6834 | 0.53 | 2210.5 | 150.297 | 35.5 | 2090.1 | 9328.55 | 10537.9 | 0.18 | 1.25 | 21.351 | 13.906 | 1 | 1 | 3000 | 152.4 | 2 | 4.3 | 19.05 | 1.3333 | 25 | E | Rod | 4620166.05 | 441810.4816 | 8765.4993 | 36112.0697 | 405698.4119 | 14958.1666 | 0.1143 | -115502.9976 | 115502.9976
C | Xist Rating 6835 | -87.66 | 225.281 | 150.302 | 35.9 | 2363.43 | 7069.99 | 58745.8 | 2.47 | 10.95 | 23.1 | 554.475 | 1 | 1 | 1000 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 532435.8738 | 58443.2127 | 973.9444 | 12317.2951 | 46125.9176 | 578378.9709 | 0.038101 | -4466089.1018 | 4466089.1018
C | Xist Rating 6836 | -87.54 | 227.611 | 150.303 | 35.9 | 2361.19 | 7057.68 | 58284.2 | 2.45 | 10.85 | 23.172 | 544.052 | 1 | 1 | 1010 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 537432.8171 | 59493.5166 | 993.5206 | 12440.468 | 47053.0486 | 567567.3475 | 0.038482 | -4382604.612 | 4382604.612
C | Xist Rating 6837 | -86.62 | 245.291 | 150.303 | 35.9 | 2354.42 | 7056.36 | 54967 | 2.46 | 10.07 | 23.222 | 471.47 | 1 | 1 | 1020 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 577518.0362 | 60553.0457 | 1013.2917 | 12563.641 | 47989.4047 | 492232.7211 | 0.038863 | -3800890.5955 | 3800890.5955
C | Xist Rating 6838 | -86.47 | 250.096 | 150.301 | 35.9 | 2336.44 | 6911.79 | 54178.2 | 2.38 | 9.89 | 22.684 | 455.611 | 1 | 1 | 1030 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 584334.2982 | 61621.8 | 1033.2576 | 12686.8139 | 48934.986 | 475643.8924 | 0.039244 | -3672796.0581 | 3672796.0581
C | Xist Rating 6839 | -86.38 | 252.5 | 150.301 | 35.9 | 2330.64 | 6868.49 | 53793.5 | 2.34 | 9.8 | 22.559 | 448.019 | 1 | 1 | 1040 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 588486.6 | 62699.7794 | 1053.4182 | 12809.9869 | 49889.7925 | 467727.8777 | 0.039625 | -3611670.6907 | 3611670.6907
C | Xist Rating 6840 | -86.17 | 257.184 | 150.301 | 35.9 | 2323.9 | 6824.31 | 53042.5 | 2.3 | 9.63 | 22.472 | 433.142 | 1 | 1 | 1050 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 597669.8976 | 63786.984 | 1073.7737 | 12933.1599 | 50853.8242 | 452249.9105 | 0.040006 | -3492153.9309 | 3492153.9309
C | Xist Rating 6841 | -86.03 | 259.569 | 150.301 | 35.9 | 2326.84 | 6856.85 | 52676.6 | 2.26 | 9.54 | 22.448 | 426.103 | 1 | 1 | 1060 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 603975.532 | 64883.4139 | 1094.3239 | 13056.3328 | 51827.0811 | 444917.8014 | 0.040387 | -3435537.3276 | 3435537.3276
C | Xist Rating 6842 | -85.12 | 278.568 | 150.3 | 35.9 | 2309.94 | 6768.25 | 49856.6 | 2.24 | 8.9 | 22.24 | 372.808 | 1 | 1 | 1070 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 643475.3659 | 65989.0689 | 1115.0689 | 13179.5058 | 52809.5631 | 389549.889 | 0.040768 | -3008000.9845 | 3008000.9845
C | Xist Rating 6843 | -84.88 | 282.149 | 150.3 | 35.9 | 2317.95 | 6847.83 | 49380.4 | 2.19 | 8.79 | 22.14 | 364.44 | 1 | 1 | 1080 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 654007.2745 | 67103.949 | 1136.0087 | 13302.6787 | 53801.2703 | 380817.6303 | 0.041149 | -2940572.7972 | 2940572.7972
C | Xist Rating 6844 | -84.6 | 286.913 | 150.3 | 35.9 | 2321.41 | 6892.2 | 48761.2 | 2.13 | 8.65 | 21.979 | 353.68 | 1 | 1 | 1090 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 666042.7073 | 68228.0544 | 1157.1433 | 13425.8517 | 54802.2027 | 369583.4619 | 0.04153 | -2853825.5272 | 2853825.5272
C | Xist Rating 6845 | -84.36 | 290.462 | 150.3 | 35.9 | 2329.66 | 6976.15 | 48308 | 2.09 | 8.55 | 21.981 | 345.916 | 1 | 1 | 1100 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 676677.7029 | 69361.3849 | 1178.4727 | 13549.0246 | 55812.3603 | 361498.4022 | 0.041911 | -2791394.8394 | 2791394.8394
C | Xist Rating 6846 | -84.25 | 293.034 | 150.299 | 35.9 | 2327.6 | 6964.87 | 48010.8 | 2.01 | 8.49 | 21.649 | 341.141 | 1 | 1 | 1110 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 682065.9384 | 70503.9407 | 1199.9969 | 13672.1976 | 56831.7431 | 356439.4683 | 0.042292 | -2752331.0926 | 2752331.0926
C | Xist Rating 6847 | -83.14 | 314.188 | 150.3 | 35.9 | 2323.9 | 6997.34 | 45448.2 | 2.05 | 7.92 | 21.938 | 298.497 | 1 | 1 | 1120 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 730141.4932 | 71655.7216 | 1221.7158 | 13795.3705 | 57860.3511 | 312246.4644 | 0.042673 | -2411084.4306 | 2411084.4306
C | Xist Rating 6848 | -83.01 | 316.714 | 150.299 | 35.8 | 2324.28 | 7007.95 | 45189.2 | 1.99 | 7.86 | 21.725 | 294.647 | 1 | 1 | 1130 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 736132.0159 | 72816.7277 | 1243.6296 | 13918.5435 | 58898.1842 | 308180.2626 | 0.043054 | -2379686.2982 | 2379686.2982
C | Xist Rating 6849 | -82.78 | 321.549 | 150.299 | 35.8 | 2321.56 | 6997.41 | 44681.4 | 1.93 | 7.75 | 21.531 | 286.934 | 1 | 1 | 1140 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 746495.2964 | 73986.959 | 1265.7381 | 14041.7164 | 59945.2426 | 300103.9613 | 0.043435 | -2317323.2407 | 2317323.2407
C | Xist Rating 6850 | -82.52 | 326.32 | 150.298 | 35.8 | 2322.57 | 7020.81 | 44186.2 | 1.89 | 7.64 | 21.33 | 279.475 | 1 | 1 | 1150 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 757901.0424 | 75166.4154 | 1288.0414 | 14164.8894 | 61001.5261 | 292312.4502 | 0.043816 | -2257159.2573 | 2257159.2573
C | Xist Rating 6851 | -82.29 | 331.17 | 150.298 | 35.8 | 2319.4 | 7006.03 | 43703.3 | 1.84 | 7.53 | 21.159 | 272.375 | 1 | 1 | 1160 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 768115.698 | 76355.0971 | 1310.5395 | 14288.0623 | 62067.0348 | 284885.3674 | 0.044197 | -2199809.292 | 2199809.292
C | Xist Rating 6852 | -81.32 | 350.156 | 150.298 | 35.8 | 2314.74 | 7021.23 | 41832.3 | 1.86 | 7.13 | 21.311 | 244.998 | 1 | 1 | 1170 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 810520.0994 | 77553.0039 | 1333.2324 | 14411.2353 | 63141.7687 | 256508.8683 | 0.044578 | -1980693.4884 | 1980693.4884
C | Xist Rating 6853 | -81.18 | 351.512 | 150.298 | 35.8 | 2324.39 | 7114.31 | 41724.6 | 1.81 | 7.11 | 21.231 | 243.667 | 1 | 1 | 1180 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 817050.9777 | 78760.1359 | 1356.1201 | 14534.4082 | 64225.7277 | 255080.3756 | 0.044959 | -1969663.0461 | 1969663.0461
C | Xist Rating 6854 | -80.74 | 361.04 | 150.298 | 35.8 | 2317.13 | 7074.94 | 40885.5 | 1.76 | 6.92 | 21.053 | 232.222 | 1 | 1 | 1190 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 836576.6152 | 79976.4931 | 1379.2026 | 14657.5812 | 65318.912 | 243138.6512 | 0.04534 | -1877452.2156 | 1877452.2156
C | Xist Rating 6855 | -80.52 | 363.458 | 150.298 | 35.8 | 2328.71 | 7191.33 | 40681.8 | 1.73 | 6.88 | 21.095 | 229.547 | 1 | 1 | 1200 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 846388.2792 | 81202.0755 | 1402.4799 | 14780.7541 | 66421.3214 | 240347.2123 | 0.045721 | -1855897.4645 | 1855897.4645
C | Xist Rating 6856 | -80.28 | 368.378 | 150.297 | 35.8 | 2326.9 | 7188.62 | 40280.9 | 1.67 | 6.8 | 20.938 | 224.345 | 1 | 1 | 1210 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 857178.7682 | 82436.8831 | 1425.9519 | 14903.9271 | 67532.956 | 234878.4326 | 0.046102 | -1813668.997 | 1813668.997
C | Xist Rating 6857 | -79.24 | 389.886 | 150.297 | 35.8 | 2314.93 | 7140.82 | 38537.7 | 1.68 | 6.43 | 20.944 | 201.725 | 1 | 1 | 1220 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 902558.798 | 83680.9158 | 1449.6188 | 15027.1 | 68653.8158 | 211415.2733 | 0.046483 | -1632492.7008 | 1632492.7008
C | Xist Rating 6858 | -78.94 | 394.655 | 150.297 | 35.8 | 2320.87 | 7212.03 | 38183.3 | 1.65 | 6.35 | 20.965 | 197.391 | 1 | 1 | 1230 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 915942.9498 | 84934.1738 | 1473.4804 | 15150.273 | 69783.9008 | 206897.4616 | 0.046864 | -1597607.3558 | 1597607.3558
C | Xist Rating 6859 | -78.68 | 399.565 | 150.297 | 35.8 | 2321.39 | 7231.5 | 37835.5 | 1.6 | 6.28 | 20.855 | 193.262 | 1 | 1 | 1240 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 927546.1953 | 86196.6569 | 1497.5369 | 15273.4459 | 70923.211 | 202556.9605 | 0.047245 | -1564091.157 | 1564091.157
C | Xist Rating 6860 | -78.52 | 402.127 | 150.297 | 35.8 | 2325 | 7274 | 37664.4 | 1.57 | 6.24 | 20.783 | 191.319 | 1 | 1 | 1250 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 934945.275 | 87468.3652 | 1521.7881 | 15396.6189 | 72071.7463 | 200512.7258 | 0.047626 | -1548306.1182 | 1548306.1182
C | Xist Rating 6861 | -78.13 | 409.305 | 150.297 | 35.8 | 2326.55 | 7311.21 | 37161.5 | 1.54 | 6.14 | 20.741 | 185.369 | 1 | 1 | 1260 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 952268.5478 | 88749.2987 | 1546.2341 | 15519.7918 | 73229.5068 | 194309.4189 | 0.048007 | -1500405.8273 | 1500405.8273
C | Xist Rating 6862 | -77.13 | 429.673 | 150.297 | 35.8 | 2318.21 | 7292.55 | 35777.6 | 1.54 | 5.85 | 20.807 | 169.275 | 1 | 1 | 1270 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 996072.2453 | 90039.4573 | 1570.8749 | 15642.9648 | 74396.4926 | 177615.929 | 0.048388 | -1371503.1228 | 1371503.1228
C | Xist Rating 6863 | -76.89 | 434.651 | 150.297 | 35.8 | 2317 | 7295.02 | 35477.4 | 1.5 | 5.79 | 20.689 | 166.051 | 1 | 1 | 1280 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1007086.367 | 91338.8412 | 1595.7105 | 15766.1377 | 75572.7035 | 174224.2652 | 0.048769 | -1345313.5937 | 1345313.5937
C | Xist Rating 6864 | -76.64 | 439.577 | 150.296 | 35.8 | 2316.73 | 7306.9 | 35182.8 | 1.47 | 5.73 | 20.651 | 162.901 | 1 | 1 | 1290 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1018381.2232 | 92647.4502 | 1620.7408 | 15889.3107 | 76758.1395 | 170927.7863 | 0.04915 | -1319859.0575 | 1319859.0575
C | Xist Rating 6865 | -76.26 | 446.733 | 150.296 | 35.8 | 2317.67 | 7337.99 | 34751.1 | 1.45 | 5.64 | 20.685 | 158.251 | 1 | 1 | 1300 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1035379.6721 | 93965.2844 | 1645.966 | 16012.4836 | 77952.8008 | 166091.1813 | 0.049531 | -1282512.0761 | 1282512.0761
C | Xist Rating 6866 | -76.02 | 450.506 | 150.296 | 35.8 | 2322.54 | 7398.08 | 34539.7 | 1.41 | 5.59 | 20.636 | 156.088 | 1 | 1 | 1310 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1046318.2052 | 95292.3438 | 1671.3859 | 16135.6566 | 79156.6873 | 163805.7114 | 0.049912 | -1264864.2836 | 1264864.2836
C | Xist Rating 6867 | -75 | 470.972 | 150.296 | 35.8 | 2316.91 | 7405.13 | 33363 | 1.41 | 5.35 | 20.69 | 143.732 | 1 | 1 | 1320 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1091199.7365 | 96628.6284 | 1697.0007 | 16258.8295 | 80369.7989 | 150991.5726 | 0.050293 | -1165916.9001 | 1165916.9001
C | Xist Rating 6868 | -74.64 | 478.345 | 150.296 | 35.8 | 2314.39 | 7401.34 | 32979.9 | 1.38 | 5.28 | 20.584 | 139.968 | 1 | 1 | 1330 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1107076.8846 | 97974.1382 | 1722.8102 | 16382.0025 | 81592.1357 | 147050.0163 | 0.050674 | -1135481.2473 | 1135481.2473
C | Xist Rating 6869 | -74.24 | 485.616 | 150.296 | 35.8 | 2316.34 | 7443.36 | 32606.7 | 1.35 | 5.2 | 20.494 | 136.328 | 1 | 1 | 1340 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1124851.7654 | 99328.8731 | 1748.8145 | 16505.1754 | 82823.6977 | 143238.2257 | 0.051055 | -1106047.6103 | 1106047.6103
C | Xist Rating 6870 | -74 | 489.407 | 150.296 | 35.8 | 2321.59 | 7509.14 | 32423.5 | 1.32 | 5.16 | 20.456 | 134.621 | 1 | 1 | 1350 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1136202.3971 | 100692.8333 | 1775.0136 | 16628.3484 | 84064.4849 | 141437.6703 | 0.051436 | -1092144.1993 | 1092144.1993
C | Xist Rating 6871 | -73.72 | 491.771 | 150.296 | 35.8 | 2336.23 | 7672.26 | 32303.4 | 1.3 | 5.14 | 20.541 | 133.468 | 1 | 1 | 1360 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1148890.1633 | 102066.0186 | 1801.4075 | 16751.5213 | 85314.4973 | 140234.1808 | 0.051817 | -1082851.1725 | 1082851.1725
C | Xist Rating 6872 | -72.46 | 520.796 | 150.296 | 35.8 | 2311.72 | 7503.88 | 30902.5 | 1.3 | 4.86 | 20.462 | 120.243 | 1 | 1 | 1370 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1203934.5291 | 103448.4291 | 1827.9962 | 16874.6943 | 86573.7348 | 126505.7021 | 0.052198 | -976843.4989 | 976843.4989
C | Xist Rating 6873 | -72.35 | 523.422 | 150.296 | 35.8 | 2310.47 | 7498.09 | 30794 | 1.27 | 4.84 | 20.416 | 119.335 | 1 | 1 | 1380 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1209350.8283 | 104840.0648 | 1854.7797 | 16997.8672 | 87842.1975 | 125533.0833 | 0.052579 | -969333.1939 | 969333.1939
C | Xist Rating 6874 | -72.02 | 529.6 | 150.296 | 35.8 | 2311.67 | 7529.24 | 30526.9 | 1.24 | 4.78 | 20.38 | 116.995 | 1 | 1 | 1390 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1224260.432 | 106240.9256 | 1881.7579 | 17121.0402 | 89119.8855 | 123073.6766 | 0.05296 | -950342.3072 | 950342.3072
C | Xist Rating 6875 | -71.68 | 535.774 | 150.296 | 35.8 | 2313.62 | 7568.56 | 30265 | 1.22 | 4.73 | 20.349 | 114.726 | 1 | 1 | 1400 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1239577.4419 | 107651.0117 | 1908.931 | 17244.2131 | 90406.7986 | 120700.6993 | 0.053341 | -932018.8055 | 932018.8055
C | Xist Rating 6876 | -71.3 | 543.107 | 150.296 | 35.7 | 2314.39 | 7599.29 | 29957.2 | 1.19 | 4.67 | 20.326 | 112.074 | 1 | 1 | 1410 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1256961.4097 | 109070.3229 | 1936.2988 | 17367.3861 | 91702.9368 | 117917.4163 | 0.053722 | -910527.0321 | 910527.0321
C | Xist Rating 6877 | -70.22 | 564.857 | 150.296 | 35.7 | 2309.52 | 7615.9 | 29051.6 | 1.2 | 4.49 | 20.4 | 104.272 | 1 | 1 | 1420 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1304548.5386 | 110498.8594 | 1963.8614 | 17490.559 | 93008.3003 | 109844.4837 | 0.054103 | -848189.9865 | 848189.9865
C | Xist Rating 6878 | -70.04 | 568.888 | 150.296 | 35.7 | 2308.26 | 7613.35 | 28910.6 | 1.17 | 4.47 | 20.311 | 103.199 | 1 | 1 | 1430 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1313141.4149 | 111936.621 | 1991.6188 | 17613.732 | 94322.889 | 108695.2446 | 0.054484 | -839315.8666 | 839315.8666
C | Xist Rating 6879 | -69.54 | 578.586 | 150.296 | 35.7 | 2307.94 | 7639.77 | 28541.8 | 1.15 | 4.39 | 20.296 | 100.202 | 1 | 1 | 1440 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1335341.7728 | 113383.6077 | 2019.571 | 17736.9049 | 95646.7028 | 105566.1829 | 0.054865 | -815154.0822 | 815154.0822
C | Xist Rating 6880 | -69.22 | 584.798 | 150.296 | 35.7 | 2308.44 | 7664.01 | 28316.6 | 1.13 | 4.35 | 20.269 | 98.432 | 1 | 1 | 1450 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1349971.0951 | 114839.8197 | 2047.718 | 17860.0779 | 96979.7418 | 103710.1369 | 0.055246 | -800822.1867 | 800822.1867
C | Xist Rating 6881 | -68.94 | 588.47 | 150.296 | 35.7 | 2315.7 | 7756.12 | 28183.5 | 1.11 | 4.32 | 20.3 | 97.393 | 1 | 1 | 1460 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1362719.979 | 116305.2569 | 2076.0598 | 17983.2508 | 98322.006 | 102617.1259 | 0.055627 | -792382.2455 | 792382.2455
C | Xist Rating 6882 | -67.87 | 613.014 | 150.296 | 35.7 | 2300.61 | 7665.35 | 27310 | 1.1 | 4.16 | 20.273 | 90.546 | 1 | 1 | 1470 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1410306.1385 | 117779.9192 | 2104.5964 | 18106.4238 | 99673.4954 | 95501.2945 | 0.056008 | -737435.6812 | 737435.6812
C | Xist Rating 6883 | -67.48 | 620.39 | 150.296 | 35.7 | 2301.2 | 7694.4 | 27065.8 | 1.09 | 4.11 | 20.259 | 88.728 | 1 | 1 | 1480 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1427641.468 | 119263.8067 | 2133.3277 | 18229.5967 | 101034.21 | 93608.8388 | 0.056389 | -722822.6403 | 722822.6403
C | Xist Rating 6884 | -67.15 | 626.604 | 150.296 | 35.7 | 2302.31 | 7725.62 | 26866.1 | 1.07 | 4.07 | 20.243 | 87.27 | 1 | 1 | 1490 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1442636.6552 | 120756.9194 | 2162.2539 | 18352.7697 | 102404.1497 | 92076.4015 | 0.05677 | -710989.566 | 710989.566
C | Xist Rating 6885 | -66.85 | 632.91 | 150.296 | 35.7 | 2301.59 | 7736.28 | 26669.8 | 1.05 | 4.03 | 20.212 | 85.863 | 1 | 1 | 1500 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1456699.3269 | 122259.2573 | 2191.3748 | 18475.9426 | 103783.3147 | 90595.5332 | 0.057151 | -699554.6929 | 699554.6929
C | Xist Rating 6886 | -66.39 | 640.313 | 150.296 | 35.7 | 2306.69 | 7817.23 | 26438.8 | 1.03 | 3.99 | 20.218 | 84.2 | 1 | 1 | 1510 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1477003.594 | 123770.8204 | 2220.6906 | 18599.1156 | 105171.7048 | 88851.0805 | 0.057532 | -686084.4916 | 686084.4916
C | Xist Rating 6887 | -65.18 | 664.54 | 150.296 | 35.7 | 2303.99 | 7864.94 | 25680.8 | 1.04 | 3.84 | 20.298 | 78.711 | 1 | 1 | 1520 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1531093.5146 | 125291.6086 | 2250.2011 | 18722.2885 | 106569.3201 | 83179.5411 | 0.057913 | -642290.368 | 642290.368
C | Xist Rating 6888 | -64.85 | 672.287 | 150.296 | 35.7 | 2299.26 | 7832.94 | 25468.4 | 1.01 | 3.8 | 20.223 | 77.302 | 1 | 1 | 1530 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1545762.6076 | 126821.6221 | 2279.9064 | 18845.4615 | 107976.1606 | 81678.8021 | 0.058294 | -630702.0589 | 630702.0589
C | Xist Rating 6889 | -64.56 | 676.234 | 150.296 | 35.7 | 2305.6 | 7918.61 | 25363.6 | 0.99 | 3.78 | 20.214 | 76.63 | 1 | 1 | 1540 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1559125.1104 | 128360.8607 | 2309.8065 | 18968.6344 | 109392.2263 | 80961.5518 | 0.058675 | -625163.6421 | 625163.6421
C | Xist Rating 6890 | -63.97 | 688.421 | 150.295 | 35.7 | 2303.91 | 7937.73 | 25020.8 | 0.98 | 3.72 | 20.202 | 74.309 | 1 | 1 | 1550 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1586060.0261 | 129909.3245 | 2339.9013 | 19091.8074 | 110817.5171 | 78545.3058 | 0.059056 | -606506.0312 | 606506.0312
C | Xist Rating 6891 | -63.67 | 692.143 | 150.295 | 35.7 | 2312.29 | 8050.18 | 24919.5 | 0.97 | 3.7 | 20.224 | 73.654 | 1 | 1 | 1560 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1600435.3375 | 131467.0135 | 2370.191 | 19214.9803 | 112252.0332 | 77861.3294 | 0.059437 | -601224.5467 | 601224.5467
C | Xist Rating 6892 | -62.49 | 720.542 | 150.295 | 35.7 | 2293.84 | 7920.72 | 24161.2 | 0.96 | 3.56 | 20.163 | 68.655 | 1 | 1 | 1570 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1652808.0613 | 133033.9277 | 2400.6755 | 19338.1533 | 113695.7744 | 72660.3154 | 0.059818 | -561063.6956 | 561063.6956
C | Xist Rating 6893 | -62.12 | 726.876 | 150.295 | 35.7 | 2297.13 | 7979.63 | 24006.5 | 0.94 | 3.53 | 20.157 | 67.702 | 1 | 1 | 1580 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1669728.6659 | 134610.067 | 2431.3547 | 19461.3263 | 115148.7408 | 71650.3434 | 0.0602 | -553264.9594 | 553264.9594
C | Xist Rating 6894 | -61.77 | 733.246 | 150.295 | 35.7 | 2299.33 | 8025.92 | 23854 | 0.92 | 3.5 | 20.145 | 66.774 | 1 | 1 | 1590 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1685974.5252 | 136195.4316 | 2462.2288 | 19584.4992 | 116610.9324 | 70665.591 | 0.060581 | -545660.962 | 545660.962
C | Xist Rating 6895 | -61.25 | 741.838 | 150.295 | 35.7 | 2303.28 | 8102.18 | 23644.6 | 0.91 | 3.46 | 20.166 | 65.477 | 1 | 1 | 1600 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1708660.6286 | 137790.0213 | 2493.2976 | 19707.6722 | 118082.3491 | 69313.8887 | 0.060962 | -535223.4756 | 535223.4756
C | Xist Rating 6896 | -61.03 | 745.98 | 150.295 | 35.7 | 2304.57 | 8130.3 | 23555.9 | 0.89 | 3.45 | 20.137 | 64.981 | 1 | 1 | 1610 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1719163.1286 | 139393.8362 | 2524.5612 | 19830.8451 | 119562.9911 | 68776.05 | 0.061343 | -531070.4275 | 531070.4275
C | Xist Rating 6897 | -59.61 | 777.764 | 150.295 | 35.7 | 2291.26 | 8070.49 | 22804.4 | 0.89 | 3.31 | 20.169 | 60.374 | 1 | 1 | 1620 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1782059.5426 | 141006.8763 | 2556.0196 | 19954.0181 | 121052.8582 | 64001.7893 | 0.061724 | -494204.8521 | 494204.8521
C | Xist Rating 6898 | -59.28 | 781.561 | 150.295 | 35.7 | 2299.93 | 8191.25 | 22722.7 | 0.88 | 3.29 | 20.193 | 59.915 | 1 | 1 | 1630 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1797535.5907 | 142629.1416 | 2587.6728 | 20077.191 | 122551.9506 | 63519.9715 | 0.062105 | -490484.383 | 490484.383
C | Xist Rating 6899 | -58.92 | 788.078 | 150.295 | 35.7 | 2301.83 | 8235.75 | 22588 | 0.86 | 3.27 | 20.172 | 59.167 | 1 | 1 | 1640 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1814021.5827 | 144260.632 | 2619.5208 | 20200.364 | 124060.2681 | 62720.1236 | 0.062486 | -484308.1695 | 484308.1695
C | Xist Rating 6900 | -58.51 | 797.027 | 150.295 | 35.7 | 2299.17 | 8230.36 | 22402.4 | 0.85 | 3.23 | 20.143 | 58.126 | 1 | 1 | 1650 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1832500.5676 | 145901.3477 | 2651.5635 | 20323.5369 | 125577.8108 | 61630.0805 | 0.062867 | -475891.1449 | 475891.1449
C | Xist Rating 6901 | -58.04 | 805.733 | 150.295 | 35.7 | 2301.06 | 8283.35 | 22220.3 | 0.84 | 3.2 | 20.148 | 57.098 | 1 | 1 | 1660 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1854039.977 | 147551.2885 | 2683.8011 | 20446.7099 | 127104.5786 | 60555.5031 | 0.063248 | -467593.5433 | 467593.5433
C | Xist Rating 6902 | -56.8 | 834.175 | 150.295 | 35.7 | 2289.05 | 8223.9 | 21632.5 | 0.83 | 3.09 | 20.173 | 53.776 | 1 | 1 | 1670 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1909468.2837 | 149210.4545 | 2716.2334 | 20569.8828 | 128640.5717 | 57099.6687 | 0.063629 | -440908.506 | 440908.506
C | Xist Rating 6903 | -56.5 | 838.083 | 150.295 | 35.7 | 2294.97 | 8313.21 | 21560 | 0.82 | 3.08 | 20.181 | 53.405 | 1 | 1 | 1680 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1923375.3425 | 150878.8457 | 2748.8606 | 20693.0558 | 130185.7899 | 56707.1936 | 0.06401 | -437877.9179 | 437877.9179
C | Xist Rating 6904 | -56.01 | 849.514 | 150.295 | 35.7 | 2290.32 | 8289.06 | 21345.6 | 0.81 | 3.04 | 20.15 | 52.271 | 1 | 1 | 1690 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1945658.9045 | 152556.4621 | 2781.6825 | 20816.2287 | 131740.2334 | 55519.7642 | 0.064391 | -428708.9024 | 428708.9024
C | Xist Rating 6905 | -55.59 | 857.073 | 150.295 | 35.7 | 2292.69 | 8345.01 | 21205.4 | 0.8 | 3.02 | 20.153 | 51.538 | 1 | 1 | 1700 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1965002.6964 | 154243.3036 | 2814.6992 | 20939.4017 | 133303.902 | 54750.6891 | 0.064772 | -422770.3085 | 422770.3085
C | Xist Rating 6906 | -55.14 | 865.971 | 150.295 | 35.7 | 2292.85 | 8376.08 | 21044.5 | 0.78 | 2.99 | 20.143 | 50.706 | 1 | 1 | 1710 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 1985541.6073 | 155939.3704 | 2847.9107 | 21062.5746 | 134876.7958 | 53862.3928 | 0.065153 | -415911.1195 | 415911.1195
C | Xist Rating 6907 | -54 | 892.136 | 150.295 | 35.7 | 2282.82 | 8330.96 | 20566.8 | 0.78 | 2.9 | 20.173 | 48.201 | 1 | 1 | 1720 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2036585.9035 | 157644.6623 | 2881.317 | 21185.7476 | 136458.9147 | 51269.801 | 0.065534 | -395891.8129 | 395891.8129
C | Xist Rating 6908 | -53.45 | 903.436 | 150.295 | 35.7 | 2281.64 | 8351.95 | 20374.2 | 0.77 | 2.87 | 20.161 | 47.237 | 1 | 1 | 1730 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2061315.715 | 159359.1794 | 2914.9181 | 21308.9205 | 138050.2589 | 50259.3816 | 0.065915 | -388089.6224 | 388089.6224
C | Xist Rating 6909 | -53.11 | 908.655 | 150.296 | 35.7 | 2286 | 8427.32 | 20289.7 | 0.76 | 2.85 | 20.166 | 46.836 | 1 | 1 | 1740 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2077185.33 | 161082.9217 | 2948.714 | 21432.0935 | 139650.8282 | 49834.4741 | 0.066296 | -384808.5995 | 384808.5995
C | Xist Rating 6910 | -52.66 | 918.924 | 150.296 | 35.7 | 2282.84 | 8417.65 | 20123.4 | 0.75 | 2.82 | 20.143 | 46.031 | 1 | 1 | 1750 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2097756.4642 | 162815.8892 | 2982.7046 | 21555.2664 | 141260.6228 | 48988.1808 | 0.066677 | -378273.7469 | 378273.7469
C | Xist Rating 6911 | -52.48 | 926.6 | 150.296 | 35.6 | 2274.2 | 8325.5 | 20001 | 0.73 | 2.8 | 20.389 | 45.434 | 1 | 1 | 1760 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2107273.72 | 164558.0818 | 3016.8901 | 21678.4394 | 142879.6425 | 48357.3542 | 0.067058 | -373402.6707 | 373402.6707
C | Xist Rating 6912 | -50.98 | 957.611 | 150.295 | 35.7 | 2269.89 | 8370.97 | 19497.1 | 0.74 | 2.71 | 20.172 | 42.979 | 1 | 1 | 1770 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2173671.6328 | 166309.4997 | 3051.2703 | 21801.6123 | 144507.8874 | 45817.9484 | 0.067439 | -353794.0527 | 353794.0527
C | Xist Rating 6913 | -50.57 | 965.397 | 150.296 | 35.7 | 2271.18 | 8412.99 | 19382.8 | 0.73 | 2.69 | 20.164 | 42.462 | 1 | 1 | 1780 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2192590.3585 | 168070.1427 | 3085.8453 | 21924.7853 | 146145.3574 | 45271.1751 | 0.06782 | -349572.0138 | 349572.0138
C | Xist Rating 6914 | -50.34 | 969.565 | 150.296 | 35.6 | 2272.93 | 8449.55 | 19326 | 0.71 | 2.68 | 20.156 | 42.223 | 1 | 1 | 1790 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2203753.3755 | 169840.0109 | 3120.6151 | 22047.9582 | 147792.0527 | 44996.7586 | 0.068201 | -347453.043 | 347453.043
C | Xist Rating 6915 | -49.7 | 983.384 | 150.296 | 35.6 | 2271 | 8468.27 | 19121.6 | 0.7 | 2.65 | 20.151 | 41.283 | 1 | 1 | 1800 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2233265.064 | 171619.1043 | 3155.5797 | 22171.1312 | 149447.9731 | 44010.4397 | 0.068582 | -339836.9498 | 339836.9498
C | Xist Rating 6916 | -49.53 | 991.042 | 150.296 | 35.7 | 2260.81 | 8352.31 | 19013 | 0.69 | 2.63 | 20.397 | 40.787 | 1 | 1 | 1810 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2240557.664 | 173407.4229 | 3190.7391 | 22294.3041 | 151113.1188 | 43499.0898 | 0.068963 | -335888.4409 | 335888.4409
C | Xist Rating 6917 | -47.97 | 1022.31 | 150.296 | 35.6 | 2260.71 | 8454.62 | 18562.5 | 0.69 | 2.55 | 20.181 | 38.746 | 1 | 1 | 1820 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2311146.4401 | 175204.9666 | 3226.0933 | 22417.4771 | 152787.4896 | 41373.6643 | 0.069344 | -319476.4686 | 319476.4686
C | Xist Rating 6918 | -48.22 | 1017.35 | 150.296 | 35.6 | 2263.76 | 8480.93 | 18631.2 | 0.69 | 2.56 | 20.447 | 39.056 | 1 | 1 | 1830 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2303036.236 | 177011.7356 | 3261.6423 | 22540.65 | 154471.0856 | 41716.8962 | 0.069725 | -322126.8145 | 322126.8145
C | Xist Rating 6919 | -47.74 | 1023.64 | 150.296 | 35.6 | 2270.48 | 8597.15 | 18545.1 | 0.68 | 2.55 | 20.473 | 38.685 | 1 | 1 | 1840 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2324154.1472 | 178827.7297 | 3297.386 | 22663.823 | 156163.9067 | 41322.5314 | 0.070106 | -319081.634 | 319081.634
C | Xist Rating 6920 | -47.28 | 1034.03 | 150.296 | 35.6 | 2267.64 | 8590.16 | 18409.3 | 0.67 | 2.52 | 20.461 | 38.108 | 1 | 1 | 1850 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2344807.7892 | 180652.949 | 3333.3246 | 22786.9959 | 157865.9531 | 40711.9141 | 0.070487 | -314366.6088 | 314366.6088
C | Xist Rating 6921 | -46.78 | 1045.67 | 150.296 | 35.6 | 2264.14 | 8577.88 | 18259 | 0.66 | 2.5 | 20.447 | 37.474 | 1 | 1 | 1860 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2367543.2738 | 182487.3935 | 3369.4579 | 22910.1689 | 159577.2246 | 40041.8215 | 0.070868 | -309192.3318 | 309192.3318
C | Xist Rating 6922 | -45.48 | 1074.39 | 150.296 | 35.6 | 2258 | 8587.85 | 17879.6 | 0.66 | 2.43 | 20.497 | 35.831 | 1 | 1 | 1870 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2425972.62 | 184331.0632 | 3405.7861 | 23033.3418 | 161297.7214 | 38344.3838 | 0.071249 | -296085.168 | 296085.168
C | Xist Rating 6923 | -44.96 | 1086.02 | 150.296 | 35.6 | 2255.51 | 8589.49 | 17738.8 | 0.65 | 2.41 | 20.49 | 35.26 | 1 | 1 | 1880 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2449528.9702 | 186183.9581 | 3442.309 | 23156.5148 | 163027.4433 | 37739.8088 | 0.07163 | -291416.7998 | 291416.7998
C | Xist Rating 6924 | -44.5 | 1093.73 | 150.296 | 35.6 | 2258.64 | 8660.4 | 17646.5 | 0.64 | 2.39 | 20.507 | 34.891 | 1 | 1 | 1890 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2470342.3272 | 188046.0781 | 3479.0267 | 23279.6877 | 164766.3904 | 37346.1358 | 0.072011 | -288376.9609 | 288376.9609
C | Xist Rating 6925 | -44.16 | 1101.89 | 150.296 | 35.6 | 2255.89 | 8645.45 | 17555.2 | 0.62 | 2.38 | 20.492 | 34.542 | 1 | 1 | 1900 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2485742.6321 | 189917.4233 | 3515.9392 | 23402.8607 | 166514.5627 | 36953.8604 | 0.072392 | -285347.9149 | 285347.9149
C | Xist Rating 6926 | -43.76 | 1109.78 | 150.296 | 35.6 | 2256.51 | 8679.96 | 17465 | 0.62 | 2.36 | 20.495 | 34.191 | 1 | 1 | 1910 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2504229.6678 | 191797.9938 | 3553.0464 | 23526.0336 | 168271.9601 | 36595.2017 | 0.072773 | -282578.4474 | 282578.4474
C | Xist Rating 6927 | -42.24 | 1144.65 | 150.296 | 35.6 | 2247.4 | 8665.37 | 17050.3 | 0.62 | 2.29 | 20.543 | 32.501 | 1 | 1 | 1920 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2572486.41 | 193687.7894 | 3590.3485 | 23649.2066 | 170038.5828 | 34848.3965 | 0.073154 | -269090.0802 | 269090.0802
C | Xist Rating 6928 | -41.78 | 1156.36 | 150.296 | 35.6 | 2243.04 | 8638.27 | 16923.8 | 0.61 | 2.27 | 20.536 | 32.021 | 1 | 1 | 1930 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2593761.7344 | 195586.8101 | 3627.8454 | 23772.3795 | 171814.4306 | 34337.4849 | 0.073535 | -265144.9566 | 265144.9566
C | Xist Rating 6929 | -41.41 | 1160.17 | 150.296 | 35.7 | 2250.02 | 8755.62 | 16882.1 | 0.6 | 2.26 | 20.568 | 31.869 | 1 | 1 | 1940 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2610405.7034 | 197495.0561 | 3665.537 | 23895.5525 | 173599.5036 | 34169.0599 | 0.073916 | -263844.4231 | 263844.4231
C | Xist Rating 6930 | -41.06 | 1171.12 | 150.296 | 35.6 | 2243 | 8683.89 | 16772.1 | 0.59 | 2.24 | 20.536 | 31.471 | 1 | 1 | 1950 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2626822.16 | 199412.5272 | 3703.4235 | 24018.7254 | 175393.8018 | 33741.6409 | 0.074297 | -260544.0068 | 260544.0068
C | Xist Rating 6931 | -40.54 | 1183.96 | 150.296 | 35.6 | 2238.46 | 8657.8 | 16636.9 | 0.58 | 2.22 | 20.57 | 30.965 | 1 | 1 | 1960 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2650247.1016 | 201339.2236 | 3741.5047 | 24141.8984 | 177197.3252 | 33205.2821 | 0.074678 | -256402.3865 | 256402.3865
C | Xist Rating 6932 | -39.18 | 1215.36 | 150.297 | 35.7 | 2231.34 | 8657.06 | 16303.1 | 0.58 | 2.16 | 20.637 | 29.692 | 1 | 1 | 1970 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2711881.3824 | 203275.1451 | 3779.7807 | 24265.0713 | 179010.0737 | 31892.053 | 0.075059 | -246261.9793 | 246261.9793
C | Xist Rating 6933 | -38.71 | 1224.48 | 150.297 | 35.7 | 2232.22 | 8699.49 | 16214.2 | 0.57 | 2.15 | 20.669 | 29.377 | 1 | 1 | 1980 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2733308.7456 | 205220.2918 | 3818.2515 | 24388.2443 | 180832.0475 | 31553.5942 | 0.07544 | -243648.4902 | 243648.4902
C | Xist Rating 6934 | -38.23 | 1236.38 | 150.297 | 35.7 | 2228.07 | 8673.91 | 16101.6 | 0.56 | 2.13 | 20.675 | 28.981 | 1 | 1 | 1990 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 27 | E | Rod | 2754741.1866 | 207174.6637 | 3856.9171 | 24511.4172 | 182663.2464 | 31129.4925 | 0.075821 | -240373.6894 | 240373.6894
C | Xist Rating 6935 | -37.79 | 1245.63 | 150.297 | 35.7 | 2227.67 | 8696.92 | 16015 | 0.55 | 2.12 | 20.668 | 28.681 | 1 | 1 | 2000 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 2774852.5821 | 209138.2607 | 3895.7775 | 24634.5902 | 184503.6705 | 30804.2526 | 0.076202 | -237862.2733 | 237862.2733
C | Xist Rating 6936 | -37.45 | 1252.4 | 150.297 | 35.7 | 2228.18 | 8725.61 | 15953.8 | 0.55 | 2.11 | 20.672 | 28.476 | 1 | 1 | 2010 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 2790572.632 | 211111.083 | 3934.8326 | 24757.7631 | 186353.3198 | 30596.654 | 0.076583 | -236259.2522 | 236259.2522
C | Xist Rating 6937 | -35.98 | 1287.72 | 150.297 | 35.7 | 2218.81 | 8700.53 | 15614.9 | 0.55 | 2.05 | 20.709 | 27.258 | 1 | 1 | 2020 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 2857206.0132 | 213093.1304 | 3974.0826 | 24880.9361 | 188212.1943 | 29338.702 | 0.076964 | -226545.6797 | 226545.6797
C | Xist Rating 6938 | -35.39 | 1300.51 | 150.297 | 35.7 | 2217.6 | 8723.39 | 15499.8 | 0.54 | 2.03 | 20.713 | 26.866 | 1 | 1 | 2030 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 2884010.976 | 215084.403 | 4013.5273 | 25004.109 | 190080.294 | 28918.0687 | 0.077345 | -223297.661 | 223297.661
C | Xist Rating 6939 | -35.07 | 1308.87 | 150.297 | 35.7 | 2214.95 | 8707.38 | 15431.8 | 0.53 | 2.02 | 20.705 | 26.651 | 1 | 1 | 2040 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 2899081.6065 | 217084.9008 | 4053.1669 | 25127.282 | 191957.6188 | 28680.477 | 0.077726 | -221463.0411 | 221463.0411
C | Xist Rating 6940 | -34.57 | 1316.42 | 150.297 | 35.7 | 2219.36 | 8801.15 | 15364.3 | 0.53 | 2.01 | 20.731 | 26.425 | 1 | 1 | 2050 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 2921609.8912 | 219094.6238 | 4093.0012 | 25250.4549 | 193844.1689 | 28451.9615 | 0.078107 | -219698.505 | 219698.505
C | Xist Rating 6941 | -34.15 | 1328.72 | 150.297 | 35.7 | 2213.81 | 8751.99 | 15264.2 | 0.51 | 1.99 | 20.711 | 26.105 | 1 | 1 | 2060 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 2941533.6232 | 221113.572 | 4133.0303 | 25373.6279 | 195739.9441 | 28085.3397 | 0.078488 | -216867.5488 | 216867.5488
C | Xist Rating 6942 | -32.61 | 1366.62 | 150.297 | 35.7 | 2203.28 | 8713.56 | 14936.2 | 0.52 | 1.94 | 20.749 | 24.995 | 1 | 1 | 2070 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3011046.5136 | 223141.7453 | 4173.2542 | 25496.8008 | 197644.9445 | 26958.3917 | 0.078869 | -208165.5551 | 208165.5551
C | Xist Rating 6943 | -32.2 | 1374.79 | 150.297 | 35.7 | 2204.16 | 8752.08 | 14873.5 | 0.51 | 1.93 | 20.751 | 24.804 | 1 | 1 | 2080 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3030257.1264 | 225179.1439 | 4213.6729 | 25619.9738 | 199559.1701 | 26745.6246 | 0.07925 | -206522.6237 | 206522.6237
C | Xist Rating 6944 | -31.74 | 1385.37 | 150.297 | 35.7 | 2202.57 | 8760.2 | 14790.9 | 0.5 | 1.91 | 20.748 | 24.547 | 1 | 1 | 2090 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3051374.4009 | 227225.7676 | 4254.2864 | 25743.1467 | 201482.6208 | 26463.8935 | 0.079631 | -204347.1709 | 204347.1709
C | Xist Rating 6945 | -31.28 | 1395.97 | 150.297 | 35.7 | 2201.02 | 8768.76 | 14709.3 | 0.49 | 1.9 | 20.747 | 24.294 | 1 | 1 | 2100 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3072557.8894 | 229281.6165 | 4295.0947 | 25866.3197 | 203415.2968 | 26186.2269 | 0.080012 | -202203.1032 | 202203.1032
C | Xist Rating 6946 | -30.87 | 1405.31 | 150.297 | 35.7 | 2200.03 | 8782 | 14638.7 | 0.49 | 1.89 | 20.747 | 24.08 | 1 | 1 | 2110 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3091724.1593 | 231346.6906 | 4336.0977 | 25989.4927 | 205357.1979 | 25968.5452 | 0.080393 | -200522.2222 | 200522.2222
C | Xist Rating 6947 | -29.45 | 1441.07 | 150.297 | 35.7 | 2190.21 | 8743 | 14359 | 0.49 | 1.84 | 20.782 | 23.187 | 1 | 1 | 2120 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3156245.9247 | 233420.9898 | 4377.2956 | 26112.6656 | 207308.3242 | 25047.3527 | 0.080774 | -193409.0182 | 193409.0182
C | Xist Rating 6948 | -28.92 | 1454.2 | 150.297 | 35.7 | 2187.01 | 8732.95 | 14263.7 | 0.48 | 1.83 | 20.779 | 22.901 | 1 | 1 | 2130 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3180349.942 | 235504.5143 | 4418.6882 | 26235.8386 | 209268.6757 | 24734.9273 | 0.081155 | -190996.5522 | 190996.5522
C | Xist Rating 6949 | -28.47 | 1467.36 | 150.297 | 35.7 | 2182 | 8693.82 | 14169.8 | 0.48 | 1.81 | 20.774 | 22.622 | 1 | 1 | 2140 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3201779.52 | 237597.2639 | 4460.2756 | 26359.0115 | 211238.2524 | 24449.4268 | 0.081536 | -188791.993 | 188791.993
C | Xist Rating 6950 | -28.15 | 1474.28 | 150.297 | 35.7 | 2182.03 | 8714.48 | 14123.3 | 0.47 | 1.8 | 20.776 | 22.493 | 1 | 1 | 2150 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3216923.1884 | 239699.2387 | 4502.0578 | 26482.1845 | 213217.0543 | 24300.0003 | 0.081917 | -187638.1609 | 187638.1609
C | Xist Rating 6951 | -27.74 | 1483.56 | 150.297 | 35.7 | 2181.48 | 8734.14 | 14058.9 | 0.46 | 1.79 | 20.78 | 22.307 | 1 | 1 | 2160 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3236356.4688 | 241810.4387 | 4544.0348 | 26605.3574 | 215205.0813 | 24091.2791 | 0.082298 | -186026.4716 | 186026.4716
C | Xist Rating 6952 | -26.26 | 1522.12 | 150.297 | 35.7 | 2170.38 | 8679.28 | 13785.8 | 0.46 | 1.75 | 20.81 | 21.484 | 1 | 1 | 2170 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3303578.8056 | 243930.8639 | 4586.2066 | 26728.5304 | 217202.3336 | 23242.222 | 0.082679 | -179470.2771 | 179470.2771
C | Xist Rating 6953 | -25.69 | 1535.02 | 150.297 | 35.7 | 2169.36 | 8702.85 | 13698.9 | 0.46 | 1.74 | 20.814 | 21.234 | 1 | 1 | 2180 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3330010.9872 | 246060.5143 | 4628.5732 | 26851.7033 | 219208.811 | 22987.068 | 0.08306 | -177500.0462 | 177500.0462
C | Xist Rating 6954 | -25.3 | 1544.55 | 150.297 | 35.7 | 2167.9 | 8707.5 | 13638.8 | 0.45 | 1.73 | 20.817 | 21.07 | 1 | 1 | 2190 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3348429.945 | 248199.3898 | 4671.1346 | 26974.8763 | 221224.5136 | 22800.7463 | 0.083441 | -176061.3188 | 176061.3188
C | Xist Rating 6955 | -24.99 | 1554.47 | 150.297 | 35.7 | 2164.24 | 8676.37 | 13579.2 | 0.44 | 1.72 | 20.806 | 20.913 | 1 | 1 | 2200 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3364246.1528 | 250347.4906 | 4713.8907 | 27098.0492 | 223249.4414 | 22620.8952 | 0.083822 | -174672.5567 | 174672.5567
C | Xist Rating 6956 | -24.45 | 1567.63 | 150.297 | 35.7 | 2161.34 | 8669.33 | 13495.3 | 0.44 | 1.7 | 20.812 | 20.68 | 1 | 1 | 2210 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3388181.4242 | 252504.8165 | 4756.8417 | 27221.2222 | 225283.5943 | 22383.2901 | 0.084203 | -172837.8333 | 172837.8333
C | Xist Rating 6957 | -22.95 | 1606.06 | 150.297 | 35.7 | 2152.05 | 8639.89 | 13246.1 | 0.44 | 1.66 | 20.849 | 19.966 | 1 | 1 | 2220 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3456321.423 | 254671.3676 | 4799.9874 | 27344.3951 | 227326.9725 | 21647.527 | 0.084584 | -167156.4655 | 167156.4655
C | Xist Rating 6958 | -22.48 | 1616.62 | 150.297 | 35.7 | 2151.51 | 8662.58 | 13182.4 | 0.44 | 1.65 | 20.853 | 19.796 | 1 | 1 | 2230 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3478174.0962 | 256847.1439 | 4843.3279 | 27467.5681 | 229379.5758 | 21475.2702 | 0.084965 | -165826.3443 | 165826.3443
C | Xist Rating 6959 | -22.03 | 1628.88 | 150.297 | 35.7 | 2148.26 | 8645.24 | 13111.6 | 0.43 | 1.64 | 20.849 | 19.612 | 1 | 1 | 2240 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3499257.7488 | 259032.1453 | 4886.8633 | 27590.741 | 231441.4043 | 21267.1887 | 0.085346 | -164219.5939 | 164219.5939
C | Xist Rating 6960 | -21.53 | 1642.35 | 150.297 | 35.7 | 2144.9 | 8629.83 | 13034 | 0.42 | 1.63 | 20.847 | 19.408 | 1 | 1 | 2250 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3522676.515 | 261226.372 | 4930.5934 | 27713.914 | 233512.458 | 21038.2415 | 0.085727 | -162451.7244 | 162451.7244
C | Xist Rating 6961 | -21.2 | 1649.23 | 150.297 | 35.7 | 2145.44 | 8658.01 | 12995.5 | 0.42 | 1.62 | 20.852 | 19.313 | 1 | 1 | 2260 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3538324.0112 | 263429.8238 | 4974.5182 | 27837.0869 | 235592.7369 | 20943.7216 | 0.086108 | -161721.8669 | 161721.8669
C | Xist Rating 6962 | -19.6 | 1690.54 | 150.297 | 35.7 | 2136.04 | 8631.14 | 12751.9 | 0.42 | 1.59 | 20.881 | 18.651 | 1 | 1 | 2270 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3611061.0616 | 265642.5008 | 5018.6379 | 27960.2599 | 237682.241 | 20261.4007 | 0.086489 | -156453.1655 | 156453.1655
C | Xist Rating 6963 | -19.14 | 1702.75 | 150.297 | 35.7 | 2133.41 | 8623.02 | 12686.1 | 0.41 | 1.58 | 20.875 | 18.487 | 1 | 1 | 2280 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3632663.8775 | 267864.4031 | 5062.9524 | 28083.4328 | 239780.9702 | 20073.4262 | 0.08687 | -155001.6766 | 155001.6766
C | Xist Rating 6964 | -18.53 | 1717.22 | 150.297 | 35.7 | 2132.05 | 8643.25 | 12607 | 0.41 | 1.56 | 20.877 | 18.285 | 1 | 1 | 2290 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3661198.901 | 270095.5304 | 5107.4617 | 28206.6058 | 241888.9247 | 19867.5702 | 0.087251 | -153412.1105 | 153412.1105
C | Xist Rating 6965 | -18.14 | 1726.9 | 150.297 | 35.7 | 2131.05 | 8653.87 | 12557 | 0.4 | 1.56 | 20.877 | 18.165 | 1 | 1 | 2300 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3680110.245 | 272335.883 | 5152.1657 | 28329.7787 | 244006.1043 | 19725.2637 | 0.087632 | -152313.2574 | 152313.2574
| Xist Rating 6966 | -17.78 | 1736.85 | 150.297 | 35.7 | 2128.66 | 8641.48 | 12507.6 | 0.4 | 1.55 | 20.874 | 18.049 | 1 | 1 | 2310 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3697163.121 | 274585.4608 | 5197.0645 | 28452.9517 | 246132.5091 | 19608.4168 | 0.088013 | -151410.997 | 151410.997
| Xist Rating 6967 | -16.15 | 1779.26 | 150.297 | 35.7 | 2119.63 | 8621.07 | 12277.1 | 0.4 | 1.51 | 20.905 | 17.451 | 1 | 1 | 2320 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3771372.8738 | 276844.2637 | 5242.1582 | 28576.1246 | 248268.1391 | 18992.4269 | 0.088394 | -146654.4865 | 146654.4865
| Xist Rating 6968 | -15.69 | 1791.5 | 150.297 | 35.7 | 2117.32 | 8617.28 | 12216.8 | 0.39 | 1.5 | 20.901 | 17.308 | 1 | 1 | 2330 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3793178.78 | 279112.2918 | 5287.4466 | 28699.2976 | 250412.9942 | 18825.6735 | 0.088775 | -145366.8606 | 145366.8606
| Xist Rating 6969 | -15.21 | 1803.71 | 150.297 | 35.7 | 2115.41 | 8619.78 | 12157.2 | 0.39 | 1.49 | 20.905 | 17.168 | 1 | 1 | 2340 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3815586.1711 | 281389.5451 | 5332.9298 | 28822.4705 | 252567.0746 | 18684.1012 | 0.089156 | -144273.6767 | 144273.6767
| Xist Rating 6970 | -14.82 | 1814.77 | 150.297 | 35.7 | 2112.76 | 8606.2 | 12104.7 | 0.38 | 1.49 | 20.899 | 17.047 | 1 | 1 | 2350 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3834173.4652 | 283676.0236 | 5378.6078 | 28945.6435 | 254730.3801 | 18539.8363 | 0.089537 | -143159.7018 | 143159.7018
| Xist Rating 6971 | -14.34 | 1828.29 | 150.297 | 35.7 | 2109.69 | 8593.22 | 12039.8 | 0.38 | 1.48 | 20.894 | 16.894 | 1 | 1 | 2360 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3857125.1301 | 285971.7273 | 5424.4805 | 29068.8164 | 256902.9109 | 18384.3049 | 0.089918 | -141958.7292 | 141958.7292
| Xist Rating 6972 | -12.89 | 1867.14 | 150.297 | 35.7 | 2101.38 | 8569.78 | 11846.8 | 0.38 | 1.45 | 20.92 | 16.42 | 1 | 1 | 2370 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3923570.6532 | 288276.6561 | 5470.5481 | 29191.9894 | 259084.6668 | 17896.6652 | 0.090299 | -138193.3047 | 138193.3047
| Xist Rating 6973 | -12.46 | 1879.6 | 150.297 | 35.7 | 2098.26 | 8551.46 | 11791.2 | 0.38 | 1.44 | 20.913 | 16.295 | 1 | 1 | 2380 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3943889.496 | 290590.8102 | 5516.8105 | 29315.1623 | 261275.6479 | 17770.1325 | 0.09068 | -137216.2527 | 137216.2527
| Xist Rating 6974 | -11.94 | 1892.67 | 150.297 | 35.7 | 2096.61 | 8561.22 | 11730 | 0.37 | 1.43 | 20.911 | 16.153 | 1 | 1 | 2390 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 3968190.8487 | 292914.1894 | 5563.2676 | 29438.3353 | 263475.8541 | 17603.7443 | 0.091061 | -135931.4475 | 135931.4475
C | Xist Rating 6977 | -1.84 | 2171.73 | 150.297 | 35.7 | 2038.12 | 8375.14 | 10538 | 0.4 | 1.25 | 20.943 | 13.458 | 1 | 1 | 2420 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4426246.3476 | 299939.6782 | 5703.8078 | 29807.8541 | 270131.824 | 14884.834 | 0.092204 | -114936.7423 | 114936.7423
C | Xist Rating 6978 | -1.71 | 2173.09 | 150.297 | 35.7 | 2039.93 | 8405.86 | 10537.9 | 0.39 | 1.25 | 20.945 | 13.469 | 1 | 1 | 2430 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4432951.4837 | 302299.9581 | 5751.0441 | 29931.0271 | 272368.931 | 14877.2855 | 0.092585 | -114878.4553 | 114878.4553
C | Xist Rating 6979 | -1.7 | 2174.46 | 150.297 | 35.7 | 2039.58 | 8399.93 | 10537.9 | 0.38 | 1.25 | 20.937 | 13.48 | 1 | 1 | 2440 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4434985.1268 | 304669.4633 | 5798.4752 | 30054.2 | 274615.2632 | 14869.13 | 0.092966 | -114815.4808 | 114815.4808
C | Xist Rating 6980 | -1.69 | 2175.79 | 150.297 | 35.7 | 2039.16 | 8392.89 | 10537.9 | 0.38 | 1.25 | 20.936 | 13.491 | 1 | 1 | 2450 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4436783.9364 | 307048.1936 | 5846.1011 | 30177.373 | 276870.8206 | 14884.0781 | 0.093347 | -114930.9055 | 114930.9055
C | Xist Rating 6981 | -1.68 | 2177.26 | 150.297 | 35.7 | 2038.49 | 8381.59 | 10537.9 | 0.37 | 1.25 | 20.93 | 13.502 | 1 | 1 | 2460 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4438322.7374 | 309436.1491 | 5893.9217 | 30300.5459 | 279135.6032 | 14875.737 | 0.093728 | -114866.4981 | 114866.4981
C | Xist Rating 6982 | -1.63 | 2178.61 | 150.297 | 35.7 | 2038.87 | 8387.91 | 10537.9 | 0.36 | 1.25 | 20.962 | 13.512 | 1 | 1 | 2470 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4441902.5707 | 311833.3298 | 5941.9372 | 30423.7189 | 281409.6109 | 14867.6957 | 0.094109 | -114804.4051 | 114804.4051
C | Xist Rating 6983 | -1.63 | 2179.96 | 150.297 | 35.7 | 2038.36 | 8379.35 | 10537.9 | 0.36 | 1.25 | 20.956 | 13.523 | 1 | 1 | 2480 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4443543.2656 | 314239.7357 | 5990.1474 | 30546.8918 | 283692.8438 | 14882.2617 | 0.09449 | -114916.8797 | 114916.8797
C | Xist Rating 6984 | -1.62 | 2181.36 | 150.297 | 35.7 | 2037.76 | 8369.18 | 10537.9 | 0.35 | 1.25 | 20.95 | 13.534 | 1 | 1 | 2490 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4445088.1536 | 316655.3667 | 6038.5525 | 30670.0648 | 285985.3019 | 14873.4427 | 0.094871 | -114848.782 | 114848.782
C | Xist Rating 6985 | -1.59 | 2182.34 | 150.297 | 35.7 | 2038.04 | 8373.87 | 10537.9 | 0.35 | 1.25 | 20.947 | 13.542 | 1 | 1 | 2500 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4447696.2136 | 319080.223 | 6087.1523 | 30793.2377 | 288286.9852 | 14884.9198 | 0.095252 | -114937.4051 | 114937.4051
C | Xist Rating 6986 | -1.61 | 2184.19 | 150.297 | 35.7 | 2036.47 | 8347.54 | 10537.9 | 0.34 | 1.25 | 20.941 | 13.555 | 1 | 1 | 2510 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4448037.4093 | 321514.3044 | 6135.9469 | 30916.4107 | 290597.8937 | 14877.9096 | 0.095633 | -114883.2743 | 114883.2743
C | Xist Rating 6987 | -1.6 | 2185.65 | 150.297 | 35.7 | 2035.88 | 8337.58 | 10537.8 | 0.34 | 1.25 | 20.978 | 13.566 | 1 | 1 | 2520 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4449721.122 | 323957.611 | 6184.9363 | 31039.5836 | 292918.0273 | 14893.9456 | 0.096014 | -115007.0999 | 115007.0999
C | Xist Rating 6988 | -1.58 | 2186.98 | 150.297 | 35.6 | 2035.44 | 8330.19 | 10537.8 | 0.33 | 1.25 | 20.973 | 13.576 | 1 | 1 | 2530 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4451466.5712 | 326410.1428 | 6234.1205 | 31162.7566 | 295247.3862 | 14883.5502 | 0.096395 | -114926.8294 | 114926.8294
C | Xist Rating 6989 | -1.57 | 2188.13 | 150.297 | 35.6 | 2035.34 | 8328.6 | 10537.8 | 0.33 | 1.25 | 20.968 | 13.586 | 1 | 1 | 2540 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4453588.5142 | 328871.8998 | 6283.4995 | 31285.9295 | 297585.9702 | 14896.8497 | 0.096776 | -115029.5244 | 115029.5244
C | Xist Rating 6990 | -1.57 | 2189.68 | 150.297 | 35.6 | 2034.46 | 8313.83 | 10537.8 | 0.32 | 1.25 | 20.964 | 13.597 | 1 | 1 | 2550 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4454816.3728 | 331342.8819 | 6333.0732 | 31409.1025 | 299933.7794 | 14887.2614 | 0.097157 | -114955.4866 | 114955.4866
C | Xist Rating 6991 | -1.52 | 2191.13 | 150.297 | 35.6 | 2034.65 | 8317.04 | 10537.8 | 0.32 | 1.25 | 20.957 | 13.607 | 1 | 1 | 2560 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4458182.6545 | 333823.0893 | 6382.8418 | 31532.2754 | 302290.8138 | 14900.3964 | 0.097538 | -115056.9116 | 115056.9116
C | Xist Rating 6992 | -1.51 | 2192.52 | 150.297 | 35.6 | 2034.35 | 8312.13 | 10537.7 | 0.31 | 1.25 | 20.952 | 13.618 | 1 | 1 | 2570 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4460353.062 | 336312.5218 | 6432.8051 | 31655.4484 | 304657.0734 | 14890.5051 | 0.097919 | -114980.5331 | 114980.5331
C | Xist Rating 6993 | -1.47 | 2193.88 | 150.297 | 35.6 | 2034.46 | 8314.01 | 10537.7 | 0.31 | 1.25 | 21 | 13.628 | 1 | 1 | 2580 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4463361.1048 | 338811.1795 | 6482.9633 | 31778.6213 | 307032.5581 | 14905.5223 | 0.0983 | -115096.4923 | 115096.4923
C | Xist Rating 6994 | -1.44 | 2195.24 | 150.297 | 35.6 | 2034.46 | 8313.96 | 10537.7 | 0.3 | 1.25 | 21.004 | 13.638 | 1 | 1 | 2590 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4466127.9704 | 341319.0624 | 6533.3162 | 31901.7943 | 309417.2681 | 14894.5846 | 0.098681 | -115012.0339 | 115012.0339
C | Xist Rating 6995 | -1.43 | 2196.42 | 150.298 | 35.6 | 2034.31 | 8311.42 | 10537.7 | 0.3 | 1.25 | 21.001 | 13.647 | 1 | 1 | 2600 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4468199.1702 | 343836.1705 | 6583.8639 | 32024.9672 | 311811.2032 | 14906.6507 | 0.099062 | -115105.205 | 115105.205
C | Xist Rating 6996 | -1.42 | 2198.11 | 150.298 | 35.6 | 2033.54 | 8298.56 | 10537.7 | 0.29 | 1.25 | 20.999 | 13.659 | 1 | 1 | 2610 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4469944.6094 | 346362.5037 | 6634.6064 | 32148.1402 | 314214.3635 | 14897.2993 | 0.099443 | -115032.9964 | 115032.9964
C | Xist Rating 6997 | -1.39 | 2199.51 | 150.298 | 35.6 | 2033.42 | 8296.65 | 10537.7 | 0.29 | 1.25 | 21 | 13.669 | 1 | 1 | 2620 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4472527.6242 | 348898.0622 | 6685.5437 | 32271.3132 | 316626.749 | 14910.448 | 0.099824 | -115134.5274 | 115134.5274
C | Xist Rating 6998 | -1.35 | 2200.93 | 150.298 | 35.6 | 2033.42 | 8296.61 | 10537.7 | 0.29 | 1.25 | 21.042 | 13.679 | 1 | 1 | 2630 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4475415.0806 | 351442.8458 | 6736.6758 | 32394.4861 | 319048.3597 | 14924.9987 | 0.10021 | -115246.884 | 115246.884
C | Xist Rating 6999 | -1.33 | 2202.18 | 150.298 | 35.6 | 2033.35 | 8295.47 | 10537.6 | 0.28 | 1.25 | 21.039 | 13.689 | 1 | 1 | 2640 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4477802.703 | 353996.8546 | 6788.0027 | 32517.6591 | 321479.1955 | 14913.1191 | 0.10059 | -115155.1527 | 115155.1527
C | Xist Rating 7000 | -1.31 | 2203.68 | 150.298 | 35.6 | 2032.95 | 8288.86 | 10537.6 | 0.28 | 1.25 | 21.034 | 13.699 | 1 | 1 | 2650 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4479971.256 | 356560.0886 | 6839.5243 | 32640.832 | 323919.2566 | 14925.9784 | 0.10097 | -115254.4486 | 115254.4486
C | Xist Rating 7001 | -1.27 | 2205.02 | 150.298 | 35.6 | 2033.14 | 8292.01 | 10537.6 | 0.27 | 1.25 | 21.036 | 13.709 | 1 | 1 | 2660 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4483114.3628 | 359132.5478 | 6891.2408 | 32764.005 | 326368.5428 | 14913.9881 | 0.10135 | -115161.8629 | 115161.8629
C | Xist Rating 7002 | -1.24 | 2206.41 | 150.298 | 35.6 | 2033.05 | 8290.63 | 10537.5 | 0.27 | 1.25 | 21.038 | 13.719 | 1 | 1 | 2670 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4485741.8505 | 361714.2321 | 6943.152 | 32887.1779 | 328827.0542 | 14926.9836 | 0.10173 | -115262.211 | 115262.211
C | Xist Rating 7003 | -1.17 | 2207.82 | 150.298 | 35.6 | 2033.82 | 8303.29 | 10537.6 | 0.27 | 1.25 | 21.082 | 13.729 | 1 | 1 | 2680 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4490308.4724 | 364305.1417 | 6995.258 | 33010.3509 | 331294.7908 | 14941.3419 | 0.10211 | -115373.0818 | 115373.0818
C | Xist Rating 7004 | -1.12 | 2209.2 | 150.298 | 35.6 | 2034.21 | 8309.81 | 10537.6 | 0.26 | 1.25 | 21.081 | 13.739 | 1 | 1 | 2690 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4493976.732 | 366905.2764 | 7047.5588 | 33133.5238 | 333771.7526 | 14928.8267 | 0.10249 | -115276.4427 | 115276.4427
C | Xist Rating 7005 | -1.05 | 2210.4 | 150.298 | 35.6 | 2035.13 | 8325.29 | 10537.5 | 0.26 | 1.25 | 21.08 | 13.748 | 1 | 1 | 2700 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4498451.352 | 369514.6363 | 7100.0544 | 33256.6968 | 336257.9396 | 14940.5986 | 0.10287 | -115367.3421 | 115367.3421
C | Xist Rating 7006 | -0.99 | 2212.06 | 150.298 | 35.6 | 2035.61 | 8333.37 | 10537.5 | 0.26 | 1.25 | 21.079 | 13.759 | 1 | 1 | 2710 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4502891.4566 | 372133.2214 | 7152.7448 | 33379.8697 | 338753.3517 | 14954.4473 | 0.10325 | -115474.2777 | 115474.2777
C | Xist Rating 7007 | -0.97 | 2213.4 | 150.298 | 35.6 | 2035.35 | 8329.06 | 10537.4 | 0.25 | 1.25 | 21.076 | 13.769 | 1 | 1 | 2720 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4505043.69 | 374761.0317 | 7205.63 | 33503.0427 | 341257.989 | 14941.4973 | 0.10363 | -115374.2814 | 115374.2814
C | Xist Rating 7008 | -0.96 | 2214.72 | 150.298 | 35.6 | 2034.79 | 8319.68 | 10537.5 | 0.25 | 1.25 | 21.111 | 13.778 | 1 | 1 | 2730 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4506490.1088 | 377398.0672 | 7258.71 | 33626.2156 | 343771.8515 | 14954.2763 | 0.10402 | -115472.9578 | 115472.9578
C | Xist Rating 7009 | -0.97 | 2216.01 | 150.298 | 35.6 | 2033.93 | 8305.2 | 10537.5 | 0.25 | 1.25 | 21.106 | 13.787 | 1 | 1 | 2740 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4507209.2193 | 380044.3278 | 7311.9847 | 33749.3886 | 346294.9392 | 14965.835 | 0.1044 | -115562.2109 | 115562.2109
C | Xist Rating 7010 | -0.97 | 2217.56 | 150.298 | 35.6 | 2033.02 | 8290.01 | 10537.5 | 0.25 | 1.25 | 21.106 | 13.798 | 1 | 1 | 2750 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4508343.8312 | 382699.8136 | 7365.4543 | 33872.5615 | 348827.2521 | 14979.6237 | 0.10478 | -115668.6833 | 115668.6833
C | Xist Rating 7011 | -1 | 2218.98 | 150.298 | 35.6 | 2031.8 | 8269.82 | 10537.5 | 0.24 | 1.25 | 21.101 | 13.808 | 1 | 1 | 2760 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4508523.564 | 385364.5246 | 7419.1186 | 33995.7345 | 351368.7902 | 14966.1139 | 0.10516 | -115564.3641 | 115564.3641
C | Xist Rating 7012 | -0.99 | 2220.22 | 150.298 | 35.6 | 2031.46 | 8264.24 | 10537.5 | 0.24 | 1.25 | 21.104 | 13.817 | 1 | 1 | 2770 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4510288.1212 | 388038.4608 | 7472.9777 | 34118.9074 | 353919.5534 | 14977.8198 | 0.10554 | -115654.7541 | 115654.7541
C | Xist Rating 7013 | -0.97 | 2221.76 | 150.298 | 35.6 | 2030.94 | 8255.54 | 10537.5 | 0.24 | 1.25 | 21.15 | 13.827 | 1 | 1 | 2780 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4512261.2544 | 390721.6222 | 7527.0316 | 34242.0804 | 356479.5418 | 14991.8508 | 0.10592 | -115763.0982 | 115763.0982
C | Xist Rating 7014 | -1 | 2223.17 | 150.298 | 35.6 | 2029.68 | 8234.78 | 10537.5 | 0.23 | 1.25 | 21.142 | 13.836 | 1 | 1 | 2790 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4512323.6856 | 393414.0088 | 7581.2803 | 34365.2533 | 359048.7555 | 14976.7921 | 0.1063 | -115646.819 | 115646.819
C | Xist Rating 7015 | -0.95 | 2224.15 | 150.298 | 35.6 | 2030.33 | 8245.45 | 10537.5 | 0.23 | 1.25 | 21.15 | 13.844 | 1 | 1 | 2800 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4515758.4695 | 396115.6205 | 7635.7238 | 34488.4263 | 361627.1943 | 14987.5107 | 0.10668 | -115729.5852 | 115729.5852
C | Xist Rating 7016 | -0.95 | 2225.89 | 150.298 | 35.6 | 2029.36 | 8229.48 | 10537.5 | 0.23 | 1.25 | 21.154 | 13.855 | 1 | 1 | 2810 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4517132.1304 | 398826.4575 | 7690.3621 | 34611.5992 | 364214.8582 | 15001.2306 | 0.10706 | -115835.5263 | 115835.5263
C | Xist Rating 7017 | -0.96 | 2227.37 | 150.298 | 35.6 | 2028.22 | 8210.88 | 10537.5 | 0.23 | 1.25 | 21.151 | 13.865 | 1 | 1 | 2820 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4517596.3814 | 401546.5196 | 7745.1952 | 34734.7722 | 366811.7474 | 15013.7093 | 0.10744 | -115931.8833 | 115931.8833
C | Xist Rating 7018 | -0.93 | 2228.74 | 150.298 | 35.6 | 2028.17 | 8210.01 | 10537.5 | 0.22 | 1.25 | 21.197 | 13.875 | 1 | 1 | 2830 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4520263.6058 | 404275.8069 | 7800.223 | 34857.9451 | 369417.8617 | 15000.7278 | 0.10783 | -115831.6436 | 115831.6436
C | Xist Rating 7019 | -0.85 | 2230.06 | 150.298 | 35.6 | 2029.15 | 8226.13 | 10537.6 | 0.22 | 1.25 | 21.212 | 13.884 | 1 | 1 | 2840 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4525126.249 | 407014.3193 | 7855.4457 | 34981.1181 | 372033.2013 | 15012.5847 | 0.10821 | -115923.1995 | 115923.1995
C | Xist Rating 7020 | -0.87 | 2231.5 | 150.298 | 35.6 | 2028.01 | 8207.35 | 10537.6 | 0.22 | 1.25 | 21.201 | 13.893 | 1 | 1 | 2850 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4525504.315 | 409762.057 | 7910.8631 | 35104.291 | 374657.766 | 15023.7138 | 0.10859 | -116009.1357 | 116009.1357
C | Xist Rating 7021 | -0.81 | 2232.91 | 150.298 | 35.6 | 2028.55 | 8216.16 | 10537.6 | 0.22 | 1.25 | 21.213 | 13.903 | 1 | 1 | 2860 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4529569.5805 | 412519.0199 | 7966.4753 | 35227.464 | 377291.5559 | 15036.528 | 0.10897 | -116108.0832 | 116108.0832
C | Xist Rating 7022 | -0.64 | 2234.1 | 150.298 | 35.6 | 2031.54 | 8265.45 | 10537.7 | 0.21 | 1.25 | 21.247 | 13.912 | 1 | 1 | 2870 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4538663.514 | 415285.2079 | 8022.2824 | 35350.6369 | 379934.571 | 15021.5951 | 0.10935 | -115992.7753 | 115992.7753
C | Xist Rating 7023 | -0.63 | 2235.61 | 150.298 | 35.6 | 2030.94 | 8255.48 | 10537.7 | 0.21 | 1.25 | 21.288 | 13.921 | 1 | 1 | 2880 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4540389.7734 | 418060.6211 | 8078.2842 | 35473.8099 | 382586.8112 | 15034.0531 | 0.10973 | -116088.9727 | 116088.9727
C | Xist Rating 7024 | -0.22 | 2236.95 | 150.298 | 35.6 | 2038.79 | 8386.63 | 10537.9 | 0.21 | 1.25 | 21.335 | 13.931 | 1 | 1 | 2890 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4560671.2905 | 420845.2595 | 8134.4807 | 35596.9828 | 385248.2767 | 15047.7205 | 0.11011 | -116194.5092 | 116194.5092
C | Xist Rating 7025 | 0.36 | 2238.33 | 150.298 | 35.6 | 2050.28 | 8584.41 | 10538 | 0.2 | 1.25 | 21.4 | 13.941 | 1 | 1 | 2900 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4589203.2324 | 423639.1231 | 8190.8721 | 35720.1558 | 387918.9673 | 15034.07 | 0.11049 | -116089.1036 | 116089.1036
C | Xist Rating 7026 | 0.72 | 2239.87 | 150.298 | 35.6 | 2056.97 | 8702.89 | 10538.1 | 0.2 | 1.25 | 21.437 | 13.952 | 1 | 1 | 2910 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4607345.3939 | 426442.2119 | 8247.4583 | 35843.3287 | 390598.8831 | 15048.3772 | 0.11087 | -116199.5802 | 116199.5802
C | Xist Rating 7027 | 0.44 | 2241.26 | 150.298 | 35.6 | 2050.53 | 8588.81 | 10538 | 0.2 | 1.25 | 21.397 | 13.961 | 1 | 1 | 2920 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4595770.8678 | 429254.5258 | 8304.2393 | 35966.5017 | 393288.0241 | 15058.5984 | 0.11125 | -116278.5056 | 116278.5056
C | Xist Rating 7028 | 1.06 | 2242.65 | 150.298 | 35.6 | 2062.63 | 8805.19 | 10538.1 | 0.2 | 1.25 | 21.505 | 13.971 | 1 | 1 | 2930 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4625757.1695 | 432076.0649 | 8361.215 | 36089.6746 | 395986.3903 | 15073.7385 | 0.11164 | -116395.4132 | 116395.4132
C | Xist Rating 7029 | 1.43 | 2244.02 | 150.298 | 35.6 | 2069.62 | 8933.86 | 10538.1 | 0.19 | 1.25 | 21.543 | 13.98 | 1 | 1 | 2940 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4644268.6724 | 434906.8292 | 8418.3855 | 36212.8476 | 398693.9817 | 15057.6241 | 0.11202 | -116270.9823 | 116270.9823
C | Xist Rating 7030 | 1.66 | 2245.43 | 150.298 | 35.6 | 2073.74 | 9011.18 | 10538.1 | 0.19 | 1.25 | 21.565 | 13.99 | 1 | 1 | 2950 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4656438.0082 | 437746.8187 | 8475.7509 | 36336.0205 | 401410.7982 | 15070.3966 | 0.1124 | -116369.6079 | 116369.6079
C | Xist Rating 7031 | 2.37 | 2246.8 | 150.298 | 35.6 | 2087.79 | 9282.65 | 10538 | 0.19 | 1.25 | 21.639 | 14 | 1 | 1 | 2960 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4690846.572 | 440596.0334 | 8533.311 | 36459.1935 | 404136.8399 | 15084.4837 | 0.11278 | -116478.3847 | 116478.3847
C | Xist Rating 7032 | 2.45 | 2248.18 | 150.298 | 35.6 | 2089.12 | 9309.04 | 10537.9 | 0.18 | 1.25 | 21.625 | 14.009 | 1 | 1 | 2970 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4696717.8016 | 443454.4733 | 8591.0659 | 36582.3664 | 406872.1069 | 15066.5298 | 0.11316 | -116339.7494 | 116339.7494
C | Xist Rating 7033 | 2.45 | 2249.4 | 150.298 | 35.6 | 2088.52 | 9297.16 | 10537.9 | 0.18 | 1.25 | 21.66 | 14.018 | 1 | 1 | 2980 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4697916.888 | 446322.1383 | 8649.0156 | 36705.5394 | 409616.599 | 15078.4626 | 0.11354 | -116431.8915 | 116431.8915
C | Xist Rating 7034 | 2.48 | 2250.96 | 150.298 | 35.6 | 2088.09 | 9288.75 | 10538 | 0.18 | 1.25 | 21.667 | 14.027 | 1 | 1 | 2990 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4700207.0664 | 449199.0286 | 8707.16 | 36828.7123 | 412370.3162 | 15089.7256 | 0.11392 | -116518.8613 | 116518.8613
C | Xist Rating 7035 | 2.48 | 2252.39 | 150.298 | 35.6 | 2087.43 | 9275.53 | 10538 | 0.18 | 1.25 | 21.663 | 14.037 | 1 | 1 | 3000 | 152.4 | 2 | 4.4 | 19.05 | 1.3333 | 26 | E | Rod | 4701706.4577 | 452085.144 | 8765.4993 | 36951.8853 | 415133.2587 | 15101.762 | 0.1143 | -116611.8028 | 116611.8028
C | Xist Rating 7036 | -87.4 | 230.057 | 150.303 | 35.9 | 2361.23 | 7050.39 | 58745.8 | 2.47 | 10.95 | 23.497 | 562.544 | 1 | 1 | 1000 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 543217.4901 | 59771.4676 | 973.9444 | 12597.2336 | 47174.2339 | 586802.5692 | 0.038101 | -4531133.8953 | 4531133.8953
C | Xist Rating 7037 | -87.28 | 232.435 | 150.304 | 35.9 | 2358.9 | 7037.3 | 58284.2 | 2.45 | 10.85 | 23.573 | 551.967 | 1 | 1 | 1010 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 548290.9215 | 60845.642 | 993.5206 | 12723.206 | 48122.436 | 575831.5409 | 0.038482 | -4446418.5224 | 4446418.5224
C | Xist Rating 7038 | -86.35 | 250.485 | 150.304 | 35.9 | 2350.88 | 7024.7 | 54967.5 | 2.47 | 10.07 | 23.624 | 478.333 | 1 | 1 | 1020 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 588860.1768 | 61929.2513 | 1013.2917 | 12849.1783 | 49080.073 | 499415.9514 | 0.038863 | -3856357.5964 | 3856357.5964
C | Xist Rating 7039 | -86.18 | 255.386 | 150.302 | 35.9 | 2334.22 | 6892.42 | 54177.9 | 2.38 | 9.89 | 23.066 | 462.231 | 1 | 1 | 1030 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 596127.1089 | 63022.2954 | 1033.2576 | 12975.1506 | 50047.1448 | 482560.7273 | 0.039244 | -3726206.0238 | 3726206.0238
C | Xist Rating 7040 | -86.09 | 257.839 | 150.302 | 35.9 | 2328.1 | 6846.44 | 53793.2 | 2.34 | 9.8 | 22.937 | 454.523 | 1 | 1 | 1040 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 600274.9759 | 64124.7744 | 1053.4182 | 13101.123 | 51023.6514 | 474523.5057 | 0.039625 | -3664144.7283 | 3664144.7283
C | Xist Rating 7041 | -85.88 | 262.618 | 150.302 | 35.9 | 2321.94 | 6807.51 | 53042.1 | 2.3 | 9.63 | 22.849 | 439.428 | 1 | 1 | 1050 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 609783.2389 | 65236.6882 | 1073.7737 | 13227.0953 | 52009.5929 | 458818.7224 | 0.040006 | -3542876.5551 | 3542876.5551
C | Xist Rating 7042 | -85.75 | 265.051 | 150.302 | 35.9 | 2322.06 | 6815.5 | 52676.3 | 2.27 | 9.54 | 22.82 | 432.277 | 1 | 1 | 1060 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 615464.3251 | 66358.0369 | 1094.3239 | 13353.0676 | 53004.9693 | 451380.2794 | 0.040387 | -3485438.87 | 3485438.87
C | Xist Rating 7043 | -84.81 | 284.445 | 150.301 | 35.9 | 2307.22 | 6744.9 | 49856.6 | 2.25 | 8.9 | 22.606 | 378.214 | 1 | 1 | 1070 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 656277.1929 | 67488.8204 | 1115.0689 | 13479.04 | 54009.7804 | 395214.1753 | 0.040768 | -3051739.1019 | 3051739.1019
C | Xist Rating 7044 | -84.58 | 288.098 | 150.301 | 35.9 | 2313.42 | 6808.51 | 49380.3 | 2.19 | 8.79 | 22.5 | 369.713 | 1 | 1 | 1080 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 666491.6752 | 68629.0388 | 1136.0087 | 13605.0123 | 55024.0265 | 386331.7994 | 0.041149 | -2983151.7493 | 2983151.7493
C | Xist Rating 7045 | -84.29 | 292.957 | 150.301 | 35.9 | 2318.29 | 6864.75 | 48761.2 | 2.13 | 8.65 | 22.336 | 358.8 | 1 | 1 | 1090 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 679159.2835 | 69778.692 | 1157.1433 | 13730.9846 | 56047.7073 | 374937.7266 | 0.04153 | -2895169.7397 | 2895169.7397
C | Xist Rating 7046 | -84.04 | 296.578 | 150.301 | 35.9 | 2327.21 | 6954.26 | 48307.4 | 2.09 | 8.55 | 22.337 | 350.914 | 1 | 1 | 1100 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 690199.2874 | 70937.7801 | 1178.4727 | 13856.957 | 57080.8231 | 366725.5038 | 0.041911 | -2831757.1321 | 2831757.1321
C | Xist Rating 7047 | -83.92 | 299.198 | 150.3 | 35.9 | 2325.04 | 6941.98 | 48010.8 | 2.01 | 8.49 | 21.997 | 346.071 | 1 | 1 | 1110 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 695647.3179 | 72106.303 | 1199.9969 | 13982.9293 | 58123.3736 | 361594.0684 | 0.042292 | -2792133.5481 | 2792133.5481
C | Xist Rating 7048 | -82.79 | 320.795 | 150.3 | 35.9 | 2321.26 | 6973.52 | 45448.2 | 2.05 | 7.92 | 22.294 | 302.812 | 1 | 1 | 1120 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 744648.6017 | 73284.2607 | 1221.7158 | 14108.9017 | 59175.3591 | 316764.2237 | 0.042673 | -2445969.3702 | 2445969.3702
C | Xist Rating 7049 | -82.65 | 323.369 | 150.3 | 35.9 | 2321.97 | 6986.97 | 45189.3 | 1.99 | 7.86 | 22.077 | 298.903 | 1 | 1 | 1130 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 750853.1169 | 74471.6533 | 1243.6296 | 14234.874 | 60236.7793 | 312635.5925 | 0.043054 | -2414089.1746 | 2414089.1746
C | Xist Rating 7050 | -82.42 | 328.299 | 150.299 | 35.8 | 2319.25 | 6976.45 | 44681.2 | 1.93 | 7.75 | 21.875 | 291.073 | 1 | 1 | 1140 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 761407.4557 | 75668.4808 | 1265.7381 | 14360.8463 | 61307.6344 | 304436.2327 | 0.043435 | -2350775.8916 | 2350775.8916
C | Xist Rating 7051 | -82.16 | 333.167 | 150.299 | 35.8 | 2319.82 | 6995.7 | 44186.2 | 1.89 | 7.64 | 21.666 | 283.503 | 1 | 1 | 1150 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 772887.4699 | 76874.7431 | 1288.0414 | 14486.8187 | 62387.9244 | 296528.2571 | 0.043816 | -2289712.6006 | 2289712.6006
C | Xist Rating 7052 | -81.93 | 338.113 | 150.298 | 35.8 | 2316.98 | 6983.94 | 43703.3 | 1.84 | 7.53 | 21.49 | 276.298 | 1 | 1 | 1160 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 783401.0587 | 78090.4402 | 1310.5395 | 14612.791 | 63477.6492 | 288991.0647 | 0.044197 | -2231512.3983 | 2231512.3983
C | Xist Rating 7053 | -80.93 | 357.493 | 150.299 | 35.8 | 2312.4 | 6999.77 | 41832.3 | 1.86 | 7.13 | 21.646 | 248.524 | 1 | 1 | 1170 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 826666.8132 | 79315.5722 | 1333.2324 | 14738.7633 | 64576.8088 | 260203.2922 | 0.044578 | -2009220.8497 | 2009220.8497
C | Xist Rating 7054 | -80.79 | 358.873 | 150.299 | 35.8 | 2321.3 | 7085.43 | 41724.6 | 1.81 | 7.11 | 21.561 | 247.171 | 1 | 1 | 1180 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 833051.8949 | 80550.139 | 1356.1201 | 14864.7357 | 65685.4033 | 258750.8671 | 0.044959 | -1998005.6085 | 1998005.6085
C | Xist Rating 7055 | -80.34 | 368.593 | 150.298 | 35.8 | 2314.32 | 7048.8 | 40885.6 | 1.76 | 6.92 | 21.378 | 235.558 | 1 | 1 | 1190 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 853042.1518 | 81794.1407 | 1379.2026 | 14990.708 | 66803.4327 | 246633.5932 | 0.04534 | -1904439.2311 | 1904439.2311
C | Xist Rating 7056 | -80.12 | 371.059 | 150.298 | 35.8 | 2325.8 | 7163.62 | 40681.8 | 1.73 | 6.88 | 21.422 | 232.843 | 1 | 1 | 1200 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 863009.0222 | 83047.5772 | 1402.4799 | 15116.6803 | 67930.8969 | 243800.5324 | 0.045721 | -1882563.0869 | 1882563.0869
C | Xist Rating 7057 | -79.87 | 376.074 | 150.298 | 35.8 | 2324.53 | 7166.04 | 40281.2 | 1.68 | 6.8 | 21.26 | 227.563 | 1 | 1 | 1210 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 874195.2952 | 84310.4486 | 1425.9519 | 15242.6527 | 69067.7959 | 238261.0173 | 0.046102 | -1839788.4196 | 1839788.4196
C | Xist Rating 7058 | -78.81 | 398.025 | 150.298 | 35.8 | 2312.19 | 7114.81 | 38537.7 | 1.68 | 6.43 | 21.264 | 204.614 | 1 | 1 | 1220 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 920309.4248 | 85582.7548 | 1449.6188 | 15368.625 | 70214.1298 | 214444.8945 | 0.046483 | -1655886.6323 | 1655886.6323
C | Xist Rating 7059 | -78.51 | 402.89 | 150.298 | 35.8 | 2318.11 | 7185.46 | 38183.3 | 1.65 | 6.35 | 21.286 | 200.217 | 1 | 1 | 1230 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 933943.3379 | 86864.4959 | 1473.4804 | 15494.5974 | 71369.8985 | 209861.46 | 0.046864 | -1620494.5659 | 1620494.5659
C | Xist Rating 7060 | -78.24 | 407.895 | 150.298 | 35.8 | 2318.69 | 7205.4 | 37835.3 | 1.61 | 6.28 | 21.173 | 196.026 | 1 | 1 | 1240 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 945782.0576 | 88155.6718 | 1497.5369 | 15620.5697 | 72535.1021 | 205467.419 | 0.047245 | -1586564.9464 | 1586564.9464
C | Xist Rating 7061 | -78.08 | 410.506 | 150.298 | 35.8 | 2322.51 | 7249.65 | 37664.4 | 1.57 | 6.24 | 21.101 | 194.052 | 1 | 1 | 1250 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 953404.2901 | 89456.2826 | 1521.7881 | 15746.542 | 73709.7405 | 203378.9159 | 0.047626 | -1570438.0786 | 1570438.0786
C | Xist Rating 7062 | -77.69 | 417.827 | 150.297 | 35.8 | 2322.83 | 7274.58 | 37161.3 | 1.54 | 6.14 | 21.054 | 188.013 | 1 | 1 | 1260 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 970541.0904 | 90766.3282 | 1546.2341 | 15872.5144 | 74893.8138 | 197082.4328 | 0.048007 | -1521818.3053 | 1521818.3053
C | Xist Rating 7063 | -76.66 | 438.614 | 150.298 | 35.8 | 2316.15 | 7272.26 | 35777.5 | 1.54 | 5.85 | 21.123 | 171.689 | 1 | 1 | 1270 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1015895.8161 | 92085.8086 | 1570.8749 | 15998.4867 | 76087.3219 | 180150.5673 | 0.048388 | -1391074.9278 | 1391074.9278
C | Xist Rating 7064 | -76.43 | 443.687 | 150.297 | 35.8 | 2313.31 | 7258.62 | 35477.2 | 1.5 | 5.79 | 20.998 | 168.414 | 1 | 1 | 1280 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1026385.574 | 93414.7239 | 1595.7105 | 16124.459 | 77290.2649 | 176704.8305 | 0.048769 | -1364467.8617 | 1364467.8617
C | Xist Rating 7065 | -76.16 | 448.709 | 150.297 | 35.8 | 2314.36 | 7283.35 | 35182.8 | 1.47 | 5.73 | 20.961 | 165.219 | 1 | 1 | 1290 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1038474.1612 | 94753.0741 | 1620.7408 | 16250.4314 | 78502.6427 | 173361.3759 | 0.04915 | -1338650.5916 | 1338650.5916
C | Xist Rating 7066 | -75.77 | 456.009 | 150.297 | 35.8 | 2315.27 | 7313.99 | 34751.1 | 1.45 | 5.64 | 20.995 | 160.501 | 1 | 1 | 1300 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1055783.9574 | 96100.8591 | 1645.966 | 16376.4037 | 79724.4554 | 168453.996 | 0.049531 | -1300757.1051 | 1300757.1051
C | Xist Rating 7067 | -75.53 | 459.854 | 150.297 | 35.8 | 2319.99 | 7372.36 | 34539.7 | 1.41 | 5.59 | 20.945 | 158.305 | 1 | 1 | 1310 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1066856.6815 | 97458.0789 | 1671.3859 | 16502.376 | 80955.7029 | 166133.6463 | 0.049912 | -1282839.9794 | 1282839.9794
C | Xist Rating 7068 | -74.49 | 480.739 | 150.297 | 35.8 | 2314.09 | 7376.47 | 33363 | 1.42 | 5.35 | 20.999 | 145.77 | 1 | 1 | 1320 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1112473.3125 | 98824.7336 | 1697.0007 | 16628.3484 | 82196.3852 | 153146.2363 | 0.050293 | -1182554.6422 | 1182554.6422
C | Xist Rating 7069 | -74.12 | 488.255 | 150.297 | 35.8 | 2311.9 | 7375.94 | 32979.9 | 1.38 | 5.28 | 20.892 | 141.95 | 1 | 1 | 1330 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1128796.7345 | 100200.8231 | 1722.8102 | 16754.3207 | 83446.5024 | 149133.6597 | 0.050674 | -1151570.5892 | 1151570.5892
C | Xist Rating 7070 | -73.72 | 495.67 | 150.297 | 35.8 | 2313.95 | 7418.74 | 32606.7 | 1.35 | 5.2 | 20.798 | 138.257 | 1 | 1 | 1340 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1146955.5965 | 101586.3475 | 1748.8145 | 16880.2931 | 84706.0545 | 145266.1398 | 0.051055 | -1121706.6257 | 1121706.6257
C | Xist Rating 7071 | -73.46 | 499.533 | 150.297 | 35.8 | 2319.31 | 7485.3 | 32423.5 | 1.32 | 5.16 | 20.759 | 136.523 | 1 | 1 | 1350 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1158571.8822 | 102981.3068 | 1775.0136 | 17006.2654 | 85975.0414 | 143437.0972 | 0.051436 | -1107583.2437 | 1107583.2437
C | Xist Rating 7072 | -73.18 | 501.945 | 150.297 | 35.8 | 2333.18 | 7639.42 | 32303.1 | 1.31 | 5.14 | 20.845 | 135.352 | 1 | 1 | 1360 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1171128.0351 | 104385.7008 | 1801.4075 | 17132.2377 | 87253.4631 | 142227.5113 | 0.051817 | -1098243.1418 | 1098243.1418
C | Xist Rating 7073 | -71.9 | 531.556 | 150.297 | 35.8 | 2309.46 | 7480.08 | 30902.2 | 1.3 | 4.86 | 20.764 | 121.937 | 1 | 1 | 1370 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1227607.3198 | 105799.5298 | 1827.9962 | 17258.2101 | 88541.3197 | 128289.0279 | 0.052198 | -990613.868 | 990613.868
C | Xist Rating 7074 | -71.78 | 534.231 | 150.297 | 35.8 | 2308.14 | 7473.57 | 30793.8 | 1.27 | 4.84 | 20.716 | 121.015 | 1 | 1 | 1380 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1233079.9403 | 107222.7935 | 1854.7797 | 17384.1824 | 89838.6111 | 127301.3285 | 0.052579 | -982987.115 | 982987.115
C | Xist Rating 7075 | -71.45 | 540.528 | 150.297 | 35.8 | 2309.41 | 7505.25 | 30526.9 | 1.24 | 4.78 | 20.679 | 118.64 | 1 | 1 | 1390 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1248300.7685 | 108655.4921 | 1881.7579 | 17510.1547 | 91145.3374 | 124805.1071 | 0.05296 | -963711.9551 | 963711.9551
C | Xist Rating 7076 | -71.11 | 546.822 | 150.297 | 35.8 | 2310.63 | 7536.71 | 30265 | 1.22 | 4.73 | 20.646 | 116.336 | 1 | 1 | 1400 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1263503.3179 | 110097.6256 | 1908.931 | 17636.1271 | 92461.4985 | 122395.4202 | 0.053341 | -945104.9913 | 945104.9913
C | Xist Rating 7077 | -70.71 | 554.298 | 150.296 | 35.7 | 2311.93 | 7572.87 | 29957.2 | 1.2 | 4.67 | 20.623 | 113.645 | 1 | 1 | 1410 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1281498.1751 | 111549.1939 | 1936.2988 | 17762.0994 | 93787.0945 | 119584.2694 | 0.053722 | -923398.0297 | 923398.0297
C | Xist Rating 7078 | -69.62 | 576.491 | 150.297 | 35.7 | 2306.55 | 7583.64 | 29051.6 | 1.2 | 4.49 | 20.697 | 105.731 | 1 | 1 | 1420 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1329705.3161 | 113010.1971 | 1963.8614 | 17888.0717 | 95122.1253 | 111382.3381 | 0.054103 | -860064.8906 | 860064.8906
C | Xist Rating 7079 | -69.42 | 580.594 | 150.296 | 35.7 | 2305.86 | 7587.28 | 28910.4 | 1.17 | 4.47 | 20.607 | 104.641 | 1 | 1 | 1430 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1338768.4808 | 114480.6351 | 1991.6188 | 18014.0441 | 96466.591 | 110214.9581 | 0.054484 | -851050.692 | 851050.692
C | Xist Rating 7080 | -68.92 | 590.483 | 150.296 | 35.7 | 2305.68 | 7615.11 | 28541.8 | 1.15 | 4.39 | 20.592 | 101.6 | 1 | 1 | 1440 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1361464.8434 | 115960.5079 | 2019.571 | 18140.0164 | 97820.4915 | 107039.9757 | 0.054865 | -826534.3192 | 826534.3192
C | Xist Rating 7081 | -68.58 | 596.815 | 150.296 | 35.7 | 2306.43 | 7641.87 | 28316.6 | 1.13 | 4.35 | 20.566 | 99.804 | 1 | 1 | 1450 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1376512.0204 | 117449.8156 | 2047.718 | 18265.9887 | 99183.8269 | 105156.77 | 0.055246 | -811992.7036 | 811992.7036
C | Xist Rating 7082 | -68.3 | 600.559 | 150.296 | 35.7 | 2313.42 | 7730.67 | 28183.4 | 1.12 | 4.32 | 20.596 | 98.75 | 1 | 1 | 1460 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1389345.2018 | 118948.5582 | 2076.0598 | 18391.9611 | 100556.5971 | 104061.3494 | 0.055627 | -803534.1564 | 803534.1564
C | Xist Rating 7083 | -67.21 | 625.593 | 150.296 | 35.7 | 2298.28 | 7639.6 | 27310 | 1.11 | 4.16 | 20.566 | 91.804 | 1 | 1 | 1470 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1437787.88 | 120456.7356 | 2104.5964 | 18517.9334 | 101938.8021 | 96842.5139 | 0.056008 | -747792.2225 | 747792.2225
C | Xist Rating 7084 | -66.82 | 633.113 | 150.296 | 35.7 | 2298.97 | 7669.49 | 27065.8 | 1.09 | 4.11 | 20.552 | 89.959 | 1 | 1 | 1480 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1455507.7936 | 121974.3478 | 2133.3277 | 18643.9058 | 103330.442 | 94908.4175 | 0.056389 | -732857.6426 | 732857.6426
C | Xist Rating 7085 | -66.48 | 639.447 | 150.296 | 35.7 | 2300.19 | 7701.79 | 26866.1 | 1.07 | 4.07 | 20.537 | 88.479 | 1 | 1 | 1490 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1470849.5949 | 123501.3949 | 2162.2539 | 18769.8781 | 104731.5168 | 93352.9565 | 0.05677 | -720846.7852 | 720846.7852
C | Xist Rating 7086 | -66.16 | 645.873 | 150.296 | 35.7 | 2299.99 | 7718.23 | 26669.8 | 1.05 | 4.03 | 20.504 | 87.051 | 1 | 1 | 1500 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1485501.4413 | 125037.8768 | 2191.3748 | 18895.8504 | 106142.0264 | 91849.8841 | 0.057151 | -709240.4587 | 709240.4587
C | Xist Rating 7087 | -65.73 | 653.419 | 150.296 | 35.7 | 2303.2 | 7777.32 | 26438.3 | 1.03 | 3.99 | 20.505 | 85.36 | 1 | 1 | 1510 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1504954.6408 | 126583.7936 | 2220.6906 | 19021.8228 | 107561.9708 | 90075.7471 | 0.057532 | -695541.0424 | 695541.0424
C | Xist Rating 7088 | -64.49 | 678.137 | 150.296 | 35.7 | 2300.05 | 7819.2 | 25680.7 | 1.04 | 3.84 | 20.587 | 79.794 | 1 | 1 | 1520 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1559749.0069 | 128139.1452 | 2250.2011 | 19147.7951 | 108991.3501 | 84324.7131 | 0.057913 | -651133.0825 | 651133.0825
C | Xist Rating 7089 | -64.15 | 686.028 | 150.296 | 35.7 | 2295.86 | 7793.68 | 25468 | 1.01 | 3.8 | 20.51 | 78.362 | 1 | 1 | 1530 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1575024.2441 | 129703.9317 | 2279.9064 | 19273.7674 | 110430.1642 | 82799.4902 | 0.058294 | -639355.7154 | 639355.7154
C | Xist Rating 7090 | -63.84 | 690.046 | 150.296 | 35.7 | 2303.32 | 7891.83 | 25363.6 | 0.99 | 3.78 | 20.504 | 77.682 | 1 | 1 | 1540 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1589396.7527 | 131278.153 | 2309.8065 | 19399.7398 | 111878.4132 | 82073.8706 | 0.058675 | -633752.6734 | 633752.6734
C | Xist Rating 7091 | -63.23 | 702.473 | 150.296 | 35.7 | 2301.59 | 7910.22 | 25020.8 | 0.98 | 3.72 | 20.491 | 75.328 | 1 | 1 | 1550 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1616804.8321 | 132861.8092 | 2339.9013 | 19525.7121 | 113336.0971 | 79623.2133 | 0.059056 | -614829.3472 | 614829.3472
C | Xist Rating 7092 | -62.92 | 706.267 | 150.296 | 35.7 | 2310.28 | 8025.88 | 24919.5 | 0.97 | 3.7 | 20.515 | 74.662 | 1 | 1 | 1560 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1631674.5248 | 134454.9002 | 2370.191 | 19651.6844 | 114803.2157 | 78927.8739 | 0.059437 | -609460.1209 | 609460.1209
C | Xist Rating 7093 | -61.66 | 735.228 | 150.296 | 35.7 | 2294.2 | 7924.94 | 24162.1 | 0.96 | 3.56 | 20.477 | 69.594 | 1 | 1 | 1570 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1686760.0776 | 136057.426 | 2400.6755 | 19777.6568 | 116279.7693 | 73656.6792 | 0.059818 | -568757.3525 | 568757.3525
C | Xist Rating 7094 | -61.35 | 741.682 | 150.296 | 35.7 | 2295.01 | 7954.06 | 24006.5 | 0.94 | 3.53 | 20.444 | 68.624 | 1 | 1 | 1580 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1702167.6068 | 137669.3867 | 2431.3547 | 19903.6291 | 117765.7576 | 72626.9456 | 0.0602 | -560806.0224 | 560806.0224
C | Xist Rating 7095 | -60.98 | 748.172 | 150.296 | 35.7 | 2297.45 | 8003.07 | 23854 | 0.92 | 3.5 | 20.433 | 67.682 | 1 | 1 | 1590 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1718887.7614 | 139290.7823 | 2462.2288 | 20029.6015 | 119261.1808 | 71627.4315 | 0.060581 | -553088.04 | 553088.04
C | Xist Rating 7096 | -60.46 | 756.931 | 150.296 | 35.7 | 2301.36 | 8078.48 | 23644.6 | 0.91 | 3.46 | 20.454 | 66.366 | 1 | 1 | 1600 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1741970.7262 | 140921.6127 | 2493.2976 | 20155.5738 | 120766.0389 | 70255.91 | 0.060962 | -542497.5146 | 542497.5146
C | Xist Rating 7097 | -60.23 | 761.145 | 150.296 | 35.7 | 2302.68 | 8106.76 | 23555.9 | 0.89 | 3.45 | 20.424 | 65.862 | 1 | 1 | 1610 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1752673.3686 | 142561.8779 | 2524.5612 | 20281.5461 | 122280.3318 | 69709.4009 | 0.061343 | -538277.5157 | 538277.5157
C | Xist Rating 7098 | -58.78 | 793.563 | 150.296 | 35.7 | 2289.45 | 8048.03 | 22804.4 | 0.89 | 3.31 | 20.457 | 61.19 | 1 | 1 | 1620 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 28 | E | Rod | 1816822.8103 | 144211.578 | 2556.0196 | 20407.5185 | 123804.0596 | 64867.8169 | 0.061724 | -500892.0878 | 500892.0878
C | Xist Rating 7099 | -58.44 | 797.432 | 150.296 | 35.7 | 2297.98 | 8166.48 | 22722.7 | 0.88 | 3.29 | 20.462 | 60.724 | 1 | 1 | 1630 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 1832482.7874 | 145870.713 | 2587.6728 | 20533.4908 | 125337.2222 | 64377.4125 | 0.062105 | -497105.3149 | 497105.3149
C | Xist Rating 7100 | -58.09 | 804.069 | 150.296 | 35.7 | 2299.25 | 8202.84 | 22587.9 | 0.86 | 3.27 | 20.44 | 59.964 | 1 | 1 | 1640 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 1848755.6482 | 147539.2828 | 2619.5208 | 20659.4631 | 126879.8196 | 63564.75 | 0.062486 | -490830.1505 | 490830.1505
C | Xist Rating 7101 | -57.66 | 813.186 | 150.296 | 35.7 | 2297.27 | 8206.03 | 22402.4 | 0.85 | 3.23 | 20.413 | 58.907 | 1 | 1 | 1650 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 1868107.8022 | 149217.2874 | 2651.5635 | 20785.4355 | 128431.8519 | 62458.1217 | 0.062867 | -482285.0599 | 482285.0599
C | Xist Rating 7102 | -57.18 | 822.059 | 150.296 | 35.7 | 2299.02 | 8257.05 | 22220.3 | 0.84 | 3.2 | 20.418 | 57.864 | 1 | 1 | 1660 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 1889930.0822 | 150904.7269 | 2683.8011 | 20911.4078 | 129993.3191 | 61367.8688 | 0.063248 | -473866.4161 | 473866.4161
C | Xist Rating 7103 | -55.91 | 851.063 | 150.296 | 35.7 | 2287.17 | 8199.7 | 21632.5 | 0.83 | 3.09 | 20.443 | 54.495 | 1 | 1 | 1670 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 1946525.7617 | 152601.6012 | 2716.2334 | 21037.3801 | 131564.221 | 57863.1245 | 0.063629 | -446803.7097 | 446803.7097
C | Xist Rating 7104 | -55.61 | 855.044 | 150.296 | 35.7 | 2293.07 | 8288.24 | 21560 | 0.82 | 3.08 | 20.452 | 54.118 | 1 | 1 | 1680 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 1960675.7451 | 154307.9104 | 2748.8606 | 21163.3525 | 133144.5579 | 57464.3774 | 0.06401 | -443724.6901 | 443724.6901
C | Xist Rating 7105 | -55.11 | 866.689 | 150.296 | 35.7 | 2288.48 | 8265.08 | 21345.6 | 0.81 | 3.04 | 20.421 | 52.966 | 1 | 1 | 1690 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 1983400.4427 | 156023.6544 | 2781.6825 | 21289.3248 | 134734.3296 | 56258.1493 | 0.064391 | -434410.5163 | 434410.5163
C | Xist Rating 7106 | -54.68 | 874.392 | 150.296 | 35.7 | 2290.81 | 8320.16 | 21205.4 | 0.8 | 3.02 | 20.424 | 52.222 | 1 | 1 | 1700 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2003065.9375 | 157748.8333 | 2814.6992 | 21415.2972 | 136333.5361 | 55477.5426 | 0.064772 | -428382.8785 | 428382.8785
C | Xist Rating 7107 | -54.23 | 883.458 | 150.296 | 35.7 | 2290.36 | 8342.91 | 21044.4 | 0.78 | 2.99 | 20.414 | 51.379 | 1 | 1 | 1710 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2023436.8649 | 159483.447 | 2847.9107 | 21541.2695 | 137942.1775 | 54577.5045 | 0.065153 | -421433.0228 | 421433.0228
C | Xist Rating 7108 | -53.06 | 910.138 | 150.296 | 35.7 | 2280.8 | 8304.09 | 20566.8 | 0.78 | 2.9 | 20.443 | 48.837 | 1 | 1 | 1720 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2075842.7504 | 161227.4955 | 2881.317 | 21667.2418 | 139560.2537 | 51946.5229 | 0.065534 | -401117.2801 | 401117.2801
C | Xist Rating 7109 | -52.5 | 921.653 | 150.296 | 35.7 | 2279.93 | 8329.06 | 20374.2 | 0.77 | 2.87 | 20.433 | 47.86 | 1 | 1 | 1730 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2101304.3243 | 162980.9789 | 2914.9181 | 21793.2142 | 141187.7648 | 50922.6075 | 0.065915 | -393210.8769 | 393210.8769
C | Xist Rating 7110 | -52.16 | 926.968 | 150.296 | 35.7 | 2283.5 | 8393.44 | 20289.8 | 0.76 | 2.85 | 20.434 | 47.452 | 1 | 1 | 1740 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2116731.428 | 164743.8972 | 2948.714 | 21919.1865 | 142824.7107 | 50490.0752 | 0.066296 | -389870.9769 | 389870.9769
C | Xist Rating 7111 | -51.7 | 937.428 | 150.296 | 35.7 | 2280.67 | 8388.26 | 20123.3 | 0.75 | 2.82 | 20.413 | 46.635 | 1 | 1 | 1750 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2137963.9168 | 166516.2503 | 2982.7046 | 22045.1588 | 144471.0915 | 49631.3186 | 0.066677 | -383239.8863 | 383239.8863
C | Xist Rating 7112 | -51.35 | 945.248 | 150.296 | 35.7 | 2279.11 | 8391.88 | 20000.5 | 0.74 | 2.8 | 20.408 | 46.039 | 1 | 1 | 1760 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2154324.1693 | 168298.0382 | 3016.8901 | 22171.1312 | 146126.9071 | 49002.8401 | 0.067058 | -378386.9419 | 378386.9419
C | Xist Rating 7113 | -49.98 | 976.87 | 150.296 | 35.7 | 2268.09 | 8346.54 | 19497.1 | 0.74 | 2.71 | 20.444 | 43.54 | 1 | 1 | 1770 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2215629.0783 | 170089.261 | 3051.2703 | 22297.1035 | 147792.1575 | 46416.5155 | 0.067439 | -358416.0292 | 358416.0292
C | Xist Rating 7114 | -49.56 | 984.799 | 150.296 | 35.7 | 2269.5 | 8390.05 | 19382.8 | 0.73 | 2.69 | 20.437 | 43.014 | 1 | 1 | 1780 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2235001.3305 | 171889.9187 | 3085.8453 | 22423.0758 | 149466.8428 | 45860.3271 | 0.06782 | -354121.2898 | 354121.2898
C | Xist Rating 7115 | -49.55 | 989.039 | 150.297 | 35.6 | 2263.08 | 8314.93 | 19326.3 | 0.71 | 2.68 | 20.666 | 42.762 | 1 | 1 | 1790 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2238274.3801 | 173700.0112 | 3120.6151 | 22549.0482 | 151150.963 | 45585.5628 | 0.068201 | -351999.6325 | 351999.6325
C | Xist Rating 7116 | -48.69 | 1003.12 | 150.297 | 35.6 | 2267.9 | 8425.4 | 19121.6 | 0.7 | 2.65 | 20.418 | 41.818 | 1 | 1 | 1800 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2274975.848 | 175519.5385 | 3155.5797 | 22675.0205 | 152844.518 | 44581.1163 | 0.068582 | -344243.563 | 344243.563
C | Xist Rating 7117 | -48.49 | 1010.92 | 150.297 | 35.7 | 2259.41 | 8333.23 | 19012.9 | 0.69 | 2.63 | 20.675 | 41.314 | 1 | 1 | 1810 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2284082.7572 | 177348.5007 | 3190.7391 | 22800.9929 | 154547.5078 | 44061.9413 | 0.068963 | -340234.6312 | 340234.6312
C | Xist Rating 7118 | -46.9 | 1042.8 | 150.297 | 35.6 | 2259.28 | 8434.55 | 18562.5 | 0.69 | 2.55 | 20.454 | 39.244 | 1 | 1 | 1820 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2355977.184 | 179186.8977 | 3226.0933 | 22926.9652 | 156259.9325 | 41906.2039 | 0.069344 | -323588.5983 | 323588.5983
C | Xist Rating 7119 | -47.15 | 1037.74 | 150.297 | 35.6 | 2262.6 | 8464.71 | 18631.2 | 0.69 | 2.56 | 20.723 | 39.558 | 1 | 1 | 1830 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2347990.524 | 181034.7296 | 3261.6423 | 23052.9375 | 157981.7921 | 42253.844 | 0.069725 | -326272.9833 | 326272.9833
C | Xist Rating 7120 | -46.68 | 1044.16 | 150.297 | 35.6 | 2268.86 | 8573.89 | 18545.1 | 0.68 | 2.55 | 20.75 | 39.182 | 1 | 1 | 1840 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2369052.8576 | 182891.9963 | 3297.386 | 23178.9099 | 159713.0864 | 41854.2005 | 0.070106 | -323187.0423 | 323187.0423
C | Xist Rating 7121 | -46.21 | 1054.74 | 150.297 | 35.6 | 2265.84 | 8564.37 | 18409.3 | 0.67 | 2.52 | 20.739 | 38.597 | 1 | 1 | 1850 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2389872.0816 | 184758.6979 | 3333.3246 | 23304.8822 | 161453.8157 | 41235.1855 | 0.070487 | -318407.1722 | 318407.1722
C | Xist Rating 7122 | -45.7 | 1066.59 | 150.297 | 35.6 | 2262.56 | 8555.25 | 18259 | 0.66 | 2.5 | 20.724 | 37.952 | 1 | 1 | 1860 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2413223.8704 | 186634.8343 | 3369.4579 | 23430.8545 | 163203.9798 | 40553.4662 | 0.070868 | -313143.1162 | 313143.1162
C | Xist Rating 7123 | -44.37 | 1095.88 | 150.297 | 35.6 | 2256.39 | 8564.57 | 17879.6 | 0.66 | 2.43 | 20.774 | 36.287 | 1 | 1 | 1870 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2472732.6732 | 188520.4056 | 3405.7861 | 23556.8269 | 164963.5787 | 38833.2635 | 0.071249 | -299860.1669 | 299860.1669
C | Xist Rating 7124 | -43.84 | 1107.72 | 150.297 | 35.6 | 2253.94 | 8566.74 | 17738.7 | 0.65 | 2.41 | 20.767 | 35.707 | 1 | 1 | 1880 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2496734.4168 | 190415.4117 | 3442.309 | 23682.7992 | 166732.6125 | 38219.1905 | 0.07163 | -295118.458 | 295118.458
C | Xist Rating 7125 | -43.38 | 1115.57 | 150.297 | 35.6 | 2256.71 | 8632.18 | 17646.5 | 0.64 | 2.39 | 20.785 | 35.332 | 1 | 1 | 1890 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2517517.9747 | 192319.8526 | 3479.0267 | 23808.7715 | 168511.0811 | 37819.1867 | 0.072011 | -292029.7349 | 292029.7349
C | Xist Rating 7126 | -43.03 | 1123.88 | 150.297 | 35.6 | 2254.25 | 8621.28 | 17555.2 | 0.63 | 2.38 | 20.77 | 34.978 | 1 | 1 | 1900 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2533506.49 | 194233.7284 | 3515.9392 | 23934.7439 | 170298.9845 | 37439.0142 | 0.072392 | -289094.144 | 289094.144
C | Xist Rating 7127 | -42.61 | 1131.91 | 150.297 | 35.6 | 2254.86 | 8655.49 | 17464.9 | 0.62 | 2.36 | 20.774 | 34.621 | 1 | 1 | 1910 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2552298.5826 | 196157.0391 | 3553.0464 | 24060.7162 | 172096.3229 | 37056.5657 | 0.072773 | -286140.978 | 286140.978
C | Xist Rating 7128 | -41.07 | 1167.47 | 150.297 | 35.6 | 2245.77 | 8641.07 | 17050.2 | 0.62 | 2.29 | 20.822 | 32.908 | 1 | 1 | 1920 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2621869.1019 | 198089.7846 | 3590.3485 | 24186.6886 | 173903.096 | 35285.9526 | 0.073154 | -272468.7723 | 272468.7723
C | Xist Rating 7129 | -40.63 | 1179.39 | 150.297 | 35.6 | 2240.22 | 8596.6 | 16923.8 | 0.61 | 2.27 | 20.819 | 32.421 | 1 | 1 | 1930 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2642093.0658 | 200031.9649 | 3627.8454 | 24312.6609 | 175719.304 | 34767.8188 | 0.073535 | -268467.8806 | 268467.8806
C | Xist Rating 7130 | -40.22 | 1183.27 | 150.297 | 35.7 | 2248.3 | 8729.6 | 16882.1 | 0.6 | 2.26 | 20.847 | 32.266 | 1 | 1 | 1940 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2660345.941 | 201983.5801 | 3665.537 | 24438.6332 | 177544.9469 | 34595.9008 | 0.073916 | -267140.3758 | 267140.3758
C | Xist Rating 7131 | -39.88 | 1194.41 | 150.297 | 35.7 | 2239.92 | 8637.78 | 16772.4 | 0.59 | 2.24 | 20.836 | 31.863 | 1 | 1 | 1950 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2675382.8472 | 203944.6301 | 3703.4235 | 24564.6056 | 179380.0246 | 34164.2035 | 0.074297 | -263806.9233 | 263806.9233
C | Xist Rating 7132 | -39.31 | 1207.49 | 150.297 | 35.7 | 2237.13 | 8637.78 | 16637.2 | 0.58 | 2.22 | 20.854 | 31.349 | 1 | 1 | 1960 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2701312.1037 | 205915.115 | 3741.5047 | 24690.5779 | 181224.5371 | 33618.5372 | 0.074678 | -259593.4327 | 259593.4327
C | Xist Rating 7133 | -37.92 | 1239.5 | 150.297 | 35.7 | 2230.02 | 8637.05 | 16303.3 | 0.58 | 2.16 | 20.922 | 30.058 | 1 | 1 | 1970 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2764109.79 | 207895.0347 | 3779.7807 | 24816.5502 | 183078.4845 | 32286.7401 | 0.075059 | -249309.649 | 249309.649
C | Xist Rating 7134 | -37.47 | 1248.79 | 150.297 | 35.7 | 2229.78 | 8662.39 | 16214.3 | 0.57 | 2.15 | 20.949 | 29.737 | 1 | 1 | 1980 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2784526.9662 | 209884.3893 | 3818.2515 | 24942.5226 | 184941.8668 | 31941.6185 | 0.07544 | -246644.7116 | 246644.7116
C | Xist Rating 7135 | -36.95 | 1260.91 | 150.297 | 35.7 | 2227.01 | 8657.84 | 16101.7 | 0.56 | 2.13 | 20.958 | 29.336 | 1 | 1 | 1990 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2808059.1791 | 211883.1787 | 3856.9171 | 25068.4949 | 186814.6838 | 31512.296 | 0.075821 | -243329.5967 | 243329.5967
C | Xist Rating 7136 | -36.51 | 1270.32 | 150.297 | 35.7 | 2226.63 | 8681.14 | 16015 | 0.55 | 2.12 | 20.959 | 29.031 | 1 | 1 | 2000 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2828532.6216 | 213891.403 | 3895.7775 | 25194.4672 | 188696.9358 | 31182.0754 | 0.076202 | -240779.721 | 240779.721
C | Xist Rating 7137 | -36.16 | 1277.21 | 150.297 | 35.7 | 2227.38 | 8713.44 | 15953.9 | 0.55 | 2.11 | 20.963 | 28.824 | 1 | 1 | 2010 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2844832.0098 | 215909.0621 | 3934.8326 | 25320.4396 | 190588.6226 | 30972.4716 | 0.076583 | -239161.2158 | 239161.2158
C | Xist Rating 7138 | -34.67 | 1313.22 | 150.297 | 35.7 | 2217.35 | 8678.24 | 15614.8 | 0.55 | 2.05 | 21 | 27.588 | 1 | 1 | 2020 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2911868.367 | 217936.1561 | 3974.0826 | 25446.4119 | 192489.7442 | 29695.8983 | 0.076964 | -229303.8551 | 229303.8551
C | Xist Rating 7139 | -34.08 | 1326.24 | 150.297 | 35.7 | 2216.1 | 8700.3 | 15499.7 | 0.54 | 2.03 | 21.004 | 27.19 | 1 | 1 | 2030 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2939080.464 | 219972.6849 | 4013.5273 | 25572.3842 | 194400.3007 | 29268.841 | 0.077345 | -226006.2316 | 226006.2316
C | Xist Rating 7140 | -33.76 | 1334.75 | 150.297 | 35.7 | 2213.13 | 8679.26 | 15431.7 | 0.53 | 2.02 | 20.996 | 26.972 | 1 | 1 | 2040 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2953975.2675 | 222018.6486 | 4053.1669 | 25698.3566 | 196320.292 | 29027.9381 | 0.077726 | -224146.0439 | 224146.0439
C | Xist Rating 7141 | -33.25 | 1342.44 | 150.297 | 35.7 | 2217.52 | 8772.37 | 15364.3 | 0.53 | 2.01 | 21.024 | 26.743 | 1 | 1 | 2050 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2976887.5488 | 224074.0471 | 4093.0012 | 25824.3289 | 198249.7182 | 28796.4737 | 0.078107 | -222358.7367 | 222358.7367
C | Xist Rating 7142 | -32.78 | 1354.95 | 150.297 | 35.7 | 2213.22 | 8742.82 | 15264.2 | 0.51 | 1.99 | 21.007 | 26.418 | 1 | 1 | 2060 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 2998802.439 | 226138.8804 | 4133.0303 | 25950.3013 | 200188.5792 | 28424.3292 | 0.078488 | -219485.1357 | 219485.1357
C | Xist Rating 7143 | -31.24 | 1393.59 | 150.298 | 35.7 | 2201.81 | 8690.62 | 14936.2 | 0.52 | 1.94 | 21.041 | 25.292 | 1 | 1 | 2070 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3068420.3979 | 228213.1486 | 4173.2542 | 26076.2736 | 202136.875 | 27280.9145 | 0.078869 | -210655.9908 | 210655.9908
C | Xist Rating 7144 | -30.81 | 1401.9 | 150.297 | 35.7 | 2203.02 | 8734.22 | 14873.4 | 0.51 | 1.93 | 21.039 | 25.098 | 1 | 1 | 2080 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3088413.738 | 230296.8517 | 4213.6729 | 26202.2459 | 204094.6057 | 27064.6375 | 0.07925 | -208985.957 | 208985.957
C | Xist Rating 7145 | -30.34 | 1412.68 | 150.297 | 35.7 | 2201.46 | 8742.73 | 14790.7 | 0.5 | 1.91 | 21.036 | 24.837 | 1 | 1 | 2090 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3109958.5128 | 232389.9896 | 4254.2864 | 26328.2183 | 206061.7713 | 26778.5485 | 0.079631 | -206776.8531 | 206776.8531
C | Xist Rating 7146 | -29.88 | 1423.46 | 150.297 | 35.7 | 2199.81 | 8749.6 | 14709.2 | 0.49 | 1.9 | 21.039 | 24.581 | 1 | 1 | 2100 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3131341.5426 | 234492.5623 | 4295.0947 | 26454.1906 | 208038.3717 | 26497.7444 | 0.080012 | -204608.5581 | 204608.5581
C | Xist Rating 7147 | -29.46 | 1432.97 | 150.297 | 35.7 | 2198.83 | 8762.87 | 14638.6 | 0.49 | 1.89 | 21.04 | 24.363 | 1 | 1 | 2110 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3150857.4251 | 236604.5699 | 4336.0977 | 26580.1629 | 210024.4069 | 26276.0191 | 0.080393 | -202896.4542 | 202896.4542
C | Xist Rating 7148 | -28 | 1469.42 | 150.298 | 35.7 | 2189.08 | 8725.03 | 14358.9 | 0.49 | 1.84 | 21.074 | 23.458 | 1 | 1 | 2120 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3216677.9336 | 238726.0123 | 4377.2956 | 26706.1353 | 212019.877 | 25342.3824 | 0.080774 | -195687.1595 | 195687.1595
C | Xist Rating 7149 | -27.48 | 1482.79 | 150.298 | 35.7 | 2185.69 | 8711.87 | 14263.7 | 0.48 | 1.83 | 21.072 | 23.167 | 1 | 1 | 2130 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3240919.2751 | 240856.8896 | 4418.6882 | 26832.1076 | 214024.782 | 25024.5957 | 0.081155 | -193233.2947 | 193233.2947
C | Xist Rating 7150 | -27.01 | 1496.18 | 150.298 | 35.7 | 2180.85 | 8675.51 | 14169.7 | 0.48 | 1.81 | 21.065 | 22.884 | 1 | 1 | 2140 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3262944.153 | 242997.2017 | 4460.2756 | 26958.0799 | 216039.1218 | 24734.9122 | 0.081536 | -190996.4352 | 190996.4352
C | Xist Rating 7151 | -26.69 | 1503.22 | 150.298 | 35.7 | 2180.82 | 8695.25 | 14123.3 | 0.47 | 1.8 | 21.068 | 22.753 | 1 | 1 | 2150 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3278252.2404 | 245146.9487 | 4502.0578 | 27084.0523 | 218062.8964 | 24583.2361 | 0.081917 | -189825.2328 | 189825.2328
C | Xist Rating 7152 | -26.26 | 1512.67 | 150.298 | 35.7 | 2180.34 | 8715.91 | 14058.9 | 0.46 | 1.79 | 21.072 | 22.564 | 1 | 1 | 2160 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3298134.9078 | 247306.1305 | 4544.0348 | 27210.0246 | 220096.1059 | 24371.1783 | 0.082298 | -188187.7784 | 188187.7784
C | Xist Rating 7153 | -24.76 | 1551.96 | 150.298 | 35.7 | 2169.25 | 8661.23 | 13785.8 | 0.46 | 1.75 | 21.102 | 21.729 | 1 | 1 | 2170 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3366589.23 | 249474.7472 | 4586.2066 | 27335.997 | 222138.7502 | 23509.7193 | 0.082679 | -181535.8208 | 181535.8208
C | Xist Rating 7154 | -24.17 | 1565.1 | 150.298 | 35.7 | 2168.29 | 8685.71 | 13698.8 | 0.46 | 1.74 | 21.105 | 21.476 | 1 | 1 | 2180 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3393590.679 | 251652.7987 | 4628.5732 | 27461.9693 | 224190.8294 | 23251.4652 | 0.08306 | -179541.6506 | 179541.6506
C | Xist Rating 7155 | -23.82 | 1574.79 | 150.298 | 35.7 | 2165.64 | 8671.02 | 13638.8 | 0.45 | 1.73 | 21.111 | 21.31 | 1 | 1 | 2190 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3410428.2156 | 253840.2851 | 4671.1346 | 27587.9416 | 226252.3434 | 23062.9732 | 0.083441 | -178086.1661 | 178086.1661
C | Xist Rating 7156 | -23.48 | 1584.89 | 150.298 | 35.7 | 2161.83 | 8637.72 | 13579.3 | 0.44 | 1.72 | 21.105 | 21.151 | 1 | 1 | 2200 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3426262.7487 | 256037.2063 | 4713.8907 | 27713.914 | 228323.2923 | 22881.0315 | 0.083822 | -176681.2603 | 176681.2603
C | Xist Rating 7157 | -22.93 | 1598.29 | 150.298 | 35.7 | 2159.55 | 8640.62 | 13495.3 | 0.44 | 1.7 | 21.107 | 20.913 | 1 | 1 | 2210 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3451587.1695 | 258243.5623 | 4756.8417 | 27839.8863 | 230403.676 | 22638.1186 | 0.084203 | -174805.551 | 174805.551
C | Xist Rating 7158 | -21.39 | 1637.44 | 150.298 | 35.7 | 2150.49 | 8614.78 | 13246.1 | 0.44 | 1.66 | 21.144 | 20.189 | 1 | 1 | 2220 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3521298.3456 | 260459.3532 | 4799.9874 | 27965.8586 | 232493.4946 | 21892.0287 | 0.084584 | -169044.4424 | 169044.4424
C | Xist Rating 7159 | -20.92 | 1648.19 | 150.298 | 35.7 | 2149.91 | 8636.69 | 13182.5 | 0.44 | 1.65 | 21.148 | 20.017 | 1 | 1 | 2230 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3543460.1629 | 262684.579 | 4843.3279 | 28091.831 | 234592.748 | 21717.7531 | 0.084965 | -167698.7324 | 167698.7324
C | Xist Rating 7160 | -20.4 | 1660.67 | 150.298 | 35.7 | 2147.81 | 8637.89 | 13111.8 | 0.43 | 1.64 | 21.142 | 19.83 | 1 | 1 | 2240 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3566803.6327 | 264919.2396 | 4886.8633 | 28217.8033 | 236701.4362 | 21506.2317 | 0.085346 | -166065.4203 | 166065.4203
C | Xist Rating 7161 | -19.89 | 1674.38 | 150.298 | 35.7 | 2145.06 | 8632.42 | 13034 | 0.42 | 1.63 | 21.134 | 19.623 | 1 | 1 | 2250 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3591645.5628 | 267163.335 | 4930.5934 | 28343.7756 | 238819.5593 | 21273.6758 | 0.085727 | -164269.6855 | 164269.6855
C | Xist Rating 7162 | -19.56 | 1681.38 | 150.298 | 35.7 | 2145.61 | 8660.82 | 12995.6 | 0.42 | 1.62 | 21.139 | 19.526 | 1 | 1 | 2260 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3607585.7418 | 269416.8653 | 4974.5182 | 28469.748 | 240947.1173 | 21177.133 | 0.086108 | -163524.2072 | 163524.2072
C | Xist Rating 7163 | -17.97 | 1723.47 | 150.298 | 35.7 | 2135.11 | 8616.11 | 12751.8 | 0.42 | 1.59 | 21.171 | 18.855 | 1 | 1 | 2270 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3679798.0317 | 271679.8304 | 5018.6379 | 28595.7203 | 243084.1101 | 20485.6478 | 0.086489 | -158184.7419 | 158184.7419
C | Xist Rating 7164 | -17.51 | 1735.89 | 150.298 | 35.7 | 2132.13 | 8602.17 | 12686.1 | 0.41 | 1.58 | 21.165 | 18.688 | 1 | 1 | 2280 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3701143.1457 | 273952.2304 | 5062.9524 | 28721.6927 | 245230.5377 | 20294.316 | 0.08687 | -156707.329 | 156707.329
C | Xist Rating 7165 | -16.89 | 1750.63 | 150.298 | 35.7 | 2130.84 | 8623.36 | 12607 | 0.41 | 1.56 | 21.169 | 18.483 | 1 | 1 | 2290 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3730312.4292 | 276234.0652 | 5107.4617 | 28847.665 | 247386.4002 | 20085.4819 | 0.087251 | -155094.7674 | 155094.7674
C | Xist Rating 7166 | -16.47 | 1760.48 | 150.298 | 35.7 | 2130.02 | 8636.83 | 12557 | 0.4 | 1.56 | 21.17 | 18.362 | 1 | 1 | 2300 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3749857.6096 | 278525.3349 | 5152.1657 | 28973.6373 | 249551.6976 | 19941.9308 | 0.087632 | -153986.3035 | 153986.3035
| Xist Rating 7167 | -16.11 | 1770.6 | 150.298 | 35.7 | 2127.7 | 8625.8 | 12507.6 | 0.4 | 1.55 | 21.167 | 18.244 | 1 | 1 | 2310 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3767305.62 | 280826.0394 | 5197.0645 | 29099.6097 | 251726.4298 | 19823.0595 | 0.088013 | -153068.4107 | 153068.4107
| Xist Rating 7168 | -14.45 | 1813.8 | 150.298 | 35.7 | 2118.51 | 8602.59 | 12277.1 | 0.4 | 1.51 | 21.197 | 17.638 | 1 | 1 | 2320 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3842553.438 | 283136.1788 | 5242.1582 | 29225.582 | 253910.5968 | 19198.7726 | 0.088394 | -148247.8326 | 148247.8326
| Xist Rating 7169 | -13.97 | 1826.26 | 150.298 | 35.7 | 2116.38 | 8601.74 | 12216.8 | 0.39 | 1.5 | 21.194 | 17.493 | 1 | 1 | 2330 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3865060.1388 | 285455.753 | 5287.4466 | 29351.5543 | 256104.1987 | 19029.7302 | 0.088775 | -146942.5326 | 146942.5326
| Xist Rating 7170 | -13.49 | 1838.69 | 150.298 | 35.7 | 2114.5 | 8604.69 | 12157.1 | 0.39 | 1.49 | 21.198 | 17.35 | 1 | 1 | 2340 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3887910.005 | 287784.7621 | 5332.9298 | 29477.5267 | 258307.2354 | 18885.0936 | 0.089156 | -145825.6872 | 145825.6872
| Xist Rating 7171 | -13.11 | 1849.94 | 150.298 | 35.7 | 2111.35 | 8582.98 | 12104.7 | 0.38 | 1.49 | 21.191 | 17.227 | 1 | 1 | 2350 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3905870.819 | 290123.206 | 5378.6078 | 29603.499 | 260519.707 | 18738.4544 | 0.089537 | -144693.3775 | 144693.3775
| Xist Rating 7172 | -12.62 | 1863.69 | 150.298 | 35.7 | 2108.31 | 8570.29 | 12039.8 | 0.38 | 1.48 | 21.186 | 17.072 | 1 | 1 | 2360 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3929236.2639 | 292471.0847 | 5424.4805 | 29729.4713 | 262741.6134 | 18580.8956 | 0.089918 | -143476.7509 | 143476.7509
| Xist Rating 7173 | -11.11 | 1903.28 | 150.298 | 35.7 | 2100.51 | 8555.3 | 11846.8 | 0.38 | 1.45 | 21.215 | 16.591 | 1 | 1 | 2370 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 3997858.6728 | 294828.3983 | 5470.5481 | 29855.4437 | 264972.9546 | 18086.1573 | 0.090299 | -139656.5125 | 139656.5125
| Xist Rating 7174 | -10.69 | 1915.95 | 150.298 | 35.7 | 2097.2 | 8534 | 11791.2 | 0.38 | 1.44 | 21.208 | 16.465 | 1 | 1 | 2380 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4018130.34 | 297195.1468 | 5516.8105 | 29981.416 | 267213.7308 | 17958.6363 | 0.09068 | -138671.8296 | 138671.8296
| Xist Rating 7175 | -10.16 | 1929.26 | 150.298 | 35.7 | 2095.63 | 8544.94 | 11730 | 0.37 | 1.43 | 21.206 | 16.321 | 1 | 1 | 2390 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4043015.1338 | 299571.3301 | 5563.2676 | 30107.3884 | 269463.9417 | 17789.9054 | 0.091061 | -137368.934 | 137368.934
C | Xist Rating 7179 | 0.24 | 2214.98 | 150.298 | 35.7 | 2038.34 | 8378.9 | 10538 | 0.39 | 1.25 | 21.237 | 13.599 | 1 | 1 | 2430 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4514882.3332 | 309170.4117 | 5751.0441 | 30611.2777 | 278559.134 | 15024.6946 | 0.092585 | -116016.7089 | 116016.7089
C | Xist Rating 7180 | 0.26 | 2216.35 | 150.298 | 35.7 | 2037.95 | 8372.29 | 10538 | 0.38 | 1.25 | 21.229 | 13.61 | 1 | 1 | 2440 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4516810.4825 | 311593.7692 | 5798.4752 | 30737.25 | 280856.5192 | 15016.2708 | 0.092966 | -115951.6625 | 115951.6625
C | Xist Rating 7181 | 0.27 | 2217.68 | 150.298 | 35.7 | 2037.55 | 8365.57 | 10538 | 0.38 | 1.25 | 21.229 | 13.621 | 1 | 1 | 2450 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4518633.884 | 314026.5616 | 5846.1011 | 30863.2224 | 283163.3393 | 15031.3103 | 0.093347 | -116067.7935 | 116067.7935
C | Xist Rating 7182 | 0.3 | 2219.15 | 150.298 | 35.7 | 2037.55 | 8365.52 | 10538 | 0.37 | 1.25 | 21.219 | 13.632 | 1 | 1 | 2460 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4521629.0825 | 316468.7888 | 5893.9217 | 30989.1947 | 285479.5941 | 15022.5328 | 0.093728 | -116000.0166 | 116000.0166
C | Xist Rating 7183 | 0.32 | 2220.5 | 150.298 | 35.7 | 2037.3 | 8361.36 | 10538 | 0.36 | 1.25 | 21.254 | 13.643 | 1 | 1 | 2470 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4523824.65 | 318920.4509 | 5941.9372 | 31115.167 | 287805.2839 | 15015.3775 | 0.094109 | -115944.7652 | 115944.7652
C | Xist Rating 7184 | 0.33 | 2221.85 | 150.298 | 35.7 | 2036.72 | 8351.69 | 10538 | 0.36 | 1.25 | 21.248 | 13.653 | 1 | 1 | 2480 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4525286.332 | 321381.5478 | 5990.1474 | 31241.1394 | 290140.4085 | 15028.9521 | 0.09449 | -116049.5846 | 116049.5846
C | Xist Rating 7185 | 0.33 | 2223.25 | 150.298 | 35.7 | 2036.09 | 8341.05 | 10537.9 | 0.35 | 1.25 | 21.242 | 13.664 | 1 | 1 | 2490 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4526737.0925 | 323852.0796 | 6038.5525 | 31367.1117 | 292484.9679 | 15019.8544 | 0.094871 | -115979.3342 | 115979.3342
C | Xist Rating 7186 | 0.36 | 2224.23 | 150.298 | 35.7 | 2036.35 | 8345.43 | 10537.9 | 0.35 | 1.25 | 21.239 | 13.673 | 1 | 1 | 2500 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4529310.7605 | 326332.0462 | 6087.1523 | 31493.0841 | 294838.9622 | 15032.4158 | 0.095252 | -116076.33 | 116076.33
C | Xist Rating 7187 | 0.34 | 2226.08 | 150.298 | 35.7 | 2034.8 | 8319.44 | 10537.9 | 0.34 | 1.25 | 21.232 | 13.685 | 1 | 1 | 2510 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4529627.584 | 328821.4477 | 6135.9469 | 31619.0564 | 297202.3913 | 15024.0461 | 0.095633 | -116011.7017 | 116011.7017
C | Xist Rating 7188 | 0.35 | 2227.54 | 150.298 | 35.7 | 2034.2 | 8309.43 | 10537.9 | 0.34 | 1.25 | 21.269 | 13.696 | 1 | 1 | 2520 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4531261.868 | 331320.284 | 6184.9363 | 31745.0287 | 299575.2552 | 15040.1265 | 0.096014 | -116135.8698 | 116135.8698
C | Xist Rating 7189 | 0.36 | 2228.88 | 150.298 | 35.7 | 2033.74 | 8301.83 | 10537.9 | 0.33 | 1.25 | 21.264 | 13.707 | 1 | 1 | 2530 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4532962.4112 | 333828.5551 | 6234.1205 | 31871.0011 | 301957.5541 | 15030.4839 | 0.096395 | -116061.4125 | 116061.4125
C | Xist Rating 7190 | 0.38 | 2230.03 | 150.298 | 35.6 | 2033.75 | 8301.91 | 10537.9 | 0.33 | 1.25 | 21.26 | 13.716 | 1 | 1 | 2540 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4535323.5125 | 336346.2611 | 6283.4995 | 31996.9734 | 304349.2877 | 15042.8255 | 0.096776 | -116156.7111 | 116156.7111
C | Xist Rating 7191 | 0.38 | 2231.57 | 150.298 | 35.6 | 2032.76 | 8285.6 | 10537.9 | 0.32 | 1.25 | 21.255 | 13.727 | 1 | 1 | 2550 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4536246.2332 | 338873.402 | 6333.0732 | 32122.9457 | 306750.4562 | 15032.9101 | 0.097157 | -116080.1471 | 116080.1471
C | Xist Rating 7192 | 0.42 | 2233.02 | 150.298 | 35.6 | 2032.9 | 8287.9 | 10537.8 | 0.32 | 1.25 | 21.248 | 13.738 | 1 | 1 | 2560 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4539506.358 | 341409.9776 | 6382.8418 | 32248.9181 | 309161.0596 | 15047.1253 | 0.097538 | -116189.9134 | 116189.9134
C | Xist Rating 7193 | 0.43 | 2234.41 | 150.298 | 35.6 | 2032.58 | 8282.66 | 10537.8 | 0.31 | 1.25 | 21.243 | 13.748 | 1 | 1 | 2570 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4541617.0778 | 343955.9882 | 6432.8051 | 32374.8904 | 311581.0978 | 15035.902 | 0.097919 | -116103.2497 | 116103.2497
C | Xist Rating 7194 | 0.47 | 2235.78 | 150.298 | 35.6 | 2032.68 | 8284.28 | 10537.7 | 0.31 | 1.25 | 21.291 | 13.758 | 1 | 1 | 2580 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4544625.2904 | 346511.4336 | 6482.9633 | 32500.8627 | 314010.5708 | 15050.9597 | 0.0983 | -116219.521 | 116219.521
C | Xist Rating 7195 | 0.48 | 2237.14 | 150.298 | 35.6 | 2032.49 | 8281.12 | 10537.7 | 0.3 | 1.25 | 21.293 | 13.768 | 1 | 1 | 2590 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4546964.6786 | 349076.3138 | 6533.3162 | 32626.8351 | 316449.4787 | 15039.6549 | 0.098681 | -116132.2283 | 116132.2283
C | Xist Rating 7196 | 0.5 | 2238.31 | 150.298 | 35.6 | 2032.45 | 8280.51 | 10537.7 | 0.3 | 1.25 | 21.292 | 13.777 | 1 | 1 | 2600 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4549253.1595 | 351650.6289 | 6583.8639 | 32752.8074 | 318897.8215 | 15051.8297 | 0.099062 | -116226.2395 | 116226.2395
C | Xist Rating 7197 | 0.52 | 2240 | 150.298 | 35.6 | 2031.79 | 8269.55 | 10537.7 | 0.29 | 1.25 | 21.292 | 13.789 | 1 | 1 | 2610 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4551209.6 | 354234.3788 | 6634.6064 | 32878.7797 | 321355.5991 | 15042.2449 | 0.099443 | -116152.2282 | 116152.2282
C | Xist Rating 7198 | 0.52 | 2241.4 | 150.298 | 35.6 | 2031.24 | 8260.43 | 10537.7 | 0.29 | 1.25 | 21.287 | 13.799 | 1 | 1 | 2620 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4552821.336 | 356827.5636 | 6685.5437 | 33004.7521 | 323822.8115 | 15055.2274 | 0.099824 | -116252.4754 | 116252.4754
C | Xist Rating 7199 | 0.6 | 2242.82 | 150.298 | 35.6 | 2031.81 | 8269.88 | 10537.7 | 0.29 | 1.25 | 21.332 | 13.809 | 1 | 1 | 2630 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4556984.1042 | 359430.1832 | 6736.6758 | 33130.7244 | 326299.4588 | 15069.918 | 0.10021 | -116365.912 | 116365.912
C | Xist Rating 7200 | 0.6 | 2244.07 | 150.298 | 35.6 | 2031.44 | 8263.77 | 10537.6 | 0.28 | 1.25 | 21.328 | 13.819 | 1 | 1 | 2640 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4558693.5608 | 362042.2377 | 6788.0027 | 33256.6968 | 328785.5409 | 15057.6997 | 0.10059 | -116271.566 | 116271.566
C | Xist Rating 7201 | 0.6 | 2245.57 | 150.298 | 35.6 | 2030.69 | 8251.45 | 10537.6 | 0.28 | 1.25 | 21.325 | 13.829 | 1 | 1 | 2650 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4560056.5433 | 364663.727 | 6839.5243 | 33382.6691 | 331281.0579 | 15070.6618 | 0.10097 | -116371.6556 | 116371.6556
C | Xist Rating 7202 | 0.65 | 2246.91 | 150.298 | 35.6 | 2031.01 | 8256.63 | 10537.6 | 0.27 | 1.25 | 21.327 | 13.839 | 1 | 1 | 2660 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4563496.6791 | 367294.6511 | 6891.2408 | 33508.6414 | 333786.0097 | 15058.3611 | 0.10135 | -116276.6728 | 116276.6728
C | Xist Rating 7203 | 0.71 | 2248.3 | 150.298 | 35.6 | 2031.54 | 8265.45 | 10537.6 | 0.27 | 1.25 | 21.332 | 13.849 | 1 | 1 | 2670 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4567511.382 | 369935.0101 | 6943.152 | 33634.6138 | 336300.3964 | 15071.4888 | 0.10173 | -116378.0413 | 116378.0413
C | Xist Rating 7204 | 0.75 | 2249.72 | 150.298 | 35.6 | 2031.6 | 8266.47 | 10537.7 | 0.27 | 1.25 | 21.371 | 13.859 | 1 | 1 | 2680 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 27 | E | Rod | 4570531.152 | 372584.804 | 6995.258 | 33760.5861 | 338824.2179 | 15085.7205 | 0.10211 | -116487.9347 | 116487.9347
C | Xist Rating 7205 | 0.79 | 2251.09 | 150.298 | 35.6 | 2031.85 | 8270.55 | 10537.6 | 0.26 | 1.25 | 21.368 | 13.869 | 1 | 1 | 2690 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4573877.2165 | 375244.0327 | 7047.5588 | 33886.5584 | 341357.4742 | 15072.8291 | 0.10249 | -116388.3907 | 116388.3907
C | Xist Rating 7206 | 0.85 | 2252.3 | 150.298 | 35.6 | 2032.66 | 8283.97 | 10537.6 | 0.26 | 1.25 | 21.368 | 13.878 | 1 | 1 | 2700 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4578160.118 | 377912.6962 | 7100.0544 | 34012.5308 | 343900.1655 | 15084.6659 | 0.10287 | -116479.7913 | 116479.7913
C | Xist Rating 7207 | 0.93 | 2253.95 | 150.298 | 35.6 | 2033.53 | 8298.49 | 10537.5 | 0.26 | 1.25 | 21.369 | 13.889 | 1 | 1 | 2710 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4583474.9435 | 380590.7946 | 7152.7448 | 34138.5031 | 346452.2915 | 15098.6112 | 0.10325 | -116587.4739 | 116587.4739
C | Xist Rating 7208 | 0.92 | 2255.3 | 150.298 | 35.6 | 2032.6 | 8283.04 | 10537.5 | 0.25 | 1.25 | 21.366 | 13.899 | 1 | 1 | 2720 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4584122.78 | 383278.3279 | 7205.63 | 34264.4754 | 349013.8524 | 15085.3415 | 0.10363 | -116485.0083 | 116485.0083
C | Xist Rating 7209 | 0.96 | 2256.62 | 150.298 | 35.6 | 2032.66 | 8284.12 | 10537.5 | 0.25 | 1.25 | 21.4 | 13.908 | 1 | 1 | 2730 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4586941.2092 | 385975.296 | 7258.71 | 34390.4478 | 351584.8482 | 15098.1224 | 0.10402 | -116583.6994 | 116583.6994
C | Xist Rating 7210 | 0.95 | 2257.9 | 150.298 | 35.6 | 2031.8 | 8269.81 | 10537.5 | 0.25 | 1.25 | 21.393 | 13.918 | 1 | 1 | 2740 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4587601.22 | 388681.6989 | 7311.9847 | 34516.4201 | 354165.2788 | 15110.6906 | 0.1044 | -116680.7474 | 116680.7474
C | Xist Rating 7211 | 0.94 | 2259.45 | 150.298 | 35.6 | 2030.86 | 8254.3 | 10537.5 | 0.25 | 1.25 | 21.393 | 13.928 | 1 | 1 | 2750 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4588626.627 | 391397.5367 | 7365.4543 | 34642.3925 | 356755.1442 | 15123.4729 | 0.10478 | -116779.4491 | 116779.4491
C | Xist Rating 7212 | 0.95 | 2260.87 | 150.298 | 35.6 | 2030.19 | 8243.25 | 10537.6 | 0.24 | 1.25 | 21.397 | 13.938 | 1 | 1 | 2760 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4589995.6653 | 394122.8093 | 7419.1186 | 34768.3648 | 359354.4445 | 15109.9074 | 0.10516 | -116674.7 | 116674.7
C | Xist Rating 7213 | 0.93 | 2262.11 | 150.298 | 35.6 | 2029.33 | 8229.04 | 10537.5 | 0.24 | 1.25 | 21.392 | 13.947 | 1 | 1 | 2770 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4590567.6863 | 396857.5168 | 7472.9777 | 34894.3371 | 361963.1796 | 15121.4068 | 0.10554 | -116763.4951 | 116763.4951
C | Xist Rating 7214 | 0.94 | 2263.66 | 150.299 | 35.6 | 2028.74 | 8219.29 | 10537.5 | 0.24 | 1.25 | 21.436 | 13.957 | 1 | 1 | 2780 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4592377.5884 | 399601.6591 | 7527.0316 | 35020.3095 | 364581.3496 | 15135.409 | 0.10592 | -116871.6165 | 116871.6165
C | Xist Rating 7215 | 0.92 | 2265.07 | 150.298 | 35.6 | 2027.49 | 8198.98 | 10537.5 | 0.23 | 1.25 | 21.429 | 13.967 | 1 | 1 | 2790 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4592406.7743 | 402355.2363 | 7581.2803 | 35146.2818 | 367208.9544 | 15121.0907 | 0.1063 | -116761.0542 | 116761.0542
C | Xist Rating 7216 | 0.96 | 2266.04 | 150.299 | 35.6 | 2028.07 | 8208.37 | 10537.6 | 0.23 | 1.25 | 21.437 | 13.974 | 1 | 1 | 2800 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4595687.7428 | 405118.2483 | 7635.7238 | 35272.2541 | 369845.9941 | 15130.8004 | 0.10668 | -116836.0298 | 116836.0298
C | Xist Rating 7217 | 0.98 | 2267.78 | 150.299 | 35.6 | 2027.45 | 8198.15 | 10537.6 | 0.23 | 1.25 | 21.445 | 13.986 | 1 | 1 | 2810 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4597810.561 | 407890.6951 | 7690.3621 | 35398.2265 | 372492.4687 | 15145.7042 | 0.10706 | -116951.1132 | 116951.1132
C | Xist Rating 7218 | 0.94 | 2269.26 | 150.298 | 35.6 | 2025.93 | 8173.47 | 10537.6 | 0.23 | 1.25 | 21.437 | 13.995 | 1 | 1 | 2820 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4597361.9118 | 410672.5768 | 7745.1952 | 35524.1988 | 375148.378 | 15157.029 | 0.10744 | -117038.5604 | 117038.5604
C | Xist Rating 7219 | 0.98 | 2270.63 | 150.299 | 35.6 | 2025.97 | 8174.01 | 10537.6 | 0.22 | 1.25 | 21.485 | 14.005 | 1 | 1 | 2830 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4600228.2611 | 413463.8934 | 7800.223 | 35650.1711 | 377813.7222 | 15143.77 | 0.10783 | -116936.1779 | 116936.1779
C | Xist Rating 7220 | 1.05 | 2271.95 | 150.299 | 35.6 | 2026.72 | 8186.2 | 10537.6 | 0.22 | 1.25 | 21.494 | 14.014 | 1 | 1 | 2840 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4604606.504 | 416264.6448 | 7855.4457 | 35776.1435 | 380488.5013 | 15155.4873 | 0.10821 | -117026.6556 | 117026.6556
C | Xist Rating 7221 | 1.02 | 2273.39 | 150.299 | 35.6 | 2025.49 | 8166.29 | 10537.6 | 0.22 | 1.25 | 21.486 | 14.023 | 1 | 1 | 2850 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4604728.7111 | 419074.831 | 7910.8631 | 35902.1158 | 383172.7152 | 15166.7286 | 0.10859 | -117113.4576 | 117113.4576
C | Xist Rating 7222 | 1.08 | 2274.8 | 150.299 | 35.6 | 2026.07 | 8175.72 | 10537.6 | 0.22 | 1.25 | 21.499 | 14.033 | 1 | 1 | 2860 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4608904.036 | 421894.4521 | 7966.4753 | 36028.0882 | 385866.364 | 15179.599 | 0.10897 | -117212.8399 | 117212.8399
C | Xist Rating 7223 | 1.22 | 2275.99 | 150.299 | 35.6 | 2028.38 | 8213.38 | 10537.7 | 0.21 | 1.25 | 21.527 | 14.042 | 1 | 1 | 2870 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4616572.5962 | 424723.5081 | 8022.2824 | 36154.0605 | 388569.4476 | 15164.1643 | 0.10935 | -117093.657 | 117093.657
C | Xist Rating 7224 | 1.4 | 2277.5 | 150.299 | 35.6 | 2031.05 | 8257.13 | 10537.8 | 0.21 | 1.25 | 21.6 | 14.052 | 1 | 1 | 2880 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4625716.375 | 427561.9989 | 8078.2842 | 36280.0328 | 391281.966 | 15178.5547 | 0.10973 | -117204.7757 | 117204.7757
C | Xist Rating 7225 | 1.51 | 2278.84 | 150.299 | 35.6 | 2032.19 | 8276.01 | 10538 | 0.21 | 1.25 | 21.601 | 14.061 | 1 | 1 | 2890 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4631035.8596 | 430409.9245 | 8134.4807 | 36406.0052 | 394003.9193 | 15189.9616 | 0.11011 | -117292.8571 | 117292.8571
C | Xist Rating 7226 | 2.12 | 2280.23 | 150.299 | 35.6 | 2044.48 | 8483.61 | 10538 | 0.2 | 1.25 | 21.676 | 14.071 | 1 | 1 | 2900 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4661884.6304 | 433267.285 | 8190.8721 | 36531.9775 | 396735.3075 | 15176.2503 | 0.11049 | -117186.9823 | 117186.9823
C | Xist Rating 7227 | 2.57 | 2281.76 | 150.299 | 35.6 | 2052.96 | 8631.43 | 10538.1 | 0.2 | 1.25 | 21.727 | 14.082 | 1 | 1 | 2910 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4684362.0096 | 436134.0803 | 8247.4583 | 36657.9498 | 399476.1305 | 15190.9475 | 0.11087 | -117300.4703 | 117300.4703
C | Xist Rating 7228 | 2.06 | 2283.16 | 150.299 | 35.6 | 2042.06 | 8442.13 | 10538 | 0.2 | 1.25 | 21.648 | 14.09 | 1 | 1 | 2920 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4662349.7096 | 439010.3105 | 8304.2393 | 36783.9222 | 402226.3883 | 15199.1353 | 0.11125 | -117363.694 | 117363.694
C | Xist Rating 7229 | 2.85 | 2284.54 | 150.299 | 35.6 | 2057.4 | 8710.49 | 10538.1 | 0.2 | 1.25 | 21.788 | 14.101 | 1 | 1 | 2930 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4700212.596 | 441895.9755 | 8361.215 | 36909.8945 | 404986.081 | 15216.1769 | 0.11164 | -117495.2849 | 117495.2849
C | Xist Rating 7230 | 3.27 | 2285.91 | 150.299 | 35.6 | 2065.22 | 8852.51 | 10538.2 | 0.19 | 1.25 | 21.831 | 14.111 | 1 | 1 | 2940 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4720907.0502 | 444791.0754 | 8418.3855 | 37035.8668 | 407755.2085 | 15200.8787 | 0.11202 | -117377.1558 | 117377.1558
C | Xist Rating 7231 | 3.54 | 2287.32 | 150.299 | 35.6 | 2070.07 | 8942.18 | 10538.2 | 0.19 | 1.25 | 21.858 | 14.12 | 1 | 1 | 2950 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4734912.5124 | 447695.6101 | 8475.7509 | 37161.8392 | 410533.7709 | 15212.7628 | 0.1124 | -117468.9218 | 117468.9218
C | Xist Rating 7232 | 3.96 | 2288.69 | 150.299 | 35.6 | 2077.97 | 9091.66 | 10538.1 | 0.19 | 1.25 | 21.911 | 14.13 | 1 | 1 | 2960 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4755829.1593 | 450609.5796 | 8533.311 | 37287.8115 | 413321.7681 | 15226.3455 | 0.11278 | -117573.8035 | 117573.8035
C | Xist Rating 7233 | 4.39 | 2290.07 | 150.299 | 35.6 | 2086.2 | 9251.3 | 10538 | 0.18 | 1.25 | 21.934 | 14.14 | 1 | 1 | 2970 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4777544.034 | 453532.9841 | 8591.0659 | 37413.7839 | 416119.2002 | 15209.9777 | 0.11316 | -117447.4164 | 117447.4164
C | Xist Rating 7234 | 4.39 | 2291.3 | 150.299 | 35.6 | 2085.6 | 9239.59 | 10538 | 0.18 | 1.25 | 21.969 | 14.148 | 1 | 1 | 2980 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4778735.28 | 456465.8233 | 8649.0156 | 37539.7562 | 418926.0671 | 15220.897 | 0.11354 | -117531.732 | 117531.732
C | Xist Rating 7235 | 4.4 | 2292.86 | 150.299 | 35.6 | 2084.87 | 9225.2 | 10538 | 0.18 | 1.25 | 21.965 | 14.158 | 1 | 1 | 2990 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4780315.0282 | 459408.0974 | 8707.16 | 37665.7285 | 421742.3689 | 15232.958 | 0.11392 | -117624.8642 | 117624.8642
C | Xist Rating 7236 | 4.4 | 2294.28 | 150.299 | 35.6 | 2084.28 | 9213.68 | 10537.9 | 0.18 | 1.25 | 21.946 | 14.167 | 1 | 1 | 3000 | 152.4 | 2 | 4.5 | 19.05 | 1.3333 | 26 | E | Rod | 4781921.9184 | 462359.8064 | 8765.4993 | 37791.7009 | 424568.1055 | 15243.6169 | 0.1143 | -117707.1687 | 117707.1687
C | Xist Rating 7237 | -87.14 | 234.833 | 150.304 | 35.9 | 2359.02 | 7030.7 | 58745.8 | 2.48 | 10.95 | 23.893 | 570.612 | 1 | 1 | 1000 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 553975.7437 | 61099.7224 | 973.9444 | 12877.1721 | 48222.5503 | 595235.7283 | 0.038101 | -4596252.5144 | 4596252.5144
C | Xist Rating 7238 | -87.02 | 237.259 | 150.304 | 35.9 | 2356.5 | 7016.01 | 58284.1 | 2.46 | 10.85 | 23.972 | 559.88 | 1 | 1 | 1010 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 559100.8335 | 62197.7674 | 993.5206 | 13005.9439 | 49191.8235 | 584104.2882 | 0.038482 | -4510298.4844 | 4510298.4844
C | Xist Rating 7239 | -86.07 | 255.68 | 150.304 | 35.9 | 2348.44 | 7002.95 | 54967.2 | 2.47 | 10.07 | 24.023 | 485.189 | 1 | 1 | 1020 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 600449.1392 | 63305.4569 | 1013.2917 | 13134.7156 | 50170.7413 | 506580.9561 | 0.038863 | -3911683.8635 | 3911683.8635
C | Xist Rating 7240 | -85.9 | 260.677 | 150.303 | 35.9 | 2332.23 | 6875.14 | 54177.8 | 2.38 | 9.89 | 23.448 | 468.851 | 1 | 1 | 1030 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 607958.7197 | 64422.7909 | 1033.2576 | 13263.4873 | 51159.3036 | 489477.5622 | 0.039244 | -3779615.9894 | 3779615.9894
C | Xist Rating 7241 | -85.81 | 263.177 | 150.303 | 35.9 | 2326.11 | 6829.32 | 53793.1 | 2.34 | 9.8 | 23.316 | 461.031 | 1 | 1 | 1040 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 612178.6515 | 65549.7694 | 1053.4182 | 13392.259 | 52157.5104 | 481323.3967 | 0.039625 | -3716651.6844 | 3716651.6844
C | Xist Rating 7242 | -85.59 | 268.052 | 150.303 | 35.9 | 2319.77 | 6788.87 | 53042.1 | 2.3 | 9.63 | 23.226 | 445.716 | 1 | 1 | 1050 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 621818.988 | 66686.3924 | 1073.7737 | 13521.0308 | 53165.3617 | 465389.6113 | 0.040006 | -3593615.2174 | 3593615.2174
C | Xist Rating 7243 | -85.46 | 270.533 | 150.303 | 35.9 | 2319.26 | 6791.45 | 52676 | 2.27 | 9.54 | 23.195 | 438.457 | 1 | 1 | 1060 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 627436.3656 | 67832.6599 | 1094.3239 | 13649.8025 | 54182.8575 | 457838.6461 | 0.040387 | -3535308.6652 | 3535308.6652
C | Xist Rating 7244 | -84.5 | 290.322 | 150.302 | 35.9 | 2304.61 | 6722.66 | 49856.6 | 2.25 | 8.9 | 22.972 | 383.618 | 1 | 1 | 1070 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 669078.9844 | 68988.572 | 1115.0689 | 13778.5742 | 55209.9978 | 400865.7178 | 0.040768 | -3095378.8148 | 3095378.8148
C | Xist Rating 7245 | -84.27 | 294.046 | 150.302 | 35.9 | 2310.09 | 6779.71 | 49380 | 2.19 | 8.79 | 22.862 | 374.992 | 1 | 1 | 1080 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 679272.7241 | 70154.1285 | 1136.0087 | 13907.3459 | 56246.7826 | 391852.4115 | 0.041149 | -3025780.4528 | 3025780.4528
C | Xist Rating 7246 | -83.98 | 299.002 | 150.301 | 35.9 | 2313.95 | 6826.89 | 48761.2 | 2.13 | 8.65 | 22.693 | 363.92 | 1 | 1 | 1090 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 691875.6779 | 71329.3296 | 1157.1433 | 14036.1176 | 57293.212 | 380291.9913 | 0.04153 | -2936513.9523 | 2936513.9523
C | Xist Rating 7247 | -83.72 | 302.694 | 150.301 | 35.9 | 2324.18 | 6927.31 | 48307.4 | 2.09 | 8.55 | 22.695 | 355.919 | 1 | 1 | 1100 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 703515.3409 | 72514.1752 | 1178.4727 | 14164.8894 | 58349.2858 | 371960.081 | 0.041911 | -2872177.1494 | 2872177.1494
C | Xist Rating 7248 | -83.59 | 305.362 | 150.301 | 35.9 | 2322.56 | 6919.91 | 48010.8 | 2.01 | 8.49 | 22.345 | 351.002 | 1 | 1 | 1110 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 709221.5667 | 73708.6653 | 1199.9969 | 14293.6611 | 59415.0042 | 366749.707 | 0.042292 | -2831944.0226 | 2831944.0226
C | Xist Rating 7249 | -82.45 | 327.402 | 150.301 | 35.9 | 2318.22 | 6946.12 | 45448.2 | 2.05 | 7.92 | 22.649 | 307.126 | 1 | 1 | 1120 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 758989.8644 | 74912.7998 | 1221.7158 | 14422.4328 | 60490.367 | 321280.8415 | 0.042673 | -2480845.496 | 2480845.496
C | Xist Rating 7250 | -82.3 | 330.024 | 150.301 | 35.9 | 2319.53 | 6964.89 | 45189.3 | 1.99 | 7.86 | 22.427 | 303.158 | 1 | 1 | 1130 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 765500.5687 | 76126.5789 | 1243.6296 | 14551.2045 | 61575.3744 | 317089.6823 | 0.043054 | -2448482.4753 | 2448482.4753
C | Xist Rating 7251 | -82.06 | 335.05 | 150.3 | 35.8 | 2316.79 | 6954.25 | 44681.2 | 1.93 | 7.75 | 22.218 | 295.213 | 1 | 1 | 1140 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 776240.4895 | 77350.0026 | 1265.7381 | 14679.9762 | 62670.0263 | 308769.4439 | 0.043435 | -2384235.7999 | 2384235.7999
C | Xist Rating 7252 | -81.8 | 340.013 | 150.3 | 35.8 | 2317.47 | 6974.42 | 44186.2 | 1.89 | 7.64 | 22.003 | 287.531 | 1 | 1 | 1150 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 787969.9271 | 78583.0707 | 1288.0414 | 14808.748 | 63774.3227 | 300744.1615 | 0.043816 | -2322266.6963 | 2322266.6963
C | Xist Rating 7253 | -81.56 | 345.055 | 150.299 | 35.8 | 2314.18 | 6958.6 | 43703.3 | 1.84 | 7.53 | 21.821 | 280.219 | 1 | 1 | 1160 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 798519.3799 | 79825.7833 | 1310.5395 | 14937.5197 | 64888.2636 | 293094.685 | 0.044197 | -2263199.4665 | 2263199.4665
C | Xist Rating 7254 | -80.54 | 364.83 | 150.3 | 35.8 | 2310.17 | 6979.3 | 41832.3 | 1.86 | 7.13 | 21.981 | 252.051 | 1 | 1 | 1170 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 842819.3211 | 81078.1405 | 1333.2324 | 15066.2914 | 66011.849 | 263898.7545 | 0.044578 | -2037756.2301 | 2037756.2301
C | Xist Rating 7255 | -80.41 | 366.234 | 150.299 | 35.8 | 2317.79 | 7052.9 | 41724.6 | 1.81 | 7.11 | 21.891 | 250.674 | 1 | 1 | 1180 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 848853.5029 | 82340.1421 | 1356.1201 | 15195.0631 | 67145.079 | 262420.3201 | 0.044959 | -2026340.1519 | 2026340.1519
C | Xist Rating 7256 | -79.95 | 376.145 | 150.299 | 35.8 | 2311.07 | 7018.75 | 40885.5 | 1.76 | 6.92 | 21.702 | 238.893 | 1 | 1 | 1190 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 869297.4252 | 83611.7883 | 1379.2026 | 15323.8349 | 68287.9534 | 250127.4028 | 0.04534 | -1931417.5026 | 1931417.5026
C | Xist Rating 7257 | -79.72 | 378.659 | 150.299 | 35.8 | 2322.97 | 7136.83 | 40681.7 | 1.73 | 6.88 | 21.748 | 236.139 | 1 | 1 | 1200 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 879613.4972 | 84893.0789 | 1402.4799 | 15452.6066 | 69440.4724 | 247253.7595 | 0.045721 | -1909227.9907 | 1909227.9907
C | Xist Rating 7258 | -79.47 | 383.77 | 150.299 | 35.8 | 2321.72 | 7139.39 | 40281 | 1.68 | 6.8 | 21.581 | 230.779 | 1 | 1 | 1210 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 891006.4844 | 86184.0141 | 1425.9519 | 15581.3783 | 70602.6358 | 241630.0776 | 0.046102 | -1865803.4101 | 1865803.4101
C | Xist Rating 7259 | -78.39 | 406.164 | 150.299 | 35.8 | 2309.54 | 7089.77 | 38537.7 | 1.68 | 6.43 | 21.585 | 207.504 | 1 | 1 | 1220 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 938052.0046 | 87484.5938 | 1449.6188 | 15710.15 | 71774.4438 | 217475.646 | 0.046483 | -1679289.2923 | 1679289.2923
C | Xist Rating 7260 | -78.07 | 411.125 | 150.299 | 35.8 | 2315.42 | 7159.69 | 38183.3 | 1.65 | 6.35 | 21.607 | 203.043 | 1 | 1 | 1230 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 951927.0475 | 88794.818 | 1473.4804 | 15838.9217 | 72955.8963 | 212825.4584 | 0.046864 | -1643381.7761 | 1643381.7761
C | Xist Rating 7261 | -77.81 | 416.226 | 150.298 | 35.8 | 2315.96 | 7179.09 | 37835.3 | 1.61 | 6.28 | 21.491 | 198.79 | 1 | 1 | 1240 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 963962.767 | 90114.6867 | 1497.5369 | 15967.6935 | 74146.9933 | 208366.2858 | 0.047245 | -1608949.2273 | 1608949.2273
C | Xist Rating 7262 | -77.63 | 418.884 | 150.298 | 35.8 | 2320.35 | 7228.6 | 37664.3 | 1.57 | 6.24 | 21.418 | 196.787 | 1 | 1 | 1250 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 971957.4894 | 91444.2 | 1521.7881 | 16096.4652 | 75347.7348 | 206247.095 | 0.047626 | -1592585.3978 | 1592585.3978
C | Xist Rating 7263 | -77.24 | 426.349 | 150.298 | 35.8 | 2320.45 | 7251.3 | 37161.4 | 1.54 | 6.14 | 21.371 | 190.659 | 1 | 1 | 1260 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 29 | E | Rod | 989321.537 | 92783.3577 | 1546.2341 | 16225.2369 | 76558.1208 | 199857.8716 | 0.048007 | -1543249.5077 | 1543249.5077
C | Xist Rating 7264 | -76.19 | 447.555 | 150.298 | 35.8 | 2313.59 | 7247.08 | 35777.3 | 1.55 | 5.85 | 21.385 | 174.103 | 1 | 1 | 1270 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1035458.7725 | 94132.1599 | 1570.8749 | 16354.0086 | 77778.1513 | 182692.6454 | 0.048388 | -1410704.1812 | 1410704.1812
C | Xist Rating 7265 | -75.95 | 452.724 | 150.298 | 35.8 | 2311.35 | 7239.38 | 35477.1 | 1.5 | 5.79 | 21.26 | 170.779 | 1 | 1 | 1280 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1046403.6174 | 95490.6067 | 1595.7105 | 16482.7803 | 79007.8263 | 179183.4278 | 0.048769 | -1383606.9335 | 1383606.9335
C | Xist Rating 7266 | -75.69 | 457.842 | 150.298 | 35.8 | 2310.88 | 7249.05 | 35182.6 | 1.47 | 5.73 | 21.218 | 167.535 | 1 | 1 | 1290 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1058017.921 | 96858.6979 | 1620.7408 | 16611.5521 | 80247.1459 | 175788.3835 | 0.04915 | -1357391.3009 | 1357391.3009
C | Xist Rating 7267 | -75.28 | 465.285 | 150.298 | 35.8 | 2312.91 | 7290.47 | 34751.2 | 1.45 | 5.64 | 21.256 | 162.75 | 1 | 1 | 1300 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1076162.3294 | 98236.4337 | 1645.966 | 16740.3238 | 81496.1099 | 170811.632 | 0.049531 | -1318962.1454 | 1318962.1454
C | Xist Rating 7268 | -75.03 | 469.202 | 150.298 | 35.8 | 2317.5 | 7347.29 | 34539.8 | 1.41 | 5.59 | 21.21 | 160.521 | 1 | 1 | 1310 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1087375.635 | 99623.814 | 1671.3859 | 16869.0955 | 82754.7185 | 168456.8996 | 0.049912 | -1300779.5258 | 1300779.5258
C | Xist Rating 7269 | -73.97 | 490.506 | 150.298 | 35.8 | 2311.5 | 7350.15 | 33363.1 | 1.42 | 5.35 | 21.264 | 147.809 | 1 | 1 | 1320 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1133804.619 | 101020.8388 | 1697.0007 | 16997.8672 | 84022.9716 | 155285.9997 | 0.050293 | -1199077.3279 | 1199077.3279
C | Xist Rating 7270 | -73.6 | 498.166 | 150.298 | 35.8 | 2309.22 | 7348.71 | 32980 | 1.38 | 5.28 | 21.155 | 143.932 | 1 | 1 | 1330 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1150374.8905 | 102427.5081 | 1722.8102 | 17126.639 | 85300.8691 | 151213.6009 | 0.050674 | -1167631.3437 | 1167631.3437
C | Xist Rating 7271 | -73.19 | 505.725 | 150.297 | 35.8 | 2311.33 | 7391.87 | 32606.8 | 1.35 | 5.2 | 21.061 | 140.185 | 1 | 1 | 1340 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1168897.3643 | 103843.8219 | 1748.8145 | 17255.4107 | 86588.4112 | 147289.6908 | 0.051055 | -1137331.9505 | 1137331.9505
C | Xist Rating 7272 | -72.93 | 509.659 | 150.297 | 35.8 | 2317.06 | 7461.88 | 32423.5 | 1.32 | 5.16 | 21.023 | 138.426 | 1 | 1 | 1350 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1180910.4825 | 105269.7802 | 1775.0136 | 17384.1824 | 87885.5978 | 145434.4474 | 0.051436 | -1123006.2522 | 1123006.2522
C | Xist Rating 7273 | -72.64 | 512.119 | 150.298 | 35.8 | 2330.76 | 7613.59 | 32303.1 | 1.31 | 5.14 | 21.11 | 137.238 | 1 | 1 | 1360 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1193626.4804 | 106705.3831 | 1801.4075 | 17512.9541 | 89192.429 | 144207.2821 | 0.051817 | -1113530.4072 | 1113530.4072
C | Xist Rating 7274 | -71.33 | 542.317 | 150.297 | 35.8 | 2307.21 | 7456.6 | 30902.2 | 1.3 | 4.86 | 21.028 | 123.631 | 1 | 1 | 1370 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1251239.2056 | 108150.6304 | 1827.9962 | 17641.7258 | 90508.9046 | 130069.3201 | 0.052198 | -1004360.8121 | 1004360.8121
C | Xist Rating 7275 | -71.21 | 545.039 | 150.297 | 35.8 | 2306.22 | 7453.56 | 30793.8 | 1.27 | 4.84 | 20.983 | 122.694 | 1 | 1 | 1380 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1256979.8426 | 109605.5223 | 1854.7797 | 17770.4976 | 91835.0247 | 129065.9428 | 0.052579 | -996612.9988 | 996612.9988
C | Xist Rating 7276 | -70.87 | 551.456 | 150.297 | 35.8 | 2307.2 | 7481.98 | 30526.9 | 1.24 | 4.78 | 20.943 | 120.284 | 1 | 1 | 1390 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1272319.2832 | 111070.0586 | 1881.7579 | 17899.2693 | 93170.7893 | 126532.7951 | 0.05296 | -977052.7037 | 977052.7037
C | Xist Rating 7277 | -70.53 | 557.87 | 150.297 | 35.8 | 2308.38 | 7512.77 | 30264.9 | 1.22 | 4.73 | 20.911 | 117.947 | 1 | 1 | 1400 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1287775.9506 | 112544.2395 | 1908.931 | 18028.041 | 94516.1985 | 124088.7297 | 0.053341 | -958180.2783 | 958180.2783
C | Xist Rating 7278 | -70.13 | 565.489 | 150.297 | 35.8 | 2309.04 | 7541.97 | 29957.2 | 1.2 | 4.67 | 20.887 | 115.216 | 1 | 1 | 1410 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1305736.7206 | 114028.0649 | 1936.2988 | 18156.8127 | 95871.2522 | 121235.773 | 0.053722 | -936150.5031 | 936150.5031
C | Xist Rating 7279 | -69.01 | 588.126 | 150.297 | 35.8 | 2304.24 | 7558.8 | 29051.6 | 1.2 | 4.49 | 20.962 | 107.19 | 1 | 1 | 1420 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1355183.4542 | 115521.5348 | 1963.8614 | 18285.5844 | 97235.9503 | 112917.7483 | 0.054103 | -871920.9213 | 871920.9213
C | Xist Rating 7280 | -68.82 | 592.3 | 150.297 | 35.7 | 2302.88 | 7555.14 | 28910.4 | 1.17 | 4.47 | 20.87 | 106.082 | 1 | 1 | 1430 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1363995.824 | 117024.6492 | 1991.6188 | 18414.3562 | 98610.293 | 111731.1583 | 0.054484 | -862758.388 | 862758.388
C | Xist Rating 7281 | -68.29 | 602.381 | 150.297 | 35.7 | 2303.43 | 7590.57 | 28541.8 | 1.15 | 4.39 | 20.857 | 102.998 | 1 | 1 | 1440 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1387542.4668 | 118537.4081 | 2019.571 | 18543.1279 | 99994.2802 | 108511.4673 | 0.054865 | -837896.7876 | 837896.7876
C | Xist Rating 7282 | -67.96 | 608.832 | 150.297 | 35.7 | 2304.07 | 7616.09 | 28316.6 | 1.13 | 4.35 | 20.831 | 101.175 | 1 | 1 | 1450 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1402791.5462 | 120059.8115 | 2047.718 | 18671.8996 | 101387.9119 | 106600.0143 | 0.055246 | -823137.0536 | 823137.0536
C | Xist Rating 7283 | -67.66 | 612.648 | 150.297 | 35.7 | 2311.44 | 7708.58 | 28183.4 | 1.12 | 4.32 | 20.863 | 100.106 | 1 | 1 | 1460 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1416099.0931 | 121591.8595 | 2076.0598 | 18800.6713 | 102791.1881 | 105489.1236 | 0.055627 | -814559.0505 | 814559.0505
C | Xist Rating 7284 | -66.55 | 638.173 | 150.297 | 35.7 | 2296.14 | 7615.94 | 27310 | 1.11 | 4.16 | 20.832 | 93.061 | 1 | 1 | 1470 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1465334.5522 | 123133.5519 | 2104.5964 | 18929.4431 | 104204.1088 | 98167.3618 | 0.056008 | -758022.3464 | 758022.3464
C | Xist Rating 7285 | -66.15 | 645.836 | 150.297 | 35.7 | 2296.81 | 7645.55 | 27065.8 | 1.09 | 4.11 | 20.818 | 91.189 | 1 | 1 | 1480 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1483362.5832 | 124684.8889 | 2133.3277 | 19058.2148 | 105626.6741 | 96205.0053 | 0.056389 | -742869.55 | 742869.55
C | Xist Rating 7286 | -65.8 | 652.29 | 150.297 | 35.7 | 2298.15 | 7678.9 | 26866 | 1.07 | 4.07 | 20.804 | 89.688 | 1 | 1 | 1490 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1499060.2635 | 126245.8703 | 2162.2539 | 19186.9865 | 107058.8838 | 94627.582 | 0.05677 | -730689.1051 | 730689.1051
C | Xist Rating 7287 | -65.48 | 658.835 | 150.297 | 35.7 | 2297.91 | 7694.87 | 26669.6 | 1.05 | 4.03 | 20.771 | 88.238 | 1 | 1 | 1500 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1513943.5348 | 127816.4963 | 2191.3748 | 19315.7582 | 108500.7381 | 93101.4317 | 0.057151 | -718904.5768 | 718904.5768
C | Xist Rating 7288 | -65.03 | 666.526 | 150.297 | 35.7 | 2301.11 | 7753.48 | 26438.6 | 1.03 | 3.99 | 20.774 | 86.524 | 1 | 1 | 1510 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1533749.6439 | 129396.7668 | 2220.6906 | 19444.5299 | 109952.2368 | 91303.3128 | 0.057532 | -705019.9794 | 705019.9794
C | Xist Rating 7289 | -63.77 | 691.734 | 150.297 | 35.7 | 2298.09 | 7796.61 | 25680.7 | 1.04 | 3.84 | 20.853 | 80.879 | 1 | 1 | 1520 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1589666.9881 | 130986.6818 | 2250.2011 | 19573.3017 | 111413.3801 | 85470.3323 | 0.057913 | -659979.2505 | 659979.2505
C | Xist Rating 7290 | -63.43 | 699.768 | 150.297 | 35.7 | 2293.92 | 7771.39 | 25468 | 1.01 | 3.8 | 20.776 | 79.425 | 1 | 1 | 1530 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1605211.8106 | 132586.2413 | 2279.9064 | 19702.0734 | 112884.1679 | 83921.8392 | 0.058294 | -648022.1968 | 648022.1968
C | Xist Rating 7291 | -63.11 | 703.859 | 150.297 | 35.7 | 2301.04 | 7865.09 | 25363.6 | 0.99 | 3.78 | 20.771 | 78.735 | 1 | 1 | 1540 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1619607.7134 | 134195.4453 | 2309.8065 | 19830.8451 | 114364.6002 | 83185.6561 | 0.058675 | -642337.5865 | 642337.5865
C | Xist Rating 7292 | -62.5 | 716.525 | 150.297 | 35.7 | 2299.34 | 7883.71 | 25020.8 | 0.98 | 3.72 | 20.73 | 76.346 | 1 | 1 | 1550 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1647534.5935 | 135814.2938 | 2339.9013 | 19959.6168 | 115854.677 | 80696.6779 | 0.059056 | -623118.3562 | 623118.3562
C | Xist Rating 7293 | -62.18 | 720.391 | 150.297 | 35.7 | 2308.02 | 7998.62 | 24919.5 | 0.97 | 3.7 | 20.782 | 75.671 | 1 | 1 | 1560 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1662676.8358 | 137442.7868 | 2370.191 | 20088.3885 | 117354.3983 | 79993.8291 | 0.059437 | -617691.1441 | 617691.1441
C | Xist Rating 7294 | -60.89 | 749.914 | 150.297 | 35.7 | 2291.96 | 7898.31 | 24162.1 | 0.96 | 3.56 | 20.744 | 70.531 | 1 | 1 | 1570 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1718772.8914 | 139080.9244 | 2400.6755 | 20217.1603 | 118863.7641 | 74647.7907 | 0.059818 | -576410.4525 | 576410.4525
C | Xist Rating 7295 | -60.57 | 756.488 | 150.296 | 35.7 | 2292.79 | 7927.53 | 24006.5 | 0.94 | 3.53 | 20.711 | 69.547 | 1 | 1 | 1580 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1734468.1215 | 140728.7064 | 2431.3547 | 20345.932 | 120382.7745 | 73603.2548 | 0.0602 | -568344.8231 | 568344.8231
C | Xist Rating 7296 | -60.2 | 763.098 | 150.296 | 35.7 | 2295.46 | 7978.97 | 23854 | 0.92 | 3.5 | 20.7 | 68.591 | 1 | 1 | 1590 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1751660.9351 | 142386.133 | 2462.2288 | 20474.7037 | 121911.4293 | 72588.9337 | 0.060581 | -560512.5045 | 560512.5045
C | Xist Rating 7297 | -59.66 | 772.024 | 150.297 | 35.7 | 2299.46 | 8055.13 | 23644.6 | 0.91 | 3.46 | 20.723 | 67.255 | 1 | 1 | 1600 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1775238.307 | 144053.2041 | 2493.2976 | 20603.4754 | 123449.7287 | 71196.6913 | 0.060962 | -549761.9784 | 549761.9784
C | Xist Rating 7298 | -59.43 | 776.31 | 150.296 | 35.7 | 2300.79 | 8083.37 | 23555.9 | 0.89 | 3.45 | 20.693 | 66.743 | 1 | 1 | 1610 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1786126.2849 | 145729.9197 | 2524.5612 | 20732.2472 | 124997.6725 | 70641.5957 | 0.061343 | -545475.6766 | 545475.6766
C | Xist Rating 7299 | -57.96 | 809.362 | 150.297 | 35.7 | 2287.58 | 8025 | 22804.4 | 0.89 | 3.31 | 20.726 | 62.005 | 1 | 1 | 1620 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1851480.324 | 147416.2798 | 2556.0196 | 20861.0189 | 126555.2609 | 65731.5781 | 0.061724 | -507561.8228 | 507561.8228
C | Xist Rating 7300 | -57.61 | 813.303 | 150.297 | 35.7 | 2296.04 | 8142.03 | 22722.7 | 0.88 | 3.29 | 20.75 | 61.532 | 1 | 1 | 1630 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1867376.2201 | 149112.2844 | 2587.6728 | 20989.7906 | 128122.4938 | 65235.0366 | 0.062105 | -503727.661 | 503727.661
C | Xist Rating 7301 | -57.26 | 820.06 | 150.297 | 35.7 | 2296.88 | 8172.79 | 22587.9 | 0.87 | 3.27 | 20.726 | 60.76 | 1 | 1 | 1640 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1883579.4128 | 150817.9335 | 2619.5208 | 21118.5623 | 129699.3712 | 64424.7121 | 0.062486 | -497470.5495 | 497470.5495
C | Xist Rating 7302 | -56.83 | 829.344 | 150.296 | 35.7 | 2294.75 | 8173.92 | 22402.4 | 0.85 | 3.23 | 20.699 | 59.688 | 1 | 1 | 1650 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1903137.144 | 152533.2271 | 2651.5635 | 21247.334 | 131285.8931 | 63287.1688 | 0.062867 | -488686.7419 | 488686.7419
C | Xist Rating 7303 | -56.33 | 838.385 | 150.297 | 35.7 | 2297.08 | 8232.08 | 22220.3 | 0.84 | 3.2 | 20.705 | 58.63 | 1 | 1 | 1660 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1925837.4158 | 154258.1652 | 2683.8011 | 21376.1058 | 132882.0595 | 62181.2971 | 0.063248 | -480147.4938 | 480147.4938
C | Xist Rating 7304 | -55.04 | 867.952 | 150.297 | 35.7 | 2284.61 | 8166.81 | 21632.5 | 0.84 | 3.09 | 20.727 | 55.213 | 1 | 1 | 1670 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1982931.8187 | 155992.7479 | 2716.2334 | 21504.8775 | 134487.8704 | 58641.9274 | 0.063629 | -452817.4188 | 452817.4188
C | Xist Rating 7305 | -54.72 | 872.004 | 150.297 | 35.7 | 2290.97 | 8260.89 | 21560 | 0.82 | 3.08 | 20.738 | 54.83 | 1 | 1 | 1680 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 1997735.0039 | 157736.975 | 2748.8606 | 21633.6492 | 136103.3258 | 58221.4489 | 0.06401 | -449570.5955 | 449570.5955
C | Xist Rating 7306 | -54.21 | 883.865 | 150.297 | 35.7 | 2286.44 | 8238.52 | 21345.6 | 0.81 | 3.04 | 20.706 | 53.662 | 1 | 1 | 1690 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2020904.2906 | 159490.8467 | 2781.6825 | 21762.4209 | 137728.4258 | 56998.4319 | 0.064391 | -440126.7826 | 440126.7826
C | Xist Rating 7307 | -53.77 | 891.712 | 150.297 | 35.7 | 2288.94 | 8295.49 | 21205.4 | 0.8 | 3.02 | 20.71 | 52.907 | 1 | 1 | 1700 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2041075.2653 | 161254.3629 | 2814.6992 | 21891.1926 | 139363.1702 | 56206.349 | 0.064772 | -434010.5284 | 434010.5284
C | Xist Rating 7308 | -53.31 | 900.945 | 150.297 | 35.7 | 2288.64 | 8320.23 | 21044.4 | 0.78 | 2.99 | 20.701 | 52.051 | 1 | 1 | 1710 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2061938.7648 | 163027.5236 | 2847.9107 | 22019.9644 | 141007.5592 | 55292.5343 | 0.065153 | -426954.2937 | 426954.2937
C | Xist Rating 7309 | -52.12 | 928.14 | 150.297 | 35.7 | 2279.01 | 8280.41 | 20566.8 | 0.78 | 2.9 | 20.728 | 49.474 | 1 | 1 | 1720 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2115240.3414 | 164810.3288 | 2881.317 | 22148.7361 | 142661.5927 | 52625.1853 | 0.065534 | -406357.7318 | 406357.7318
C | Xist Rating 7310 | -51.56 | 939.87 | 150.297 | 35.7 | 2277.45 | 8296.14 | 20374 | 0.77 | 2.87 | 20.718 | 48.482 | 1 | 1 | 1730 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2140506.9315 | 166602.7785 | 2914.9181 | 22277.5078 | 144325.2707 | 51585.5711 | 0.065915 | -398330.1063 | 398330.1063
C | Xist Rating 7311 | -51.21 | 945.281 | 150.297 | 35.7 | 2281.56 | 8367.39 | 20289.8 | 0.76 | 2.85 | 20.718 | 48.069 | 1 | 1 | 1740 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2156715.3184 | 168404.8727 | 2948.714 | 22406.2795 | 145998.5932 | 51147.6631 | 0.066296 | -394948.6967 | 394948.6967
C | Xist Rating 7312 | -50.73 | 955.933 | 150.297 | 35.7 | 2278.86 | 8363.8 | 20123.3 | 0.75 | 2.82 | 20.697 | 47.239 | 1 | 1 | 1750 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2178437.4764 | 170216.6114 | 2982.7046 | 22535.0513 | 147681.5602 | 50275.28 | 0.066677 | -388212.3858 | 388212.3858
C | Xist Rating 7313 | -50.38 | 963.896 | 150.297 | 35.7 | 2277.11 | 8364.82 | 20000.4 | 0.74 | 2.8 | 20.691 | 46.634 | 1 | 1 | 1760 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2194897.2206 | 172037.9946 | 3016.8901 | 22663.823 | 149374.1717 | 49637.2681 | 0.067058 | -383285.8267 | 383285.8267
C | Xist Rating 7314 | -48.98 | 996.128 | 150.297 | 35.7 | 2266.22 | 8321.18 | 19497.1 | 0.74 | 2.71 | 20.727 | 44.1 | 1 | 1 | 1770 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2257445.1962 | 173869.0224 | 3051.2703 | 22792.5947 | 151076.4277 | 47014.6899 | 0.067439 | -363034.9735 | 363034.9735
C | Xist Rating 7315 | -48.55 | 1004.2 | 150.297 | 35.7 | 2267.53 | 8363.23 | 19382.8 | 0.73 | 2.69 | 20.72 | 43.566 | 1 | 1 | 1780 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2277053.626 | 175709.6946 | 3085.8453 | 22921.3664 | 152788.3282 | 46450.0616 | 0.06782 | -358675.0634 | 358675.0634
C | Xist Rating 7316 | -48.51 | 1008.51 | 150.297 | 35.6 | 2262.47 | 8306.76 | 19326.3 | 0.71 | 2.68 | 20.958 | 43.31 | 1 | 1 | 1790 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2281723.6197 | 177560.0114 | 3120.6151 | 23050.1381 | 154509.8733 | 46171.2945 | 0.068201 | -356522.4973 | 356522.4973
C | Xist Rating 7317 | -47.95 | 1022.86 | 150.297 | 35.6 | 2256.57 | 8271.1 | 19121.6 | 0.7 | 2.65 | 20.945 | 42.342 | 1 | 1 | 1800 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2308155.1902 | 179419.9727 | 3155.5797 | 23178.9099 | 156241.0628 | 45155.0539 | 0.068582 | -348675.3573 | 348675.3573
C | Xist Rating 7318 | -47.49 | 1030.8 | 150.297 | 35.6 | 2257 | 8300.57 | 19012.9 | 0.69 | 2.63 | 20.966 | 41.842 | 1 | 1 | 1810 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2326515.6 | 181289.5785 | 3190.7391 | 23307.6816 | 157981.8969 | 44626.5591 | 0.068963 | -344594.4601 | 344594.4601
C | Xist Rating 7319 | -46.1 | 1063.3 | 150.297 | 35.6 | 2246.49 | 8258.83 | 18563.3 | 0.69 | 2.55 | 20.997 | 39.735 | 1 | 1 | 1820 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2388692.817 | 183168.8288 | 3226.0933 | 23436.4533 | 159732.3755 | 42446.6725 | 0.069344 | -327761.9537 | 327761.9537
C | Xist Rating 7320 | -46.09 | 1058.14 | 150.298 | 35.6 | 2261.3 | 8446.44 | 18631.1 | 0.69 | 2.56 | 21.012 | 40.061 | 1 | 1 | 1830 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2392771.982 | 185057.7236 | 3261.6423 | 23565.225 | 161492.4985 | 42792.5662 | 0.069725 | -330432.8528 | 330432.8528
C | Xist Rating 7321 | -45.62 | 1064.68 | 150.298 | 35.6 | 2266.54 | 8540.9 | 18545.2 | 0.68 | 2.55 | 21.04 | 39.679 | 1 | 1 | 1840 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2413139.8072 | 186956.2629 | 3297.386 | 23693.9967 | 163262.2661 | 42386.5988 | 0.070106 | -327298.0804 | 327298.0804
C | Xist Rating 7322 | -45.14 | 1075.44 | 150.298 | 35.6 | 2264.25 | 8541.73 | 18409.3 | 0.67 | 2.52 | 21.027 | 39.085 | 1 | 1 | 1850 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2435065.02 | 188864.4467 | 3333.3246 | 23822.7685 | 165041.6782 | 41757.9741 | 0.070487 | -322444.0068 | 322444.0068
C | Xist Rating 7323 | -44.62 | 1087.52 | 150.298 | 35.6 | 2260.6 | 8527.3 | 18259 | 0.66 | 2.5 | 21.013 | 38.431 | 1 | 1 | 1860 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2458447.712 | 190782.2751 | 3369.4579 | 23951.5402 | 166830.7349 | 41066.8096 | 0.070868 | -317107.0184 | 317107.0184
C | Xist Rating 7324 | -43.27 | 1117.36 | 150.298 | 35.6 | 2254.45 | 8536.82 | 17879.5 | 0.66 | 2.43 | 21.063 | 36.742 | 1 | 1 | 1870 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2519032.252 | 192709.7479 | 3405.7861 | 24080.3119 | 168629.436 | 39321.7685 | 0.071249 | -303632.2731 | 303632.2731
C | Xist Rating 7325 | -42.72 | 1129.42 | 150.298 | 35.6 | 2252.25 | 8542.36 | 17738.7 | 0.65 | 2.41 | 21.056 | 36.154 | 1 | 1 | 1880 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2543736.195 | 194646.8653 | 3442.309 | 24209.0836 | 170437.7816 | 38699.2294 | 0.07163 | -298825.1918 | 298825.1918
C | Xist Rating 7326 | -42.25 | 1137.42 | 150.298 | 35.6 | 2254.84 | 8604.82 | 17646.4 | 0.64 | 2.39 | 21.074 | 35.774 | 1 | 1 | 1890 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2564700.1128 | 196593.6271 | 3479.0267 | 24337.8554 | 172255.7718 | 38293.8725 | 0.072011 | -295695.1332 | 295695.1332
C | Xist Rating 7327 | -41.92 | 1145.87 | 150.298 | 35.6 | 2251.41 | 8579.92 | 17555.2 | 0.63 | 2.38 | 21.064 | 35.414 | 1 | 1 | 1900 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2579823.1767 | 198550.0335 | 3515.9392 | 24466.6271 | 174083.4064 | 37907.5742 | 0.072392 | -292712.2395 | 292712.2395
C | Xist Rating 7328 | -41.5 | 1154.04 | 150.298 | 35.6 | 2252.08 | 8614.77 | 17465 | 0.62 | 2.36 | 21.067 | 35.052 | 1 | 1 | 1910 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2598990.4032 | 200516.0844 | 3553.0464 | 24595.3988 | 175920.6856 | 37519.7114 | 0.072773 | -289717.266 | 289717.266
C | Xist Rating 7329 | -39.91 | 1190.28 | 150.298 | 35.6 | 2243.19 | 8603.05 | 17050.3 | 0.62 | 2.29 | 21.115 | 33.315 | 1 | 1 | 1920 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2670024.1932 | 202491.7798 | 3590.3485 | 24724.1705 | 177767.6093 | 35724.2557 | 0.073154 | -275853.2328 | 275853.2328
C | Xist Rating 7330 | -39.42 | 1202.42 | 150.298 | 35.6 | 2238.92 | 8577.53 | 16923.9 | 0.61 | 2.27 | 21.109 | 32.821 | 1 | 1 | 1930 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2692122.1864 | 204477.1197 | 3627.8454 | 24852.9422 | 179624.1774 | 35198.522 | 0.073535 | -271793.657 | 271793.657
C | Xist Rating 7331 | -39.05 | 1206.37 | 150.298 | 35.7 | 2245.62 | 8689.36 | 16882.2 | 0.6 | 2.26 | 21.14 | 32.664 | 1 | 1 | 1940 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2709048.5994 | 206472.1041 | 3665.537 | 24981.714 | 181490.3901 | 35024.5107 | 0.073916 | -270449.9878 | 270449.9878
C | Xist Rating 7332 | -38.67 | 1217.71 | 150.298 | 35.7 | 2238.63 | 8618.56 | 16772.5 | 0.59 | 2.24 | 21.125 | 32.254 | 1 | 1 | 1950 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2726002.1373 | 208476.733 | 3703.4235 | 25110.4857 | 183366.2473 | 34585.1603 | 0.074297 | -267057.4404 | 267057.4404
C | Xist Rating 7333 | -38.09 | 1231.03 | 150.298 | 35.7 | 2235.99 | 8620.83 | 16637.2 | 0.58 | 2.22 | 21.142 | 31.732 | 1 | 1 | 1960 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2752570.7697 | 210491.0065 | 3741.5047 | 25239.2574 | 185251.7491 | 34030.9576 | 0.074678 | -262778.0338 | 262778.0338
C | Xist Rating 7334 | -36.67 | 1263.65 | 150.298 | 35.7 | 2228.87 | 8619.87 | 16303.3 | 0.58 | 2.16 | 21.209 | 30.423 | 1 | 1 | 1970 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2816511.5755 | 212514.9244 | 3779.7807 | 25368.0291 | 187146.8953 | 32680.4912 | 0.075059 | -252350.0906 | 252350.0906
C | Xist Rating 7335 | -36.2 | 1273.1 | 150.298 | 35.7 | 2229.2 | 8653.65 | 16214.3 | 0.57 | 2.15 | 21.236 | 30.098 | 1 | 1 | 1980 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2837994.52 | 214548.4869 | 3818.2515 | 25496.8008 | 189051.686 | 32331.0355 | 0.07544 | -249651.6864 | 249651.6864
C | Xist Rating 7336 | -35.73 | 1285.43 | 150.298 | 35.7 | 2224.61 | 8621.74 | 16101.3 | 0.56 | 2.13 | 21.243 | 29.69 | 1 | 1 | 1990 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2859580.4323 | 216591.6938 | 3856.9171 | 25625.5726 | 190966.1213 | 31894.1609 | 0.075821 | -246278.2565 | 246278.2565
C | Xist Rating 7337 | -35.26 | 1295.02 | 150.298 | 35.7 | 2224.83 | 8653.84 | 16015 | 0.55 | 2.12 | 21.25 | 29.382 | 1 | 1 | 2000 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2881199.3466 | 218644.5453 | 3895.7775 | 25754.3443 | 192890.201 | 31560.9367 | 0.076202 | -243705.1876 | 243705.1876
C | Xist Rating 7338 | -34.9 | 1302.02 | 150.298 | 35.7 | 2225.57 | 8685.82 | 15953.7 | 0.55 | 2.11 | 21.254 | 29.171 | 1 | 1 | 2010 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2897736.6514 | 220707.0413 | 3934.8326 | 25883.116 | 194823.9253 | 31347.2507 | 0.076583 | -242055.1604 | 242055.1604
C | Xist Rating 7339 | -33.37 | 1338.71 | 150.298 | 35.7 | 2215.77 | 8653.99 | 15614.9 | 0.55 | 2.05 | 21.292 | 27.918 | 1 | 1 | 2020 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2966273.4567 | 222779.1818 | 3974.0826 | 26011.8877 | 196767.2941 | 30053.1444 | 0.076964 | -232062.415 | 232062.415
C | Xist Rating 7340 | -32.76 | 1351.98 | 150.298 | 35.7 | 2214.73 | 8679.21 | 15499.8 | 0.54 | 2.03 | 21.297 | 27.514 | 1 | 1 | 2030 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 2994270.6654 | 224860.9668 | 4013.5273 | 26140.6595 | 198720.3073 | 29619.7115 | 0.077345 | -228715.5611 | 228715.5611
C | Xist Rating 7341 | -32.43 | 1360.63 | 150.298 | 35.7 | 2211.91 | 8660.51 | 15431.7 | 0.53 | 2.02 | 21.29 | 27.293 | 1 | 1 | 2040 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3009591.1033 | 226952.3963 | 4053.1669 | 26269.4312 | 200682.9651 | 29375.5447 | 0.077726 | -226830.1693 | 226830.1693
C | Xist Rating 7342 | -31.93 | 1368.46 | 150.298 | 35.7 | 2215.78 | 8745.17 | 15364.3 | 0.53 | 2.01 | 21.315 | 27.06 | 1 | 1 | 2050 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3032206.2988 | 229053.4703 | 4093.0012 | 26398.2029 | 202655.2674 | 29139.85 | 0.078107 | -225010.1973 | 225010.1973
C | Xist Rating 7343 | -31.44 | 1381.19 | 150.298 | 35.7 | 2211.9 | 8722.27 | 15264.1 | 0.52 | 1.99 | 21.294 | 26.731 | 1 | 1 | 2060 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3055054.161 | 231164.1889 | 4133.0303 | 26526.9746 | 204637.2143 | 28782.5575 | 0.078488 | -222251.2793 | 222251.2793
C | Xist Rating 7344 | -29.84 | 1420.56 | 150.298 | 35.7 | 2201.39 | 8684.1 | 14936 | 0.52 | 1.94 | 21.331 | 25.589 | 1 | 1 | 2070 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3127206.5784 | 233284.5519 | 4173.2542 | 26655.7463 | 206628.8056 | 27603.3409 | 0.078869 | -213145.6813 | 213145.6813
C | Xist Rating 7345 | -29.42 | 1429.01 | 150.298 | 35.7 | 2201.9 | 8716.68 | 14873.4 | 0.51 | 1.93 | 21.331 | 25.392 | 1 | 1 | 2080 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3146537.119 | 235414.5595 | 4213.6729 | 26784.5181 | 208630.0414 | 27383.8407 | 0.07925 | -211450.7589 | 211450.7589
C | Xist Rating 7346 | -28.95 | 1439.98 | 150.298 | 35.7 | 2200.3 | 8724.39 | 14790.7 | 0.5 | 1.91 | 21.329 | 25.127 | 1 | 1 | 2090 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3168387.994 | 237554.2116 | 4254.2864 | 26913.2898 | 210640.9218 | 27093.4377 | 0.079631 | -209208.3439 | 209208.3439
C | Xist Rating 7347 | -28.48 | 1450.95 | 150.298 | 35.7 | 2198.67 | 8731.57 | 14709.1 | 0.5 | 1.9 | 21.327 | 24.867 | 1 | 1 | 2100 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3190160.2365 | 239703.5081 | 4295.0947 | 27042.0615 | 212661.4466 | 26828.1143 | 0.080012 | -207159.587 | 207159.587
C | Xist Rating 7348 | -28.07 | 1460.63 | 150.298 | 35.7 | 2197.08 | 8735.12 | 14638.7 | 0.49 | 1.89 | 21.332 | 24.646 | 1 | 1 | 2110 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3209120.9604 | 241862.4492 | 4336.0977 | 27170.8332 | 214691.616 | 26583.4466 | 0.080393 | -205270.3284 | 205270.3284
C | Xist Rating 7349 | -26.59 | 1497.76 | 150.298 | 35.7 | 2187.19 | 8695.22 | 14359 | 0.49 | 1.84 | 21.366 | 23.728 | 1 | 1 | 2120 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3275885.6944 | 244031.0348 | 4377.2956 | 27299.6049 | 216731.4299 | 25636.3736 | 0.080774 | -197957.2817 | 197957.2817
C | Xist Rating 7350 | -26.04 | 1511.37 | 150.298 | 35.7 | 2184.48 | 8692.67 | 14263.6 | 0.48 | 1.83 | 21.363 | 23.434 | 1 | 1 | 2130 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3301557.5376 | 246209.2649 | 4418.6882 | 27428.3767 | 218780.8882 | 25315.2109 | 0.081155 | -195477.3486 | 195477.3486
C | Xist Rating 7351 | -25.56 | 1525 | 150.298 | 35.7 | 2179.65 | 8656.63 | 14169.7 | 0.48 | 1.81 | 21.357 | 23.146 | 1 | 1 | 2140 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3323966.25 | 248397.1395 | 4460.2756 | 27557.1484 | 220839.9911 | 25020.4436 | 0.081536 | -193201.233 | 193201.233
C | Xist Rating 7352 | -25.23 | 1532.16 | 150.298 | 35.7 | 2179.59 | 8675.79 | 14123.3 | 0.47 | 1.8 | 21.36 | 23.013 | 1 | 1 | 2150 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3339480.6144 | 250594.6587 | 4502.0578 | 27685.9201 | 222908.7386 | 24866.4719 | 0.081917 | -192012.3047 | 192012.3047
C | Xist Rating 7353 | -24.83 | 1541.78 | 150.298 | 35.7 | 2178.74 | 8690.34 | 14058.8 | 0.46 | 1.79 | 21.364 | 22.821 | 1 | 1 | 2160 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3359137.7572 | 252801.8223 | 4544.0348 | 27814.6918 | 224987.1305 | 24651.0774 | 0.082298 | -190349.0853 | 190349.0853
C | Xist Rating 7354 | -23.3 | 1581.8 | 150.298 | 35.7 | 2166.54 | 8618.16 | 13786 | 0.46 | 1.75 | 21.402 | 21.975 | 1 | 1 | 2170 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3427032.972 | 255018.6304 | 4586.2066 | 27943.4636 | 227075.1669 | 23778.6131 | 0.082679 | -183612.1474 | 183612.1474
C | Xist Rating 7355 | -22.71 | 1595.18 | 150.298 | 35.7 | 2165.59 | 8642.45 | 13699 | 0.46 | 1.74 | 21.407 | 21.718 | 1 | 1 | 2180 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3454505.8562 | 257245.0831 | 4628.5732 | 28072.2353 | 229172.8478 | 23516.3567 | 0.08306 | -181587.0731 | 181587.0731
C | Xist Rating 7356 | -22.31 | 1605.04 | 150.298 | 35.7 | 2164.01 | 8644.95 | 13638.9 | 0.45 | 1.73 | 21.407 | 21.549 | 1 | 1 | 2190 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3473322.6104 | 259481.1803 | 4671.1346 | 28201.007 | 231280.1733 | 23324.2501 | 0.083441 | -180103.6765 | 180103.6765
C | Xist Rating 7357 | -21.96 | 1615.3 | 150.298 | 35.7 | 2160.24 | 8612.35 | 13579.3 | 0.44 | 1.72 | 21.4 | 21.388 | 1 | 1 | 2200 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3489435.672 | 261726.922 | 4713.8907 | 28329.7787 | 233397.1432 | 23139.9558 | 0.083822 | -178680.6048 | 178680.6048
C | Xist Rating 7358 | -21.35 | 1628.94 | 150.298 | 35.7 | 2159.43 | 8638.74 | 13495.4 | 0.44 | 1.7 | 21.397 | 21.146 | 1 | 1 | 2210 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3517581.9042 | 263982.3081 | 4756.8417 | 28458.5504 | 235523.7577 | 22892.7291 | 0.084203 | -176771.5858 | 176771.5858
C | Xist Rating 7359 | -19.78 | 1668.83 | 150.298 | 35.7 | 2150.46 | 8614.25 | 13246.2 | 0.44 | 1.66 | 21.434 | 20.412 | 1 | 1 | 2220 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3588752.1618 | 266247.3388 | 4799.9874 | 28587.3222 | 237660.0167 | 22136.3114 | 0.084584 | -170930.7288 | 170930.7288
C | Xist Rating 7360 | -19.3 | 1679.77 | 150.298 | 35.7 | 2149.96 | 8637.4 | 13182.5 | 0.44 | 1.65 | 21.437 | 20.237 | 1 | 1 | 2230 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3611438.3092 | 268522.014 | 4843.3279 | 28716.0939 | 239805.9202 | 21958.9335 | 0.084965 | -169561.0638 | 169561.0638
C | Xist Rating 7361 | -18.83 | 1692.46 | 150.298 | 35.7 | 2147.02 | 8625.07 | 13111.7 | 0.43 | 1.64 | 21.43 | 20.047 | 1 | 1 | 2240 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3633745.4692 | 270806.3338 | 4886.8633 | 28844.8656 | 241961.4682 | 21744.0203 | 0.085346 | -167901.5607 | 167901.5607
C | Xist Rating 7362 | -18.3 | 1706.41 | 150.298 | 35.7 | 2143.88 | 8613.29 | 13034 | 0.42 | 1.63 | 21.426 | 19.838 | 1 | 1 | 2250 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3658338.2708 | 273100.298 | 4930.5934 | 28973.6373 | 244126.6607 | 21509.3219 | 0.085727 | -166089.282 | 166089.282
C | Xist Rating 7363 | -17.96 | 1713.53 | 150.298 | 35.7 | 2144.48 | 8642.45 | 12995.5 | 0.42 | 1.62 | 21.431 | 19.739 | 1 | 1 | 2260 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3674630.8144 | 275403.9067 | 4974.5182 | 29102.409 | 246301.4977 | 21410.757 | 0.086108 | -165328.1902 | 165328.1902
C | Xist Rating 7364 | -16.36 | 1756.4 | 150.298 | 35.7 | 2133.39 | 8588.08 | 12751.8 | 0.42 | 1.59 | 21.462 | 19.059 | 1 | 1 | 2270 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3747086.196 | 277717.16 | 5018.6379 | 29231.1808 | 248485.9792 | 20709.9376 | 0.086489 | -159916.6483 | 159916.6483
C | Xist Rating 7365 | -15.87 | 1769.04 | 150.298 | 35.7 | 2131.07 | 8584.98 | 12686.1 | 0.41 | 1.58 | 21.458 | 18.89 | 1 | 1 | 2280 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3769948.0728 | 280040.0577 | 5062.9524 | 29359.9525 | 250680.1052 | 20516.37 | 0.08687 | -158421.9711 | 158421.9711
C | Xist Rating 7366 | -15.25 | 1784.03 | 150.298 | 35.7 | 2129.21 | 8596.71 | 12606.8 | 0.41 | 1.56 | 21.459 | 18.682 | 1 | 1 | 2290 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3798574.5163 | 282372.6 | 5107.4617 | 29488.7242 | 252883.8758 | 20304.348 | 0.087251 | -156784.7933 | 156784.7933
C | Xist Rating 7367 | -14.83 | 1794.05 | 150.298 | 35.7 | 2128.46 | 8611.21 | 12557.1 | 0.4 | 1.56 | 21.461 | 18.558 | 1 | 1 | 2300 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3818563.663 | 284714.7868 | 5152.1657 | 29617.4959 | 255097.2908 | 20157.4769 | 0.087632 | -155650.6937 | 155650.6937
| Xist Rating 7368 | -14.44 | 1804.34 | 150.298 | 35.7 | 2126.55 | 8606.85 | 12507.6 | 0.4 | 1.55 | 21.459 | 18.439 | 1 | 1 | 2310 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3837019.227 | 287066.6181 | 5197.0645 | 29746.2677 | 257320.3504 | 20037.6607 | 0.088013 | -154725.5046 | 154725.5046
| Xist Rating 7369 | -12.75 | 1848.35 | 150.298 | 35.7 | 2117.4 | 8584.34 | 12277.1 | 0.4 | 1.51 | 21.489 | 17.825 | 1 | 1 | 2320 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 28 | E | Rod | 3913696.29 | 289428.0939 | 5242.1582 | 29875.0394 | 259553.0545 | 19405.1182 | 0.088394 | -149841.1787 | 149841.1787
| Xist Rating 7370 | -12.27 | 1861.02 | 150.298 | 35.7 | 2115.34 | 8584.45 | 12216.8 | 0.39 | 1.5 | 21.489 | 17.677 | 1 | 1 | 2330 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 3936690.0468 | 291799.2142 | 5287.4466 | 30003.8111 | 261795.4031 | 19232.8299 | 0.088775 | -148510.8146 | 148510.8146
| Xist Rating 7371 | -11.78 | 1873.66 | 150.298 | 35.7 | 2113.14 | 8582.3 | 12157.1 | 0.39 | 1.49 | 21.486 | 17.532 | 1 | 1 | 2340 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 3959305.8924 | 294179.979 | 5332.9298 | 30132.5828 | 264047.3962 | 19085.8816 | 0.089156 | -147376.1183 | 147376.1183
| Xist Rating 7372 | -11.38 | 1885.1 | 150.298 | 35.7 | 2110.53 | 8569.43 | 12104.7 | 0.38 | 1.49 | 21.481 | 17.408 | 1 | 1 | 2350 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 3978560.103 | 296570.3883 | 5378.6078 | 30261.3545 | 266309.0338 | 18938.0308 | 0.089537 | -146234.454 | 146234.454
| Xist Rating 7373 | -10.88 | 1899.1 | 150.298 | 35.7 | 2107.32 | 8554.01 | 12039.8 | 0.38 | 1.48 | 21.477 | 17.251 | 1 | 1 | 2360 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4002011.412 | 298970.4422 | 5424.4805 | 30390.1263 | 268580.3159 | 18778.4847 | 0.089918 | -145002.4812 | 145002.4812
| Xist Rating 7374 | -9.35 | 1939.41 | 150.298 | 35.7 | 2099.49 | 8538.49 | 11846.8 | 0.38 | 1.45 | 21.505 | 16.763 | 1 | 1 | 2370 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4071771.9009 | 301380.1405 | 5470.5481 | 30518.898 | 270861.2425 | 18276.4861 | 0.090299 | -141126.1808 | 141126.1808
| Xist Rating 7375 | -8.91 | 1952.3 | 150.298 | 35.7 | 2096.38 | 8520.38 | 11791.2 | 0.38 | 1.44 | 21.498 | 16.635 | 1 | 1 | 2380 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4092762.674 | 303799.4834 | 5516.8105 | 30647.6697 | 273151.8137 | 18146.9375 | 0.09068 | -140125.8412 | 140125.8412
| Xist Rating 7376 | -8.37 | 1965.85 | 150.298 | 35.7 | 2094.75 | 8530.29 | 11730 | 0.37 | 1.43 | 21.496 | 16.489 | 1 | 1 | 2390 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4117964.2875 | 306228.4707 | 5563.2676 | 30776.4414 | 275452.0293 | 17975.8683 | 0.091061 | -138804.8901 | 138804.8901
C | Xist Rating 7379 | 2.06 | 2255.52 | 150.298 | 35.7 | 2034.19 | 8309.09 | 10538.3 | 0.4 | 1.25 | 21.529 | 13.719 | 1 | 1 | 2420 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4588156.2288 | 313573.2999 | 5703.8078 | 31162.7566 | 282410.5433 | 15181.3087 | 0.092204 | -117226.042 | 117226.042
C | Xist Rating 7380 | 2.16 | 2256.87 | 150.298 | 35.7 | 2036.03 | 8340.01 | 10538 | 0.39 | 1.25 | 21.525 | 13.729 | 1 | 1 | 2430 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4595055.0261 | 316040.8653 | 5751.0441 | 31291.5283 | 284749.337 | 15171.9337 | 0.092585 | -117153.6504 | 117153.6504
C | Xist Rating 7381 | 2.17 | 2258.24 | 150.298 | 35.7 | 2035.62 | 8333.1 | 10538 | 0.38 | 1.25 | 21.517 | 13.74 | 1 | 1 | 2440 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4596918.5088 | 318518.0752 | 5798.4752 | 31420.3 | 287097.7752 | 15163.2453 | 0.092966 | -117086.5605 | 117086.5605
C | Xist Rating 7382 | 2.18 | 2259.57 | 150.298 | 35.7 | 2035.19 | 8325.94 | 10538 | 0.38 | 1.25 | 21.516 | 13.751 | 1 | 1 | 2450 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4598654.2683 | 321004.9297 | 5846.1011 | 31549.0718 | 289455.8579 | 15178.2921 | 0.093347 | -117202.7481 | 117202.7481
C | Xist Rating 7383 | 2.21 | 2261.04 | 150.298 | 35.7 | 2035.15 | 8325.33 | 10538 | 0.37 | 1.25 | 21.506 | 13.762 | 1 | 1 | 2460 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4601555.556 | 323501.4286 | 5893.9217 | 31677.8435 | 291823.5851 | 15169.2471 | 0.093728 | -117132.9049 | 117132.9049
C | Xist Rating 7384 | 2.23 | 2262.4 | 150.298 | 35.7 | 2034.76 | 8318.81 | 10538 | 0.36 | 1.25 | 21.542 | 13.773 | 1 | 1 | 2470 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4603441.024 | 326007.572 | 5941.9372 | 31806.6152 | 294200.9568 | 15161.8615 | 0.094109 | -117075.8752 | 117075.8752
C | Xist Rating 7385 | 2.24 | 2263.74 | 150.298 | 35.7 | 2034.25 | 8310.21 | 10538 | 0.36 | 1.25 | 21.535 | 13.783 | 1 | 1 | 2480 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4605013.095 | 328523.36 | 5990.1474 | 31935.3869 | 296587.9731 | 15175.4425 | 0.09449 | -117180.7445 | 117180.7445
C | Xist Rating 7386 | 2.24 | 2265.14 | 150.298 | 35.7 | 2033.63 | 8299.85 | 10538 | 0.35 | 1.25 | 21.53 | 13.794 | 1 | 1 | 2490 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4606456.6582 | 331048.7925 | 6038.5525 | 32064.1586 | 298984.6338 | 15166.1098 | 0.094871 | -117108.6798 | 117108.6798
C | Xist Rating 7387 | 2.27 | 2266.13 | 150.298 | 35.7 | 2033.88 | 8304.12 | 10538 | 0.35 | 1.25 | 21.527 | 13.803 | 1 | 1 | 2500 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4609036.4844 | 333583.8695 | 6087.1523 | 32192.9304 | 301390.9391 | 15178.7164 | 0.095252 | -117206.0245 | 117206.0245
C | Xist Rating 7388 | 2.25 | 2267.98 | 150.298 | 35.7 | 2032.4 | 8279.51 | 10538 | 0.34 | 1.25 | 21.52 | 13.816 | 1 | 1 | 2510 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4609442.552 | 336128.5909 | 6135.9469 | 32321.7021 | 303806.8889 | 15171.1064 | 0.095633 | -117147.2621 | 117147.2621
C | Xist Rating 7389 | 2.26 | 2269.43 | 150.298 | 35.7 | 2031.81 | 8269.65 | 10538 | 0.34 | 1.25 | 21.557 | 13.826 | 1 | 1 | 2520 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4611050.5683 | 338682.9569 | 6184.9363 | 32450.4738 | 306232.4831 | 15186.1921 | 0.096014 | -117263.7501 | 117263.7501
C | Xist Rating 7390 | 2.27 | 2270.77 | 150.298 | 35.7 | 2031.32 | 8261.53 | 10537.9 | 0.33 | 1.25 | 21.551 | 13.837 | 1 | 1 | 2530 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4612660.5164 | 341246.9675 | 6234.1205 | 32579.2455 | 308667.7219 | 15176.2294 | 0.096395 | -117186.8207 | 117186.8207
C | Xist Rating 7391 | 2.29 | 2271.92 | 150.298 | 35.7 | 2031.21 | 8259.86 | 10537.9 | 0.33 | 1.25 | 21.547 | 13.846 | 1 | 1 | 2540 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4614746.6232 | 343820.6225 | 6283.4995 | 32708.0172 | 311112.6052 | 15188.6135 | 0.096776 | -117282.4471 | 117282.4471
C | Xist Rating 7392 | 2.28 | 2273.47 | 150.298 | 35.6 | 2030.34 | 8245.47 | 10537.9 | 0.32 | 1.25 | 21.543 | 13.857 | 1 | 1 | 2550 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4615917.0798 | 346403.922 | 6333.0732 | 32836.789 | 313567.133 | 15178.4491 | 0.097157 | -117203.9603 | 117203.9603
C | Xist Rating 7393 | 2.33 | 2274.91 | 150.298 | 35.6 | 2030.52 | 8248.48 | 10537.8 | 0.32 | 1.25 | 21.535 | 13.868 | 1 | 1 | 2560 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4619250.2532 | 348996.866 | 6382.8418 | 32965.5607 | 316031.3053 | 15192.6689 | 0.097538 | -117313.762 | 117313.762
C | Xist Rating 7394 | 2.34 | 2276.3 | 150.298 | 35.6 | 2030.15 | 8242.37 | 10537.8 | 0.31 | 1.25 | 21.531 | 13.878 | 1 | 1 | 2570 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4621230.445 | 351599.4546 | 6432.8051 | 33094.3324 | 318505.1222 | 15181.1918 | 0.097919 | -117225.1389 | 117225.1389
C | Xist Rating 7395 | 2.37 | 2277.67 | 150.299 | 35.6 | 2030.23 | 8243.76 | 10537.8 | 0.31 | 1.25 | 21.58 | 13.888 | 1 | 1 | 2580 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4624193.9641 | 354211.6876 | 6482.9633 | 33223.1041 | 320988.5835 | 15196.3253 | 0.0983 | -117341.9961 | 117341.9961
C | Xist Rating 7396 | 2.38 | 2279.03 | 150.299 | 35.6 | 2029.89 | 8238.06 | 10537.8 | 0.3 | 1.25 | 21.58 | 13.898 | 1 | 1 | 2590 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4626180.2067 | 356833.5652 | 6533.3162 | 33351.8759 | 323481.6894 | 15184.6555 | 0.098681 | -117251.8849 | 117251.8849
C | Xist Rating 7397 | 2.4 | 2280.21 | 150.299 | 35.6 | 2029.95 | 8239.16 | 10537.7 | 0.3 | 1.25 | 21.58 | 13.908 | 1 | 1 | 2600 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4628712.2895 | 359465.0873 | 6583.8639 | 33480.6476 | 325984.4397 | 15197.9424 | 0.099062 | -117354.4831 | 117354.4831
C | Xist Rating 7398 | 2.42 | 2281.89 | 150.299 | 35.6 | 2029.44 | 8230.76 | 10537.7 | 0.3 | 1.25 | 21.572 | 13.919 | 1 | 1 | 2610 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4630958.8416 | 362106.2539 | 6634.6064 | 33609.4193 | 328496.8346 | 15211.9871 | 0.099443 | -117462.9321 | 117462.9321
C | Xist Rating 7399 | 2.42 | 2283.29 | 150.299 | 35.6 | 2028.92 | 8222.22 | 10537.7 | 0.29 | 1.25 | 21.573 | 13.929 | 1 | 1 | 2620 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4632612.7468 | 364757.065 | 6685.5437 | 33738.191 | 331018.874 | 15199.9727 | 0.099824 | -117370.1603 | 117370.1603
C | Xist Rating 7400 | 2.43 | 2284.72 | 150.299 | 35.6 | 2028.31 | 8212.28 | 10537.7 | 0.29 | 1.25 | 21.61 | 13.939 | 1 | 1 | 2630 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4634120.4232 | 367417.5206 | 6736.6758 | 33866.9627 | 333550.5579 | 15214.427 | 0.10021 | -117481.7721 | 117481.7721
C | Xist Rating 7401 | 2.49 | 2285.96 | 150.299 | 35.6 | 2028.82 | 8220.56 | 10537.7 | 0.28 | 1.25 | 21.618 | 13.949 | 1 | 1 | 2640 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4637801.3672 | 370087.6207 | 6788.0027 | 33995.7345 | 336091.8863 | 15202.3135 | 0.10059 | -117388.2352 | 117388.2352
C | Xist Rating 7402 | 2.5 | 2287.47 | 150.299 | 35.6 | 2028.27 | 8211.64 | 10537.7 | 0.28 | 1.25 | 21.613 | 13.96 | 1 | 1 | 2650 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4639606.7769 | 372767.3653 | 6839.5243 | 34124.5062 | 338642.8592 | 15216.2839 | 0.10097 | -117496.1112 | 117496.1112
C | Xist Rating 7403 | 2.54 | 2288.81 | 150.299 | 35.6 | 2028.41 | 8213.9 | 10537.6 | 0.28 | 1.25 | 21.614 | 13.969 | 1 | 1 | 2660 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4642645.0921 | 375456.7545 | 6891.2408 | 34253.2779 | 341203.4766 | 15228.3764 | 0.10135 | -117589.4862 | 117589.4862
C | Xist Rating 7404 | 2.6 | 2290.19 | 150.299 | 35.6 | 2028.81 | 8220.46 | 10537.6 | 0.27 | 1.25 | 21.619 | 13.979 | 1 | 1 | 2670 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4646360.3739 | 378155.7881 | 6943.152 | 34382.0496 | 343773.7385 | 15215.7677 | 0.10173 | -117492.125 | 117492.125
C | Xist Rating 7405 | 2.65 | 2291.61 | 150.299 | 35.6 | 2029.07 | 8224.7 | 10537.7 | 0.27 | 1.25 | 21.661 | 13.989 | 1 | 1 | 2680 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4649837.1027 | 380864.4663 | 6995.258 | 34510.8213 | 346353.6449 | 15230.1314 | 0.10211 | -117603.038 | 117603.038
C | Xist Rating 7406 | 2.68 | 2292.99 | 150.299 | 35.6 | 2029.06 | 8224.46 | 10537.7 | 0.26 | 1.25 | 21.659 | 13.999 | 1 | 1 | 2690 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4652614.2894 | 383582.789 | 7047.5588 | 34639.5931 | 348943.1959 | 15216.9568 | 0.10249 | -117501.307 | 117501.307
C | Xist Rating 7407 | 2.78 | 2294.19 | 150.299 | 35.6 | 2030.52 | 8248.65 | 10537.7 | 0.26 | 1.25 | 21.662 | 14.008 | 1 | 1 | 2700 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4658398.6788 | 386310.7561 | 7100.0544 | 34768.3648 | 351542.3914 | 15228.9219 | 0.10287 | -117593.6984 | 117593.6984
C | Xist Rating 7408 | 2.83 | 2295.84 | 150.299 | 35.6 | 2030.88 | 8254.6 | 10537.5 | 0.26 | 1.25 | 21.66 | 14.019 | 1 | 1 | 2710 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4662575.5392 | 389048.3678 | 7152.7448 | 34897.1365 | 354151.2313 | 15242.8068 | 0.10325 | -117700.9139 | 117700.9139
C | Xist Rating 7409 | 2.82 | 2297.19 | 150.299 | 35.6 | 2030 | 8240.15 | 10537.5 | 0.25 | 1.25 | 21.657 | 14.029 | 1 | 1 | 2720 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4663295.7 | 391795.624 | 7205.63 | 35025.9082 | 356769.7158 | 15229.2162 | 0.10363 | -117595.9705 | 117595.9705
C | Xist Rating 7410 | 2.85 | 2298.51 | 150.299 | 35.6 | 2030.03 | 8240.52 | 10537.5 | 0.25 | 1.25 | 21.693 | 14.039 | 1 | 1 | 2730 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4666044.2553 | 394552.5247 | 7258.71 | 35154.68 | 359397.8448 | 15243.1294 | 0.10402 | -117703.4049 | 117703.4049
C | Xist Rating 7411 | 2.85 | 2299.79 | 150.299 | 35.6 | 2029.38 | 8229.88 | 10537.6 | 0.25 | 1.25 | 21.687 | 14.048 | 1 | 1 | 2740 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4667147.8302 | 397319.07 | 7311.9847 | 35283.4517 | 362035.6183 | 15254.7226 | 0.1044 | -117792.9246 | 117792.9246
C | Xist Rating 7412 | 2.84 | 2301.34 | 150.299 | 35.6 | 2028.37 | 8213.32 | 10537.6 | 0.25 | 1.25 | 21.686 | 14.058 | 1 | 1 | 2750 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4667969.0158 | 400095.2597 | 7365.4543 | 35412.2234 | 364683.0363 | 15267.5071 | 0.10478 | -117891.6427 | 117891.6427
C | Xist Rating 7413 | 2.84 | 2302.77 | 150.299 | 35.6 | 2027.56 | 8199.9 | 10537.6 | 0.24 | 1.25 | 21.686 | 14.068 | 1 | 1 | 2760 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4669004.3412 | 402881.0939 | 7419.1186 | 35540.9951 | 367340.0988 | 15253.4932 | 0.10516 | -117783.4311 | 117783.4311
C | Xist Rating 7414 | 2.83 | 2304 | 150.299 | 35.6 | 2026.81 | 8187.81 | 10537.6 | 0.24 | 1.25 | 21.684 | 14.077 | 1 | 1 | 2770 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4669770.24 | 405676.5727 | 7472.9777 | 35669.7668 | 370006.8058 | 15265.113 | 0.10554 | -117873.1564 | 117873.1564
C | Xist Rating 7415 | 2.83 | 2305.55 | 150.299 | 35.6 | 2025.93 | 8173.43 | 10537.6 | 0.24 | 1.25 | 21.725 | 14.087 | 1 | 1 | 2780 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4670882.9115 | 408481.696 | 7527.0316 | 35798.5386 | 372683.1574 | 15279.0569 | 0.10592 | -117980.8277 | 117980.8277
C | Xist Rating 7416 | 2.81 | 2306.96 | 150.299 | 35.6 | 2025.01 | 8158.49 | 10537.6 | 0.23 | 1.25 | 21.721 | 14.097 | 1 | 1 | 2790 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4671617.0696 | 411296.4637 | 7581.2803 | 35927.3103 | 375369.1534 | 15264.4946 | 0.1063 | -117868.3809 | 117868.3809
C | Xist Rating 7417 | 2.84 | 2307.93 | 150.299 | 35.6 | 2025.23 | 8162.04 | 10537.6 | 0.23 | 1.25 | 21.725 | 14.105 | 1 | 1 | 2800 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4674089.0739 | 414120.876 | 7635.7238 | 36056.082 | 378064.794 | 15275.1574 | 0.10668 | -117950.7164 | 117950.7164
C | Xist Rating 7418 | 2.85 | 2309.68 | 150.299 | 35.6 | 2024.53 | 8150.65 | 10537.6 | 0.23 | 1.25 | 21.732 | 14.116 | 1 | 1 | 2810 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4676016.4504 | 416954.9328 | 7690.3621 | 36184.8537 | 380770.0791 | 15289.0234 | 0.10706 | -118057.7864 | 118057.7864
C | Xist Rating 7419 | 2.81 | 2311.15 | 150.299 | 35.6 | 2023.02 | 8126.19 | 10537.6 | 0.23 | 1.25 | 21.725 | 14.125 | 1 | 1 | 2820 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4675502.673 | 419798.6341 | 7745.1952 | 36313.6255 | 383485.0086 | 15300.4069 | 0.10744 | -118145.6865 | 118145.6865
C | Xist Rating 7420 | 2.86 | 2312.52 | 150.299 | 35.6 | 2023.2 | 8129.2 | 10537.6 | 0.22 | 1.25 | 21.771 | 14.135 | 1 | 1 | 2830 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4678690.464 | 422651.9799 | 7800.223 | 36442.3972 | 386209.5827 | 15286.7565 | 0.10783 | -118040.2813 | 118040.2813
C | Xist Rating 7421 | 2.91 | 2313.84 | 150.299 | 35.6 | 2023.71 | 8137.34 | 10537.7 | 0.22 | 1.25 | 21.779 | 14.144 | 1 | 1 | 2840 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4682541.1464 | 425514.9702 | 7855.4457 | 36571.1689 | 388943.8013 | 15298.4739 | 0.10821 | -118130.7605 | 118130.7605
C | Xist Rating 7422 | 2.88 | 2315.28 | 150.299 | 35.6 | 2022.46 | 8117.18 | 10537.6 | 0.22 | 1.25 | 21.772 | 14.154 | 1 | 1 | 2850 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4682561.1888 | 428387.6051 | 7910.8631 | 36699.9406 | 391687.6644 | 15310.8099 | 0.10859 | -118226.0155 | 118226.0155
C | Xist Rating 7423 | 3.01 | 2316.69 | 150.299 | 35.6 | 2023.72 | 8137.48 | 10537.8 | 0.22 | 1.25 | 21.786 | 14.163 | 1 | 1 | 2860 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4688331.8868 | 431269.8844 | 7966.4753 | 36828.7123 | 394441.1721 | 15322.6983 | 0.10897 | -118317.8143 | 118317.8143
C | Xist Rating 7424 | 3.1 | 2317.88 | 150.299 | 35.6 | 2025.38 | 8164.41 | 10537.8 | 0.21 | 1.25 | 21.799 | 14.172 | 1 | 1 | 2870 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4694587.7944 | 434161.8082 | 8022.2824 | 36957.4841 | 397204.3242 | 15306.5174 | 0.10935 | -118192.8699 | 118192.8699
C | Xist Rating 7425 | 3.26 | 2319.39 | 150.299 | 35.6 | 2027.74 | 8202.73 | 10537.9 | 0.21 | 1.25 | 21.871 | 14.182 | 1 | 1 | 2880 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4703119.8786 | 437063.3766 | 8078.2842 | 37086.2558 | 399977.1208 | 15320.9063 | 0.10973 | -118303.977 | 118303.977
C | Xist Rating 7426 | 3.24 | 2320.73 | 150.299 | 35.6 | 2027.19 | 8193.73 | 10537.8 | 0.21 | 1.25 | 21.861 | 14.191 | 1 | 1 | 2890 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4704560.6487 | 439974.5895 | 8134.4807 | 37215.0275 | 402759.562 | 15332.0395 | 0.11011 | -118389.9446 | 118389.9446
C | Xist Rating 7427 | 3.8 | 2322.12 | 150.299 | 35.6 | 2037.19 | 8359.53 | 10538.1 | 0.2 | 1.25 | 21.938 | 14.201 | 1 | 1 | 2900 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4730599.6428 | 442895.4469 | 8190.8721 | 37343.7992 | 405551.6476 | 15318.0667 | 0.11049 | -118282.0506 | 118282.0506
C | Xist Rating 7428 | 4.33 | 2323.66 | 150.299 | 35.6 | 2047.22 | 8530.92 | 10538.2 | 0.2 | 1.25 | 22.005 | 14.212 | 1 | 1 | 2910 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4757043.2252 | 445825.9488 | 8247.4583 | 37472.5709 | 408353.3778 | 15333.2048 | 0.11087 | -118398.943 | 118398.943
C | Xist Rating 7429 | 4.74 | 2325.05 | 150.299 | 35.6 | 2054.82 | 8664.41 | 10538.2 | 0.2 | 1.25 | 22.05 | 14.222 | 1 | 1 | 2920 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4777559.241 | 448766.0952 | 8304.2393 | 37601.3427 | 411164.7525 | 15346.7405 | 0.11125 | -118503.4621 | 118503.4621
C | Xist Rating 7430 | 4.53 | 2326.43 | 150.299 | 35.6 | 2049.9 | 8577.69 | 10538.2 | 0.2 | 1.25 | 22.047 | 14.23 | 1 | 1 | 2930 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4768948.857 | 451715.8861 | 8361.215 | 37730.1144 | 413985.7717 | 15356.9464 | 0.11164 | -118582.2698 | 118582.2698
C | Xist Rating 7431 | 5.07 | 2327.8 | 150.299 | 35.6 | 2060.06 | 8758.39 | 10538.2 | 0.19 | 1.25 | 22.114 | 14.241 | 1 | 1 | 2940 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4795407.668 | 454675.3215 | 8418.3855 | 37858.8861 | 416816.4354 | 15342.9695 | 0.11202 | -118474.3437 | 118474.3437
C | Xist Rating 7432 | 5.39 | 2329.21 | 150.299 | 35.6 | 2065.77 | 8862.42 | 10538.2 | 0.19 | 1.25 | 22.147 | 14.25 | 1 | 1 | 2950 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4811612.1417 | 457644.4014 | 8475.7509 | 37987.6578 | 419656.7436 | 15355.0285 | 0.1124 | -118567.4598 | 118567.4598
C | Xist Rating 7433 | 5.82 | 2330.58 | 150.299 | 35.6 | 2073.99 | 9015.85 | 10538 | 0.19 | 1.25 | 22.2 | 14.26 | 1 | 1 | 2960 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4833599.6142 | 460623.1259 | 8533.311 | 38116.4296 | 422506.6963 | 15368.6358 | 0.11278 | -118672.5316 | 118672.5316
C | Xist Rating 7434 | 6.31 | 2331.97 | 150.299 | 35.6 | 2083.17 | 9192.13 | 10538 | 0.18 | 1.25 | 22.232 | 14.27 | 1 | 1 | 2970 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4857889.9449 | 463611.4948 | 8591.0659 | 38245.2013 | 425366.2935 | 15352.1236 | 0.11316 | -118545.0289 | 118545.0289
C | Xist Rating 7435 | 6.32 | 2333.19 | 150.299 | 35.6 | 2082.67 | 9182.37 | 10538 | 0.18 | 1.25 | 22.254 | 14.278 | 1 | 1 | 2980 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4859264.8173 | 466609.5083 | 8649.0156 | 38373.973 | 428235.5353 | 15362.7543 | 0.11354 | -118627.1166 | 118627.1166
C | Xist Rating 7436 | 6.32 | 2334.75 | 150.299 | 35.6 | 2081.93 | 9167.91 | 10538 | 0.18 | 1.25 | 22.249 | 14.288 | 1 | 1 | 2990 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4860786.0675 | 469617.1662 | 8707.16 | 38502.7447 | 431114.4215 | 15374.8142 | 0.11392 | -118720.2401 | 118720.2401
C | Xist Rating 7437 | 6.32 | 2336.18 | 150.299 | 35.6 | 2081.24 | 9154.66 | 10538 | 0.18 | 1.25 | 22.244 | 14.297 | 1 | 1 | 3000 | 152.4 | 2 | 4.6 | 19.05 | 1.3333 | 27 | E | Rod | 4862151.2632 | 472634.4687 | 8765.4993 | 38631.5164 | 434002.9523 | 15385.8348 | 0.1143 | -118805.3382 | 118805.3382
C | Xist Rating 7438 | -86.88 | 239.609 | 150.305 | 35.9 | 2357.2 | 7014.52 | 58745.1 | 2.48 | 10.95 | 24.154 | 578.669 | 1 | 1 | 1000 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 564806.3348 | 62427.9772 | 973.9444 | 13157.1107 | 49270.8666 | 603631.9242 | 0.038101 | -4661085.7132 | 4661085.7132
C | Xist Rating 7439 | -86.77 | 242.082 | 150.305 | 35.9 | 2353.06 | 6985.55 | 58284.1 | 2.46 | 10.85 | 24.235 | 567.79 | 1 | 1 | 1010 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 569633.4709 | 63549.8928 | 993.5206 | 13288.6818 | 50261.211 | 592348.1013 | 0.038482 | -4573955.0244 | 4573955.0244
C | Xist Rating 7440 | -85.79 | 260.875 | 150.305 | 35.9 | 2346.03 | 6981.53 | 54967.2 | 2.47 | 10.07 | 24.287 | 492.047 | 1 | 1 | 1020 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 612020.5763 | 64681.6625 | 1013.2917 | 13420.2529 | 51261.4096 | 513732.7921 | 0.038863 | -3966908.4454 | 3966908.4454
C | Xist Rating 7441 | -85.62 | 265.967 | 150.304 | 35.9 | 2330.09 | 6856.54 | 54177.8 | 2.38 | 9.89 | 23.711 | 475.472 | 1 | 1 | 1030 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 619727.047 | 65823.2863 | 1033.2576 | 13551.824 | 52271.4623 | 496382.3595 | 0.039244 | -3832933.0039 | 3832933.0039
C | Xist Rating 7442 | -85.52 | 268.515 | 150.304 | 35.9 | 2323.96 | 6810.82 | 53793.1 | 2.34 | 9.8 | 23.577 | 467.537 | 1 | 1 | 1040 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 624018.1194 | 66974.7644 | 1053.4182 | 13683.3951 | 53291.3693 | 488108.3387 | 0.039625 | -3769043.2078 | 3769043.2078
C | Xist Rating 7443 | -85.3 | 273.486 | 150.303 | 35.9 | 2317.28 | 6767.56 | 53042.1 | 2.31 | 9.63 | 23.486 | 452.002 | 1 | 1 | 1050 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 633743.6381 | 68136.0966 | 1073.7737 | 13814.9662 | 54321.1304 | 471956.8117 | 0.040006 | -3644325.3977 | 3644325.3977
C | Xist Rating 7444 | -85.17 | 276.015 | 150.303 | 35.9 | 2317.38 | 6775.35 | 52675.2 | 2.27 | 9.54 | 23.451 | 444.629 | 1 | 1 | 1060 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 639631.6407 | 69307.283 | 1094.3239 | 13946.5373 | 55360.7457 | 464275.8697 | 0.040387 | -3585015.2 | 3585015.2
C | Xist Rating 7445 | -84.2 | 296.199 | 150.303 | 35.9 | 2302.05 | 6700.95 | 49855.9 | 2.25 | 8.9 | 23.228 | 389.014 | 1 | 1 | 1070 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 681864.908 | 70488.3235 | 1115.0689 | 14078.1084 | 56410.2151 | 406497.0816 | 0.040768 | -3138862.7133 | 3138862.7133
C | Xist Rating 7446 | -83.96 | 299.995 | 150.302 | 35.9 | 2307.11 | 6754.17 | 49380 | 2.2 | 8.79 | 23.12 | 380.273 | 1 | 1 | 1080 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 692121.4645 | 71679.2183 | 1136.0087 | 14209.6795 | 57469.5388 | 397375.2671 | 0.041149 | -3068426.4802 | 3068426.4802
C | Xist Rating 7447 | -83.67 | 305.046 | 150.302 | 35.9 | 2310.81 | 6799.56 | 48760.8 | 2.14 | 8.65 | 22.949 | 369.033 | 1 | 1 | 1090 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 704903.3473 | 72879.9672 | 1157.1433 | 14341.2506 | 58538.7166 | 385639.6881 | 0.04153 | -2977807.4495 | 2977807.4495
C | Xist Rating 7448 | -83.4 | 308.811 | 150.302 | 35.9 | 2321.03 | 6899.39 | 48307.3 | 2.09 | 8.55 | 22.954 | 360.923 | 1 | 1 | 1100 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 716759.5953 | 74090.5703 | 1178.4727 | 14472.8217 | 59617.7485 | 377183.4175 | 0.041911 | -2912510.3695 | 2912510.3695
C | Xist Rating 7449 | -83.27 | 311.526 | 150.301 | 35.9 | 2320.1 | 6898.17 | 48010.8 | 2.01 | 8.49 | 22.605 | 355.933 | 1 | 1 | 1110 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 722771.4726 | 75311.0275 | 1199.9969 | 14604.3928 | 60706.6347 | 371896.5448 | 0.042292 | -2871686.5403 | 2871686.5403
C | Xist Rating 7450 | -82.1 | 334.009 | 150.302 | 35.9 | 2315.33 | 6920.23 | 45448.2 | 2.06 | 7.92 | 22.91 | 311.439 | 1 | 1 | 1120 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 773341.058 | 76541.339 | 1221.7158 | 14735.964 | 61805.375 | 325798.2483 | 0.042673 | -2515727.7137 | 2515727.7137
C | Xist Rating 7451 | -81.95 | 336.679 | 150.301 | 35.9 | 2317.05 | 6942.59 | 45189.2 | 1.99 | 7.86 | 22.688 | 307.412 | 1 | 1 | 1130 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 780102.077 | 77781.5046 | 1243.6296 | 14867.5351 | 62913.9695 | 321533.7626 | 0.043054 | -2482798.4857 | 2482798.4857
C | Xist Rating 7452 | -81.71 | 341.801 | 150.301 | 35.8 | 2314.45 | 6933.24 | 44681.2 | 1.94 | 7.75 | 22.478 | 299.352 | 1 | 1 | 1140 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 791081.3244 | 79031.5244 | 1265.7381 | 14999.1062 | 64032.4182 | 313104.9172 | 0.043435 | -2417713.1753 | 2417713.1753
C | Xist Rating 7453 | -81.44 | 346.859 | 150.3 | 35.8 | 2315.16 | 6953.56 | 44186.2 | 1.9 | 7.64 | 22.263 | 291.56 | 1 | 1 | 1150 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 803034.0824 | 80291.3983 | 1288.0414 | 15130.6773 | 65160.721 | 304965.0787 | 0.043816 | -2354859.5 | 2354859.5
C | Xist Rating 7454 | -81.2 | 351.997 | 150.3 | 35.8 | 2311.88 | 6937.83 | 43703.3 | 1.84 | 7.53 | 22.08 | 284.141 | 1 | 1 | 1160 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 813774.8244 | 81561.1264 | 1310.5395 | 15262.2484 | 66298.878 | 297192.4553 | 0.044197 | -2294841.3626 | 2294841.3626
C | Xist Rating 7455 | -80.16 | 372.167 | 150.3 | 35.8 | 2307.58 | 6955.71 | 41832.1 | 1.87 | 7.13 | 22.244 | 255.58 | 1 | 1 | 1170 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 858805.1259 | 82840.7087 | 1333.2324 | 15393.8195 | 67446.8892 | 267600.9362 | 0.044578 | -2066343.496 | 2066343.496
C | Xist Rating 7456 | -80.03 | 373.595 | 150.3 | 35.8 | 2314.84 | 7025.57 | 41724.6 | 1.81 | 7.11 | 22.15 | 254.179 | 1 | 1 | 1180 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 864812.6498 | 84130.1452 | 1356.1201 | 15525.3906 | 68604.7546 | 266085.0528 | 0.044959 | -2054638.2465 | 2054638.2465
C | Xist Rating 7457 | -79.55 | 383.698 | 150.3 | 35.8 | 2308.52 | 6995.34 | 40885.5 | 1.76 | 6.92 | 21.961 | 242.229 | 1 | 1 | 1190 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 885774.507 | 85429.4358 | 1379.2026 | 15656.9617 | 69772.4741 | 253616.1486 | 0.04534 | -1958356.6732 | 1958356.6732
C | Xist Rating 7458 | -79.32 | 386.26 | 150.3 | 35.8 | 2320.19 | 7110.72 | 40681.8 | 1.73 | 6.88 | 22.008 | 239.435 | 1 | 1 | 1200 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 896196.5894 | 86738.5807 | 1402.4799 | 15788.5328 | 70950.0479 | 250700.8448 | 0.045721 | -1935845.47 | 1935845.47
C | Xist Rating 7459 | -79.06 | 391.466 | 150.299 | 35.8 | 2318.98 | 7113.56 | 40281 | 1.68 | 6.8 | 21.84 | 233.996 | 1 | 1 | 1210 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 907801.8247 | 88057.5796 | 1425.9519 | 15920.1039 | 72137.4757 | 244994.527 | 0.046102 | -1891782.7964 | 1891782.7964
C | Xist Rating 7460 | -77.97 | 414.303 | 150.299 | 35.8 | 2306.21 | 7058.49 | 38537.5 | 1.68 | 6.43 | 21.843 | 210.393 | 1 | 1 | 1220 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 955469.7216 | 89386.4328 | 1449.6188 | 16051.675 | 73334.7578 | 220499.5711 | 0.046483 | -1702639.2401 | 1702639.2401
C | Xist Rating 7461 | -77.64 | 419.36 | 150.299 | 35.8 | 2312.78 | 7134.55 | 38183.3 | 1.65 | 6.35 | 21.868 | 205.869 | 1 | 1 | 1230 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 969887.4208 | 90725.1401 | 1473.4804 | 16183.2461 | 74541.894 | 215783.9985 | 0.046864 | -1666226.8387 | 1666226.8387
C | Xist Rating 7462 | -77.37 | 424.557 | 150.299 | 35.8 | 2313.3 | 7153.64 | 37835.3 | 1.61 | 6.28 | 21.752 | 201.554 | 1 | 1 | 1240 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 982127.7081 | 92073.7017 | 1497.5369 | 16314.8172 | 75758.8844 | 211260.0518 | 0.047245 | -1631294.1212 | 1631294.1212
C | Xist Rating 7463 | -77.19 | 427.263 | 150.299 | 35.8 | 2317.69 | 7202.91 | 37664.2 | 1.57 | 6.24 | 21.679 | 199.521 | 1 | 1 | 1250 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 990263.1825 | 93432.1173 | 1521.7881 | 16446.3883 | 76985.729 | 209109.3095 | 0.047626 | -1614686.6588 | 1614686.6588
C | Xist Rating 7464 | -76.79 | 434.871 | 150.299 | 35.8 | 2318.11 | 7228.48 | 37161.3 | 1.54 | 6.14 | 21.632 | 193.306 | 1 | 1 | 1260 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1008078.8138 | 94800.3872 | 1546.2341 | 16577.9594 | 78222.4278 | 202629.4781 | 0.048007 | -1564651.1185 | 1564651.1185
C | Xist Rating 7465 | -75.72 | 456.496 | 150.299 | 35.8 | 2310.83 | 7220.1 | 35777.3 | 1.55 | 5.85 | 21.7 | 176.516 | 1 | 1 | 1270 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1054884.6517 | 96178.5112 | 1570.8749 | 16709.5306 | 79468.9807 | 185226.3368 | 0.048388 | -1430268.6749 | 1430268.6749
C | Xist Rating 7466 | -75.47 | 461.761 | 150.299 | 35.8 | 2309.15 | 7217.87 | 35477 | 1.51 | 5.79 | 21.575 | 173.145 | 1 | 1 | 1280 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1066275.4132 | 97566.4894 | 1595.7105 | 16841.1017 | 80725.3878 | 181680.0038 | 0.048769 | -1402884.8314 | 1402884.8314
C | Xist Rating 7467 | -75.21 | 466.974 | 150.298 | 35.8 | 2308.31 | 7223.79 | 35182.7 | 1.47 | 5.73 | 21.525 | 169.852 | 1 | 1 | 1290 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1077920.7539 | 98964.3218 | 1620.7408 | 16972.6728 | 81991.649 | 178220.6796 | 0.04915 | -1376172.847 | 1376172.847
C | Xist Rating 7468 | -74.81 | 474.561 | 150.298 | 35.8 | 2309.29 | 7254.68 | 34751 | 1.45 | 5.64 | 21.559 | 164.998 | 1 | 1 | 1300 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1095898.9717 | 100372.0084 | 1645.966 | 17104.2439 | 83267.7645 | 173171.7783 | 0.049531 | -1337186.5693 | 1337186.5693
C | Xist Rating 7469 | -74.54 | 478.55 | 150.298 | 35.8 | 2314.78 | 7319.95 | 34539.9 | 1.41 | 5.59 | 21.519 | 162.738 | 1 | 1 | 1310 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1107737.969 | 101789.5491 | 1671.3859 | 17235.815 | 84553.7341 | 170784.8345 | 0.049912 | -1318755.2216 | 1318755.2216
C | Xist Rating 7470 | -73.47 | 500.273 | 150.298 | 35.8 | 2308.73 | 7322.24 | 33363.1 | 1.42 | 5.35 | 21.573 | 149.847 | 1 | 1 | 1320 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1154995.2833 | 103216.944 | 1697.0007 | 17367.3861 | 85849.5579 | 157428.4215 | 0.050293 | -1215620.5408 | 1215620.5408
C | Xist Rating 7471 | -73.09 | 508.076 | 150.298 | 35.8 | 2306.55 | 7321.83 | 32980 | 1.38 | 5.28 | 21.461 | 145.915 | 1 | 1 | 1330 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1171902.6978 | 104654.1931 | 1722.8102 | 17498.9572 | 87155.2359 | 153298.1182 | 0.050674 | -1183727.434 | 1183727.434
C | Xist Rating 7472 | -72.67 | 515.779 | 150.298 | 35.8 | 2308.65 | 7364.56 | 32606.7 | 1.35 | 5.2 | 21.364 | 142.114 | 1 | 1 | 1340 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1190753.1883 | 106101.2963 | 1748.8145 | 17630.5283 | 88470.768 | 149317.5239 | 0.051055 | -1152990.3398 | 1152990.3398
C | Xist Rating 7473 | -72.39 | 519.785 | 150.298 | 35.8 | 2314.78 | 7438.28 | 32423.5 | 1.32 | 5.16 | 21.326 | 140.329 | 1 | 1 | 1350 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1203187.9223 | 107558.2537 | 1775.0136 | 17762.0994 | 89796.1543 | 147434.9128 | 0.051436 | -1138453.3156 | 1138453.3156
C | Xist Rating 7474 | -72.11 | 522.293 | 150.298 | 35.8 | 2328.35 | 7587.95 | 32303 | 1.31 | 5.14 | 21.415 | 139.123 | 1 | 1 | 1360 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1216080.9065 | 109025.0653 | 1801.4075 | 17893.6705 | 91131.3948 | 146189.2088 | 0.051817 | -1128834.3198 | 1128834.3198
C | Xist Rating 7475 | -70.77 | 553.077 | 150.298 | 35.8 | 2304.74 | 7430.86 | 30902.2 | 1.3 | 4.86 | 21.329 | 125.324 | 1 | 1 | 1370 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1274698.685 | 110501.7311 | 1827.9962 | 18025.2416 | 92476.4895 | 131851.5275 | 0.052198 | -1018122.5457 | 1018122.5457
C | Xist Rating 7476 | -70.64 | 555.847 | 150.298 | 35.8 | 2304 | 7430.45 | 30793.8 | 1.27 | 4.84 | 21.284 | 124.374 | 1 | 1 | 1380 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1280671.488 | 111988.251 | 1854.7797 | 18156.8127 | 93831.4383 | 130834.2666 | 0.052579 | -1010267.5265 | 1010267.5265
C | Xist Rating 7477 | -70.3 | 562.384 | 150.298 | 35.8 | 2304.99 | 7458.82 | 30526.9 | 1.25 | 4.78 | 21.242 | 121.929 | 1 | 1 | 1390 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1296289.4962 | 113484.6251 | 1881.7579 | 18288.3838 | 95196.2413 | 128277.4608 | 0.05296 | -990524.5495 | 990524.5495
C | Xist Rating 7478 | -69.95 | 568.917 | 150.298 | 35.8 | 2306.18 | 7489.55 | 30264.9 | 1.22 | 4.73 | 21.209 | 119.558 | 1 | 1 | 1400 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1312025.0071 | 114990.8534 | 1908.931 | 18419.9549 | 96570.8985 | 125784.5657 | 0.053341 | -971275.0742 | 971275.0742
C | Xist Rating 7479 | -69.54 | 576.68 | 150.298 | 35.8 | 2306.86 | 7518.73 | 29957.2 | 1.2 | 4.67 | 21.184 | 116.787 | 1 | 1 | 1410 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1330320.0248 | 116506.9359 | 1936.2988 | 18551.526 | 97955.4098 | 122889.7795 | 0.053722 | -948922.3027 | 948922.3027
C | Xist Rating 7480 | -68.4 | 599.76 | 150.298 | 35.8 | 2302 | 7534.74 | 29051.6 | 1.21 | 4.49 | 21.26 | 108.649 | 1 | 1 | 1420 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1380647.52 | 118032.8725 | 1963.8614 | 18683.0972 | 99349.7753 | 114469.2113 | 0.054103 | -883900.9073 | 883900.9073
C | Xist Rating 7481 | -68.2 | 604.006 | 150.298 | 35.7 | 2300.87 | 7533.58 | 28910.4 | 1.17 | 4.47 | 21.167 | 107.524 | 1 | 1 | 1430 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1389739.2852 | 119568.6633 | 1991.6188 | 18814.6683 | 100753.995 | 113250.9469 | 0.054484 | -874493.7925 | 874493.7925
C | Xist Rating 7482 | -67.68 | 614.278 | 150.298 | 35.7 | 2300.12 | 7554.7 | 28541.8 | 1.15 | 4.39 | 21.149 | 104.395 | 1 | 1 | 1440 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1412913.1134 | 121114.3083 | 2019.571 | 18946.2394 | 102168.0689 | 109983.9247 | 0.054865 | -849266.7129 | 849266.7129
C | Xist Rating 7483 | -67.33 | 620.849 | 150.298 | 35.7 | 2301.89 | 7592.32 | 28316.6 | 1.13 | 4.35 | 21.125 | 102.547 | 1 | 1 | 1450 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1429126.1046 | 122669.8074 | 2047.718 | 19077.8105 | 103591.997 | 108046.427 | 0.055246 | -834305.8692 | 834305.8692
C | Xist Rating 7484 | -67.03 | 624.737 | 150.298 | 35.7 | 2309.12 | 7682.87 | 28183.4 | 1.12 | 4.32 | 21.159 | 101.462 | 1 | 1 | 1460 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1442592.7014 | 124235.1607 | 2076.0598 | 19209.3816 | 105025.7792 | 106919.0235 | 0.055627 | -825600.3581 | 825600.3581
C | Xist Rating 7485 | -65.89 | 650.753 | 150.298 | 35.7 | 2293.94 | 7591.81 | 27310 | 1.11 | 4.16 | 21.125 | 94.318 | 1 | 1 | 1470 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1492788.3368 | 125810.3682 | 2104.5964 | 19340.9527 | 106469.4156 | 99494.1844 | 0.056008 | -768267.7192 | 768267.7192
C | Xist Rating 7486 | -65.48 | 658.56 | 150.298 | 35.7 | 2294.78 | 7623.1 | 27065.8 | 1.09 | 4.11 | 21.112 | 92.419 | 1 | 1 | 1480 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1511250.3168 | 127395.4299 | 2133.3277 | 19472.5238 | 107922.9061 | 97503.6179 | 0.056389 | -752897.0917 | 752897.0917
C | Xist Rating 7487 | -65.13 | 665.133 | 150.298 | 35.7 | 2296.03 | 7655.32 | 26866 | 1.07 | 4.07 | 21.097 | 90.896 | 1 | 1 | 1490 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1527165.322 | 128990.3458 | 2162.2539 | 19604.0949 | 109386.2509 | 95903.027 | 0.05677 | -740537.7535 | 740537.7535
C | Xist Rating 7488 | -64.8 | 671.798 | 150.297 | 35.7 | 2295.79 | 7671.16 | 26669.5 | 1.05 | 4.03 | 21.063 | 89.425 | 1 | 1 | 1500 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1542307.1304 | 130595.1158 | 2191.3748 | 19735.666 | 110859.4498 | 94354.7441 | 0.057151 | -728582.3235 | 728582.3235
C | Xist Rating 7489 | -64.35 | 679.632 | 150.297 | 35.7 | 2298.99 | 7729.44 | 26438.3 | 1.03 | 3.99 | 21.063 | 87.686 | 1 | 1 | 1510 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1562467.1717 | 132209.74 | 2220.6906 | 19867.2371 | 112342.5029 | 92530.1958 | 0.057532 | -714493.6449 | 714493.6449
C | Xist Rating 7490 | -63.07 | 705.331 | 150.298 | 35.7 | 2295.56 | 7767.58 | 25680.7 | 1.04 | 3.84 | 21.145 | 81.963 | 1 | 1 | 1520 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1619129.6304 | 133834.2183 | 2250.2011 | 19998.8082 | 113835.4101 | 86616.7554 | 0.057913 | -668831.6255 | 668831.6255
C | Xist Rating 7491 | -62.72 | 713.509 | 150.297 | 35.7 | 2291.46 | 7743.2 | 25468 | 1.01 | 3.8 | 21.065 | 80.488 | 1 | 1 | 1530 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1634977.3331 | 135468.5509 | 2279.9064 | 20130.3793 | 115338.1715 | 85045.7813 | 0.058294 | -656700.98 | 656700.98
C | Xist Rating 7492 | -62.41 | 717.671 | 150.297 | 35.7 | 2297.86 | 7828.15 | 25363 | 0.99 | 3.78 | 21.057 | 79.785 | 1 | 1 | 1540 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1649107.4841 | 137112.7376 | 2309.8065 | 20261.9504 | 116850.7871 | 84295.6246 | 0.058675 | -650908.4689 | 650908.4689
C | Xist Rating 7493 | -61.75 | 730.577 | 150.297 | 35.7 | 2297.91 | 7866.95 | 25020.8 | 0.98 | 3.72 | 21.024 | 77.365 | 1 | 1 | 1550 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1678800.1941 | 138766.7785 | 2339.9013 | 20393.5215 | 118373.2569 | 81774.9258 | 0.059056 | -631444.301 | 631444.301
C | Xist Rating 7494 | -61.44 | 734.514 | 150.297 | 35.7 | 2305.75 | 7971.45 | 24919.5 | 0.97 | 3.7 | 21.072 | 76.68 | 1 | 1 | 1560 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1693605.6555 | 140430.6735 | 2370.191 | 20525.0926 | 119905.5809 | 81061.3443 | 0.059437 | -625934.2136 | 625934.2136
C | Xist Rating 7495 | -60.13 | 764.6 | 150.298 | 35.7 | 2289.79 | 7872.55 | 24162.1 | 0.96 | 3.56 | 21.032 | 71.467 | 1 | 1 | 1570 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1750773.434 | 142104.4227 | 2400.6755 | 20656.6638 | 121447.759 | 75639.2824 | 0.059818 | -584066.4888 | 584066.4888
C | Xist Rating 7496 | -59.8 | 771.294 | 150.297 | 35.7 | 2290.64 | 7901.83 | 24006.5 | 0.94 | 3.53 | 20.997 | 70.469 | 1 | 1 | 1580 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1766756.8882 | 143788.0262 | 2431.3547 | 20788.2349 | 122999.7913 | 74579.7903 | 0.0602 | -575885.372 | 575885.372
C | Xist Rating 7497 | -59.42 | 778.023 | 150.297 | 35.7 | 2293.29 | 7952.8 | 23854 | 0.92 | 3.5 | 20.986 | 69.499 | 1 | 1 | 1590 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1784232.3657 | 145481.4837 | 2462.2288 | 20919.806 | 124561.6778 | 73550.6431 | 0.060581 | -567938.5699 | 567938.5699
C | Xist Rating 7498 | -58.87 | 787.117 | 150.297 | 35.7 | 2297.57 | 8031.9 | 23644.6 | 0.91 | 3.46 | 21.01 | 68.144 | 1 | 1 | 1600 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1808456.4057 | 147184.7955 | 2493.2976 | 21051.3771 | 126133.4184 | 72138.6474 | 0.060962 | -557035.5134 | 557035.5134
C | Xist Rating 7499 | -58.63 | 791.475 | 150.297 | 35.7 | 2298.94 | 8060.65 | 23555.9 | 0.89 | 3.45 | 20.98 | 67.624 | 1 | 1 | 1610 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1819553.5365 | 148897.9614 | 2524.5612 | 21182.9482 | 127715.0132 | 71574.9466 | 0.061343 | -552682.7649 | 552682.7649
C | Xist Rating 7500 | -57.13 | 825.162 | 150.297 | 35.7 | 2285.68 | 8001.67 | 22804.4 | 0.9 | 3.31 | 21.013 | 62.82 | 1 | 1 | 1620 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1886056.2802 | 150620.9815 | 2556.0196 | 21314.5193 | 129306.4622 | 66611.7614 | 0.061724 | -514358.3648 | 514358.3648
C | Xist Rating 7501 | -56.78 | 829.175 | 150.297 | 35.7 | 2294.14 | 8118.21 | 22722.7 | 0.88 | 3.29 | 21.038 | 62.34 | 1 | 1 | 1630 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1902243.5345 | 152353.8558 | 2587.6728 | 21446.0904 | 130907.7654 | 66092.6607 | 0.062105 | -510350.007 | 510350.007
C | Xist Rating 7502 | -56.42 | 836.051 | 150.297 | 35.7 | 2294.84 | 8147.07 | 22587.9 | 0.87 | 3.27 | 21.013 | 61.557 | 1 | 1 | 1640 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1918603.2768 | 154096.5842 | 2619.5208 | 21577.6615 | 132518.9227 | 65270.7506 | 0.062486 | -504003.4349 | 504003.4349
C | Xist Rating 7503 | -55.98 | 845.503 | 150.297 | 35.7 | 2293.01 | 8151.87 | 22402.3 | 0.85 | 3.23 | 20.985 | 60.469 | 1 | 1 | 1650 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1938746.834 | 155849.1668 | 2651.5635 | 21709.2326 | 134139.9342 | 64116.2159 | 0.062867 | -495088.4238 | 495088.4238
C | Xist Rating 7504 | -55.47 | 854.711 | 150.297 | 35.7 | 2295.21 | 8208.05 | 22220.3 | 0.84 | 3.2 | 20.991 | 59.396 | 1 | 1 | 1660 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 1961741.2343 | 157611.6036 | 2683.8011 | 21840.8037 | 135770.7999 | 62994.6629 | 0.063248 | -486428.0888 | 486428.0888
C | Xist Rating 7505 | -54.16 | 884.841 | 150.297 | 35.7 | 2282.96 | 8145.81 | 21632.5 | 0.84 | 3.09 | 21.014 | 55.931 | 1 | 1 | 1670 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2020056.6094 | 159383.8946 | 2716.2334 | 21972.3748 | 137411.5198 | 59405.6158 | 0.063629 | -458714.4184 | 458714.4184
C | Xist Rating 7506 | -53.83 | 888.965 | 150.297 | 35.7 | 2289.1 | 8236.58 | 21560 | 0.82 | 3.08 | 21.024 | 55.543 | 1 | 1 | 1680 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2034929.7815 | 161166.0397 | 2748.8606 | 22103.9459 | 139062.0938 | 58979.5589 | 0.06401 | -455424.52 | 455424.52
C | Xist Rating 7507 | -53.31 | 901.041 | 150.297 | 35.7 | 2284.69 | 8215.85 | 21345.6 | 0.81 | 3.04 | 20.992 | 54.358 | 1 | 1 | 1690 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2058599.3623 | 162958.039 | 2781.6825 | 22235.517 | 140722.522 | 57738.7759 | 0.064391 | -445843.5227 | 445843.5227
C | Xist Rating 7508 | -52.86 | 909.031 | 150.297 | 35.7 | 2287.13 | 8271.77 | 21205.4 | 0.8 | 3.02 | 20.996 | 53.592 | 1 | 1 | 1700 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2079072.071 | 164759.8925 | 2814.6992 | 22367.0881 | 142392.8044 | 56935.1554 | 0.064772 | -439638.1783 | 439638.1783
C | Xist Rating 7509 | -52.4 | 918.432 | 150.297 | 35.7 | 2286.67 | 8294.21 | 21044.4 | 0.79 | 2.99 | 20.985 | 52.723 | 1 | 1 | 1710 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2100150.9014 | 166571.6002 | 2847.9107 | 22498.6592 | 144072.9409 | 56023.4698 | 0.065153 | -432598.384 | 432598.384
C | Xist Rating 7510 | -51.18 | 946.141 | 150.297 | 35.7 | 2277.25 | 8257.23 | 20566.8 | 0.78 | 2.9 | 21.013 | 50.11 | 1 | 1 | 1720 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2154599.5922 | 168393.162 | 2881.317 | 22630.2304 | 145762.9316 | 53302.8093 | 0.065534 | -411590.1645 | 411590.1645
C | Xist Rating 7511 | -50.61 | 958.088 | 150.297 | 35.7 | 2275.81 | 8274.4 | 20374 | 0.77 | 2.87 | 21.004 | 49.104 | 1 | 1 | 1730 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2180426.2513 | 170224.578 | 2914.9181 | 22761.8015 | 147462.7765 | 52248.5944 | 0.065915 | -403449.7968 | 403449.7968
C | Xist Rating 7512 | -50.25 | 963.594 | 150.297 | 35.7 | 2279.87 | 8344.62 | 20289.7 | 0.76 | 2.85 | 21.004 | 48.685 | 1 | 1 | 1740 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2196869.0528 | 172065.8482 | 2948.714 | 22893.3726 | 149172.4756 | 51804.3311 | 0.066296 | -400019.3129 | 400019.3129
C | Xist Rating 7513 | -49.77 | 974.437 | 150.297 | 35.7 | 2277.29 | 8342.71 | 20123.3 | 0.75 | 2.82 | 20.983 | 47.844 | 1 | 1 | 1750 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2219075.6357 | 173916.9725 | 2982.7046 | 23024.9437 | 150892.0289 | 50920.3976 | 0.066677 | -393193.8129 | 393193.8129
C | Xist Rating 7514 | -49.41 | 982.544 | 150.297 | 35.7 | 2275.45 | 8342.37 | 20000.5 | 0.74 | 2.8 | 20.976 | 47.23 | 1 | 1 | 1760 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2235729.7448 | 175777.951 | 3016.8901 | 23156.5148 | 152621.4363 | 50272.8513 | 0.067058 | -388193.632 | 388193.632
C | Xist Rating 7515 | -47.98 | 1015.39 | 150.297 | 35.7 | 2264.53 | 8298.46 | 19497.1 | 0.74 | 2.71 | 21.011 | 44.66 | 1 | 1 | 1770 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2299381.1167 | 177648.7837 | 3051.2703 | 23288.0859 | 154360.6979 | 47612.9231 | 0.067439 | -367654.3712 | 367654.3712
C | Xist Rating 7516 | -47.55 | 1023.6 | 150.297 | 35.7 | 2265.59 | 8336.94 | 19382.7 | 0.73 | 2.69 | 21.003 | 44.119 | 1 | 1 | 1780 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2319057.924 | 179529.4706 | 3085.8453 | 23419.657 | 156109.8136 | 47040.8346 | 0.06782 | -363236.8559 | 363236.8559
C | Xist Rating 7517 | -47.27 | 1027.99 | 150.298 | 35.7 | 2268.52 | 8388.95 | 19326.2 | 0.71 | 2.68 | 20.997 | 43.87 | 1 | 1 | 1790 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2332015.8748 | 181420.0117 | 3120.6151 | 23551.2281 | 157868.7836 | 46755.0753 | 0.068201 | -361030.2983 | 361030.2983
C | Xist Rating 7518 | -46.86 | 1042.6 | 150.298 | 35.7 | 2254.09 | 8237.65 | 19122.7 | 0.7 | 2.65 | 21.251 | 42.88 | 1 | 1 | 1800 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2350114.234 | 183320.4069 | 3155.5797 | 23682.7992 | 159637.6077 | 45731.0487 | 0.068582 | -353123.036 | 353123.036
C | Xist Rating 7519 | -46.44 | 1050.68 | 150.298 | 35.7 | 2255.63 | 8282 | 19013.1 | 0.69 | 2.63 | 21.256 | 42.37 | 1 | 1 | 1810 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2369945.3284 | 185230.6563 | 3190.7391 | 23814.3703 | 161416.286 | 45191.1209 | 0.068963 | -348953.8567 | 348953.8567
C | Xist Rating 7520 | -45.05 | 1083.79 | 150.298 | 35.7 | 2243.52 | 8218.84 | 18563.5 | 0.69 | 2.55 | 21.285 | 40.233 | 1 | 1 | 1820 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2431504.5408 | 187150.7598 | 3226.0933 | 23945.9414 | 163204.8184 | 42980.0565 | 0.069344 | -331880.6033 | 331880.6033
C | Xist Rating 7521 | -45.06 | 1078.54 | 150.298 | 35.6 | 2259.42 | 8420.33 | 18631 | 0.69 | 2.56 | 21.301 | 40.563 | 1 | 1 | 1830 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2436874.8468 | 189080.7176 | 3261.6423 | 24077.5125 | 165003.205 | 43330.2498 | 0.069725 | -334584.7033 | 334584.7033
C | Xist Rating 7522 | -44.56 | 1085.19 | 150.298 | 35.6 | 2264.71 | 8514.97 | 18545.2 | 0.68 | 2.55 | 21.331 | 40.176 | 1 | 1 | 1840 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2457640.6449 | 191020.5295 | 3297.386 | 24209.0836 | 166811.4458 | 42919.0531 | 0.070106 | -331409.5516 | 331409.5516
C | Xist Rating 7523 | -44.05 | 1096.15 | 150.298 | 35.6 | 2262.88 | 8522.32 | 18409.3 | 0.67 | 2.52 | 21.318 | 39.573 | 1 | 1 | 1850 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2480455.912 | 192970.1956 | 3333.3246 | 24340.6547 | 168629.5408 | 42280.9293 | 0.070487 | -326482.1285 | 326482.1285
C | Xist Rating 7524 | -43.56 | 1108.44 | 150.298 | 35.6 | 2258.3 | 8494.7 | 18259 | 0.66 | 2.5 | 21.302 | 38.91 | 1 | 1 | 1860 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2503190.052 | 194929.7158 | 3369.4579 | 24472.2258 | 170457.49 | 41580.1531 | 0.070868 | -321070.9206 | 321070.9206
C | Xist Rating 7525 | -42.18 | 1138.85 | 150.298 | 35.6 | 2252.24 | 8505.11 | 17879.5 | 0.66 | 2.43 | 21.353 | 37.197 | 1 | 1 | 1870 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2564963.524 | 196899.0902 | 3405.7861 | 24603.797 | 172295.2933 | 39810.3288 | 0.071249 | -307404.8065 | 307404.8065
C | Xist Rating 7526 | -41.64 | 1151.12 | 150.298 | 35.6 | 2249.36 | 8501 | 17738.5 | 0.65 | 2.41 | 21.347 | 36.601 | 1 | 1 | 1880 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2589283.2832 | 198878.3188 | 3442.309 | 24735.3681 | 174142.9508 | 39179.378 | 0.07163 | -302532.7714 | 302532.7714
C | Xist Rating 7527 | -41.15 | 1159.26 | 150.298 | 35.6 | 2252.29 | 8567.86 | 17646.4 | 0.64 | 2.39 | 21.365 | 36.215 | 1 | 1 | 1890 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2610989.7054 | 200867.4016 | 3479.0267 | 24866.9392 | 176000.4625 | 38767.6283 | 0.072011 | -299353.3498 | 299353.3498
C | Xist Rating 7528 | -40.77 | 1167.86 | 150.298 | 35.6 | 2250.19 | 8562.16 | 17555.3 | 0.63 | 2.38 | 21.353 | 35.85 | 1 | 1 | 1900 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2627906.8934 | 202866.3386 | 3515.9392 | 24998.5103 | 177867.8283 | 38375.8658 | 0.072392 | -296328.2634 | 296328.2634
C | Xist Rating 7529 | -40.38 | 1176.17 | 150.298 | 35.7 | 2249.31 | 8574.34 | 17465.1 | 0.62 | 2.36 | 21.359 | 35.483 | 1 | 1 | 1910 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2645570.9427 | 204875.1297 | 3553.0464 | 25130.0814 | 179745.0483 | 37982.804 | 0.072773 | -293293.1441 | 293293.1441
C | Xist Rating 7530 | -38.73 | 1213.09 | 150.298 | 35.6 | 2241.96 | 8585.07 | 17050.2 | 0.62 | 2.29 | 21.399 | 33.721 | 1 | 1 | 1920 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2719699.2564 | 206893.775 | 3590.3485 | 25261.6525 | 181632.1225 | 36161.0401 | 0.073154 | -279225.9661 | 279225.9661
C | Xist Rating 7531 | -38.21 | 1225.45 | 150.298 | 35.7 | 2238.01 | 8564.22 | 16923.8 | 0.61 | 2.27 | 21.391 | 33.221 | 1 | 1 | 1930 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2742569.3545 | 208922.2745 | 3627.8454 | 25393.2236 | 183529.0509 | 35628.8031 | 0.073535 | -275116.1735 | 275116.1735
C | Xist Rating 7532 | -37.85 | 1229.47 | 150.298 | 35.7 | 2244.3 | 8669.52 | 16882.2 | 0.6 | 2.26 | 21.43 | 33.061 | 1 | 1 | 1940 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2759299.521 | 210960.6281 | 3665.537 | 25524.7947 | 185435.8334 | 35451.9256 | 0.073916 | -273750.3723 | 273750.3723
C | Xist Rating 7533 | -37.47 | 1241 | 150.298 | 35.7 | 2237.58 | 8603.15 | 16772 | 0.59 | 2.24 | 21.397 | 32.645 | 1 | 1 | 1950 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 29 | E | Rod | 2776836.78 | 213008.8359 | 3703.4235 | 25656.3658 | 187352.4701 | 35005.2404 | 0.074297 | -270301.1878 | 270301.1878
C | Xist Rating 7534 | -36.89 | 1254.56 | 150.298 | 35.7 | 2234.28 | 8595.43 | 16637 | 0.58 | 2.22 | 21.421 | 32.116 | 1 | 1 | 1960 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 2803038.3168 | 215066.8979 | 3741.5047 | 25787.9369 | 189278.961 | 34443.9579 | 0.074678 | -265967.1127 | 265967.1127
C | Xist Rating 7535 | -35.45 | 1287.79 | 150.298 | 35.7 | 2226.94 | 8591.13 | 16303.2 | 0.58 | 2.16 | 21.491 | 30.789 | 1 | 1 | 1970 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 2867831.0626 | 217134.8141 | 3779.7807 | 25919.508 | 191215.306 | 33075.0247 | 0.075059 | -255396.5738 | 255396.5738
C | Xist Rating 7536 | -34.97 | 1297.41 | 150.298 | 35.7 | 2227.15 | 8622.91 | 16214.2 | 0.57 | 2.15 | 21.519 | 30.459 | 1 | 1 | 1980 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 2889526.6815 | 219212.5844 | 3818.2515 | 26051.0791 | 193161.5053 | 32720.2502 | 0.07544 | -252657.0987 | 252657.0987
C | Xist Rating 7537 | -34.47 | 1309.96 | 150.298 | 35.7 | 2223.41 | 8603.83 | 16101.3 | 0.56 | 2.13 | 21.524 | 30.045 | 1 | 1 | 1990 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 2912578.1636 | 221300.2089 | 3856.9171 | 26182.6502 | 195117.5587 | 32276.8645 | 0.075821 | -249233.3923 | 249233.3923
C | Xist Rating 7538 | -33.99 | 1319.71 | 150.298 | 35.7 | 2223.31 | 8630.91 | 16015 | 0.55 | 2.12 | 21.534 | 29.732 | 1 | 1 | 2000 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 2934124.4401 | 223397.6876 | 3895.7775 | 26314.2213 | 197083.4663 | 31938.4144 | 0.076202 | -246619.9701 | 246619.9701
C | Xist Rating 7539 | -33.63 | 1326.84 | 150.298 | 35.7 | 2224.04 | 8662.53 | 15953.8 | 0.55 | 2.11 | 21.539 | 29.518 | 1 | 1 | 2010 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 2950945.2336 | 225505.0205 | 3934.8326 | 26445.7924 | 199059.228 | 31721.7324 | 0.076583 | -244946.8092 | 244946.8092
C | Xist Rating 7540 | -32.07 | 1364.21 | 150.299 | 35.7 | 2214.26 | 8631.11 | 15614.8 | 0.55 | 2.05 | 21.575 | 28.248 | 1 | 1 | 2020 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3020715.6346 | 227622.2075 | 3974.0826 | 26577.3636 | 201044.8439 | 30409.9424 | 0.076964 | -234817.5141 | 234817.5141
C | Xist Rating 7541 | -31.45 | 1377.71 | 150.299 | 35.7 | 2213.22 | 8656.02 | 15499.8 | 0.54 | 2.03 | 21.586 | 27.839 | 1 | 1 | 2030 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3049175.3262 | 229749.2487 | 4013.5273 | 26708.9347 | 203040.314 | 29971.424 | 0.077345 | -231431.3919 | 231431.3919
C | Xist Rating 7542 | -31.11 | 1386.51 | 150.299 | 35.7 | 2210.65 | 8641.34 | 15431.7 | 0.53 | 2.02 | 21.574 | 27.614 | 1 | 1 | 2040 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3065088.3315 | 231886.1441 | 4053.1669 | 26840.5058 | 205045.6383 | 29722.6666 | 0.077726 | -229510.5525 | 229510.5525
C | Xist Rating 7543 | -30.6 | 1394.49 | 150.299 | 35.7 | 2214.36 | 8723.03 | 15364.2 | 0.53 | 2.01 | 21.6 | 27.378 | 1 | 1 | 2050 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3087902.8764 | 234032.8936 | 4093.0012 | 26972.0769 | 207060.8167 | 29483.9725 | 0.078107 | -227667.4205 | 227667.4205
C | Xist Rating 7544 | -30.11 | 1407.43 | 150.299 | 35.7 | 2210.36 | 8698.24 | 15264.2 | 0.52 | 1.99 | 21.576 | 27.044 | 1 | 1 | 2060 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3110926.9748 | 236189.4973 | 4133.0303 | 27103.648 | 209085.8494 | 29121.148 | 0.078488 | -224865.7858 | 224865.7858
C | Xist Rating 7545 | -28.46 | 1447.52 | 150.299 | 35.7 | 2200.27 | 8666.73 | 14936 | 0.52 | 1.94 | 21.614 | 25.886 | 1 | 1 | 2070 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3184934.8304 | 238355.9552 | 4173.2542 | 27235.2191 | 211120.7361 | 27925.4294 | 0.078869 | -215632.7639 | 215632.7639
C | Xist Rating 7546 | -28.03 | 1456.12 | 150.299 | 35.7 | 2200.83 | 8699.88 | 14873.4 | 0.51 | 1.93 | 21.616 | 25.686 | 1 | 1 | 2080 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3204672.5796 | 240532.2673 | 4213.6729 | 27366.7902 | 213165.4771 | 27702.7109 | 0.07925 | -213912.9907 | 213912.9907
C | Xist Rating 7547 | -27.55 | 1467.28 | 150.299 | 35.7 | 2199.17 | 8706.66 | 14790.7 | 0.5 | 1.91 | 21.613 | 25.417 | 1 | 1 | 2090 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3226798.1576 | 242718.4335 | 4254.2864 | 27498.3613 | 215220.0722 | 27407.9053 | 0.079631 | -211636.5794 | 211636.5794
C | Xist Rating 7548 | -27.07 | 1478.45 | 150.299 | 35.7 | 2197.59 | 8714.55 | 14709.1 | 0.5 | 1.9 | 21.612 | 25.153 | 1 | 1 | 2100 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3249026.9355 | 244914.454 | 4295.0947 | 27629.9324 | 217284.5215 | 27138.5386 | 0.080012 | -209556.6013 | 209556.6013
C | Xist Rating 7549 | -26.67 | 1488.29 | 150.299 | 35.7 | 2195.72 | 8713.71 | 14638.6 | 0.49 | 1.89 | 21.618 | 24.929 | 1 | 1 | 2110 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3267868.1188 | 247120.3285 | 4336.0977 | 27761.5035 | 219358.825 | 26890.5961 | 0.080393 | -207642.0553 | 207642.0553
C | Xist Rating 7550 | -25.16 | 1526.1 | 150.299 | 35.7 | 2186.01 | 8676.49 | 14358.9 | 0.49 | 1.84 | 21.652 | 23.998 | 1 | 1 | 2120 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3336069.861 | 249336.0573 | 4377.2956 | 27893.0746 | 221442.9827 | 25930.0855 | 0.080774 | -200225.2466 | 200225.2466
C | Xist Rating 7551 | -24.59 | 1539.95 | 150.299 | 35.7 | 2183.38 | 8675.39 | 14263.6 | 0.48 | 1.83 | 21.648 | 23.7 | 1 | 1 | 2130 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3362296.031 | 251561.6402 | 4418.6882 | 28024.6457 | 223536.9945 | 25604.5127 | 0.081155 | -197711.2601 | 197711.2601
C | Xist Rating 7552 | -24.14 | 1553.82 | 150.299 | 35.7 | 2177.47 | 8622.3 | 14169.8 | 0.48 | 1.81 | 21.647 | 23.408 | 1 | 1 | 2140 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3383396.4354 | 253797.0774 | 4460.2756 | 28156.2168 | 225640.8605 | 25305.8829 | 0.081536 | -195405.3197 | 195405.3197
C | Xist Rating 7553 | -23.82 | 1561.1 | 150.299 | 35.7 | 2176.91 | 8633.4 | 14123.4 | 0.47 | 1.8 | 21.65 | 23.273 | 1 | 1 | 2150 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3398374.201 | 256042.3686 | 4502.0578 | 28287.7879 | 227754.5807 | 25149.6171 | 0.081917 | -194198.6771 | 194198.6771
C | Xist Rating 7554 | -23.38 | 1570.89 | 150.299 | 35.7 | 2176.27 | 8651.12 | 14059 | 0.46 | 1.79 | 21.66 | 23.079 | 1 | 1 | 2160 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3418680.7803 | 258297.5141 | 4544.0348 | 28419.359 | 229878.155 | 24932.1932 | 0.082298 | -192519.7868 | 192519.7868
C | Xist Rating 7555 | -21.82 | 1611.64 | 150.299 | 35.7 | 2165.01 | 8593.98 | 13786 | 0.46 | 1.75 | 21.691 | 22.221 | 1 | 1 | 2170 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3489216.7164 | 260562.5137 | 4586.2066 | 28550.9302 | 232011.5836 | 24047.0147 | 0.082679 | -185684.6735 | 185684.6735
C | Xist Rating 7556 | -21.21 | 1625.26 | 150.299 | 35.7 | 2164.06 | 8618.18 | 13699 | 0.46 | 1.74 | 21.696 | 21.96 | 1 | 1 | 2180 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3517160.1556 | 262837.3675 | 4628.5732 | 28682.5013 | 234154.8663 | 23780.6639 | 0.08306 | -183627.9833 | 183627.9833
C | Xist Rating 7557 | -20.8 | 1635.29 | 150.299 | 35.7 | 2162.5 | 8620.8 | 13638.9 | 0.45 | 1.73 | 21.696 | 21.789 | 1 | 1 | 2190 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3536314.625 | 265122.0755 | 4671.1346 | 28814.0724 | 236308.0031 | 23586.2562 | 0.083441 | -182126.8182 | 182126.8182
C | Xist Rating 7558 | -20.39 | 1645.71 | 150.299 | 35.7 | 2160.51 | 8616.69 | 13579.3 | 0.44 | 1.72 | 21.68 | 21.624 | 1 | 1 | 2200 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3555572.9121 | 267416.6376 | 4713.8907 | 28945.6435 | 238470.9942 | 23397.1907 | 0.083822 | -180666.9045 | 180666.9045
C | Xist Rating 7559 | -19.82 | 1659.59 | 150.299 | 35.7 | 2158.43 | 8622.72 | 13495.4 | 0.44 | 1.7 | 21.682 | 21.38 | 1 | 1 | 2210 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3582108.8437 | 269721.054 | 4756.8417 | 29077.2146 | 240643.8394 | 23148.1601 | 0.084203 | -178743.9568 | 178743.9568
C | Xist Rating 7560 | -18.22 | 1700.21 | 150.299 | 35.7 | 2149.28 | 8595.35 | 13246.2 | 0.44 | 1.66 | 21.72 | 20.636 | 1 | 1 | 2220 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3654227.3488 | 272035.3245 | 4799.9874 | 29208.7857 | 242826.5388 | 22381.4575 | 0.084584 | -172823.6818 | 172823.6818
C | Xist Rating 7561 | -17.73 | 1711.34 | 150.299 | 35.7 | 2148.81 | 8618.93 | 13182.5 | 0.44 | 1.65 | 21.723 | 20.458 | 1 | 1 | 2230 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3677344.5054 | 274359.4491 | 4843.3279 | 29340.3568 | 245019.0923 | 22201.0205 | 0.084965 | -171430.3953 | 171430.3953
C | Xist Rating 7562 | -17.25 | 1724.25 | 150.299 | 35.7 | 2145.9 | 8607.05 | 13111.6 | 0.43 | 1.64 | 21.716 | 20.265 | 1 | 1 | 2240 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3700068.075 | 276693.428 | 4886.8633 | 29471.9279 | 247221.5001 | 21982.761 | 0.085346 | -169745.0534 | 169745.0534
C | Xist Rating 7563 | -16.73 | 1738.44 | 150.299 | 35.7 | 2142.2 | 8586.31 | 13034 | 0.42 | 1.63 | 21.712 | 20.053 | 1 | 1 | 2250 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3724086.168 | 279037.261 | 4930.5934 | 29603.499 | 249433.762 | 21744.7138 | 0.085727 | -167906.916 | 167906.916
C | Xist Rating 7564 | -16.38 | 1745.68 | 150.299 | 35.7 | 2142.83 | 8615.73 | 12995.5 | 0.42 | 1.62 | 21.718 | 19.953 | 1 | 1 | 2260 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3740695.4744 | 281390.9482 | 4974.5182 | 29735.0701 | 251655.8781 | 21645.2068 | 0.086108 | -167138.5495 | 167138.5495
C | Xist Rating 7565 | -14.73 | 1789.32 | 150.299 | 35.7 | 2132.28 | 8570.14 | 12751.8 | 0.42 | 1.59 | 21.749 | 19.263 | 1 | 1 | 2270 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3815331.2496 | 283754.4895 | 5018.6379 | 29866.6412 | 253887.8483 | 20934.0564 | 0.086489 | -161647.2347 | 161647.2347
C | Xist Rating 7566 | -14.23 | 1802.18 | 150.299 | 35.7 | 2130.03 | 8568.06 | 12686.1 | 0.41 | 1.58 | 21.746 | 19.092 | 1 | 1 | 2280 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3838697.4654 | 286127.8851 | 5062.9524 | 29998.2123 | 256129.6727 | 20738.2145 | 0.08687 | -160134.9953 | 160134.9953
C | Xist Rating 7567 | -13.6 | 1817.44 | 150.299 | 35.7 | 2128.11 | 8578.85 | 12606.8 | 0.41 | 1.56 | 21.747 | 18.881 | 1 | 1 | 2290 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3867712.2384 | 288511.1348 | 5107.4617 | 30129.7834 | 258381.3514 | 20523.1299 | 0.087251 | -158474.1692 | 158474.1692
C | Xist Rating 7568 | -13.17 | 1827.63 | 150.299 | 35.7 | 2127.37 | 8593.45 | 12557.1 | 0.4 | 1.56 | 21.75 | 18.755 | 1 | 1 | 2300 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3888045.2331 | 290904.2387 | 5152.1657 | 30261.3545 | 260642.8841 | 20373.9791 | 0.087632 | -157322.466 | 157322.466
| Xist Rating 7569 | -12.78 | 1838.08 | 150.299 | 35.7 | 2125.34 | 8587.1 | 12507.6 | 0.4 | 1.55 | 21.753 | 18.634 | 1 | 1 | 2310 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3906544.9472 | 293307.1967 | 5197.0645 | 30392.9256 | 262914.2711 | 20252.3448 | 0.088013 | -156383.2381 | 156383.2381
| Xist Rating 7570 | -11.08 | 1882.89 | 150.299 | 35.7 | 2115.81 | 8558.22 | 12277.2 | 0.4 | 1.51 | 21.777 | 18.012 | 1 | 1 | 2320 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 3983837.4909 | 295720.009 | 5242.1582 | 30524.4968 | 265195.5122 | 19611.2974 | 0.088394 | -151433.24 | 151433.24
| Xist Rating 7571 | -10.56 | 1895.78 | 150.299 | 35.7 | 2114.23 | 8566.26 | 12216.8 | 0.39 | 1.5 | 21.783 | 17.862 | 1 | 1 | 2330 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4008114.9494 | 298142.6754 | 5287.4466 | 30656.0679 | 267486.6075 | 19436.9274 | 0.088775 | -150086.8011 | 150086.8011
| Xist Rating 7572 | -10.06 | 1908.64 | 150.299 | 35.7 | 2112.15 | 8565.97 | 12157.2 | 0.39 | 1.49 | 21.781 | 17.715 | 1 | 1 | 2340 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4031333.976 | 300575.1959 | 5332.9298 | 30787.639 | 269787.557 | 19287.9943 | 0.089156 | -148936.7795 | 148936.7795
| Xist Rating 7573 | -9.65 | 1920.27 | 150.299 | 35.7 | 2109.54 | 8553.02 | 12104.7 | 0.38 | 1.49 | 21.776 | 17.588 | 1 | 1 | 2350 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4050886.3758 | 303017.5707 | 5378.6078 | 30919.2101 | 272098.3606 | 19136.7689 | 0.089537 | -147769.0569 | 147769.0569
| Xist Rating 7574 | -9.14 | 1934.51 | 150.299 | 35.7 | 2106.51 | 8540.6 | 12039.8 | 0.38 | 1.48 | 21.772 | 17.429 | 1 | 1 | 2360 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4075064.6601 | 305469.7996 | 5424.4805 | 31050.7812 | 274419.0184 | 18975.196 | 0.089918 | -146521.4341 | 146521.4341
| Xist Rating 7575 | -7.57 | 1975.55 | 150.299 | 35.7 | 2098.77 | 8526.51 | 11846.9 | 0.38 | 1.45 | 21.801 | 16.935 | 1 | 1 | 2370 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4146225.0735 | 307931.8827 | 5470.5481 | 31182.3523 | 276749.5304 | 18467.057 | 0.090299 | -142597.7193 | 142597.7193
| Xist Rating 7576 | -7.13 | 1988.65 | 150.299 | 35.7 | 2095.44 | 8504.85 | 11791.2 | 0.38 | 1.44 | 21.793 | 16.804 | 1 | 1 | 2380 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4167096.756 | 310403.82 | 5516.8105 | 31313.9234 | 279089.8966 | 18334.4029 | 0.09068 | -141573.399 | 141573.399
| Xist Rating 7577 | -6.58 | 2002.44 | 150.299 | 35.7 | 2093.82 | 8514.9 | 11730 | 0.37 | 1.43 | 21.792 | 16.657 | 1 | 1 | 2390 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4192748.9208 | 312885.6114 | 5563.2676 | 31445.4945 | 281440.1169 | 18162.069 | 0.091061 | -140242.6826 | 140242.6826
C | Xist Rating 7580 | 3.91 | 2297.41 | 150.299 | 35.7 | 2031.25 | 8260.3 | 10538.1 | 0.4 | 1.25 | 21.811 | 13.849 | 1 | 1 | 2420 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4666614.0625 | 320390.1108 | 5703.8078 | 31840.2078 | 288549.9029 | 15328.5496 | 0.092204 | -118362.9968 | 118362.9968
C | Xist Rating 7581 | 4.07 | 2298.77 | 150.299 | 35.7 | 2033.66 | 8300.39 | 10538 | 0.39 | 1.25 | 21.816 | 13.86 | 1 | 1 | 2430 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4674916.5982 | 322911.3189 | 5751.0441 | 31971.7789 | 290939.54 | 15320.3388 | 0.092585 | -118299.595 | 118299.595
C | Xist Rating 7582 | 4.08 | 2300.14 | 150.299 | 35.7 | 2033.24 | 8293.32 | 10538 | 0.38 | 1.25 | 21.809 | 13.87 | 1 | 1 | 2440 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4676736.6536 | 325442.3812 | 5798.4752 | 32103.35 | 293339.0312 | 15310.386 | 0.092966 | -118222.7422 | 118222.7422
C | Xist Rating 7583 | 4.09 | 2301.46 | 150.299 | 35.7 | 2032.8 | 8286.01 | 10538 | 0.38 | 1.25 | 21.808 | 13.881 | 1 | 1 | 2450 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4678407.888 | 327983.2977 | 5846.1011 | 32234.9211 | 295748.3766 | 15325.4825 | 0.093347 | -118339.3138 | 118339.3138
C | Xist Rating 7584 | 4.13 | 2302.93 | 150.299 | 35.7 | 2032.81 | 8286.29 | 10538 | 0.37 | 1.25 | 21.792 | 13.892 | 1 | 1 | 2460 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4681419.1333 | 330534.0684 | 5893.9217 | 32366.4922 | 298167.5761 | 15315.9205 | 0.093728 | -118265.4782 | 118265.4782
C | Xist Rating 7585 | 4.13 | 2304.29 | 150.299 | 35.7 | 2032.34 | 8278.41 | 10538 | 0.37 | 1.25 | 21.833 | 13.903 | 1 | 1 | 2470 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4683100.7386 | 333094.6932 | 5941.9372 | 32498.0634 | 300596.6298 | 15332.6378 | 0.094109 | -118394.5646 | 118394.5646
C | Xist Rating 7586 | 4.14 | 2305.64 | 150.299 | 35.7 | 2031.82 | 8269.8 | 10538 | 0.36 | 1.25 | 21.827 | 13.913 | 1 | 1 | 2480 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4684645.4648 | 335665.1722 | 5990.1474 | 32629.6345 | 303035.5377 | 15322.133 | 0.09449 | -118313.4495 | 118313.4495
C | Xist Rating 7587 | 4.14 | 2307.03 | 150.299 | 35.7 | 2031.17 | 8259.05 | 10538 | 0.35 | 1.25 | 21.821 | 13.924 | 1 | 1 | 2490 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4685970.1251 | 338245.5054 | 6038.5525 | 32761.2056 | 305484.2998 | 15312.4824 | 0.094871 | -118238.9304 | 118238.9304
C | Xist Rating 7588 | 4.17 | 2308.02 | 150.299 | 35.7 | 2031.41 | 8263.11 | 10538 | 0.35 | 1.25 | 21.818 | 13.933 | 1 | 1 | 2500 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4688534.9082 | 340835.6927 | 6087.1523 | 32892.7767 | 307942.916 | 15325.1347 | 0.095252 | -118336.6276 | 118336.6276
C | Xist Rating 7589 | 4.15 | 2309.87 | 150.299 | 35.7 | 2029.88 | 8237.72 | 10538 | 0.34 | 1.25 | 21.812 | 13.946 | 1 | 1 | 2510 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4688758.9156 | 343435.7342 | 6135.9469 | 33024.3478 | 310411.3864 | 15317.2812 | 0.095633 | -118275.9849 | 118275.9849
C | Xist Rating 7590 | 4.16 | 2311.32 | 150.299 | 35.7 | 2029.24 | 8227.24 | 10538 | 0.34 | 1.25 | 21.848 | 13.957 | 1 | 1 | 2520 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4690222.9968 | 346045.6299 | 6184.9363 | 33155.9189 | 312889.711 | 15333.4115 | 0.096014 | -118400.539 | 118400.539
C | Xist Rating 7591 | 4.16 | 2312.66 | 150.299 | 35.7 | 2028.72 | 8218.75 | 10538 | 0.33 | 1.25 | 21.843 | 13.967 | 1 | 1 | 2530 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4691739.5952 | 348665.3798 | 6234.1205 | 33287.49 | 315377.8898 | 15322.162 | 0.096395 | -118313.6738 | 118313.6738
C | Xist Rating 7592 | 4.18 | 2313.81 | 150.299 | 35.7 | 2028.59 | 8216.6 | 10538 | 0.33 | 1.25 | 21.839 | 13.976 | 1 | 1 | 2540 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4693771.8279 | 351294.9838 | 6283.4995 | 33419.0611 | 317875.9227 | 15334.5893 | 0.096776 | -118409.6337 | 118409.6337
C | Xist Rating 7593 | 4.18 | 2315.36 | 150.299 | 35.7 | 2027.83 | 8204.18 | 10538 | 0.32 | 1.25 | 21.834 | 13.987 | 1 | 1 | 2550 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4695156.4688 | 353934.442 | 6333.0732 | 33550.6322 | 320383.8098 | 15324.0977 | 0.097157 | -118328.6207 | 118328.6207
C | Xist Rating 7594 | 4.22 | 2316.81 | 150.299 | 35.7 | 2027.92 | 8205.74 | 10537.9 | 0.32 | 1.25 | 21.827 | 13.998 | 1 | 1 | 2560 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4698305.3352 | 356583.7544 | 6382.8418 | 33682.2033 | 322901.5511 | 15338.396 | 0.097538 | -118439.0283 | 118439.0283
C | Xist Rating 7595 | 4.23 | 2318.2 | 150.299 | 35.6 | 2027.63 | 8200.91 | 10537.8 | 0.31 | 1.25 | 21.821 | 14.008 | 1 | 1 | 2570 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4700451.866 | 359242.921 | 6432.8051 | 33813.7744 | 325429.1466 | 15326.553 | 0.097919 | -118347.5797 | 118347.5797
C | Xist Rating 7596 | 4.25 | 2319.56 | 150.299 | 35.6 | 2027.53 | 8199.4 | 10537.8 | 0.31 | 1.25 | 21.871 | 14.018 | 1 | 1 | 2580 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4702977.4868 | 361911.9417 | 6482.9633 | 33945.3455 | 327966.5962 | 15341.7627 | 0.0983 | -118465.0249 | 118465.0249
C | Xist Rating 7597 | 4.29 | 2320.92 | 150.299 | 35.6 | 2027.89 | 8205.29 | 10537.8 | 0.3 | 1.25 | 21.864 | 14.028 | 1 | 1 | 2590 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4706570.4588 | 364590.8166 | 6533.3162 | 34076.9166 | 330513.9 | 15329.5517 | 0.098681 | -118370.7346 | 118370.7346
C | Xist Rating 7598 | 4.33 | 2322.1 | 150.299 | 35.6 | 2028.06 | 8207.98 | 10537.8 | 0.3 | 1.25 | 21.869 | 14.038 | 1 | 1 | 2600 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4709358.126 | 367279.5457 | 6583.8639 | 34208.4877 | 333071.058 | 15343.0516 | 0.099062 | -118474.9776 | 118474.9776
C | Xist Rating 7599 | 4.29 | 2323.79 | 150.299 | 35.6 | 2026.58 | 8183.84 | 10537.7 | 0.3 | 1.25 | 21.864 | 14.049 | 1 | 1 | 2610 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4709346.3382 | 369978.129 | 6634.6064 | 34340.0588 | 335638.0701 | 15357.2404 | 0.099443 | -118584.5398 | 118584.5398
C | Xist Rating 7600 | 4.32 | 2325.18 | 150.3 | 35.6 | 2026.3 | 8179.23 | 10537.8 | 0.29 | 1.25 | 21.864 | 14.059 | 1 | 1 | 2620 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4711512.234 | 372686.5664 | 6685.5437 | 34471.63 | 338214.9364 | 15344.8883 | 0.099824 | -118489.1602 | 118489.1602
C | Xist Rating 7601 | 4.35 | 2326.61 | 150.3 | 35.6 | 2026.15 | 8176.96 | 10537.7 | 0.29 | 1.25 | 21.901 | 14.07 | 1 | 1 | 2630 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4714060.8515 | 375404.858 | 6736.6758 | 34603.2011 | 340801.6569 | 15360.4189 | 0.10021 | -118609.0831 | 118609.0831
C | Xist Rating 7602 | 4.38 | 2327.86 | 150.3 | 35.6 | 2026.39 | 8180.79 | 10537.7 | 0.28 | 1.25 | 21.907 | 14.079 | 1 | 1 | 2640 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4717152.2254 | 378133.0038 | 6788.0027 | 34734.7722 | 343398.2316 | 15346.8941 | 0.10059 | -118504.6485 | 118504.6485
C | Xist Rating 7603 | 4.41 | 2329.36 | 150.3 | 35.6 | 2025.94 | 8173.49 | 10537.7 | 0.28 | 1.25 | 21.907 | 14.09 | 1 | 1 | 2650 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4719143.5984 | 380871.0037 | 6839.5243 | 34866.3433 | 346004.6604 | 15361.0671 | 0.10097 | -118614.0887 | 118614.0887
C | Xist Rating 7604 | 4.44 | 2330.7 | 150.3 | 35.6 | 2025.97 | 8173.93 | 10537.7 | 0.28 | 1.25 | 21.906 | 14.1 | 1 | 1 | 2660 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4721928.279 | 383618.8578 | 6891.2408 | 34997.9144 | 348620.9435 | 15374.1683 | 0.10135 | -118715.2521 | 118715.2521
C | Xist Rating 7605 | 4.49 | 2332.09 | 150.3 | 35.6 | 2026.14 | 8176.81 | 10537.7 | 0.27 | 1.25 | 21.909 | 14.11 | 1 | 1 | 2670 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4725140.8326 | 386376.5661 | 6943.152 | 35129.4855 | 351247.0807 | 15361.1821 | 0.10173 | -118614.9763 | 118614.9763
C | Xist Rating 7606 | 4.53 | 2333.5 | 150.3 | 35.6 | 2026.38 | 8180.61 | 10537.8 | 0.27 | 1.25 | 21.951 | 14.12 | 1 | 1 | 2680 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4728557.73 | 389144.1286 | 6995.258 | 35261.0566 | 353883.072 | 15375.5809 | 0.10211 | -118726.1603 | 118726.1603
C | Xist Rating 7607 | 4.56 | 2334.88 | 150.3 | 35.6 | 2026.34 | 8179.99 | 10537.7 | 0.26 | 1.25 | 21.948 | 14.129 | 1 | 1 | 2690 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4731260.7392 | 391921.5453 | 7047.5588 | 35392.6277 | 356528.9175 | 15361.0219 | 0.10249 | -118613.7391 | 118613.7391
C | Xist Rating 7608 | 4.66 | 2336.08 | 150.3 | 35.6 | 2027.79 | 8203.64 | 10537.7 | 0.26 | 1.25 | 21.953 | 14.139 | 1 | 1 | 2700 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4737079.6632 | 394708.8161 | 7100.0544 | 35524.1988 | 359184.6173 | 15374.1221 | 0.10287 | -118714.8956 | 118714.8956
C | Xist Rating 7609 | 4.72 | 2337.74 | 150.3 | 35.6 | 2028.35 | 8212.94 | 10537.6 | 0.26 | 1.25 | 21.951 | 14.15 | 1 | 1 | 2710 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4741754.929 | 397505.9411 | 7152.7448 | 35655.7699 | 361850.1711 | 15388.0409 | 0.10325 | -118822.3729 | 118822.3729
C | Xist Rating 7610 | 4.71 | 2339.08 | 150.3 | 35.6 | 2027.49 | 8198.78 | 10537.6 | 0.25 | 1.25 | 21.947 | 14.159 | 1 | 1 | 2720 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4742461.3092 | 400312.9202 | 7205.63 | 35787.341 | 364525.5792 | 15373.0604 | 0.10363 | -118706.6974 | 118706.6974
C | Xist Rating 7611 | 4.74 | 2340.4 | 150.3 | 35.6 | 2027.45 | 8198.17 | 10537.6 | 0.25 | 1.25 | 21.984 | 14.169 | 1 | 1 | 2730 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4745043.98 | 403129.7535 | 7258.71 | 35918.9121 | 367210.8414 | 15387.0367 | 0.10402 | -118814.619 | 118814.619
C | Xist Rating 7612 | 4.74 | 2341.69 | 150.3 | 35.6 | 2026.82 | 8187.83 | 10537.6 | 0.25 | 1.25 | 21.977 | 14.178 | 1 | 1 | 2740 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4746184.1258 | 405956.4411 | 7311.9847 | 36050.4832 | 369905.9578 | 15398.6318 | 0.1044 | -118904.1534 | 118904.1534
C | Xist Rating 7613 | 4.73 | 2343.23 | 150.3 | 35.6 | 2025.79 | 8171.12 | 10537.6 | 0.25 | 1.25 | 21.975 | 14.188 | 1 | 1 | 2750 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4746891.9017 | 408792.9827 | 7365.4543 | 36182.0543 | 372610.9284 | 15411.418 | 0.10478 | -119002.8845 | 119002.8845
C | Xist Rating 7614 | 4.73 | 2344.66 | 150.3 | 35.6 | 2025.09 | 8159.72 | 10537.7 | 0.24 | 1.25 | 21.977 | 14.198 | 1 | 1 | 2760 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4748147.5194 | 411639.3786 | 7419.1186 | 36313.6255 | 375325.7531 | 15397.1383 | 0.10516 | -118892.6206 | 118892.6206
C | Xist Rating 7615 | 4.71 | 2345.89 | 150.3 | 35.6 | 2024.19 | 8145.02 | 10537.7 | 0.24 | 1.25 | 21.972 | 14.207 | 1 | 1 | 2770 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4748527.0791 | 414495.6286 | 7472.9777 | 36445.1966 | 378050.4321 | 15408.7001 | 0.10554 | -118981.8974 | 118981.8974
C | Xist Rating 7616 | 4.72 | 2347.44 | 150.3 | 35.6 | 2023.48 | 8133.57 | 10537.7 | 0.24 | 1.25 | 22.016 | 14.217 | 1 | 1 | 2780 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4749997.8912 | 417361.7328 | 7527.0316 | 36576.7677 | 380784.9652 | 15422.7647 | 0.10592 | -119090.5007 | 119090.5007
C | Xist Rating 7617 | 4.74 | 2348.85 | 150.3 | 35.6 | 2023.16 | 8128.41 | 10537.7 | 0.23 | 1.25 | 22.02 | 14.227 | 1 | 1 | 2790 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4752099.366 | 420237.6912 | 7581.2803 | 36708.3388 | 383529.3524 | 15408.0998 | 0.1063 | -118977.2624 | 118977.2624
C | Xist Rating 7618 | 4.72 | 2349.82 | 150.3 | 35.6 | 2022.54 | 8118.39 | 10537.6 | 0.23 | 1.25 | 22.013 | 14.235 | 1 | 1 | 2800 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4752604.9428 | 423123.5037 | 7635.7238 | 36839.9099 | 386283.5939 | 15418.4759 | 0.10668 | -119057.384 | 119057.384
C | Xist Rating 7619 | 4.73 | 2351.57 | 150.3 | 35.6 | 2021.83 | 8106.98 | 10537.7 | 0.23 | 1.25 | 22.02 | 14.246 | 1 | 1 | 2810 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4754474.7731 | 426019.1705 | 7690.3621 | 36971.481 | 389047.6895 | 15432.3716 | 0.10706 | -119164.6832 | 119164.6832
C | Xist Rating 7620 | 4.75 | 2353.04 | 150.3 | 35.6 | 2021.43 | 8100.63 | 10537.7 | 0.23 | 1.25 | 22.026 | 14.256 | 1 | 1 | 2820 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4756505.6472 | 428924.6914 | 7745.1952 | 37103.0521 | 391821.6393 | 15445.2013 | 0.10744 | -119263.7501 | 119263.7501
C | Xist Rating 7621 | 4.75 | 2354.42 | 150.3 | 35.6 | 2020.83 | 8091.05 | 10537.7 | 0.22 | 1.25 | 22.061 | 14.265 | 1 | 1 | 2830 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4757882.5686 | 431840.0664 | 7800.223 | 37234.6232 | 394605.4432 | 15429.8545 | 0.10783 | -119145.2466 | 119145.2466
C | Xist Rating 7622 | 4.79 | 2355.73 | 150.3 | 35.6 | 2020.91 | 8092.24 | 10537.7 | 0.22 | 1.25 | 22.066 | 14.274 | 1 | 1 | 2840 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4760718.3143 | 434765.2957 | 7855.4457 | 37366.1943 | 397399.1014 | 15441.5166 | 0.10821 | -119235.2978 | 119235.2978
C | Xist Rating 7623 | 4.9 | 2357.18 | 150.3 | 35.6 | 2021.89 | 8107.84 | 10537.8 | 0.22 | 1.25 | 22.08 | 14.284 | 1 | 1 | 2850 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4765958.6702 | 437700.3791 | 7910.8631 | 37497.7654 | 400202.6137 | 15454.471 | 0.10859 | -119335.3289 | 119335.3289
C | Xist Rating 7624 | 4.85 | 2358.58 | 150.3 | 35.6 | 2021.05 | 8094.54 | 10537.7 | 0.22 | 1.25 | 22.058 | 14.293 | 1 | 1 | 2860 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4766808.109 | 440645.3167 | 7966.4753 | 37629.3365 | 403015.9802 | 15465.3744 | 0.10897 | -119419.5221 | 119419.5221
C | Xist Rating 7625 | 4.96 | 2359.77 | 150.3 | 35.6 | 2022.63 | 8119.78 | 10537.7 | 0.21 | 1.25 | 22.079 | 14.302 | 1 | 1 | 2870 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4772941.5951 | 443600.1084 | 8022.2824 | 37760.9076 | 405839.2008 | 15449.0866 | 0.10935 | -119293.7516 | 119293.7516
C | Xist Rating 7626 | 5.09 | 2361.28 | 150.3 | 35.6 | 2024.51 | 8150.25 | 10537.8 | 0.21 | 1.25 | 22.146 | 14.312 | 1 | 1 | 2880 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4780434.9728 | 446564.7544 | 8078.2842 | 37892.4787 | 408672.2756 | 15463.3663 | 0.10973 | -119404.0156 | 119404.0156
C | Xist Rating 7627 | 5.12 | 2362.62 | 150.3 | 35.6 | 2024.44 | 8149.05 | 10537.8 | 0.21 | 1.25 | 22.147 | 14.321 | 1 | 1 | 2890 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4782982.4328 | 449539.2545 | 8134.4807 | 38024.0498 | 411515.2046 | 15474.8246 | 0.11011 | -119492.4938 | 119492.4938
C | Xist Rating 7628 | 5.51 | 2364.01 | 150.3 | 35.6 | 2031.36 | 8262.24 | 10538 | 0.21 | 1.25 | 22.206 | 14.331 | 1 | 1 | 2900 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4802155.3536 | 452523.6088 | 8190.8721 | 38155.6209 | 414367.9878 | 15488.9049 | 0.11049 | -119601.2182 | 119601.2182
C | Xist Rating 7629 | 6.1 | 2365.55 | 150.3 | 35.6 | 2042.01 | 8441.13 | 10538.1 | 0.2 | 1.25 | 22.275 | 14.342 | 1 | 1 | 2910 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4830476.7555 | 455517.8172 | 8247.4583 | 38287.1921 | 417230.6252 | 15475.2533 | 0.11087 | -119495.8042 | 119495.8042
C | Xist Rating 7630 | 6.53 | 2366.94 | 150.3 | 35.6 | 2049.8 | 8575.94 | 10538.2 | 0.2 | 1.25 | 22.332 | 14.352 | 1 | 1 | 2920 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4851753.612 | 458521.8798 | 8304.2393 | 38418.7632 | 420103.1167 | 15489.1274 | 0.11125 | -119602.9359 | 119602.9359
C | Xist Rating 7631 | 6.53 | 2368.33 | 150.3 | 35.6 | 2049.37 | 8568.4 | 10538.1 | 0.2 | 1.25 | 22.353 | 14.361 | 1 | 1 | 2930 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4853584.4521 | 461535.7966 | 8361.215 | 38550.3343 | 422985.4624 | 15501.0275 | 0.11164 | -119694.8256 | 119694.8256
C | Xist Rating 7632 | 6.89 | 2369.69 | 150.3 | 35.6 | 2055.47 | 8675.98 | 10538.2 | 0.19 | 1.25 | 22.391 | 14.37 | 1 | 1 | 2940 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4870826.7043 | 464559.5676 | 8418.3855 | 38681.9054 | 425877.6622 | 15483.8716 | 0.11202 | -119562.3525 | 119562.3525
C | Xist Rating 7633 | 7.22 | 2371.1 | 150.3 | 35.6 | 2061.43 | 8783.2 | 10538.3 | 0.19 | 1.25 | 22.435 | 14.38 | 1 | 1 | 2950 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4887856.673 | 467593.1928 | 8475.7509 | 38813.4765 | 428779.7163 | 15497.2691 | 0.1124 | -119665.8038 | 119665.8038
C | Xist Rating 7634 | 7.7 | 2372.47 | 150.3 | 35.6 | 2070.19 | 8944.41 | 10538.2 | 0.19 | 1.25 | 22.49 | 14.39 | 1 | 1 | 2960 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4911463.6693 | 470636.6721 | 8533.311 | 38945.0476 | 431691.6245 | 15510.9513 | 0.11278 | -119771.4543 | 119771.4543
C | Xist Rating 7635 | 8.24 | 2373.86 | 150.3 | 35.6 | 2080.32 | 9136.76 | 10538 | 0.18 | 1.25 | 22.516 | 14.4 | 1 | 1 | 2970 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4938388.4352 | 473690.0056 | 8591.0659 | 39076.6187 | 434613.3869 | 15493.9339 | 0.11316 | -119640.051 | 119640.051
C | Xist Rating 7636 | 8.24 | 2375.08 | 150.3 | 35.6 | 2079.71 | 9125.11 | 10538 | 0.18 | 1.25 | 22.552 | 14.408 | 1 | 1 | 2980 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4939477.6268 | 476753.1932 | 8649.0156 | 39208.1898 | 437545.0034 | 15504.9242 | 0.11354 | -119724.9148 | 119724.9148
C | Xist Rating 7637 | 8.24 | 2376.64 | 150.3 | 35.6 | 2078.96 | 9110.56 | 10538 | 0.18 | 1.25 | 22.547 | 14.418 | 1 | 1 | 2990 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4940939.4944 | 479826.2351 | 8707.16 | 39339.7609 | 440486.4742 | 15517.0082 | 0.11392 | -119818.2239 | 119818.2239
C | Xist Rating 7638 | 8.27 | 2378.07 | 150.3 | 35.6 | 2078.86 | 9108.82 | 10538 | 0.18 | 1.25 | 22.545 | 14.427 | 1 | 1 | 3000 | 152.4 | 2 | 4.7 | 19.05 | 1.3333 | 28 | E | Rod | 4943674.6002 | 482909.1311 | 8765.4993 | 39471.332 | 443437.7991 | 15528.1254 | 0.1143 | -119904.0685 | 119904.0685
C | Xist Rating 7639 | -86.63 | 244.384 | 150.306 | 35.9 | 2353.83 | 6984.82 | 58744.8 | 2.48 | 10.95 | 24.549 | 586.729 | 1 | 1 | 1000 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 575238.3907 | 63756.2321 | 973.9444 | 13437.0492 | 50319.1829 | 612046.1317 | 0.038101 | -4726057.9931 | 4726057.9931
C | Xist Rating 7640 | -86.51 | 246.906 | 150.306 | 35.9 | 2350.91 | 6966.63 | 58283.2 | 2.46 | 10.84 | 24.631 | 575.688 | 1 | 1 | 1010 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 580453.7845 | 64902.0181 | 993.5206 | 13571.4197 | 51330.5985 | 600594.2649 | 0.038482 | -4637629.7136 | 4637629.7136
C | Xist Rating 7641 | -85.51 | 266.069 | 150.306 | 35.9 | 2344.17 | 6965.11 | 54967.1 | 2.47 | 10.07 | 24.686 | 498.907 | 1 | 1 | 1020 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 623710.9677 | 66057.868 | 1013.2917 | 13705.7902 | 52352.0779 | 520901.9509 | 0.038863 | -4022266.7886 | 4022266.7886
C | Xist Rating 7642 | -85.34 | 271.257 | 150.305 | 35.9 | 2327.93 | 6837.87 | 54177.8 | 2.39 | 9.89 | 24.092 | 482.092 | 1 | 1 | 1030 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 631467.308 | 67223.7818 | 1033.2576 | 13840.1607 | 53383.6211 | 503310.2077 | 0.039244 | -3886428.0108 | 3886428.0108
C | Xist Rating 7643 | -85.24 | 273.854 | 150.304 | 35.9 | 2321.81 | 6792.39 | 53793.1 | 2.34 | 9.8 | 23.956 | 474.043 | 1 | 1 | 1040 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 635836.9557 | 68399.7594 | 1053.4182 | 13974.5312 | 54425.2282 | 494906.1527 | 0.039625 | -3821534.1258 | 3821534.1258
C | Xist Rating 7644 | -85.01 | 278.92 | 150.304 | 35.9 | 2315.13 | 6749.26 | 53042.1 | 2.31 | 9.63 | 23.863 | 458.289 | 1 | 1 | 1050 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 645736.0596 | 69585.8008 | 1073.7737 | 14108.9017 | 55476.8991 | 478526.8395 | 0.040006 | -3695057.411 | 3695057.411
C | Xist Rating 7645 | -84.89 | 281.497 | 150.304 | 35.9 | 2314.13 | 6747.65 | 52676 | 2.27 | 9.54 | 23.831 | 450.82 | 1 | 1 | 1060 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 651420.6526 | 70781.906 | 1094.3239 | 14243.2721 | 56538.6339 | 470746.1991 | 0.040387 | -3634977.3685 | 3634977.3685
C | Xist Rating 7646 | -83.89 | 302.076 | 150.304 | 35.9 | 2299.48 | 6679.19 | 49855.9 | 2.25 | 8.9 | 23.594 | 394.418 | 1 | 1 | 1070 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 694617.7205 | 71988.0751 | 1115.0689 | 14377.6426 | 57610.4325 | 412148.624 | 0.040768 | -3182502.4262 | 3182502.4262
C | Xist Rating 7647 | -83.66 | 305.944 | 150.303 | 35.9 | 2303.89 | 6726.65 | 49379.9 | 2.2 | 8.79 | 23.482 | 385.552 | 1 | 1 | 1080 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 704861.3222 | 73204.308 | 1136.0087 | 14512.0131 | 58692.2949 | 402896.0545 | 0.041149 | -3111056.5369 | 3111056.5369
C | Xist Rating 7648 | -83.36 | 311.091 | 150.303 | 35.9 | 2307.87 | 6774.21 | 48760.6 | 2.14 | 8.65 | 23.306 | 374.154 | 1 | 1 | 1090 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 717957.5862 | 74430.6048 | 1157.1433 | 14646.3836 | 59784.2212 | 390995.1657 | 0.04153 | -3019161.028 | 3019161.028
C | Xist Rating 7649 | -83.09 | 314.927 | 150.303 | 35.9 | 2317.71 | 6870.13 | 48307.3 | 2.1 | 8.55 | 23.311 | 365.928 | 1 | 1 | 1100 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 729909.4572 | 75666.9654 | 1178.4727 | 14780.7541 | 60886.2113 | 382429.3856 | 0.041911 | -2953018.3445 | 2953018.3445
C | Xist Rating 7650 | -82.95 | 317.691 | 150.302 | 35.9 | 2317.27 | 6873.15 | 48010.8 | 2.01 | 8.49 | 22.952 | 360.863 | 1 | 1 | 1110 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 736175.8236 | 76913.3898 | 1199.9969 | 14915.1246 | 61998.2652 | 377051.0449 | 0.042292 | -2911488.2236 | 2911488.2236
C | Xist Rating 7651 | -81.76 | 340.616 | 150.303 | 35.9 | 2311.28 | 6884.24 | 45448.2 | 2.06 | 7.92 | 23.265 | 315.753 | 1 | 1 | 1120 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 787258.9485 | 78169.8781 | 1221.7158 | 15049.4951 | 63120.383 | 330315.0444 | 0.042673 | -2550605.2157 | 2550605.2157
C | Xist Rating 7652 | -81.61 | 343.334 | 150.302 | 35.9 | 2314.12 | 6916.36 | 45189.2 | 1.99 | 7.86 | 23.036 | 311.667 | 1 | 1 | 1130 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 794516.0761 | 79436.4302 | 1243.6296 | 15183.8656 | 64252.5646 | 325987.6508 | 0.043054 | -2517190.2297 | 2517190.2297
C | Xist Rating 7653 | -81.35 | 348.551 | 150.302 | 35.9 | 2312.31 | 6914.01 | 44681.3 | 1.94 | 7.75 | 22.824 | 303.492 | 1 | 1 | 1140 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 805957.9628 | 80713.0461 | 1265.7381 | 15318.2361 | 65394.8101 | 317438.601 | 0.043435 | -2451176.7335 | 2451176.7335
C | Xist Rating 7654 | -81.08 | 353.706 | 150.301 | 35.8 | 2312.87 | 6932.88 | 44186.2 | 1.9 | 7.64 | 22.6 | 295.589 | 1 | 1 | 1150 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 818075.9962 | 81999.7259 | 1288.0414 | 15452.6066 | 66547.1194 | 309182.1952 | 0.043816 | -2387422.9561 | 2387422.9561
C | Xist Rating 7655 | -80.84 | 358.939 | 150.301 | 35.8 | 2309.26 | 6914.27 | 43702.9 | 1.84 | 7.53 | 22.414 | 288.064 | 1 | 1 | 1160 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 828883.4751 | 83296.4695 | 1310.5395 | 15586.9771 | 67709.4925 | 301298.4396 | 0.044197 | -2326546.6851 | 2326546.6851
C | Xist Rating 7656 | -79.78 | 379.504 | 150.301 | 35.8 | 2305.35 | 6935.47 | 41832.2 | 1.87 | 7.13 | 22.579 | 259.107 | 1 | 1 | 1170 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 874889.5464 | 84603.277 | 1333.2324 | 15721.3476 | 68881.9294 | 271296.5742 | 0.044578 | -2094880.2329 | 2094880.2329
C | Xist Rating 7657 | -79.65 | 380.956 | 150.301 | 35.8 | 2312.06 | 7000.08 | 41724.5 | 1.82 | 7.11 | 22.481 | 257.684 | 1 | 1 | 1180 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 880793.1294 | 85920.1483 | 1356.1201 | 15855.7181 | 70064.4302 | 269768.5694 | 0.044959 | -2083081.3855 | 2083081.3855
C | Xist Rating 7658 | -79.16 | 391.25 | 150.3 | 35.8 | 2305.45 | 6967.2 | 40885.5 | 1.77 | 6.92 | 22.286 | 245.564 | 1 | 1 | 1190 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 902007.3125 | 87247.0834 | 1379.2026 | 15990.0885 | 71256.9949 | 257121.9397 | 0.04534 | -1985427.463 | 1985427.463
C | Xist Rating 7659 | -78.93 | 393.86 | 150.301 | 35.8 | 2317.22 | 7082.91 | 40682 | 1.74 | 6.88 | 22.333 | 242.729 | 1 | 1 | 1200 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 912660.2692 | 88584.0824 | 1402.4799 | 16124.459 | 72459.6233 | 254163.9146 | 0.045721 | -1962586.3771 | 1962586.3771
C | Xist Rating 7660 | -78.66 | 399.163 | 150.3 | 35.8 | 2316.12 | 7086.76 | 40280.8 | 1.68 | 6.8 | 22.162 | 237.214 | 1 | 1 | 1210 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 924509.4076 | 89931.1452 | 1425.9519 | 16258.8295 | 73672.3156 | 248365.7554 | 0.046102 | -1917814.5285 | 1917814.5285
C | Xist Rating 7661 | -77.54 | 422.442 | 150.3 | 35.8 | 2304.01 | 7037.99 | 38537.6 | 1.68 | 6.43 | 22.167 | 213.283 | 1 | 1 | 1220 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 973310.5924 | 91288.2718 | 1449.6188 | 16393.2 | 74895.0718 | 223530.5983 | 0.046483 | -1726044.0284 | 1726044.0284
C | Xist Rating 7662 | -77.21 | 427.595 | 150.3 | 35.8 | 2310.16 | 7109.66 | 38183.3 | 1.66 | 6.35 | 22.189 | 208.695 | 1 | 1 | 1230 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 987812.8652 | 92655.4623 | 1473.4804 | 16527.5705 | 76127.8918 | 218760.2307 | 0.046864 | -1689208.5147 | 1689208.5147
C | Xist Rating 7663 | -76.94 | 432.887 | 150.3 | 35.8 | 2310.69 | 7128.71 | 37835.3 | 1.61 | 6.28 | 22.069 | 204.318 | 1 | 1 | 1240 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1000267.662 | 94032.7166 | 1497.5369 | 16661.941 | 77370.7756 | 214158.8291 | 0.047245 | -1653677.7111 | 1653677.7111
C | Xist Rating 7664 | -76.76 | 435.641 | 150.3 | 35.8 | 2315.05 | 7177.48 | 37664.1 | 1.57 | 6.24 | 21.994 | 202.255 | 1 | 1 | 1250 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1008530.6971 | 95420.0347 | 1521.7881 | 16796.3115 | 78623.7232 | 211976.2742 | 0.047626 | -1636824.6004 | 1636824.6004
C | Xist Rating 7665 | -76.35 | 443.393 | 150.299 | 35.8 | 2315.37 | 7201.95 | 37161.2 | 1.54 | 6.14 | 21.947 | 195.952 | 1 | 1 | 1260 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1026618.8504 | 96817.4167 | 1546.2341 | 16930.682 | 79886.7347 | 205404.7429 | 0.048007 | -1586080.9777 | 1586080.9777
C | Xist Rating 7666 | -75.26 | 465.437 | 150.3 | 35.8 | 2308.2 | 7194.43 | 35777.3 | 1.55 | 5.85 | 22.016 | 178.93 | 1 | 1 | 1270 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1074321.6834 | 98224.8625 | 1570.8749 | 17065.0525 | 81159.8101 | 187761.155 | 0.048388 | -1449841.869 | 1449841.869
C | Xist Rating 7667 | -75 | 470.798 | 150.299 | 35.8 | 2306.71 | 7194.03 | 35477.1 | 1.51 | 5.79 | 21.886 | 175.51 | 1 | 1 | 1280 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1085994.4546 | 99642.3722 | 1595.7105 | 17199.423 | 82442.9492 | 184162.9967 | 0.048769 | -1422057.8444 | 1422057.8444
C | Xist Rating 7668 | -74.73 | 476.107 | 150.299 | 35.8 | 2306.47 | 7205.81 | 35182.6 | 1.47 | 5.73 | 21.835 | 172.171 | 1 | 1 | 1290 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1098126.5123 | 101069.9457 | 1620.7408 | 17333.7935 | 83736.1522 | 180655.3078 | 0.04915 | -1394972.4001 | 1394972.4001
C | Xist Rating 7669 | -74.32 | 483.837 | 150.299 | 35.8 | 2306.77 | 7229.92 | 34751 | 1.45 | 5.64 | 21.867 | 167.247 | 1 | 1 | 1300 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1116100.6765 | 102507.583 | 1645.966 | 17468.164 | 85039.4191 | 175533.3855 | 0.049531 | -1355422.2744 | 1355422.2744
C | Xist Rating 7670 | -74.06 | 487.898 | 150.299 | 35.8 | 2312.06 | 7292.88 | 34539.9 | 1.42 | 5.59 | 21.828 | 164.954 | 1 | 1 | 1310 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1128049.4499 | 103955.2842 | 1671.3859 | 17602.5344 | 86352.7497 | 173124.5483 | 0.049912 | -1336821.8714 | 1336821.8714
C | Xist Rating 7671 | -72.97 | 510.04 | 150.299 | 35.8 | 2304.71 | 7282 | 33362.7 | 1.42 | 5.35 | 21.879 | 151.883 | 1 | 1 | 1320 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1175494.2884 | 105413.0492 | 1697.0007 | 17736.9049 | 87676.1442 | 159568.5141 | 0.050293 | -1232145.7693 | 1232145.7693
C | Xist Rating 7672 | -72.57 | 517.987 | 150.299 | 35.8 | 2303.9 | 7295.11 | 32980 | 1.38 | 5.28 | 21.767 | 147.897 | 1 | 1 | 1330 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1193390.2493 | 106880.878 | 1722.8102 | 17871.2754 | 89009.6026 | 155381.5971 | 0.050674 | -1199815.5054 | 1199815.5054
C | Xist Rating 7673 | -72.14 | 525.833 | 150.299 | 35.8 | 2306.29 | 7340.63 | 32606.8 | 1.35 | 5.2 | 21.669 | 144.042 | 1 | 1 | 1340 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1212723.3896 | 108358.7707 | 1748.8145 | 18005.6459 | 90353.1248 | 151344.4806 | 0.051055 | -1168641.9623 | 1168641.9623
C | Xist Rating 7674 | -71.86 | 529.911 | 150.298 | 35.8 | 2312.16 | 7411.39 | 32423.6 | 1.32 | 5.16 | 21.627 | 142.231 | 1 | 1 | 1350 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1225239.0178 | 109846.7272 | 1775.0136 | 18140.0164 | 91706.7108 | 149434.1799 | 0.051436 | -1153891.1264 | 1153891.1264
C | Xist Rating 7675 | -71.57 | 532.467 | 150.299 | 35.8 | 2326.01 | 7563.14 | 32303 | 1.31 | 5.14 | 21.72 | 141.008 | 1 | 1 | 1360 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1238523.5667 | 111344.7475 | 1801.4075 | 18274.3869 | 93070.3606 | 148171.1355 | 0.051817 | -1144138.2324 | 1144138.2324
C | Xist Rating 7676 | -70.21 | 563.838 | 150.299 | 35.8 | 2302.23 | 7404.8 | 30902.2 | 1.3 | 4.86 | 21.63 | 127.018 | 1 | 1 | 1370 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1298084.7587 | 112852.8317 | 1827.9962 | 18408.7574 | 94444.0743 | 133634.7735 | 0.052198 | -1031892.2984 | 1031892.2984
C | Xist Rating 7677 | -70.08 | 566.655 | 150.299 | 35.8 | 2301.7 | 7406.56 | 30793.8 | 1.27 | 4.84 | 21.583 | 126.053 | 1 | 1 | 1380 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1304269.8135 | 114370.9798 | 1854.7797 | 18543.1279 | 95827.8519 | 132601.3948 | 0.052579 | -1023912.8219 | 1023912.8219
C | Xist Rating 7678 | -69.73 | 573.312 | 150.298 | 35.8 | 2302.74 | 7435.35 | 30526.6 | 1.25 | 4.78 | 21.541 | 123.573 | 1 | 1 | 1390 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1320188.4749 | 115899.1916 | 1881.7579 | 18677.4984 | 97221.6932 | 130008.0391 | 0.05296 | -1003887.617 | 1003887.617
C | Xist Rating 7679 | -69.37 | 579.965 | 150.298 | 35.8 | 2303.97 | 7466.25 | 30264.9 | 1.22 | 4.73 | 21.506 | 121.168 | 1 | 1 | 1400 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1336221.9611 | 117437.4673 | 1908.931 | 18811.8689 | 98625.5984 | 127479.2866 | 0.053341 | -984361.26 | 984361.26
C | Xist Rating 7680 | -68.95 | 587.872 | 150.298 | 35.8 | 2304.87 | 7497.67 | 29957.2 | 1.2 | 4.67 | 21.483 | 118.359 | 1 | 1 | 1410 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1354968.5366 | 118985.8068 | 1936.2988 | 18946.2394 | 100039.5675 | 124544.9761 | 0.053722 | -961703.2926 | 961703.2926
C | Xist Rating 7681 | -67.79 | 611.394 | 150.298 | 35.8 | 2299.81 | 7511.24 | 29051.6 | 1.21 | 4.49 | 21.558 | 110.108 | 1 | 1 | 1420 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1406090.0351 | 120544.2102 | 1963.8614 | 19080.6099 | 101463.6003 | 116007.3318 | 0.054103 | -895777.8659 | 895777.8659
C | Xist Rating 7682 | -67.59 | 615.712 | 150.298 | 35.7 | 2298.74 | 7510.72 | 28910.4 | 1.17 | 4.47 | 21.463 | 108.967 | 1 | 1 | 1430 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1415361.8029 | 122112.6774 | 1991.6188 | 19214.9803 | 102897.6971 | 114771.699 | 0.054484 | -886236.6369 | 886236.6369
C | Xist Rating 7683 | -67.06 | 626.176 | 150.298 | 35.7 | 2297.85 | 7530.33 | 28541.6 | 1.15 | 4.39 | 21.444 | 105.794 | 1 | 1 | 1440 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1438858.5216 | 123691.2084 | 2019.571 | 19349.3508 | 104341.8576 | 111458.6817 | 0.054865 | -860654.3957 | 860654.3957
C | Xist Rating 7684 | -66.7 | 632.867 | 150.298 | 35.7 | 2299.22 | 7563.38 | 28316.6 | 1.13 | 4.35 | 21.418 | 103.918 | 1 | 1 | 1450 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1455100.4637 | 125279.8033 | 2047.718 | 19483.7213 | 105796.082 | 109491.7278 | 0.055246 | -845466.0987 | 845466.0987
C | Xist Rating 7685 | -66.4 | 636.826 | 150.298 | 35.7 | 2306.88 | 7658.1 | 28183.4 | 1.12 | 4.32 | 21.454 | 102.819 | 1 | 1 | 1460 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1469081.1629 | 126878.462 | 2076.0598 | 19618.0918 | 107260.3702 | 108349.8885 | 0.055627 | -836649.1187 | 836649.1187
C | Xist Rating 7686 | -65.24 | 663.333 | 150.298 | 35.7 | 2291.24 | 7562.36 | 27310 | 1.11 | 4.16 | 21.417 | 95.575 | 1 | 1 | 1470 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1519855.1029 | 128487.1846 | 2104.5964 | 19752.4623 | 108734.7223 | 100820.9339 | 0.056008 | -778512.5272 | 778512.5272
C | Xist Rating 7687 | -64.82 | 671.283 | 150.298 | 35.7 | 2292.64 | 7599.43 | 27065.8 | 1.09 | 4.11 | 21.405 | 93.65 | 1 | 1 | 1480 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1539010.2571 | 130105.971 | 2133.3277 | 19886.8328 | 110219.1382 | 98803.1966 | 0.056389 | -762932.0941 | 762932.0941
C | Xist Rating 7688 | -64.46 | 677.976 | 150.298 | 35.7 | 2293.91 | 7631.87 | 26866 | 1.07 | 4.07 | 21.389 | 92.105 | 1 | 1 | 1490 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1555215.9262 | 131734.8212 | 2162.2539 | 20021.2033 | 111713.6179 | 97179.4391 | 0.05677 | -750393.8691 | 750393.8691
C | Xist Rating 7689 | -64.12 | 684.761 | 150.298 | 35.7 | 2293.68 | 7647.67 | 26669.5 | 1.05 | 4.03 | 21.354 | 90.613 | 1 | 1 | 1500 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1570622.6105 | 133373.7353 | 2191.3748 | 20155.5738 | 113218.1615 | 95609.0245 | 0.057151 | -738267.5441 | 738267.5441
C | Xist Rating 7690 | -63.67 | 692.739 | 150.298 | 35.7 | 2296.55 | 7701.93 | 26438.3 | 1.03 | 3.99 | 21.353 | 88.848 | 1 | 1 | 1510 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1590909.7505 | 135022.7132 | 2220.6906 | 20289.9443 | 114732.7689 | 93757.1485 | 0.057532 | -723967.8487 | 723967.8487
C | Xist Rating 7691 | -62.36 | 718.928 | 150.298 | 35.7 | 2293.11 | 7739.56 | 25680.5 | 1.04 | 3.84 | 21.436 | 83.047 | 1 | 1 | 1520 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1648580.9861 | 136681.7549 | 2250.2011 | 20424.3148 | 116257.4401 | 87763.1076 | 0.057913 | -677683.4533 | 677683.4533
C | Xist Rating 7692 | -62.01 | 727.25 | 150.298 | 35.7 | 2289.04 | 7715.64 | 25468 | 1.01 | 3.8 | 21.354 | 81.55 | 1 | 1 | 1530 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1664704.34 | 138350.8605 | 2279.9064 | 20558.6853 | 117792.1752 | 86168.6849 | 0.058294 | -665371.7443 | 665371.7443
C | Xist Rating 7693 | -61.68 | 731.484 | 150.298 | 35.7 | 2296.13 | 7808.16 | 25363.1 | 0.99 | 3.78 | 21.346 | 80.837 | 1 | 1 | 1540 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1679582.3569 | 140030.0299 | 2309.8065 | 20693.0558 | 119336.9741 | 85407.8751 | 0.058675 | -659496.9724 | 659496.9724
C | Xist Rating 7694 | -61.03 | 744.629 | 150.298 | 35.7 | 2294.3 | 7824.78 | 25021 | 0.98 | 3.72 | 21.311 | 78.384 | 1 | 1 | 1550 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1708402.3147 | 141719.2631 | 2339.9013 | 20827.4263 | 120891.8369 | 82852.6971 | 0.059056 | -639766.5655 | 639766.5655
C | Xist Rating 7695 | -60.7 | 748.638 | 150.298 | 35.7 | 2303.5 | 7944.66 | 24919.5 | 0.97 | 3.7 | 21.362 | 77.688 | 1 | 1 | 1560 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1724487.633 | 143418.5602 | 2370.191 | 20961.7967 | 122456.7634 | 82127.821 | 0.059437 | -634169.2642 | 634169.2642
C | Xist Rating 7696 | -59.44 | 779.287 | 150.298 | 35.7 | 2284.45 | 7810 | 24161 | 0.96 | 3.56 | 21.288 | 72.4 | 1 | 1 | 1570 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1780242.1871 | 145127.9211 | 2400.6755 | 21096.1672 | 124031.7539 | 76625.4967 | 0.059818 | -591681.7743 | 591681.7743
C | Xist Rating 7697 | -59.03 | 786.1 | 150.298 | 35.7 | 2288.52 | 7876.67 | 24006.4 | 0.94 | 3.53 | 21.283 | 71.391 | 1 | 1 | 1580 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1799005.572 | 146847.3459 | 2431.3547 | 21230.5377 | 125616.8081 | 75556.3259 | 0.0602 | -583425.921 | 583425.921
C | Xist Rating 7698 | -58.64 | 792.949 | 150.298 | 35.7 | 2291.18 | 7927.43 | 23854 | 0.93 | 3.5 | 21.272 | 70.407 | 1 | 1 | 1590 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 30 | E | Rod | 1816788.8898 | 148576.8344 | 2462.2288 | 21364.9082 | 127211.9262 | 74527.5134 | 0.060581 | -575481.703 | 575481.703
C | Xist Rating 7699 | -58.1 | 802.211 | 150.298 | 35.7 | 2295.17 | 8002.76 | 23644.2 | 0.91 | 3.46 | 21.272 | 69.031 | 1 | 1 | 1600 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 1841210.6209 | 150316.3869 | 2493.2976 | 21499.2787 | 128817.1082 | 73076.8949 | 0.060962 | -564280.4115 | 564280.4115
C | Xist Rating 7700 | -57.83 | 806.64 | 150.298 | 35.7 | 2297.12 | 8038.27 | 23555.9 | 0.89 | 3.45 | 21.248 | 68.505 | 1 | 1 | 1610 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 1852948.8768 | 152066.0031 | 2524.5612 | 21633.6492 | 130432.3539 | 72507.0771 | 0.061343 | -559880.4299 | 559880.4299
C | Xist Rating 7701 | -56.31 | 840.961 | 150.298 | 35.7 | 2283.63 | 7976.54 | 22804.4 | 0.9 | 3.31 | 21.282 | 63.635 | 1 | 1 | 1620 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 1920443.7684 | 153825.6832 | 2556.0196 | 21768.0197 | 132057.6635 | 67475.7179 | 0.061724 | -521029.6081 | 521029.6081
C | Xist Rating 7702 | -55.94 | 845.046 | 150.298 | 35.7 | 2292.27 | 8094.92 | 22722.7 | 0.89 | 3.29 | 21.307 | 63.148 | 1 | 1 | 1630 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 1937073.5944 | 155595.4272 | 2587.6728 | 21902.3902 | 133693.037 | 66964.631 | 0.062105 | -517083.1302 | 517083.1302
C | Xist Rating 7703 | -55.58 | 852.042 | 150.298 | 35.7 | 2292.91 | 8122.72 | 22587.9 | 0.87 | 3.27 | 21.283 | 62.354 | 1 | 1 | 1640 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 1953655.6222 | 157375.2349 | 2619.5208 | 22036.7607 | 135338.4743 | 66115.7019 | 0.062486 | -510527.925 | 510527.925
C | Xist Rating 7704 | -55.13 | 861.661 | 150.298 | 35.7 | 2291.29 | 8130.3 | 22402.3 | 0.85 | 3.23 | 21.255 | 61.25 | 1 | 1 | 1650 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 1974315.2327 | 159165.1065 | 2651.5635 | 22171.1312 | 136993.9754 | 64944.2571 | 0.062867 | -501482.3388 | 501482.3388
C | Xist Rating 7705 | -54.62 | 871.037 | 150.298 | 35.7 | 2292.83 | 8177.71 | 22220.3 | 0.84 | 3.2 | 21.26 | 60.162 | 1 | 1 | 1660 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 1997139.7647 | 160965.042 | 2683.8011 | 22305.5017 | 138659.5403 | 63806.9661 | 0.063248 | -492700.479 | 492700.479
C | Xist Rating 7706 | -53.27 | 901.729 | 150.298 | 35.7 | 2281.28 | 8124.5 | 21632.5 | 0.84 | 3.09 | 21.284 | 56.649 | 1 | 1 | 1670 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2057096.3331 | 162775.0413 | 2716.2334 | 22439.8722 | 140335.1691 | 60168.2353 | 0.063629 | -464603.1638 | 464603.1638
C | Xist Rating 7707 | -52.95 | 905.925 | 150.298 | 35.7 | 2287.27 | 8212.94 | 21560 | 0.82 | 3.08 | 21.295 | 56.255 | 1 | 1 | 1680 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2072095.0747 | 164595.1044 | 2748.8606 | 22574.2426 | 142020.8617 | 59735.7041 | 0.06401 | -461263.2731 | 461263.2731
C | Xist Rating 7708 | -52.42 | 918.217 | 150.298 | 35.7 | 2282.81 | 8191.6 | 21345.6 | 0.81 | 3.04 | 21.262 | 55.053 | 1 | 1 | 1690 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2096114.9498 | 166425.2313 | 2781.6825 | 22708.6131 | 143716.6182 | 58477.0996 | 0.064391 | -451544.6628 | 451544.6628
C | Xist Rating 7709 | -51.96 | 926.351 | 150.298 | 35.7 | 2285.15 | 8245.99 | 21205.4 | 0.8 | 3.02 | 21.266 | 54.277 | 1 | 1 | 1700 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2116850.9877 | 168265.4221 | 2814.6992 | 22842.9836 | 145422.4385 | 57662.9865 | 0.064772 | -445258.2966 | 445258.2966
C | Xist Rating 7710 | -51.48 | 935.92 | 150.298 | 35.7 | 2284.95 | 8271.6 | 21044.4 | 0.79 | 2.99 | 21.256 | 53.396 | 1 | 1 | 1710 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2138530.404 | 170115.6768 | 2847.9107 | 22977.3541 | 147138.3226 | 56738.7893 | 0.065153 | -438121.8913 | 438121.8913
C | Xist Rating 7711 | -50.25 | 964.143 | 150.298 | 35.7 | 2275.21 | 8230.54 | 20566.7 | 0.78 | 2.9 | 21.282 | 50.746 | 1 | 1 | 1720 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2193627.795 | 171975.9952 | 2881.317 | 23111.7246 | 148864.2706 | 53979.4711 | 0.065534 | -416815.1674 | 416815.1674
C | Xist Rating 7712 | -49.67 | 976.305 | 150.298 | 35.7 | 2274.25 | 8253.87 | 20373.7 | 0.77 | 2.87 | 21.274 | 49.726 | 1 | 1 | 1730 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2220361.6462 | 173846.3775 | 2914.9181 | 23246.0951 | 150600.2824 | 52910.6624 | 0.065915 | -408562.1101 | 408562.1101
C | Xist Rating 7713 | -49.3 | 981.907 | 150.298 | 35.7 | 2278.04 | 8320.15 | 20289.7 | 0.76 | 2.85 | 21.274 | 49.301 | 1 | 1 | 1740 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2236823.4223 | 175726.8237 | 2948.714 | 23380.4656 | 152346.3581 | 52460.0507 | 0.066296 | -405082.6056 | 405082.6056
C | Xist Rating 7714 | -48.8 | 992.942 | 150.298 | 35.7 | 2275.54 | 8319.21 | 20123.3 | 0.75 | 2.82 | 21.253 | 48.448 | 1 | 1 | 1750 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2259479.2387 | 177617.3336 | 2982.7046 | 23514.8361 | 154102.4976 | 51563.5354 | 0.066677 | -398159.9524 | 398159.9524
C | Xist Rating 7715 | -48.45 | 1001.19 | 150.298 | 35.7 | 2273.64 | 8318.26 | 20000.2 | 0.74 | 2.8 | 21.246 | 47.824 | 1 | 1 | 1760 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2276345.6316 | 179517.9075 | 3016.8901 | 23649.2066 | 155868.7009 | 50905.4819 | 0.067058 | -393078.6375 | 393078.6375
C | Xist Rating 7716 | -46.98 | 1034.65 | 150.298 | 35.7 | 2262.78 | 8274.98 | 19497.1 | 0.74 | 2.71 | 21.282 | 45.22 | 1 | 1 | 1770 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2341185.327 | 181428.5451 | 3051.2703 | 23783.5771 | 157644.968 | 48210.393 | 0.067439 | -372267.8752 | 372267.8752
C | Xist Rating 7717 | -46.54 | 1043.01 | 150.298 | 35.7 | 2263.65 | 8310.63 | 19382.8 | 0.73 | 2.69 | 21.273 | 44.671 | 1 | 1 | 1780 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2361009.5865 | 183349.2466 | 3085.8453 | 23917.9476 | 159431.299 | 47629.812 | 0.06782 | -367784.7826 | 367784.7826
C | Xist Rating 7718 | -46.49 | 1047.46 | 150.299 | 35.7 | 2257.22 | 8236.23 | 19327 | 0.71 | 2.68 | 21.536 | 44.41 | 1 | 1 | 1790 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2364347.6612 | 185280.0119 | 3120.6151 | 24052.3181 | 161227.6938 | 47346.57 | 0.068201 | -365597.6637 | 365597.6637
C | Xist Rating 7719 | -45.84 | 1062.33 | 150.299 | 35.6 | 2255.17 | 8252.24 | 19122 | 0.7 | 2.65 | 21.517 | 43.412 | 1 | 1 | 1800 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2395734.7461 | 187220.8411 | 3155.5797 | 24186.6886 | 163034.1525 | 46298.5533 | 0.068582 | -357505.156 | 357505.156
C | Xist Rating 7720 | -45.44 | 1070.57 | 150.299 | 35.6 | 2255.94 | 8286.32 | 19012.1 | 0.7 | 2.63 | 21.512 | 42.893 | 1 | 1 | 1810 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2415141.6858 | 189171.7341 | 3190.7391 | 24321.059 | 164850.675 | 45766.0401 | 0.068963 | -353393.2302 | 353393.2302
C | Xist Rating 7721 | -43.72 | 1104.28 | 150.299 | 35.6 | 2253.79 | 8358.55 | 18562.5 | 0.7 | 2.55 | 21.297 | 40.739 | 1 | 1 | 1820 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2488815.2212 | 191132.6909 | 3226.0933 | 24455.4295 | 166677.2614 | 43523.5864 | 0.069344 | -336077.5976 | 336077.5976
C | Xist Rating 7722 | -43.98 | 1098.93 | 150.299 | 35.6 | 2258.08 | 8401.69 | 18631.1 | 0.69 | 2.56 | 21.58 | 41.066 | 1 | 1 | 1830 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2481471.8544 | 193103.7116 | 3261.6423 | 24589.8 | 168513.9115 | 43868.4059 | 0.069725 | -338740.2023 | 338740.2023
C | Xist Rating 7723 | -43.52 | 1105.71 | 150.299 | 35.6 | 2262.58 | 8485.01 | 18545.1 | 0.68 | 2.55 | 21.609 | 40.673 | 1 | 1 | 1840 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2501757.3318 | 195084.7961 | 3297.386 | 24724.1705 | 170360.6255 | 43450.7784 | 0.070106 | -335515.393 | 335515.393
C | Xist Rating 7724 | -43.01 | 1116.86 | 150.299 | 35.6 | 2260.09 | 8482.78 | 18409.3 | 0.67 | 2.52 | 21.596 | 40.061 | 1 | 1 | 1850 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2524204.1174 | 197075.9444 | 3333.3246 | 24858.541 | 172217.4034 | 42803.1622 | 0.070487 | -330514.6729 | 330514.6729
C | Xist Rating 7725 | -42.45 | 1129.36 | 150.299 | 35.6 | 2256.86 | 8474.25 | 18259.2 | 0.66 | 2.5 | 21.582 | 39.389 | 1 | 1 | 1860 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2548807.4096 | 199077.1566 | 3369.4579 | 24992.9115 | 174084.2451 | 42093.0013 | 0.070868 | -325030.9987 | 325030.9987
C | Xist Rating 7726 | -41.05 | 1160.33 | 150.299 | 35.6 | 2250.8 | 8484.63 | 17879.6 | 0.66 | 2.43 | 21.636 | 37.653 | 1 | 1 | 1870 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2611670.764 | 201088.4326 | 3405.7861 | 25127.282 | 175961.1506 | 40299.5404 | 0.071249 | -311182.3685 | 311182.3685
C | Xist Rating 7727 | -40.52 | 1172.82 | 150.299 | 35.6 | 2247.47 | 8474.05 | 17738.5 | 0.65 | 2.41 | 21.626 | 37.048 | 1 | 1 | 1880 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2635877.7654 | 203109.7724 | 3442.309 | 25261.6525 | 177848.12 | 39658.8692 | 0.07163 | -306235.2755 | 306235.2755
C | Xist Rating 7728 | -40.01 | 1181.1 | 150.299 | 35.6 | 2250.87 | 8547.25 | 17646.5 | 0.64 | 2.39 | 21.644 | 36.657 | 1 | 1 | 1890 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2658502.557 | 205141.1761 | 3479.0267 | 25396.023 | 179745.1531 | 39241.772 | 0.072011 | -303014.5614 | 303014.5614
C | Xist Rating 7729 | -39.62 | 1189.84 | 150.299 | 35.6 | 2248.94 | 8544.16 | 17555.4 | 0.63 | 2.38 | 21.63 | 36.286 | 1 | 1 | 1900 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2675878.7696 | 207182.6436 | 3515.9392 | 25530.3935 | 181652.2502 | 38843.5136 | 0.072392 | -299939.3155 | 299939.3155
C | Xist Rating 7730 | -39.18 | 1198.3 | 150.299 | 35.7 | 2249.75 | 8580.65 | 17465.1 | 0.62 | 2.36 | 21.634 | 35.914 | 1 | 1 | 1910 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2695875.425 | 209234.175 | 3553.0464 | 25664.764 | 183569.411 | 38444.9942 | 0.072773 | -296862.0542 | 296862.0542
C | Xist Rating 7731 | -37.55 | 1235.91 | 150.299 | 35.6 | 2240.39 | 8561.95 | 17050.2 | 0.62 | 2.29 | 21.677 | 34.128 | 1 | 1 | 1920 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2768920.4049 | 211295.7702 | 3590.3485 | 25799.1345 | 185496.6357 | 36598.5428 | 0.073154 | -282604.2462 | 282604.2462
C | Xist Rating 7732 | -37.04 | 1248.47 | 150.299 | 35.7 | 2236.26 | 8538.52 | 16923.9 | 0.61 | 2.27 | 21.668 | 33.62 | 1 | 1 | 1930 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2791903.5222 | 213367.4292 | 3627.8454 | 25933.5049 | 187433.9243 | 36057.7819 | 0.073535 | -278428.6336 | 278428.6336
C | Xist Rating 7733 | -36.66 | 1252.57 | 150.299 | 35.7 | 2242.58 | 8644.01 | 16882.1 | 0.6 | 2.26 | 21.711 | 33.458 | 1 | 1 | 1940 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2808988.4306 | 215449.1521 | 3665.537 | 26067.8754 | 189381.2767 | 35878.8709 | 0.073916 | -277047.1307 | 277047.1307
C | Xist Rating 7734 | -36.28 | 1264.29 | 150.299 | 35.7 | 2235.79 | 8576.71 | 16772.2 | 0.59 | 2.24 | 21.681 | 33.036 | 1 | 1 | 1950 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2826686.9391 | 217540.9388 | 3703.4235 | 26202.2459 | 191338.6929 | 35425.9394 | 0.074297 | -273549.7138 | 273549.7138
C | Xist Rating 7735 | -35.68 | 1278.09 | 150.299 | 35.7 | 2232.76 | 8573.07 | 16637 | 0.58 | 2.22 | 21.711 | 32.5 | 1 | 1 | 1960 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2853668.2284 | 219642.7894 | 3741.5047 | 26336.6164 | 193306.1729 | 34857.5187 | 0.074678 | -269160.5197 | 269160.5197
C | Xist Rating 7736 | -34.21 | 1311.93 | 150.299 | 35.7 | 2225.45 | 8569.01 | 16303.2 | 0.58 | 2.16 | 21.782 | 31.154 | 1 | 1 | 1970 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2919634.6185 | 221754.7037 | 3779.7807 | 26470.9869 | 195283.7168 | 33468.9807 | 0.075059 | -258438.5974 | 258438.5974
C | Xist Rating 7737 | -33.72 | 1321.72 | 150.299 | 35.7 | 2225.74 | 8601.77 | 16214.1 | 0.57 | 2.15 | 21.814 | 30.82 | 1 | 1 | 1980 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2941805.0728 | 223876.6819 | 3818.2515 | 26605.3574 | 197271.3245 | 33110.0719 | 0.07544 | -255667.1987 | 255667.1987
C | Xist Rating 7738 | -33.21 | 1334.48 | 150.299 | 35.7 | 2222.05 | 8583.51 | 16101.3 | 0.56 | 2.13 | 21.817 | 30.4 | 1 | 1 | 1990 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2965281.284 | 226008.724 | 3856.9171 | 26739.7279 | 199268.9961 | 32660.1676 | 0.075821 | -252193.1569 | 252193.1569
C | Xist Rating 7739 | -32.76 | 1344.4 | 150.299 | 35.7 | 2220.86 | 8594.13 | 16014.9 | 0.56 | 2.12 | 21.822 | 30.082 | 1 | 1 | 2000 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 2985724.184 | 228150.8299 | 3895.7775 | 26874.0984 | 201276.7315 | 32335.6526 | 0.076202 | -249687.3379 | 249687.3379
C | Xist Rating 7740 | -32.35 | 1351.65 | 150.299 | 35.7 | 2222.61 | 8640.86 | 15953.7 | 0.55 | 2.11 | 21.829 | 29.865 | 1 | 1 | 2010 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3004190.8065 | 230302.9996 | 3934.8326 | 27008.4689 | 203294.5307 | 32096.4619 | 0.076583 | -247840.3711 | 247840.3711
C | Xist Rating 7741 | -30.77 | 1389.7 | 150.299 | 35.7 | 2212.88 | 8610.11 | 15614.8 | 0.55 | 2.05 | 21.866 | 28.578 | 1 | 1 | 2020 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3075239.336 | 232465.2332 | 3974.0826 | 27142.8394 | 205322.3938 | 30767.1387 | 0.076964 | -237575.6895 | 237575.6895
C | Xist Rating 7742 | -30.13 | 1403.45 | 150.299 | 35.7 | 2211.81 | 8634.58 | 15499.8 | 0.54 | 2.03 | 21.877 | 28.163 | 1 | 1 | 2030 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3104164.7445 | 234637.5306 | 4013.5273 | 27277.2099 | 207360.3207 | 30322.1963 | 0.077345 | -234139.9626 | 234139.9626
C | Xist Rating 7743 | -29.78 | 1412.38 | 150.299 | 35.7 | 2209.45 | 8623.03 | 15431.6 | 0.53 | 2.02 | 21.865 | 27.934 | 1 | 1 | 2040 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3120582.991 | 236819.8918 | 4053.1669 | 27411.5804 | 209408.3114 | 30069.0892 | 0.077726 | -232185.5363 | 232185.5363
C | Xist Rating 7744 | -29.24 | 1420.51 | 150.299 | 35.7 | 2214.28 | 8721.92 | 15364.2 | 0.53 | 2.01 | 21.895 | 27.695 | 1 | 1 | 2050 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3145406.8828 | 239012.3169 | 4093.0012 | 27545.9509 | 211466.366 | 29827.5436 | 0.078107 | -230320.3854 | 230320.3854
C | Xist Rating 7745 | -28.76 | 1433.66 | 150.299 | 35.7 | 2209.18 | 8680.15 | 15264.2 | 0.52 | 1.99 | 21.867 | 27.356 | 1 | 1 | 2060 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3167212.9988 | 241214.8058 | 4133.0303 | 27680.3213 | 213534.4844 | 29459.1322 | 0.078488 | -227475.6103 | 227475.6103
C | Xist Rating 7746 | -27.11 | 1474.49 | 150.299 | 35.7 | 2198.65 | 8641.69 | 14936 | 0.52 | 1.94 | 21.904 | 26.182 | 1 | 1 | 2070 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3241887.4385 | 243427.3585 | 4173.2542 | 27814.6918 | 215612.6667 | 28246.8172 | 0.078869 | -218114.4354 | 218114.4354
C | Xist Rating 7747 | -26.65 | 1483.23 | 150.299 | 35.7 | 2199.7 | 8682.34 | 14873.4 | 0.51 | 1.93 | 21.907 | 25.98 | 1 | 1 | 2080 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3262661.031 | 245649.9751 | 4213.6729 | 27949.0623 | 217700.9128 | 28021.8665 | 0.07925 | -216377.4255 | 216377.4255
C | Xist Rating 7748 | -26.16 | 1494.58 | 150.299 | 35.7 | 2198.08 | 8689.6 | 14790.7 | 0.5 | 1.91 | 21.905 | 25.707 | 1 | 1 | 2090 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3285206.4064 | 247882.6555 | 4254.2864 | 28083.4328 | 219799.2227 | 27722.7476 | 0.079631 | -214067.7084 | 214067.7084
C | Xist Rating 7749 | -25.7 | 1505.94 | 150.299 | 35.7 | 2195.66 | 8684.32 | 14709.2 | 0.5 | 1.9 | 21.909 | 25.44 | 1 | 1 | 2100 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3306532.2204 | 250125.3998 | 4295.0947 | 28217.8033 | 221907.5965 | 27450.5662 | 0.080012 | -211965.9958 | 211965.9958
C | Xist Rating 7750 | -25.26 | 1515.95 | 150.299 | 35.7 | 2194.58 | 8695.81 | 14638.6 | 0.49 | 1.89 | 21.91 | 25.212 | 1 | 1 | 2110 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3326873.551 | 252378.2079 | 4336.0977 | 28352.1738 | 224026.0341 | 27198.0237 | 0.080393 | -210015.9295 | 210015.9295
C | Xist Rating 7751 | -23.72 | 1554.45 | 150.299 | 35.7 | 2184.93 | 8659.6 | 14358.9 | 0.49 | 1.84 | 21.943 | 24.269 | 1 | 1 | 2120 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3396364.4385 | 254641.0798 | 4377.2956 | 28486.5443 | 226154.5355 | 26225.0686 | 0.080774 | -202503.0283 | 202503.0283
C | Xist Rating 7752 | -23.18 | 1568.53 | 150.299 | 35.7 | 2181.47 | 8645.35 | 14263.6 | 0.48 | 1.83 | 21.94 | 23.966 | 1 | 1 | 2130 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3421701.1391 | 256914.0156 | 4418.6882 | 28620.9148 | 228293.1008 | 25894.1353 | 0.081155 | -199947.6488 | 199947.6488
C | Xist Rating 7753 | -22.7 | 1582.65 | 150.299 | 35.7 | 2175.56 | 8592.47 | 14169.8 | 0.48 | 1.81 | 21.94 | 23.67 | 1 | 1 | 2140 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3443150.034 | 259197.0152 | 4460.2756 | 28755.2853 | 230441.7299 | 25591.4603 | 0.081536 | -197610.473 | 197610.473
C | Xist Rating 7754 | -22.37 | 1590.04 | 150.299 | 35.7 | 2175.15 | 8605.82 | 14123.4 | 0.47 | 1.8 | 21.949 | 23.533 | 1 | 1 | 2150 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3458575.506 | 261490.0786 | 4502.0578 | 28889.6558 | 232600.4228 | 25433.17 | 0.081917 | -196388.1974 | 196388.1974
C | Xist Rating 7755 | -21.92 | 1600 | 150.299 | 35.7 | 2174.83 | 8628.48 | 14059 | 0.46 | 1.79 | 21.955 | 23.336 | 1 | 1 | 2160 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3479728 | 263793.2059 | 4544.0348 | 29024.0263 | 234769.1796 | 25212.2259 | 0.082298 | -194682.1253 | 194682.1253
C | Xist Rating 7756 | -20.3 | 1641.48 | 150.299 | 35.7 | 2164.31 | 8582.99 | 13785.9 | 0.46 | 1.75 | 21.977 | 22.466 | 1 | 1 | 2170 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3552671.5788 | 266106.397 | 4586.2066 | 29158.3968 | 236948.0002 | 24314.2436 | 0.082679 | -187748.1442 | 187748.1442
C | Xist Rating 7757 | -19.69 | 1655.34 | 150.3 | 35.7 | 2163.19 | 8604.4 | 13699 | 0.46 | 1.74 | 21.988 | 22.202 | 1 | 1 | 2180 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3580814.9346 | 268429.6519 | 4628.5732 | 29292.7672 | 239136.8847 | 24045.106 | 0.08306 | -185669.9348 | 185669.9348
C | Xist Rating 7758 | -19.26 | 1665.53 | 150.299 | 35.7 | 2161.88 | 8611.12 | 13638.9 | 0.45 | 1.73 | 21.987 | 22.028 | 1 | 1 | 2190 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3600675.9964 | 270762.9707 | 4671.1346 | 29427.1377 | 241335.833 | 23847.3121 | 0.083441 | -184142.6231 | 184142.6231
C | Xist Rating 7759 | -18.87 | 1676.13 | 150.299 | 35.7 | 2159.28 | 8597.18 | 13579.3 | 0.44 | 1.72 | 21.973 | 21.861 | 1 | 1 | 2200 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3619233.9864 | 273106.3533 | 4713.8907 | 29561.5082 | 243544.8451 | 23656.0281 | 0.083822 | -182665.5788 | 182665.5788
C | Xist Rating 7760 | -18.29 | 1690.25 | 150.299 | 35.7 | 2157.18 | 8602.87 | 13495.4 | 0.44 | 1.7 | 21.975 | 21.613 | 1 | 1 | 2210 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3646173.495 | 275459.7998 | 4756.8417 | 29695.8787 | 245763.9211 | 23402.9014 | 0.084203 | -180711.0013 | 180711.0013
C | Xist Rating 7761 | -16.68 | 1731.59 | 150.3 | 35.7 | 2147.58 | 8568.21 | 13246.2 | 0.44 | 1.66 | 22.011 | 20.859 | 1 | 1 | 2220 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3718728.0522 | 277823.3101 | 4799.9874 | 29830.2492 | 247993.0609 | 22625.784 | 0.084584 | -174710.3062 | 174710.3062
C | Xist Rating 7762 | -16.18 | 1742.92 | 150.3 | 35.7 | 2147.12 | 8591.8 | 13182.5 | 0.44 | 1.65 | 22.014 | 20.679 | 1 | 1 | 2230 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3742258.3904 | 280196.8842 | 4843.3279 | 29964.6197 | 250232.2645 | 22443.3274 | 0.084965 | -173301.4249 | 173301.4249
C | Xist Rating 7763 | -15.68 | 1756.04 | 150.3 | 35.7 | 2144.18 | 8579.42 | 13111.7 | 0.43 | 1.64 | 22.008 | 20.483 | 1 | 1 | 2240 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3765265.8472 | 282580.5222 | 4886.8633 | 30098.9902 | 252481.532 | 22221.7608 | 0.085346 | -171590.5464 | 171590.5464
C | Xist Rating 7764 | -15.14 | 1770.47 | 150.3 | 35.7 | 2141.08 | 8568.32 | 13034 | 0.42 | 1.63 | 22.004 | 20.268 | 1 | 1 | 2250 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3790717.9076 | 284974.224 | 4930.5934 | 30233.3607 | 254740.8633 | 21980.3599 | 0.085727 | -169726.5125 | 169726.5125
C | Xist Rating 7765 | -14.78 | 1777.83 | 150.3 | 35.7 | 2141.74 | 8598.06 | 12995.5 | 0.42 | 1.62 | 22.011 | 20.166 | 1 | 1 | 2260 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3807649.6242 | 287377.9896 | 4974.5182 | 30367.7312 | 257010.2584 | 21878.8734 | 0.086108 | -168942.861 | 168942.861
C | Xist Rating 7766 | -13.1 | 1822.25 | 150.3 | 35.7 | 2131.17 | 8552.2 | 12751.8 | 0.42 | 1.59 | 22.042 | 19.467 | 1 | 1 | 2270 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3883524.5325 | 289791.8191 | 5018.6379 | 30502.1017 | 259289.7174 | 21158.4317 | 0.086489 | -163379.8011 | 163379.8011
C | Xist Rating 7767 | -12.59 | 1835.32 | 150.3 | 35.7 | 2128.92 | 8550.17 | 12686.1 | 0.41 | 1.58 | 22.038 | 19.293 | 1 | 1 | 2280 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3907249.4544 | 292215.7124 | 5062.9524 | 30636.4722 | 261579.2403 | 20959.1881 | 0.08687 | -161841.2948 | 161841.2948
C | Xist Rating 7768 | -11.96 | 1850.84 | 150.3 | 35.7 | 2126.99 | 8560.66 | 12606.8 | 0.41 | 1.56 | 22.039 | 19.08 | 1 | 1 | 2290 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3936718.1716 | 294649.6696 | 5107.4617 | 30770.8427 | 263878.8269 | 20742.0802 | 0.087251 | -160164.8451 | 160164.8451
C | Xist Rating 7769 | -11.52 | 1861.2 | 150.3 | 35.7 | 2126.23 | 8574.86 | 12557.1 | 0.4 | 1.56 | 22.043 | 18.952 | 1 | 1 | 2300 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3957339.276 | 297093.6906 | 5152.1657 | 30905.2131 | 266188.4774 | 20590.6462 | 0.087632 | -158995.5121 | 158995.5121
| Xist Rating 7770 | -11.13 | 1871.82 | 150.3 | 35.7 | 2123.91 | 8563.74 | 12507.7 | 0.4 | 1.55 | 22.045 | 18.829 | 1 | 1 | 2310 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 3975577.2162 | 299547.7754 | 5197.0645 | 31039.5836 | 268508.1917 | 20466.946 | 0.088013 | -158040.332 | 158040.332
| Xist Rating 7771 | -9.38 | 1917.43 | 150.3 | 35.7 | 2114.71 | 8540.22 | 12277.2 | 0.4 | 1.51 | 22.071 | 18.198 | 1 | 1 | 2320 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4054808.3953 | 302011.924 | 5242.1582 | 31173.9541 | 270837.9699 | 19816.6877 | 0.088394 | -153019.2095 | 153019.2095
| Xist Rating 7772 | -8.85 | 1930.53 | 150.3 | 35.7 | 2113.19 | 8549.18 | 12216.8 | 0.39 | 1.5 | 22.077 | 18.047 | 1 | 1 | 2330 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4079576.6907 | 304486.1365 | 5287.4466 | 31308.3246 | 273177.8119 | 19641.0249 | 0.088775 | -151662.7876 | 151662.7876
| Xist Rating 7773 | -8.34 | 1943.61 | 150.3 | 35.7 | 2111.38 | 8553.22 | 12157.2 | 0.39 | 1.49 | 22.076 | 17.897 | 1 | 1 | 2340 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4103699.2818 | 306970.4129 | 5332.9298 | 31442.6951 | 275527.7177 | 19489.0686 | 0.089156 | -150489.4217 | 150489.4217
| Xist Rating 7774 | -7.92 | 1955.43 | 150.3 | 35.7 | 2108.77 | 8540.49 | 12104.7 | 0.38 | 1.49 | 22.071 | 17.769 | 1 | 1 | 2350 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4123552.1211 | 309464.753 | 5378.6078 | 31577.0656 | 277887.6874 | 19336.5455 | 0.089537 | -149311.6788 | 149311.6788
| Xist Rating 7775 | -7.4 | 1969.91 | 150.3 | 35.7 | 2105.54 | 8524.69 | 12039.8 | 0.38 | 1.48 | 22.068 | 17.607 | 1 | 1 | 2360 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4147724.3014 | 311969.157 | 5424.4805 | 31711.4361 | 280257.7209 | 19171.9476 | 0.089918 | -148040.6974 | 148040.6974
| Xist Rating 7776 | -5.81 | 2011.68 | 150.3 | 35.7 | 2097.79 | 8510.36 | 11846.8 | 0.38 | 1.45 | 22.095 | 17.106 | 1 | 1 | 2370 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4220082.1872 | 314483.6249 | 5470.5481 | 31845.8066 | 282637.8183 | 18656.5088 | 0.090299 | -144060.6154 | 144060.6154
| Xist Rating 7777 | -5.35 | 2025 | 150.3 | 35.7 | 2094.7 | 8492.63 | 11791.2 | 0.38 | 1.44 | 22.087 | 16.974 | 1 | 1 | 2380 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4241767.5 | 317008.1566 | 5516.8105 | 31980.1771 | 285027.9795 | 18522.8662 | 0.09068 | -143028.6628 | 143028.6628
| Xist Rating 7778 | -4.79 | 2039.03 | 150.3 | 35.7 | 2093.14 | 8503.62 | 11730 | 0.37 | 1.43 | 22.086 | 16.824 | 1 | 1 | 2390 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4267975.2542 | 319542.7521 | 5563.2676 | 32114.5476 | 287428.2045 | 18347.1519 | 0.091061 | -141671.844 | 141671.844
C | Xist Rating 7781 | 5.8 | 2339.3 | 150.3 | 35.7 | 2028.71 | 8218.44 | 10538.1 | 0.4 | 1.25 | 22.102 | 13.979 | 1 | 1 | 2420 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4745761.303 | 327206.9216 | 5703.8078 | 32517.6591 | 294689.2626 | 15476.181 | 0.092204 | -119502.967 | 119502.967
C | Xist Rating 7782 | 5.97 | 2340.66 | 150.3 | 35.7 | 2031.23 | 8260.1 | 10538.1 | 0.39 | 1.25 | 22.108 | 13.99 | 1 | 1 | 2430 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4754418.8118 | 329781.7725 | 5751.0441 | 32652.0295 | 297129.743 | 15467.7478 | 0.092585 | -119437.8486 | 119437.8486
C | Xist Rating 7783 | 5.98 | 2342.03 | 150.3 | 35.7 | 2030.77 | 8252.36 | 10538.1 | 0.38 | 1.25 | 22.1 | 14.001 | 1 | 1 | 2440 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4756124.2631 | 332366.6872 | 5798.4752 | 32786.4 | 299580.2872 | 15458.5236 | 0.092966 | -119366.622 | 119366.622
C | Xist Rating 7784 | 6 | 2343.36 | 150.3 | 35.7 | 2030.45 | 8247.09 | 10538 | 0.38 | 1.25 | 22.093 | 14.011 | 1 | 1 | 2450 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4758075.312 | 334961.6657 | 5846.1011 | 32920.7705 | 302040.8952 | 15472.3809 | 0.093347 | -119473.6239 | 119473.6239
C | Xist Rating 7785 | 6.03 | 2344.83 | 150.3 | 35.7 | 2030.35 | 8245.42 | 10538.1 | 0.37 | 1.25 | 22.083 | 14.022 | 1 | 1 | 2460 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4760825.5905 | 337566.7081 | 5893.9217 | 33055.141 | 304511.5671 | 15462.7979 | 0.093728 | -119399.6267 | 119399.6267
C | Xist Rating 7786 | 6.03 | 2346.18 | 150.3 | 35.7 | 2029.87 | 8237.52 | 10538.1 | 0.37 | 1.25 | 22.124 | 14.033 | 1 | 1 | 2470 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4762440.3966 | 340181.8143 | 5941.9372 | 33189.5115 | 306992.3028 | 15479.5635 | 0.094109 | -119529.0858 | 119529.0858
C | Xist Rating 7787 | 6.04 | 2347.53 | 150.3 | 35.7 | 2029.35 | 8228.97 | 10538.1 | 0.36 | 1.25 | 22.118 | 14.044 | 1 | 1 | 2480 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4763960.0055 | 342806.9844 | 5990.1474 | 33323.882 | 309483.1024 | 15469.8219 | 0.09449 | -119453.8644 | 119453.8644
C | Xist Rating 7788 | 6.04 | 2348.93 | 150.3 | 35.7 | 2028.69 | 8218.22 | 10538.1 | 0.35 | 1.25 | 22.112 | 14.054 | 1 | 1 | 2490 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4765250.8017 | 345442.2182 | 6038.5525 | 33458.2525 | 311983.9657 | 15458.855 | 0.094871 | -119369.1809 | 119369.1809
C | Xist Rating 7789 | 6.07 | 2349.91 | 150.3 | 35.7 | 2028.93 | 8222.16 | 10538 | 0.35 | 1.25 | 22.109 | 14.063 | 1 | 1 | 2500 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4767802.8963 | 348087.516 | 6087.1523 | 33592.623 | 314494.893 | 15471.5529 | 0.095252 | -119467.2307 | 119467.2307
C | Xist Rating 7790 | 6.05 | 2351.76 | 150.3 | 35.7 | 2027.39 | 8196.87 | 10538 | 0.34 | 1.25 | 22.102 | 14.076 | 1 | 1 | 2510 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4767934.7064 | 350742.8775 | 6135.9469 | 33726.9935 | 317015.884 | 15463.3794 | 0.095633 | -119404.117 | 119404.117
C | Xist Rating 7791 | 6.05 | 2353.22 | 150.3 | 35.7 | 2026.76 | 8186.6 | 10538 | 0.34 | 1.25 | 22.139 | 14.087 | 1 | 1 | 2520 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4769412.1672 | 353408.3029 | 6184.9363 | 33861.364 | 319546.9389 | 15479.5924 | 0.096014 | -119529.3089 | 119529.3089
C | Xist Rating 7792 | 6.06 | 2354.55 | 150.3 | 35.7 | 2026.28 | 8178.77 | 10538 | 0.33 | 1.25 | 22.133 | 14.097 | 1 | 1 | 2530 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4770977.574 | 356083.7921 | 6234.1205 | 33995.7345 | 322088.0577 | 15468.0198 | 0.096395 | -119439.949 | 119439.949
C | Xist Rating 7793 | 6.08 | 2355.7 | 150.3 | 35.7 | 2026.16 | 8176.89 | 10538 | 0.33 | 1.25 | 22.129 | 14.106 | 1 | 1 | 2540 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4773025.112 | 358769.3452 | 6283.4995 | 34130.105 | 324639.2402 | 15480.49 | 0.096776 | -119536.2401 | 119536.2401
C | Xist Rating 7794 | 6.12 | 2357.25 | 150.3 | 35.7 | 2026.01 | 8174.39 | 10538 | 0.32 | 1.25 | 22.122 | 14.118 | 1 | 1 | 2550 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4775812.0725 | 361464.9621 | 6333.0732 | 34264.4754 | 327200.4866 | 15470.6752 | 0.097157 | -119460.4529 | 119460.4529
C | Xist Rating 7795 | 6.12 | 2358.7 | 150.3 | 35.6 | 2025.54 | 8166.92 | 10537.9 | 0.32 | 1.25 | 22.115 | 14.128 | 1 | 1 | 2560 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4777641.198 | 364170.6428 | 6382.8418 | 34398.8459 | 329771.7969 | 15483.9763 | 0.097538 | -119563.1605 | 119563.1605
C | Xist Rating 7796 | 6.17 | 2360.09 | 150.3 | 35.6 | 2026.02 | 8174.68 | 10537.9 | 0.31 | 1.25 | 22.106 | 14.138 | 1 | 1 | 2570 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4781589.5418 | 366886.3874 | 6432.8051 | 34533.2164 | 332353.171 | 15471.7357 | 0.097919 | -119468.6417 | 119468.6417
C | Xist Rating 7797 | 6.19 | 2361.45 | 150.3 | 35.6 | 2025.93 | 8173.16 | 10537.9 | 0.31 | 1.25 | 22.155 | 14.148 | 1 | 1 | 2580 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4784132.3985 | 369612.1958 | 6482.9633 | 34667.5869 | 334944.6089 | 15486.9491 | 0.0983 | -119586.1159 | 119586.1159
C | Xist Rating 7798 | 6.18 | 2362.81 | 150.3 | 35.6 | 2025.25 | 8162.23 | 10537.8 | 0.3 | 1.25 | 22.156 | 14.159 | 1 | 1 | 2590 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4785280.9525 | 372348.0681 | 6533.3162 | 34801.9574 | 337546.1106 | 15475.765 | 0.098681 | -119499.7549 | 119499.7549
C | Xist Rating 7799 | 6.2 | 2363.99 | 150.3 | 35.6 | 2025.24 | 8161.98 | 10537.8 | 0.3 | 1.25 | 22.16 | 14.168 | 1 | 1 | 2600 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4787647.1076 | 375094.0041 | 6583.8639 | 34936.3279 | 340157.6762 | 15488.2307 | 0.099062 | -119596.0121 | 119596.0121
C | Xist Rating 7800 | 6.21 | 2365.68 | 150.3 | 35.6 | 2024.31 | 8147.01 | 10537.8 | 0.3 | 1.25 | 22.157 | 14.179 | 1 | 1 | 2610 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4788869.6808 | 377850.0041 | 6634.6064 | 35070.6984 | 342779.3057 | 15502.5288 | 0.099443 | -119706.4185 | 119706.4185
C | Xist Rating 7801 | 6.22 | 2367.07 | 150.3 | 35.6 | 2023.98 | 8141.63 | 10537.8 | 0.29 | 1.25 | 22.153 | 14.189 | 1 | 1 | 2620 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4790902.3386 | 380616.0678 | 6685.5437 | 35205.0689 | 345410.9989 | 15489.7358 | 0.099824 | -119607.6342 | 119607.6342
C | Xist Rating 7802 | 6.22 | 2368.5 | 150.3 | 35.6 | 2023.44 | 8132.91 | 10537.7 | 0.29 | 1.25 | 22.192 | 14.2 | 1 | 1 | 2630 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4792517.64 | 383392.1954 | 6736.6758 | 35339.4394 | 348052.756 | 15505.3723 | 0.10021 | -119728.3751 | 119728.3751
C | Xist Rating 7803 | 6.25 | 2369.75 | 150.3 | 35.6 | 2023.34 | 8131.31 | 10537.7 | 0.28 | 1.25 | 22.191 | 14.209 | 1 | 1 | 2640 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4794809.965 | 386178.3868 | 6788.0027 | 35473.8099 | 350704.577 | 15491.3091 | 0.10059 | -119619.7825 | 119619.7825
C | Xist Rating 7804 | 6.29 | 2371.25 | 150.3 | 35.6 | 2023.32 | 8130.95 | 10537.8 | 0.28 | 1.25 | 22.198 | 14.22 | 1 | 1 | 2650 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 29 | E | Rod | 4797797.55 | 388974.6421 | 6839.5243 | 35608.1804 | 353366.4617 | 15505.7506 | 0.10097 | -119731.2957 | 119731.2957
C | Xist Rating 7805 | 6.33 | 2372.59 | 150.3 | 35.6 | 2023.33 | 8131.16 | 10537.7 | 0.28 | 1.25 | 22.195 | 14.23 | 1 | 1 | 2660 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4800532.5247 | 391780.9612 | 6891.2408 | 35742.5509 | 356038.4103 | 15518.8214 | 0.10135 | -119832.2256 | 119832.2256
C | Xist Rating 7806 | 6.37 | 2373.98 | 150.3 | 35.6 | 2023.49 | 8133.7 | 10537.7 | 0.27 | 1.25 | 22.197 | 14.24 | 1 | 1 | 2670 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4803724.7902 | 394597.3441 | 6943.152 | 35876.9214 | 358720.4228 | 15505.4933 | 0.10173 | -119729.3096 | 119729.3096
C | Xist Rating 7807 | 6.42 | 2375.4 | 150.301 | 35.6 | 2023.75 | 8137.86 | 10537.8 | 0.27 | 1.25 | 22.239 | 14.25 | 1 | 1 | 2680 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4807215.75 | 397423.7909 | 6995.258 | 36011.2918 | 361412.4991 | 15519.927 | 0.10211 | -119840.7627 | 119840.7627
C | Xist Rating 7808 | 6.48 | 2376.77 | 150.301 | 35.6 | 2024.25 | 8145.93 | 10537.8 | 0.26 | 1.25 | 22.241 | 14.26 | 1 | 1 | 2690 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4811176.6725 | 400260.3015 | 7047.5588 | 36145.6623 | 364114.6392 | 15506.2508 | 0.10249 | -119735.1585 | 119735.1585
C | Xist Rating 7809 | 6.56 | 2377.97 | 150.301 | 35.6 | 2025.39 | 8164.47 | 10537.8 | 0.26 | 1.25 | 22.243 | 14.269 | 1 | 1 | 2700 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4816316.6583 | 403106.876 | 7100.0544 | 36280.0328 | 366826.8432 | 15518.2523 | 0.10287 | -119827.8308 | 119827.8308
C | Xist Rating 7810 | 6.61 | 2379.63 | 150.301 | 35.6 | 2025.83 | 8171.74 | 10537.6 | 0.26 | 1.25 | 22.24 | 14.28 | 1 | 1 | 2710 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4820725.8429 | 405963.5143 | 7152.7448 | 36414.4033 | 369549.1109 | 15532.1733 | 0.10325 | -119935.3252 | 119935.3252
C | Xist Rating 7811 | 6.61 | 2380.97 | 150.301 | 35.6 | 2025.12 | 8160.25 | 10537.6 | 0.25 | 1.25 | 22.238 | 14.289 | 1 | 1 | 2720 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4821749.9664 | 408830.2164 | 7205.63 | 36548.7738 | 372281.4426 | 15516.9351 | 0.10363 | -119817.6597 | 119817.6597
C | Xist Rating 7812 | 6.63 | 2382.3 | 150.301 | 35.6 | 2024.98 | 8157.93 | 10537.6 | 0.25 | 1.25 | 22.275 | 14.299 | 1 | 1 | 2730 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4824109.854 | 411706.9823 | 7258.71 | 36683.1443 | 375023.838 | 15530.944 | 0.10402 | -119925.8331 | 119925.8331
C | Xist Rating 7813 | 6.63 | 2383.58 | 150.301 | 35.6 | 2024.23 | 8145.82 | 10537.7 | 0.25 | 1.25 | 22.265 | 14.308 | 1 | 1 | 2740 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4824914.1434 | 414593.8121 | 7311.9847 | 36817.5148 | 377776.2973 | 15542.4796 | 0.1044 | -120014.908 | 120014.908
C | Xist Rating 7814 | 6.62 | 2385.13 | 150.301 | 35.6 | 2023.2 | 8129.06 | 10537.7 | 0.25 | 1.25 | 22.262 | 14.319 | 1 | 1 | 2750 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4825595.016 | 417490.7058 | 7365.4543 | 36951.8853 | 380538.8205 | 15556.3057 | 0.10478 | -120121.6693 | 120121.6693
C | Xist Rating 7815 | 6.62 | 2386.55 | 150.301 | 35.6 | 2022.48 | 8117.49 | 10537.7 | 0.24 | 1.25 | 22.264 | 14.328 | 1 | 1 | 2760 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4826749.644 | 420397.6632 | 7419.1186 | 37086.2558 | 383311.4075 | 15540.6647 | 0.10516 | -120000.8931 | 120000.8931
C | Xist Rating 7816 | 6.6 | 2387.79 | 150.301 | 35.6 | 2021.62 | 8103.67 | 10537.7 | 0.24 | 1.25 | 22.26 | 14.337 | 1 | 1 | 2770 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4827204.0198 | 423314.6845 | 7472.9777 | 37220.6263 | 386094.0583 | 15552.2871 | 0.10554 | -120090.6384 | 120090.6384
C | Xist Rating 7817 | 6.6 | 2389.33 | 150.301 | 35.6 | 2020.85 | 8091.2 | 10537.7 | 0.24 | 1.25 | 22.302 | 14.348 | 1 | 1 | 2780 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4828477.5305 | 426241.7697 | 7527.0316 | 37354.9968 | 388886.7729 | 15567.3614 | 0.10592 | -120207.0381 | 120207.0381
C | Xist Rating 7818 | 6.61 | 2390.74 | 150.301 | 35.6 | 2020.43 | 8084.44 | 10537.7 | 0.23 | 1.25 | 22.306 | 14.357 | 1 | 1 | 2790 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4830322.8182 | 429178.9187 | 7581.2803 | 37489.3673 | 391689.5514 | 15551.3311 | 0.1063 | -120083.2565 | 120083.2565
C | Xist Rating 7819 | 6.59 | 2391.72 | 150.301 | 35.6 | 2019.81 | 8074.57 | 10537.7 | 0.23 | 1.25 | 22.299 | 14.365 | 1 | 1 | 2800 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4830819.9732 | 432126.1315 | 7635.7238 | 37623.7377 | 394502.3937 | 15561.7367 | 0.10668 | -120163.6057 | 120163.6057
C | Xist Rating 7820 | 6.6 | 2393.46 | 150.301 | 35.6 | 2019.06 | 8062.66 | 10537.7 | 0.23 | 1.25 | 22.306 | 14.376 | 1 | 1 | 2810 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4832539.3476 | 435083.4081 | 7690.3621 | 37758.1082 | 397325.2999 | 15575.6619 | 0.10706 | -120271.1326 | 120271.1326
C | Xist Rating 7821 | 6.63 | 2394.94 | 150.301 | 35.6 | 2018.82 | 8058.84 | 10537.8 | 0.23 | 1.25 | 22.311 | 14.386 | 1 | 1 | 2820 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4834952.7708 | 438050.7486 | 7745.1952 | 37892.4787 | 400158.2699 | 15588.4919 | 0.10744 | -120370.2027 | 120370.2027
C | Xist Rating 7822 | 6.62 | 2396.31 | 150.301 | 35.6 | 2018.04 | 8046.44 | 10537.7 | 0.22 | 1.25 | 22.345 | 14.395 | 1 | 1 | 2830 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4835849.4324 | 441028.1529 | 7800.223 | 38026.8492 | 403001.3037 | 15572.7851 | 0.10783 | -120248.9189 | 120248.9189
C | Xist Rating 7823 | 6.68 | 2397.63 | 150.301 | 35.6 | 2018.62 | 8055.68 | 10537.7 | 0.22 | 1.25 | 22.34 | 14.404 | 1 | 1 | 2840 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4839903.8706 | 444015.6211 | 7855.4457 | 38161.2197 | 405854.4014 | 15584.1951 | 0.10821 | -120337.0238 | 120337.0238
C | Xist Rating 7824 | 6.74 | 2399.07 | 150.301 | 35.6 | 2019.27 | 8066.03 | 10537.7 | 0.22 | 1.25 | 22.349 | 14.414 | 1 | 1 | 2850 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4844370.0789 | 447013.1531 | 7910.8631 | 38295.5902 | 408717.5629 | 15597.0361 | 0.10859 | -120436.1784 | 120436.1784
C | Xist Rating 7825 | 6.71 | 2400.47 | 150.301 | 35.6 | 2018.11 | 8047.54 | 10537.7 | 0.22 | 1.25 | 22.339 | 14.423 | 1 | 1 | 2860 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4844412.5117 | 450020.7489 | 7966.4753 | 38429.9607 | 411590.7882 | 15608.3045 | 0.10897 | -120523.1899 | 120523.1899
C | Xist Rating 7826 | 6.83 | 2401.67 | 150.301 | 35.6 | 2020.01 | 8077.72 | 10537.7 | 0.21 | 1.25 | 22.364 | 14.432 | 1 | 1 | 2870 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4851397.4167 | 453038.4086 | 8022.2824 | 38564.3312 | 414474.0774 | 15591.7909 | 0.10935 | -120395.6764 | 120395.6764
C | Xist Rating 7827 | 6.93 | 2403.17 | 150.301 | 35.6 | 2021.12 | 8095.51 | 10537.8 | 0.21 | 1.25 | 22.424 | 14.442 | 1 | 1 | 2880 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4857094.9504 | 456066.1321 | 8078.2842 | 38698.7017 | 417367.4304 | 15605.9076 | 0.10973 | -120504.6822 | 120504.6822
C | Xist Rating 7828 | 6.95 | 2404.52 | 150.301 | 35.6 | 2020.93 | 8092.43 | 10537.8 | 0.21 | 1.25 | 22.425 | 14.451 | 1 | 1 | 2890 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4859366.6036 | 459103.9195 | 8134.4807 | 38833.0722 | 420270.8473 | 15617.3921 | 0.11011 | -120593.3625 | 120593.3625
C | Xist Rating 7829 | 7.25 | 2405.9 | 150.301 | 35.6 | 2025.98 | 8174.03 | 10537.9 | 0.21 | 1.25 | 22.479 | 14.461 | 1 | 1 | 2900 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4874305.282 | 462151.7706 | 8190.8721 | 38967.4427 | 423184.328 | 15631.3621 | 0.11049 | -120701.235 | 120701.235
C | Xist Rating 7830 | 7.82 | 2407.44 | 150.301 | 35.6 | 2036.19 | 8342.72 | 10538.1 | 0.2 | 1.25 | 22.546 | 14.472 | 1 | 1 | 2910 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4902005.2536 | 465209.6857 | 8247.4583 | 39101.8132 | 426107.8725 | 15617.328 | 0.11087 | -120592.8668 | 120592.8668
C | Xist Rating 7831 | 8.36 | 2408.83 | 150.301 | 35.6 | 2045.97 | 8509.19 | 10538.2 | 0.2 | 1.25 | 22.608 | 14.482 | 1 | 1 | 2920 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4928393.9151 | 468277.6645 | 8304.2393 | 39236.1837 | 429041.4809 | 15631.3572 | 0.11125 | -120701.1968 | 120701.1968
C | Xist Rating 7832 | 8.44 | 2410.22 | 150.301 | 35.6 | 2047.02 | 8527.49 | 10538.2 | 0.2 | 1.25 | 22.651 | 14.491 | 1 | 1 | 2930 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4933768.5444 | 471355.7072 | 8361.215 | 39370.5541 | 431985.1531 | 15643.86 | 0.11164 | -120797.7398 | 120797.7398
C | Xist Rating 7833 | 8.86 | 2411.59 | 150.301 | 35.6 | 2054.31 | 8655.32 | 10538.2 | 0.19 | 1.25 | 22.694 | 14.501 | 1 | 1 | 2940 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4954153.4529 | 474443.8137 | 8418.3855 | 39504.9246 | 434938.8891 | 15627.5018 | 0.11202 | -120671.4262 | 120671.4262
C | Xist Rating 7834 | 9.15 | 2412.99 | 150.301 | 35.6 | 2059.15 | 8741.79 | 10538.3 | 0.19 | 1.25 | 22.725 | 14.51 | 1 | 1 | 2950 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4968708.3585 | 477541.9841 | 8475.7509 | 39639.2951 | 437902.689 | 15639.5599 | 0.1124 | -120764.5358 | 120764.5358
C | Xist Rating 7835 | 9.58 | 2414.37 | 150.301 | 35.6 | 2066.67 | 8878.93 | 10538.3 | 0.19 | 1.25 | 22.783 | 14.52 | 1 | 1 | 2960 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 4989706.0479 | 480650.2183 | 8533.311 | 39773.6656 | 440876.5527 | 15653.3424 | 0.11278 | -120870.9609 | 120870.9609
C | Xist Rating 7836 | 10.15 | 2415.75 | 150.301 | 35.6 | 2077.25 | 9077.79 | 10538.2 | 0.18 | 1.25 | 22.826 | 14.53 | 1 | 1 | 2970 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 5018116.6875 | 483768.5163 | 8591.0659 | 39908.0361 | 443860.4802 | 15636.3674 | 0.11316 | -120739.8839 | 120739.8839
C | Xist Rating 7837 | 10.15 | 2416.97 | 150.301 | 35.6 | 2076.79 | 9069 | 10538 | 0.18 | 1.25 | 22.849 | 14.539 | 1 | 1 | 2980 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 5019539.1263 | 486896.8782 | 8649.0156 | 40042.4066 | 446854.4716 | 15648.1085 | 0.11354 | -120830.5464 | 120830.5464
C | Xist Rating 7838 | 10.19 | 2418.53 | 150.301 | 35.6 | 2076.63 | 9066.06 | 10538 | 0.18 | 1.25 | 22.846 | 14.548 | 1 | 1 | 2990 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 5022391.9539 | 490035.3039 | 8707.16 | 40176.7771 | 449858.5268 | 15659.2262 | 0.11392 | -120916.3941 | 120916.3941
C | Xist Rating 7839 | 10.18 | 2419.96 | 150.301 | 35.6 | 2075.96 | 9053.35 | 10538 | 0.18 | 1.25 | 22.841 | 14.557 | 1 | 1 | 3000 | 152.4 | 2 | 4.8 | 19.05 | 1.3333 | 28 | E | Rod | 5023740.1616 | 493183.7935 | 8765.4993 | 40311.1476 | 452872.6459 | 15670.295 | 0.1143 | -121001.8642 | 121001.8642
C | Xist Rating 7840 | -86.37 | 249.16 | 150.307 | 35.9 | 2351.56 | 6964.82 | 58744.5 | 2.48 | 10.95 | 24.945 | 594.795 | 1 | 1 | 1000 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 585914.6896 | 65084.4869 | 973.9444 | 13716.9877 | 51367.4992 | 620466.6813 | 0.038101 | -4791079.2453 | 4791079.2453
C | Xist Rating 7841 | -86.25 | 251.73 | 150.307 | 35.9 | 2348.48 | 6945.34 | 58282.9 | 2.46 | 10.84 | 25.031 | 583.6 | 1 | 1 | 1010 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 591182.8704 | 66254.1435 | 993.5206 | 13854.1576 | 52399.9859 | 608855.4129 | 0.038482 | -4701420.1088 | 4701420.1088
C | Xist Rating 7842 | -85.23 | 271.264 | 150.307 | 35.9 | 2341.8 | 6944.21 | 54967.1 | 2.47 | 10.07 | 25.085 | 505.765 | 1 | 1 | 1020 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 635246.0352 | 67434.0736 | 1013.2917 | 13991.3275 | 53442.7462 | 528069.0326 | 0.038863 | -4077609.0939 | 4077609.0939
C | Xist Rating 7843 | -85.06 | 276.548 | 150.305 | 35.9 | 2325.65 | 6818.22 | 54177.8 | 2.39 | 9.89 | 24.474 | 488.712 | 1 | 1 | 1030 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 643153.8562 | 68624.2772 | 1033.2576 | 14128.4974 | 54495.7799 | 510227.2189 | 0.039244 | -3939839.3383 | 3939839.3383
C | Xist Rating 7844 | -84.96 | 279.192 | 150.305 | 35.9 | 2319.67 | 6774.05 | 53793 | 2.35 | 9.8 | 24.335 | 480.548 | 1 | 1 | 1040 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 647633.3066 | 69824.7543 | 1053.4182 | 14265.6672 | 55559.0871 | 501714.2726 | 0.039625 | -3874104.6233 | 3874104.6233
C | Xist Rating 7845 | -84.73 | 284.354 | 150.305 | 35.9 | 2312.87 | 6730.05 | 53042.8 | 2.31 | 9.63 | 24.246 | 464.586 | 1 | 1 | 1050 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 657673.836 | 71035.505 | 1073.7737 | 14402.8371 | 56632.6679 | 485107.9046 | 0.040006 | -3745874.6516 | 3745874.6516
C | Xist Rating 7846 | -84.6 | 286.979 | 150.305 | 35.9 | 2311.44 | 6724.8 | 52676 | 2.27 | 9.54 | 24.206 | 457.001 | 1 | 1 | 1060 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 663334.7398 | 72256.5291 | 1094.3239 | 14540.007 | 57716.5221 | 477205.6042 | 0.040387 | -3684855.1827 | 3684855.1827
C | Xist Rating 7847 | -83.58 | 307.953 | 150.304 | 35.9 | 2296.49 | 6654.03 | 49856.7 | 2.26 | 8.9 | 23.966 | 399.832 | 1 | 1 | 1070 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 707210.985 | 73487.8267 | 1115.0689 | 14677.1769 | 58810.6498 | 417822.6936 | 0.040768 | -3226316.0878 | 3226316.0878
C | Xist Rating 7848 | -83.35 | 311.893 | 150.304 | 35.9 | 2300.66 | 6699.18 | 49379.9 | 2.2 | 8.79 | 23.843 | 390.831 | 1 | 1 | 1080 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 717559.7494 | 74729.3978 | 1136.0087 | 14814.3467 | 59915.051 | 408416.7354 | 0.041149 | -3153685.7712 | 3153685.7712
C | Xist Rating 7849 | -83.04 | 317.135 | 150.304 | 35.9 | 2304.84 | 6748.2 | 48760.6 | 2.14 | 8.65 | 23.664 | 379.273 | 1 | 1 | 1090 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 730945.4334 | 75981.2424 | 1157.1433 | 14951.5166 | 61029.7258 | 396348.6708 | 0.04153 | -3060499.3758 | 3060499.3758
C | Xist Rating 7850 | -82.78 | 321.043 | 150.304 | 35.9 | 2313.37 | 6832.11 | 48307.1 | 2.1 | 8.55 | 23.666 | 370.926 | 1 | 1 | 1100 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 742691.2449 | 77243.3605 | 1178.4727 | 15088.6865 | 62154.674 | 387656.5591 | 0.041911 | -2993381.1931 | 2993381.1931
C | Xist Rating 7851 | -82.63 | 323.855 | 150.303 | 35.9 | 2314.43 | 6848.29 | 48010.7 | 2.02 | 8.49 | 23.3 | 365.793 | 1 | 1 | 1110 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 749539.7277 | 78515.7521 | 1199.9969 | 15225.8564 | 63289.8957 | 382217.238 | 0.042292 | -2951380.1971 | 2951380.1971
C | Xist Rating 7852 | -81.43 | 347.223 | 150.304 | 35.9 | 2308.07 | 6855.77 | 45447.9 | 2.06 | 7.92 | 23.616 | 320.062 | 1 | 1 | 1120 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 801414.9896 | 79798.4172 | 1221.7158 | 15363.0262 | 64435.391 | 334826.2343 | 0.042673 | -2585439.4284 | 2585439.4284
C | Xist Rating 7853 | -81.26 | 349.989 | 150.303 | 35.9 | 2311.35 | 6891.72 | 45189.2 | 2 | 7.86 | 23.385 | 315.921 | 1 | 1 | 1130 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 808947.0751 | 81091.3558 | 1243.6296 | 15500.1961 | 65591.1597 | 330452.4462 | 0.043054 | -2551666.1965 | 2551666.1965
C | Xist Rating 7854 | -81 | 355.302 | 150.302 | 35.9 | 2309.52 | 6889.19 | 44681.2 | 1.94 | 7.75 | 23.167 | 307.631 | 1 | 1 | 1140 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 820577.075 | 82394.5679 | 1265.7381 | 15637.366 | 66757.2019 | 321770.949 | 0.043435 | -2484629.9763 | 2484629.9763
C | Xist Rating 7855 | -80.72 | 360.552 | 150.302 | 35.8 | 2310.51 | 6911.76 | 44186.2 | 1.9 | 7.64 | 22.936 | 299.618 | 1 | 1 | 1150 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 833059.0015 | 83708.0535 | 1288.0414 | 15774.5359 | 67933.5177 | 313399.2138 | 0.043816 | -2419985.6559 | 2419985.6559
C | Xist Rating 7856 | -80.47 | 365.881 | 150.301 | 35.8 | 2307.12 | 6895.11 | 43703.1 | 1.85 | 7.53 | 22.746 | 291.989 | 1 | 1 | 1160 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 844131.3727 | 85031.8127 | 1310.5395 | 15911.7058 | 69120.1069 | 305418.1367 | 0.044197 | -2358357.8943 | 2358357.8943
C | Xist Rating 7857 | -79.39 | 386.842 | 150.302 | 35.8 | 2303.11 | 6915.3 | 41832.2 | 1.87 | 7.13 | 22.915 | 262.634 | 1 | 1 | 1170 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 890939.6786 | 86365.8453 | 1333.2324 | 16048.8756 | 70316.9696 | 274992.3102 | 0.044578 | -2123417.7272 | 2123417.7272
C | Xist Rating 7858 | -79.27 | 388.317 | 150.302 | 35.8 | 2309.18 | 6973.71 | 41724.5 | 1.82 | 7.11 | 22.811 | 261.188 | 1 | 1 | 1180 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 896693.8501 | 87710.1514 | 1356.1201 | 16186.0455 | 71524.1059 | 273439.2355 | 0.044959 | -2111425.2957 | 2111425.2957
C | Xist Rating 7859 | -78.77 | 398.803 | 150.301 | 35.8 | 2302.69 | 6942.02 | 40885.5 | 1.77 | 6.92 | 22.611 | 248.9 | 1 | 1 | 1190 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 918319.6801 | 89064.731 | 1379.2026 | 16323.2154 | 72741.5156 | 260617.055 | 0.04534 | -2012415.8171 | 2012415.8171
C | Xist Rating 7860 | -78.53 | 401.461 | 150.301 | 35.8 | 2314.58 | 7058.26 | 40681.8 | 1.74 | 6.88 | 22.659 | 246.024 | 1 | 1 | 1200 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 929213.6014 | 90429.5841 | 1402.4799 | 16460.3853 | 73969.1988 | 257616.2785 | 0.045721 | -1989244.616 | 1989244.616
C | Xist Rating 7861 | -78.27 | 406.859 | 150.301 | 35.8 | 2312.92 | 7056.87 | 40280.8 | 1.68 | 6.8 | 22.482 | 240.429 | 1 | 1 | 1210 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 941032.3183 | 91804.7107 | 1425.9519 | 16597.5551 | 75207.1556 | 251733.6861 | 0.046102 | -1943820.7964 | 1943820.7964
C | Xist Rating 7862 | -77.12 | 430.581 | 150.301 | 35.8 | 2301.53 | 7014.81 | 38537.6 | 1.69 | 6.43 | 22.487 | 216.173 | 1 | 1 | 1220 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 31 | E | Rod | 990995.0889 | 93190.1108 | 1449.6188 | 16734.725 | 76455.3858 | 226573.5552 | 0.046483 | -1749540.9351 | 1749540.9351
C | Xist Rating 7863 | -76.79 | 435.829 | 150.301 | 35.8 | 2307.05 | 7080.27 | 38183.3 | 1.66 | 6.35 | 22.448 | 211.52 | 1 | 1 | 1230 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1005479.2945 | 94585.7844 | 1473.4804 | 16871.8949 | 77713.8895 | 221717.6932 | 0.046864 | -1712045.2561 | 1712045.2561
C | Xist Rating 7864 | -76.5 | 441.218 | 150.3 | 35.8 | 2308.03 | 7103.42 | 37835.7 | 1.61 | 6.28 | 22.338 | 207.086 | 1 | 1 | 1240 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1018344.3805 | 95991.7315 | 1497.5369 | 17009.0648 | 78982.6667 | 217057.465 | 0.047245 | -1676060.209 | 1676060.209
C | Xist Rating 7865 | -76.32 | 444.02 | 150.3 | 35.8 | 2312.46 | 7152.59 | 37664.1 | 1.57 | 6.24 | 22.255 | 204.988 | 1 | 1 | 1250 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1026778.4892 | 97407.9521 | 1521.7881 | 17146.2347 | 80261.7175 | 214837.4501 | 0.047626 | -1658917.8425 | 1658917.8425
C | Xist Rating 7866 | -75.9 | 451.915 | 150.3 | 35.8 | 2312.7 | 7176.19 | 37161.1 | 1.54 | 6.14 | 22.207 | 198.598 | 1 | 1 | 1260 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1045143.8205 | 98834.4462 | 1546.2341 | 17283.4045 | 81551.0417 | 208175.2239 | 0.048007 | -1607473.8979 | 1607473.8979
C | Xist Rating 7867 | -74.79 | 474.378 | 150.3 | 35.8 | 2305.53 | 7168.61 | 35777.3 | 1.55 | 5.85 | 22.277 | 181.343 | 1 | 1 | 1270 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1093692.7103 | 100271.2138 | 1570.8749 | 17420.5744 | 82850.6394 | 190290.0816 | 0.048388 | -1469369.5701 | 1469369.5701
C | Xist Rating 7868 | -74.52 | 479.835 | 150.3 | 35.8 | 2304.29 | 7170.59 | 35477.1 | 1.51 | 5.79 | 22.147 | 177.874 | 1 | 1 | 1280 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1105678.9921 | 101718.2549 | 1595.7105 | 17557.7443 | 84160.5107 | 186640.6193 | 0.048769 | -1441189.3889 | 1441189.3889
C | Xist Rating 7869 | -74.25 | 485.24 | 150.3 | 35.8 | 2304.12 | 7182.88 | 35182.4 | 1.47 | 5.73 | 22.095 | 174.489 | 1 | 1 | 1290 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1118051.1888 | 103175.5696 | 1620.7408 | 17694.9142 | 85480.6554 | 183084.6474 | 0.04915 | -1413731.1165 | 1413731.1165
C | Xist Rating 7870 | -73.83 | 493.113 | 150.3 | 35.8 | 2305.22 | 7214.63 | 34751 | 1.45 | 5.64 | 22.135 | 169.497 | 1 | 1 | 1300 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1136733.9499 | 104643.1577 | 1645.966 | 17832.084 | 86811.0736 | 177892.6515 | 0.049531 | -1373639.9007 | 1373639.9007
C | Xist Rating 7871 | -73.58 | 497.246 | 150.3 | 35.8 | 2308.14 | 7254.01 | 34539.7 | 1.42 | 5.59 | 22.087 | 167.169 | 1 | 1 | 1310 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1147713.3824 | 106121.0193 | 1671.3859 | 17969.2539 | 88151.7653 | 175446.4184 | 0.049912 | -1354750.7372 | 1354750.7372
C | Xist Rating 7872 | -72.46 | 519.807 | 150.3 | 35.8 | 2302.49 | 7259.88 | 33362.6 | 1.42 | 5.35 | 22.142 | 153.921 | 1 | 1 | 1320 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1196850.4194 | 107609.1544 | 1697.0007 | 18106.4238 | 89502.7306 | 161707.071 | 0.050293 | -1248659.1385 | 1248659.1385
C | Xist Rating 7873 | -72.08 | 527.898 | 150.299 | 35.8 | 2299.83 | 7254.52 | 32979.6 | 1.38 | 5.28 | 22.026 | 149.876 | 1 | 1 | 1330 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1214075.6573 | 109107.563 | 1722.8102 | 18243.5937 | 90863.9693 | 157458.0937 | 0.050674 | -1215849.6617 | 1215849.6617
C | Xist Rating 7874 | -71.62 | 535.887 | 150.299 | 35.8 | 2303.39 | 7311.27 | 32606.7 | 1.36 | 5.2 | 21.929 | 145.97 | 1 | 1 | 1340 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1234356.7569 | 110616.2451 | 1748.8145 | 18380.7635 | 92235.4815 | 153380.9601 | 0.051055 | -1184367.1167 | 1184367.1167
C | Xist Rating 7875 | -71.33 | 540.037 | 150.299 | 35.8 | 2309.66 | 7385.66 | 32423.6 | 1.32 | 5.16 | 21.89 | 144.133 | 1 | 1 | 1350 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1247301.8574 | 112135.2007 | 1775.0136 | 18517.9334 | 93617.2673 | 151430.4117 | 0.051436 | -1169305.4991 | 1169305.4991
C | Xist Rating 7876 | -71.03 | 542.641 | 150.299 | 35.8 | 2323.7 | 7538.76 | 32303 | 1.31 | 5.14 | 21.984 | 142.894 | 1 | 1 | 1360 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1260934.8917 | 113664.4298 | 1801.4075 | 18655.1033 | 95009.3265 | 150150.8264 | 0.051817 | -1159424.8812 | 1159424.8812
C | Xist Rating 7877 | -69.65 | 574.598 | 150.299 | 35.8 | 2299.77 | 7379.41 | 30902.2 | 1.3 | 4.86 | 21.893 | 128.712 | 1 | 1 | 1370 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1321443.2425 | 115203.9324 | 1827.9962 | 18792.2732 | 96411.6592 | 135414.9858 | 0.052198 | -1045638.626 | 1045638.626
C | Xist Rating 7878 | -69.52 | 577.464 | 150.299 | 35.8 | 2299.21 | 7380.82 | 30793.8 | 1.27 | 4.84 | 21.847 | 127.733 | 1 | 1 | 1380 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1327711.0034 | 116753.7085 | 1854.7797 | 18929.4431 | 97824.2654 | 134366.8119 | 0.052579 | -1037544.9048 | 1037544.9048
C | Xist Rating 7879 | -69.15 | 584.24 | 150.299 | 35.8 | 2300.55 | 7412.51 | 30526.6 | 1.25 | 4.78 | 21.806 | 125.218 | 1 | 1 | 1390 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1344073.332 | 118313.7581 | 1881.7579 | 19066.6129 | 99247.1452 | 131737.008 | 0.05296 | -1017238.2561 | 1017238.2561
C | Xist Rating 7880 | -68.79 | 591.013 | 150.299 | 35.8 | 2301.82 | 7443.79 | 30264.9 | 1.22 | 4.73 | 21.771 | 122.779 | 1 | 1 | 1400 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1360405.5437 | 119884.0812 | 1908.931 | 19203.7828 | 100680.2984 | 129172.5961 | 0.053341 | -997436.547 | 997436.547
C | Xist Rating 7881 | -68.36 | 599.063 | 150.299 | 35.8 | 2302.7 | 7474.73 | 29957.2 | 1.2 | 4.67 | 21.748 | 119.93 | 1 | 1 | 1410 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1379462.3701 | 121464.6778 | 1936.2988 | 19340.9527 | 102123.7251 | 126196.5556 | 0.053722 | -974456.3516 | 974456.3516
C | Xist Rating 7882 | -67.18 | 623.028 | 150.299 | 35.8 | 2297.67 | 7488.46 | 29051.6 | 1.21 | 4.49 | 21.824 | 111.568 | 1 | 1 | 1420 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1431512.7448 | 123055.5479 | 1963.8614 | 19478.1226 | 103577.4254 | 117544.0262 | 0.054103 | -907643.8127 | 907643.8127
C | Xist Rating 7883 | -66.98 | 627.418 | 150.299 | 35.8 | 2296.57 | 7487.67 | 28910.4 | 1.17 | 4.47 | 21.728 | 110.409 | 1 | 1 | 1430 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1440909.3563 | 124656.6915 | 1991.6188 | 19615.2924 | 105041.3991 | 116289.0877 | 0.054484 | -897953.5102 | 897953.5102
C | Xist Rating 7884 | -66.44 | 638.073 | 150.299 | 35.7 | 2295.98 | 7510.23 | 28541.6 | 1.15 | 4.39 | 21.712 | 107.192 | 1 | 1 | 1440 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1465002.8465 | 126268.1086 | 2019.571 | 19752.4623 | 106515.6463 | 112930.396 | 0.054865 | -872018.5837 | 872018.5837
C | Xist Rating 7885 | -66.07 | 644.884 | 150.299 | 35.7 | 2297.17 | 7541.22 | 28316.6 | 1.13 | 4.35 | 21.684 | 105.29 | 1 | 1 | 1450 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1481408.1783 | 127889.7992 | 2047.718 | 19889.6322 | 108000.167 | 110936.084 | 0.055246 | -856619.0348 | 856619.0348
C | Xist Rating 7886 | -65.76 | 648.915 | 150.299 | 35.7 | 2304.61 | 7633.15 | 28183.4 | 1.12 | 4.32 | 21.719 | 104.175 | 1 | 1 | 1460 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1495495.9981 | 129521.7633 | 2076.0598 | 20026.8021 | 109494.9613 | 109777.5161 | 0.055627 | -847672.8809 | 847672.8809
C | Xist Rating 7887 | -64.58 | 675.912 | 150.299 | 35.7 | 2289.38 | 7542.16 | 27310 | 1.11 | 4.16 | 21.684 | 96.832 | 1 | 1 | 1470 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1547419.4146 | 131164.0009 | 2104.5964 | 20163.9719 | 111000.029 | 102145.8549 | 0.056008 | -788743.2159 | 788743.2159
C | Xist Rating 7888 | -64.16 | 684.006 | 150.299 | 35.7 | 2289.93 | 7569.81 | 27065.8 | 1.09 | 4.11 | 21.669 | 94.879 | 1 | 1 | 1480 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1566325.8596 | 132816.512 | 2133.3277 | 20301.1418 | 112515.3702 | 100098.6013 | 0.056389 | -772934.8657 | 772934.8657
C | Xist Rating 7889 | -63.79 | 690.819 | 150.299 | 35.7 | 2291.75 | 7607.92 | 26866 | 1.07 | 4.07 | 21.655 | 93.313 | 1 | 1 | 1490 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1583184.4433 | 134479.2966 | 2162.2539 | 20438.3117 | 114040.9849 | 98452.9546 | 0.05677 | -760227.6182 | 760227.6182
C | Xist Rating 7890 | -63.44 | 697.724 | 150.299 | 35.7 | 2291.72 | 7625.89 | 26669.5 | 1.05 | 4.03 | 21.621 | 91.8 | 1 | 1 | 1500 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1598988.0453 | 136152.3547 | 2191.3748 | 20575.4816 | 115576.8732 | 96860.572 | 0.057151 | -747931.6623 | 747931.6623
C | Xist Rating 7891 | -62.99 | 705.845 | 150.299 | 35.7 | 2294.14 | 7674.94 | 26438.2 | 1.04 | 3.99 | 21.618 | 90.011 | 1 | 1 | 1510 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1619307.2483 | 137835.6863 | 2220.6906 | 20712.6515 | 117123.0349 | 94998.0291 | 0.057532 | -733549.5993 | 733549.5993
C | Xist Rating 7892 | -61.66 | 732.526 | 150.299 | 35.7 | 2290.66 | 7711.71 | 25680.5 | 1.04 | 3.84 | 21.701 | 84.131 | 1 | 1 | 1520 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1677968.0072 | 139529.2914 | 2250.2011 | 20849.8213 | 118679.4701 | 88907.6174 | 0.057913 | -686521.0551 | 686521.0551
C | Xist Rating 7893 | -61.3 | 740.991 | 150.299 | 35.7 | 2286.68 | 7688.86 | 25467.9 | 1.01 | 3.8 | 21.619 | 82.613 | 1 | 1 | 1530 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1694409.2999 | 141233.1701 | 2279.9064 | 20986.9912 | 120246.1788 | 87290.9646 | 0.058294 | -674037.6907 | 674037.6907
C | Xist Rating 7894 | -60.97 | 745.296 | 150.299 | 35.7 | 2293.82 | 7781.44 | 25363.1 | 0.99 | 3.78 | 21.612 | 81.889 | 1 | 1 | 1540 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1709574.8707 | 142947.3222 | 2309.8065 | 21124.1611 | 121823.1611 | 86518.5538 | 0.058675 | -668073.3388 | 668073.3388
C | Xist Rating 7895 | -60.29 | 758.681 | 150.299 | 35.7 | 2292.61 | 7805.16 | 25021 | 0.98 | 3.72 | 21.579 | 79.403 | 1 | 1 | 1550 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1739359.6474 | 144671.7478 | 2339.9013 | 21261.331 | 123410.4168 | 83929.1748 | 0.059056 | -648078.8406 | 648078.8406
C | Xist Rating 7896 | -59.92 | 762.762 | 150.299 | 35.7 | 2303.19 | 7940.87 | 24920 | 0.97 | 3.7 | 21.649 | 78.699 | 1 | 1 | 1560 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1756785.8108 | 146406.4469 | 2370.191 | 21398.5008 | 125007.946 | 83197.2097 | 0.059437 | -642426.8005 | 642426.8005
C | Xist Rating 7897 | -58.68 | 793.973 | 150.298 | 35.7 | 2282.21 | 7783.81 | 24161.1 | 0.96 | 3.56 | 21.554 | 73.336 | 1 | 1 | 1570 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1812013.1203 | 148151.4195 | 2400.6755 | 21535.6707 | 126615.7487 | 77615.5021 | 0.059818 | -599326.3336 | 599326.3336
C | Xist Rating 7898 | -58.28 | 800.906 | 150.298 | 35.7 | 2285.12 | 7836.56 | 24006.4 | 0.94 | 3.53 | 21.546 | 72.312 | 1 | 1 | 1580 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1830166.3187 | 149906.6656 | 2431.3547 | 21672.8406 | 128233.825 | 76530.2918 | 0.0602 | -590946.6274 | 590946.6274
C | Xist Rating 7899 | -57.86 | 807.875 | 150.298 | 35.7 | 2289.04 | 7901.93 | 23854 | 0.93 | 3.5 | 21.539 | 71.315 | 1 | 1 | 1590 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1849258.19 | 151672.1852 | 2462.2288 | 21810.0105 | 129862.1747 | 75488.1673 | 0.060581 | -582899.6179 | 582899.6179
C | Xist Rating 7900 | -57.29 | 817.304 | 150.298 | 35.7 | 2293.39 | 7981.07 | 23644.7 | 0.92 | 3.46 | 21.565 | 69.922 | 1 | 1 | 1600 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1874396.8206 | 153447.9783 | 2493.2976 | 21947.1804 | 131500.7979 | 74036.7858 | 0.060962 | -571692.4349 | 571692.4349
C | Xist Rating 7901 | -57.04 | 821.805 | 150.298 | 35.7 | 2295.21 | 8014.95 | 23555.9 | 0.89 | 3.45 | 21.534 | 69.387 | 1 | 1 | 1610 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1886215.054 | 155234.0449 | 2524.5612 | 22084.3502 | 133149.6946 | 73441.4023 | 0.061343 | -567095.0411 | 567095.0411
C | Xist Rating 7902 | -55.49 | 856.761 | 150.298 | 35.7 | 2281.54 | 7951.17 | 22804.4 | 0.9 | 3.31 | 21.568 | 64.45 | 1 | 1 | 1620 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1954734.4919 | 157030.385 | 2556.0196 | 22221.5201 | 134808.8649 | 68340.7855 | 0.061724 | -527709.4305 | 527709.4305
C | Xist Rating 7903 | -55.11 | 860.917 | 150.298 | 35.7 | 2290.41 | 8071.73 | 22722.7 | 0.89 | 3.29 | 21.595 | 63.956 | 1 | 1 | 1630 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1971852.906 | 158836.9986 | 2587.6728 | 22358.69 | 136478.3086 | 67822.4655 | 0.062105 | -523707.1011 | 523707.1011
C | Xist Rating 7904 | -54.75 | 868.033 | 150.298 | 35.7 | 2291.02 | 8099.05 | 22587.9 | 0.87 | 3.27 | 21.569 | 63.15 | 1 | 1 | 1640 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 1988680.9637 | 160653.8857 | 2619.5208 | 22495.8599 | 138158.0258 | 66960.638 | 0.062486 | -517052.2976 | 517052.2976
C | Xist Rating 7905 | -54.28 | 877.82 | 150.298 | 35.7 | 2289.61 | 8109.13 | 22402.3 | 0.85 | 3.23 | 21.541 | 62.031 | 1 | 1 | 1650 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2009865.4502 | 162481.0463 | 2651.5635 | 22633.0297 | 139848.0165 | 65773.3042 | 0.062867 | -507884.0208 | 507884.0208
C | Xist Rating 7906 | -53.76 | 887.363 | 150.298 | 35.7 | 2291.12 | 8155.96 | 22220.2 | 0.84 | 3.2 | 21.547 | 60.928 | 1 | 1 | 1660 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2033055.1166 | 164318.4804 | 2683.8011 | 22770.1996 | 141548.2808 | 64620.3944 | 0.063248 | -498981.5566 | 498981.5566
C | Xist Rating 7907 | -52.39 | 918.618 | 150.298 | 35.7 | 2279.64 | 8103.73 | 21632.5 | 0.84 | 3.09 | 21.571 | 57.368 | 1 | 1 | 1670 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2094118.3375 | 166166.188 | 2716.2334 | 22907.3695 | 143258.8185 | 60932.9622 | 0.063629 | -470508.1825 | 470508.1825
C | Xist Rating 7908 | -52.07 | 922.886 | 150.298 | 35.7 | 2284.93 | 8182.89 | 21560 | 0.83 | 3.08 | 21.58 | 56.967 | 1 | 1 | 1680 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2108729.908 | 168024.1691 | 2748.8606 | 23044.5394 | 144979.6297 | 60508.9648 | 0.06401 | -467234.1869 | 467234.1869
C | Xist Rating 7909 | -51.54 | 935.393 | 150.298 | 35.7 | 2280.35 | 8159.93 | 21345.5 | 0.81 | 3.04 | 21.545 | 55.749 | 1 | 1 | 1690 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2133023.4276 | 169892.4237 | 2781.6825 | 23181.7092 | 146710.7144 | 59217.2595 | 0.064391 | -457259.9814 | 457259.9814
C | Xist Rating 7910 | -51.06 | 943.671 | 150.298 | 35.7 | 2283.26 | 8221.37 | 21205.3 | 0.8 | 3.02 | 21.55 | 54.961 | 1 | 1 | 1700 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2154646.2475 | 171770.9518 | 2814.6992 | 23318.8791 | 148452.0726 | 58390.6324 | 0.064772 | -450876.9861 | 450876.9861
C | Xist Rating 7911 | -50.57 | 953.407 | 150.298 | 35.7 | 2282.99 | 8245.97 | 21044.4 | 0.79 | 2.99 | 21.54 | 54.068 | 1 | 1 | 1710 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2176618.6469 | 173659.7534 | 2847.9107 | 23456.049 | 150203.7044 | 57453.8575 | 0.065153 | -443643.4581 | 443643.4581
C | Xist Rating 7912 | -49.31 | 982.145 | 150.298 | 35.7 | 2273.5 | 8208.21 | 20566.8 | 0.78 | 2.9 | 21.567 | 51.383 | 1 | 1 | 1720 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2232906.6575 | 175558.8285 | 2881.317 | 23593.2189 | 151965.6096 | 54658.1336 | 0.065534 | -422055.619 | 422055.619
C | Xist Rating 7913 | -48.71 | 994.522 | 150.298 | 35.7 | 2272.29 | 8228.07 | 20374 | 0.77 | 2.87 | 21.558 | 50.349 | 1 | 1 | 1730 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2259842.3954 | 177468.1771 | 2914.9181 | 23730.3888 | 153737.7883 | 53574.6048 | 0.065915 | -413688.8974 | 413688.8974
C | Xist Rating 7914 | -48.34 | 1000.22 | 150.298 | 35.7 | 2276.43 | 8298.68 | 20289.8 | 0.76 | 2.85 | 21.56 | 49.917 | 1 | 1 | 1740 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2276930.8146 | 179387.7992 | 2948.714 | 23867.5586 | 155520.2405 | 53116.7187 | 0.066296 | -410153.2218 | 410153.2218
C | Xist Rating 7915 | -47.84 | 1011.45 | 150.298 | 35.7 | 2273.8 | 8296.06 | 20123.3 | 0.75 | 2.82 | 21.537 | 49.052 | 1 | 1 | 1750 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2299835.01 | 181317.6948 | 2982.7046 | 24004.7285 | 157312.9663 | 52207.4968 | 0.066677 | -403132.4519 | 403132.4519
C | Xist Rating 7916 | -47.45 | 1019.84 | 150.299 | 35.7 | 2272.04 | 8296.69 | 20000.6 | 0.74 | 2.8 | 21.531 | 48.421 | 1 | 1 | 1760 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2317117.2736 | 183257.8639 | 3016.8901 | 24141.8984 | 159115.9655 | 51542.1036 | 0.067058 | -397994.4619 | 397994.4619
C | Xist Rating 7917 | -45.98 | 1053.9 | 150.299 | 35.7 | 2261.14 | 8253.11 | 19497.1 | 0.74 | 2.71 | 21.572 | 45.781 | 1 | 1 | 1770 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2383015.446 | 185208.3065 | 3051.2703 | 24279.0683 | 160929.2382 | 48810.0169 | 0.067439 | -376898.012 | 376898.012
C | Xist Rating 7918 | -45.72 | 1062.41 | 150.299 | 35.7 | 2254.29 | 8185.64 | 19383.8 | 0.72 | 2.69 | 21.837 | 45.215 | 1 | 1 | 1780 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2394980.2389 | 187169.0226 | 3085.8453 | 24416.2381 | 162752.7844 | 48210.1821 | 0.06782 | -372266.2469 | 372266.2469
C | Xist Rating 7919 | -45.25 | 1066.93 | 150.299 | 35.7 | 2265.23 | 8344.12 | 19326 | 0.72 | 2.68 | 21.557 | 44.966 | 1 | 1 | 1790 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2416841.8439 | 189140.0122 | 3120.6151 | 24553.408 | 164586.6041 | 47942.468 | 0.068201 | -370199.0297 | 370199.0297
C | Xist Rating 7920 | -44.57 | 1082.07 | 150.299 | 35.7 | 2261.94 | 8343.73 | 19121.7 | 0.71 | 2.65 | 21.548 | 43.957 | 1 | 1 | 1800 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2447577.4158 | 191121.2753 | 3155.5797 | 24690.5779 | 166430.6974 | 46883.6716 | 0.068582 | -362023.2848 | 362023.2848
C | Xist Rating 7921 | -44.4 | 1090.45 | 150.299 | 35.7 | 2251.64 | 8228.48 | 19013 | 0.69 | 2.63 | 21.818 | 43.424 | 1 | 1 | 1810 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2455300.838 | 193112.8119 | 3190.7391 | 24827.7478 | 168285.0641 | 46317.1598 | 0.068963 | -357648.8309 | 357648.8309
C | Xist Rating 7922 | -42.67 | 1124.77 | 150.299 | 35.7 | 2252.2 | 8336.77 | 18562.5 | 0.7 | 2.55 | 21.58 | 41.237 | 1 | 1 | 1820 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2533206.994 | 195114.6219 | 3226.0933 | 24964.9177 | 170149.7043 | 44056.9198 | 0.069344 | -340195.8566 | 340195.8566
C | Xist Rating 7923 | -42.9 | 1119.33 | 150.299 | 35.6 | 2257.01 | 8386.88 | 18631.3 | 0.69 | 2.56 | 21.873 | 41.569 | 1 | 1 | 1830 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2526339.0033 | 197126.7055 | 3261.6423 | 25102.0875 | 172024.618 | 44407.3544 | 0.069725 | -342901.82 | 342901.82
C | Xist Rating 7924 | -42.44 | 1126.22 | 150.3 | 35.6 | 2261.27 | 8466.54 | 18545.3 | 0.68 | 2.55 | 21.899 | 41.17 | 1 | 1 | 1840 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2546687.4994 | 199149.0626 | 3297.386 | 25239.2574 | 173909.8052 | 43983.1766 | 0.070106 | -339626.4311 | 339626.4311
C | Xist Rating 7925 | -41.94 | 1137.56 | 150.299 | 35.6 | 2258.16 | 8455.73 | 18409.3 | 0.67 | 2.52 | 21.884 | 40.55 | 1 | 1 | 1850 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2568792.4896 | 201181.6932 | 3333.3246 | 25376.4273 | 175805.266 | 43326.9893 | 0.070487 | -334559.5266 | 334559.5266
C | Xist Rating 7926 | -41.37 | 1150.28 | 150.299 | 35.6 | 2255.12 | 8449.81 | 18259.2 | 0.66 | 2.5 | 21.869 | 39.868 | 1 | 1 | 1860 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2594019.4336 | 203224.5973 | 3369.4579 | 25513.5972 | 177711.0002 | 42606.2348 | 0.070868 | -328994.0511 | 328994.0511
C | Xist Rating 7927 | -39.96 | 1181.82 | 150.3 | 35.6 | 2248.56 | 8452.89 | 17879.5 | 0.66 | 2.43 | 21.924 | 38.108 | 1 | 1 | 1870 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2657393.1792 | 205277.7749 | 3405.7861 | 25650.767 | 179627.0079 | 40787.9901 | 0.071249 | -314954.0475 | 314954.0475
C | Xist Rating 7928 | -39.39 | 1194.52 | 150.3 | 35.6 | 2246.22 | 8456.41 | 17738.6 | 0.65 | 2.41 | 21.914 | 37.495 | 1 | 1 | 1880 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2683154.7144 | 207341.226 | 3442.309 | 25787.9369 | 181553.2891 | 40138.8534 | 0.07163 | -309941.5863 | 309941.5863
C | Xist Rating 7929 | -38.89 | 1202.95 | 150.3 | 35.6 | 2249.1 | 8521.79 | 17646.4 | 0.64 | 2.39 | 21.933 | 37.098 | 1 | 1 | 1890 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2705554.845 | 209414.9506 | 3479.0267 | 25925.1068 | 183489.8438 | 39715.4193 | 0.072011 | -306671.9407 | 306671.9407
C | Xist Rating 7930 | -38.5 | 1211.83 | 150.3 | 35.6 | 2246.75 | 8512.62 | 17555.3 | 0.63 | 2.38 | 21.919 | 36.722 | 1 | 1 | 1900 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2722679.0525 | 211498.9487 | 3515.9392 | 26062.2767 | 185436.6721 | 39311.8052 | 0.072392 | -303555.3394 | 303555.3394
C | Xist Rating 7931 | -38.05 | 1220.43 | 150.3 | 35.7 | 2247.69 | 8550.88 | 17465.1 | 0.62 | 2.36 | 21.922 | 36.345 | 1 | 1 | 1910 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2743148.3067 | 213593.2203 | 3553.0464 | 26199.4465 | 187393.7738 | 38907.8744 | 0.072773 | -300436.2928 | 300436.2928
C | Xist Rating 7932 | -36.36 | 1258.72 | 150.3 | 35.7 | 2238.89 | 8540.02 | 17050.5 | 0.62 | 2.29 | 21.972 | 34.536 | 1 | 1 | 1920 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2818135.6208 | 215697.7654 | 3590.3485 | 26336.6164 | 189361.149 | 37037.9911 | 0.073154 | -285997.5498 | 285997.5498
C | Xist Rating 7933 | -35.86 | 1271.5 | 150.3 | 35.7 | 2234.51 | 8513.14 | 16924 | 0.61 | 2.27 | 21.966 | 34.02 | 1 | 1 | 1930 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2841179.465 | 217812.584 | 3627.8454 | 26473.7863 | 191338.7977 | 36488.9073 | 0.073535 | -281757.67 | 281757.67
C | Xist Rating 7934 | -35.47 | 1275.67 | 150.3 | 35.7 | 2240.9 | 8619.05 | 16882.2 | 0.6 | 2.26 | 22.002 | 33.855 | 1 | 1 | 1940 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2858648.903 | 219937.6761 | 3665.537 | 26610.9562 | 193326.7199 | 36306.338 | 0.073916 | -280347.918 | 280347.918
C | Xist Rating 7935 | -35.1 | 1287.58 | 150.3 | 35.7 | 2233.88 | 8548.71 | 16772 | 0.59 | 2.24 | 21.968 | 33.427 | 1 | 1 | 1950 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2876299.2104 | 222073.0417 | 3703.4235 | 26748.1261 | 195324.9156 | 35846.7931 | 0.074297 | -276799.4344 | 276799.4344
C | Xist Rating 7936 | -34.47 | 1301.62 | 150.3 | 35.7 | 2231.3 | 8551.64 | 16637 | 0.58 | 2.22 | 21.999 | 32.883 | 1 | 1 | 1960 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2904304.706 | 224218.6808 | 3741.5047 | 26885.2959 | 197333.3849 | 35269.9391 | 0.074678 | -272345.1209 | 272345.1209
C | Xist Rating 7937 | -32.97 | 1336.07 | 150.3 | 35.7 | 2224.18 | 8550.24 | 16303 | 0.58 | 2.16 | 22.074 | 31.52 | 1 | 1 | 1970 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2971660.1726 | 226374.5934 | 3779.7807 | 27022.4658 | 199352.1276 | 33864.0264 | 0.075059 | -261489.0354 | 261489.0354
C | Xist Rating 7938 | -32.48 | 1346.03 | 150.3 | 35.7 | 2224.33 | 8580.86 | 16214.1 | 0.57 | 2.15 | 22.102 | 31.18 | 1 | 1 | 1980 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 2994014.9099 | 228540.7795 | 3818.2515 | 27159.6357 | 201381.1438 | 33498.501 | 0.07544 | -258666.5452 | 258666.5452
C | Xist Rating 7939 | -31.96 | 1359.01 | 150.3 | 35.7 | 2220.57 | 8561.43 | 16101.2 | 0.56 | 2.13 | 22.107 | 30.755 | 1 | 1 | 1990 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3017776.8357 | 230717.2391 | 3856.9171 | 27296.8056 | 203420.4335 | 33043.3208 | 0.075821 | -255151.7642 | 255151.7642
C | Xist Rating 7940 | -31.48 | 1369.09 | 150.3 | 35.7 | 2219.88 | 8579.48 | 16014.9 | 0.56 | 2.12 | 22.113 | 30.433 | 1 | 1 | 2000 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3039215.5092 | 232903.9722 | 3895.7775 | 27433.9754 | 205469.9967 | 32714.7748 | 0.076202 | -252614.819 | 252614.819
C | Xist Rating 7941 | -31.08 | 1376.46 | 150.3 | 35.7 | 2221.22 | 8619.95 | 15953.7 | 0.55 | 2.11 | 22.12 | 30.212 | 1 | 1 | 2010 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3057420.4812 | 235100.9788 | 3934.8326 | 27571.1453 | 207529.8335 | 32471.241 | 0.076583 | -250734.3157 | 250734.3157
C | Xist Rating 7942 | -29.47 | 1415.2 | 150.3 | 35.7 | 2211.51 | 8589.45 | 15614.8 | 0.55 | 2.05 | 22.157 | 28.908 | 1 | 1 | 2020 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3129728.952 | 237308.2589 | 3974.0826 | 27708.3152 | 209599.9437 | 31124.335 | 0.076964 | -240333.8649 | 240333.8649
C | Xist Rating 7943 | -28.82 | 1429.18 | 150.3 | 35.7 | 2210.42 | 8613.44 | 15499.8 | 0.54 | 2.03 | 22.168 | 28.487 | 1 | 1 | 2030 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3159088.0556 | 239525.8125 | 4013.5273 | 27845.4851 | 211680.3274 | 30672.9686 | 0.077345 | -236848.5332 | 236848.5332
C | Xist Rating 7944 | -28.46 | 1438.26 | 150.3 | 35.7 | 2208.13 | 8602.92 | 15431.6 | 0.53 | 2.02 | 22.156 | 28.255 | 1 | 1 | 2040 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3175865.0538 | 241753.6396 | 4053.1669 | 27982.6549 | 213770.9846 | 30416.5503 | 0.077726 | -234868.5391 | 234868.5391
C | Xist Rating 7945 | -27.92 | 1446.53 | 150.3 | 35.7 | 2212.78 | 8698.72 | 15364.1 | 0.53 | 2.01 | 22.181 | 28.013 | 1 | 1 | 2050 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3200852.6534 | 243991.7401 | 4093.0012 | 28119.8248 | 215871.9153 | 30171.7149 | 0.078107 | -232977.9846 | 232977.9846
C | Xist Rating 7946 | -27.44 | 1459.9 | 150.3 | 35.7 | 2207.58 | 8655.39 | 15264.1 | 0.52 | 1.99 | 22.157 | 27.669 | 1 | 1 | 2060 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3222846.042 | 246240.1142 | 4133.0303 | 28256.9947 | 217983.1195 | 29798.1069 | 0.078488 | -230093.0831 | 230093.0831
C | Xist Rating 7947 | -25.73 | 1501.46 | 150.3 | 35.7 | 2197.63 | 8625.87 | 14936 | 0.52 | 1.94 | 22.195 | 26.479 | 1 | 1 | 2070 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3299653.5398 | 248498.7618 | 4173.2542 | 28394.1646 | 220104.5973 | 28569.2918 | 0.078869 | -220604.4985 | 220604.4985
C | Xist Rating 7948 | -25.27 | 1510.34 | 150.3 | 35.7 | 2198.59 | 8665.05 | 14873.3 | 0.51 | 1.93 | 22.199 | 26.274 | 1 | 1 | 2080 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3320618.4206 | 250767.6829 | 4213.6729 | 28531.3345 | 222236.3485 | 28341.0697 | 0.07925 | -218842.2275 | 218842.2275
C | Xist Rating 7949 | -24.77 | 1521.88 | 150.3 | 35.7 | 2196.97 | 8672.36 | 14790.7 | 0.5 | 1.91 | 22.196 | 25.997 | 1 | 1 | 2090 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3343524.7036 | 253046.8775 | 4254.2864 | 28668.5043 | 224378.3732 | 28037.5431 | 0.079631 | -216498.4758 | 216498.4758
C | Xist Rating 7950 | -24.3 | 1533.43 | 150.3 | 35.7 | 2194.55 | 8666.97 | 14709.2 | 0.5 | 1.9 | 22.201 | 25.726 | 1 | 1 | 2100 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3365188.8065 | 255336.3456 | 4295.0947 | 28805.6742 | 226530.6714 | 27761.32 | 0.080012 | -214365.5542 | 214365.5542
C | Xist Rating 7951 | -23.88 | 1543.62 | 150.3 | 35.7 | 2192.89 | 8669.3 | 14638.6 | 0.49 | 1.89 | 22.204 | 25.495 | 1 | 1 | 2110 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3384988.8618 | 257636.0872 | 4336.0977 | 28942.8441 | 228693.2431 | 27505.5439 | 0.080393 | -212390.5193 | 212390.5193
C | Xist Rating 7952 | -22.32 | 1582.79 | 150.3 | 35.7 | 2182.75 | 8625.32 | 14359 | 0.49 | 1.84 | 22.237 | 24.539 | 1 | 1 | 2120 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3454834.8725 | 259946.1023 | 4377.2956 | 29080.014 | 230866.0883 | 26519.153 | 0.080774 | -204773.8697 | 204773.8697
C | Xist Rating 7953 | -21.74 | 1597.12 | 150.3 | 35.7 | 2179.84 | 8619.67 | 14263.7 | 0.48 | 1.83 | 22.235 | 24.232 | 1 | 1 | 2130 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3481466.0608 | 262266.3909 | 4418.6882 | 29217.1838 | 233049.207 | 26183.8953 | 0.081155 | -202185.0991 | 202185.0991
C | Xist Rating 7954 | -21.24 | 1611.47 | 150.3 | 35.7 | 2174.35 | 8573.54 | 14169.8 | 0.48 | 1.81 | 22.234 | 23.932 | 1 | 1 | 2140 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3503899.7945 | 264596.953 | 4460.2756 | 29354.3537 | 235242.5993 | 25877.0838 | 0.081536 | -199815.9818 | 199815.9818
C | Xist Rating 7955 | -20.89 | 1618.98 | 150.3 | 35.7 | 2174.62 | 8597.55 | 14123.4 | 0.47 | 1.8 | 22.235 | 23.793 | 1 | 1 | 2150 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3520666.2876 | 266937.7886 | 4502.0578 | 29491.5236 | 237446.265 | 25716.1341 | 0.081917 | -198573.1707 | 198573.1707
C | Xist Rating 7956 | -20.42 | 1629.11 | 150.3 | 35.7 | 2174.58 | 8624.43 | 14059.1 | 0.46 | 1.79 | 22.244 | 23.593 | 1 | 1 | 2160 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3542630.0238 | 269288.8977 | 4544.0348 | 29628.6935 | 239660.2042 | 25491.9914 | 0.082298 | -196842.4004 | 196842.4004
C | Xist Rating 7957 | -18.81 | 1671.32 | 150.3 | 35.7 | 2163.1 | 8563.98 | 13785.9 | 0.46 | 1.75 | 22.27 | 22.712 | 1 | 1 | 2170 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3615232.292 | 271650.2803 | 4586.2066 | 29765.8634 | 241884.4169 | 24582.8242 | 0.082679 | -189822.0523 | 189822.0523
C | Xist Rating 7958 | -18.18 | 1685.42 | 150.3 | 35.7 | 2162.15 | 8588.03 | 13698.9 | 0.46 | 1.74 | 22.275 | 22.444 | 1 | 1 | 2180 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3644130.853 | 274021.9364 | 4628.5732 | 29903.0332 | 244118.9031 | 24309.3233 | 0.08306 | -187710.1509 | 187710.1509
C | Xist Rating 7959 | -17.75 | 1695.78 | 150.3 | 35.7 | 2160.65 | 8591.51 | 13638.8 | 0.45 | 1.73 | 22.279 | 22.267 | 1 | 1 | 2190 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3663987.057 | 276403.8659 | 4671.1346 | 30040.2031 | 246363.6628 | 24108.4123 | 0.083441 | -186158.7691 | 186158.7691
C | Xist Rating 7960 | -17.35 | 1706.54 | 150.3 | 35.7 | 2158.06 | 8577.93 | 13579.3 | 0.45 | 1.72 | 22.266 | 22.098 | 1 | 1 | 2200 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3682815.7124 | 278796.069 | 4713.8907 | 30177.373 | 248618.6961 | 23936.8231 | 0.083822 | -184833.8027 | 184833.8027
C | Xist Rating 7961 | -16.76 | 1720.9 | 150.3 | 35.7 | 2156.03 | 8584.69 | 13495.3 | 0.44 | 1.7 | 22.266 | 21.847 | 1 | 1 | 2210 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3710312.027 | 281198.5456 | 4756.8417 | 30314.5429 | 250884.0028 | 23658.594 | 0.084203 | -182685.3917 | 182685.3917
C | Xist Rating 7962 | -15.12 | 1762.98 | 150.3 | 35.7 | 2146.45 | 8550.4 | 13246.2 | 0.44 | 1.66 | 22.304 | 21.082 | 1 | 1 | 2220 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3784148.421 | 283611.2957 | 4799.9874 | 30451.7127 | 253159.583 | 22870.198 | 0.084584 | -176597.6069 | 176597.6069
C | Xist Rating 7963 | -14.6 | 1774.49 | 150.3 | 35.7 | 2146 | 8573.92 | 13182.5 | 0.44 | 1.65 | 22.307 | 20.9 | 1 | 1 | 2230 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3808055.54 | 286034.3193 | 4843.3279 | 30588.8826 | 255445.4367 | 22685.7222 | 0.084965 | -175173.1338 | 175173.1338
C | Xist Rating 7964 | -14.1 | 1787.83 | 150.3 | 35.7 | 2143.07 | 8561.74 | 13111.6 | 0.43 | 1.64 | 22.301 | 20.701 | 1 | 1 | 2240 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3831444.8381 | 288467.6164 | 4886.8633 | 30726.0525 | 257741.5639 | 22460.8037 | 0.085346 | -173436.3728 | 173436.3728
C | Xist Rating 7965 | -13.55 | 1802.5 | 150.3 | 35.7 | 2139.98 | 8550.73 | 13034 | 0.42 | 1.63 | 22.297 | 20.483 | 1 | 1 | 2250 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3857313.95 | 290911.187 | 4930.5934 | 30863.2224 | 260047.9646 | 22216.0483 | 0.085727 | -171546.4361 | 171546.4361
C | Xist Rating 7966 | -13.18 | 1809.97 | 150.3 | 35.7 | 2140.63 | 8580.21 | 12995.5 | 0.42 | 1.62 | 22.304 | 20.38 | 1 | 1 | 2260 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3874476.0811 | 293365.0311 | 4974.5182 | 31000.3922 | 262364.6388 | 22113.5785 | 0.086108 | -170755.1916 | 170755.1916
C | Xist Rating 7967 | -11.47 | 1855.18 | 150.3 | 35.7 | 2130.05 | 8534.32 | 12751.8 | 0.42 | 1.59 | 22.335 | 19.672 | 1 | 1 | 2270 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3951626.159 | 295829.1487 | 5018.6379 | 31137.5621 | 264691.5865 | 21383.8455 | 0.086489 | -165120.3865 | 165120.3865
C | Xist Rating 7968 | -10.96 | 1868.46 | 150.3 | 35.7 | 2127.67 | 8530.05 | 12686.1 | 0.41 | 1.58 | 22.331 | 19.495 | 1 | 1 | 2280 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 30 | E | Rod | 3975466.2882 | 298303.5398 | 5062.9524 | 31274.732 | 267028.8078 | 21181.2421 | 0.08687 | -163555.9369 | 163555.9369
C | Xist Rating 7969 | -10.32 | 1884.25 | 150.3 | 35.7 | 2125.7 | 8539.79 | 12606.9 | 0.41 | 1.56 | 22.327 | 19.278 | 1 | 1 | 2290 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4005350.225 | 300788.2044 | 5107.4617 | 31411.9019 | 269376.3025 | 20959.8236 | 0.087251 | -161846.202 | 161846.202
C | Xist Rating 7970 | -9.87 | 1894.77 | 150.3 | 35.7 | 2124.91 | 8553.5 | 12557.1 | 0.4 | 1.56 | 22.331 | 19.149 | 1 | 1 | 2300 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4026215.7207 | 303283.1424 | 5152.1657 | 31549.0718 | 271734.0707 | 20807.1071 | 0.087632 | -160666.966 | 160666.966
| Xist Rating 7971 | -9.48 | 1905.56 | 150.3 | 35.7 | 2122.63 | 8542.97 | 12507.7 | 0.4 | 1.55 | 22.335 | 19.024 | 1 | 1 | 2310 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4044798.8228 | 305788.354 | 5197.0645 | 31686.2416 | 274102.1124 | 20681.4644 | 0.088013 | -159696.7863 | 159696.7863
| Xist Rating 7972 | -7.69 | 1951.97 | 150.3 | 35.7 | 2113.45 | 8519.61 | 12277.2 | 0.4 | 1.51 | 22.365 | 18.385 | 1 | 1 | 2320 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4125390.9965 | 308303.8391 | 5242.1582 | 31823.4115 | 276480.4276 | 20023.1165 | 0.088394 | -154613.198 | 154613.198
| Xist Rating 7973 | -7.16 | 1965.29 | 150.3 | 35.7 | 2111.89 | 8528.02 | 12216.8 | 0.39 | 1.5 | 22.366 | 18.231 | 1 | 1 | 2330 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4150476.2981 | 310829.5977 | 5287.4466 | 31960.5814 | 278869.0163 | 19843.8802 | 0.088775 | -153229.1825 | 153229.1825
| Xist Rating 7974 | -6.62 | 1978.59 | 150.3 | 35.7 | 2110.45 | 8537.98 | 12157.2 | 0.39 | 1.49 | 22.368 | 18.08 | 1 | 1 | 2340 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4175715.2655 | 313365.6298 | 5332.9298 | 32097.7513 | 281267.8785 | 19691.0586 | 0.089156 | -152049.1353 | 152049.1353
| Xist Rating 7975 | -6.19 | 1990.6 | 150.3 | 35.7 | 2107.84 | 8525.26 | 12104.7 | 0.38 | 1.49 | 22.362 | 17.949 | 1 | 1 | 2350 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4195866.304 | 315911.9354 | 5378.6078 | 32234.9211 | 283677.0142 | 19535.1235 | 0.089537 | -150845.0453 | 150845.0453
| Xist Rating 7976 | -5.66 | 2005.32 | 150.3 | 35.7 | 2104.82 | 8513 | 12039.8 | 0.38 | 1.48 | 22.358 | 17.786 | 1 | 1 | 2360 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4220837.6424 | 318468.5145 | 5424.4805 | 32372.091 | 286096.4235 | 19369.4964 | 0.089918 | -149566.1173 | 149566.1173
| Xist Rating 7977 | -4.03 | 2047.82 | 150.3 | 35.7 | 2097.14 | 8499.67 | 11846.8 | 0.38 | 1.45 | 22.385 | 17.278 | 1 | 1 | 2370 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4294565.2348 | 321035.3671 | 5470.5481 | 32509.2609 | 288526.1062 | 18846.8375 | 0.090299 | -145530.2837 | 145530.2837
| Xist Rating 7978 | -3.56 | 2061.35 | 150.3 | 35.7 | 2094.09 | 8482.58 | 11791.2 | 0.38 | 1.44 | 22.378 | 17.144 | 1 | 1 | 2380 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4316652.4215 | 323612.4932 | 5516.8105 | 32646.4308 | 290966.0624 | 18711.2079 | 0.09068 | -144482.9875 | 144482.9875
| Xist Rating 7979 | -2.99 | 2075.62 | 150.3 | 35.7 | 2092.55 | 8493.95 | 11730 | 0.37 | 1.43 | 22.376 | 16.992 | 1 | 1 | 2390 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4343338.631 | 326199.8927 | 5563.2676 | 32783.6007 | 293416.2921 | 18533.1148 | 0.091061 | -143107.8001 | 143107.8001
C | Xist Rating 7982 | 7.69 | 2381.19 | 150.301 | 35.7 | 2026.11 | 8175.95 | 10538.2 | 0.4 | 1.25 | 22.388 | 14.109 | 1 | 1 | 2420 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4824552.8709 | 334023.7325 | 5703.8078 | 33195.1103 | 300828.6222 | 15623.5954 | 0.092204 | -120641.262 | 120641.262
C | Xist Rating 7983 | 7.83 | 2382.55 | 150.301 | 35.7 | 2027.96 | 8206.2 | 10538.1 | 0.39 | 1.25 | 22.39 | 14.12 | 1 | 1 | 2430 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4831716.098 | 336652.2261 | 5751.0441 | 33332.2802 | 303319.9459 | 15614.7321 | 0.092585 | -120572.8219 | 120572.8219
C | Xist Rating 7984 | 7.88 | 2383.92 | 150.3 | 35.7 | 2028.38 | 8213.12 | 10538.1 | 0.38 | 1.25 | 22.386 | 14.131 | 1 | 1 | 2440 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4835495.6496 | 339290.9932 | 5798.4752 | 33469.45 | 305821.5431 | 15605.415 | 0.092966 | -120500.8781 | 120500.8781
C | Xist Rating 7985 | 7.9 | 2385.25 | 150.3 | 35.7 | 2028.05 | 8207.64 | 10538.1 | 0.38 | 1.25 | 22.38 | 14.141 | 1 | 1 | 2450 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4837406.2625 | 341940.0338 | 5846.1011 | 33606.6199 | 308333.4139 | 15619.3627 | 0.093347 | -120608.5784 | 120608.5784
C | Xist Rating 7986 | 7.92 | 2386.72 | 150.3 | 35.7 | 2027.94 | 8205.83 | 10538.1 | 0.37 | 1.25 | 22.37 | 14.153 | 1 | 1 | 2460 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4840124.9568 | 344599.3479 | 5893.9217 | 33743.7898 | 310855.5581 | 15610.5506 | 0.093728 | -120540.534 | 120540.534
C | Xist Rating 7987 | 7.93 | 2388.07 | 150.301 | 35.7 | 2027.44 | 8197.63 | 10538.1 | 0.37 | 1.25 | 22.411 | 14.163 | 1 | 1 | 2470 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4841668.6408 | 347268.9354 | 5941.9372 | 33880.9597 | 313387.9758 | 15626.3253 | 0.094109 | -120662.3417 | 120662.3417
C | Xist Rating 7988 | 7.94 | 2389.42 | 150.3 | 35.7 | 2026.91 | 8189.04 | 10538.1 | 0.36 | 1.25 | 22.405 | 14.174 | 1 | 1 | 2480 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4843139.2922 | 349948.7965 | 5990.1474 | 34018.1295 | 315930.667 | 15616.3123 | 0.09449 | -120585.0242 | 120585.0242
C | Xist Rating 7989 | 7.94 | 2390.82 | 150.3 | 35.7 | 2026.28 | 8178.7 | 10538.1 | 0.35 | 1.25 | 22.399 | 14.184 | 1 | 1 | 2490 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4844470.7496 | 352638.9311 | 6038.5525 | 34155.2994 | 318483.6317 | 15605.0714 | 0.094871 | -120498.2249 | 120498.2249
C | Xist Rating 7990 | 7.97 | 2391.8 | 150.3 | 35.7 | 2026.5 | 8182.33 | 10538.1 | 0.35 | 1.25 | 22.396 | 14.193 | 1 | 1 | 2500 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4846982.7 | 355339.3392 | 6087.1523 | 34292.4693 | 321046.8699 | 15617.8143 | 0.095252 | -120596.6223 | 120596.6223
C | Xist Rating 7991 | 7.94 | 2393.65 | 150.3 | 35.7 | 2024.94 | 8157.03 | 10538.1 | 0.34 | 1.25 | 22.389 | 14.206 | 1 | 1 | 2510 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4846997.631 | 358050.0208 | 6135.9469 | 34429.6392 | 323620.3816 | 15609.3629 | 0.095633 | -120531.363 | 120531.363
C | Xist Rating 7992 | 7.95 | 2395.11 | 150.3 | 35.7 | 2024.33 | 8147.06 | 10538 | 0.34 | 1.25 | 22.426 | 14.217 | 1 | 1 | 2520 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4848493.0263 | 360770.9759 | 6184.9363 | 34566.8091 | 326204.1668 | 15625.6196 | 0.096014 | -120656.8926 | 120656.8926
C | Xist Rating 7993 | 7.95 | 2396.45 | 150.3 | 35.7 | 2023.82 | 8138.85 | 10538 | 0.33 | 1.25 | 22.421 | 14.227 | 1 | 1 | 2530 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4849983.439 | 363502.2045 | 6234.1205 | 34703.9789 | 328798.2255 | 15613.8028 | 0.096395 | -120565.6461 | 120565.6461
C | Xist Rating 7994 | 7.97 | 2397.6 | 150.3 | 35.7 | 2023.72 | 8137.21 | 10538 | 0.33 | 1.25 | 22.417 | 14.237 | 1 | 1 | 2540 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4852071.072 | 366243.7065 | 6283.4995 | 34841.1488 | 331402.5577 | 15627.354 | 0.096776 | -120670.2852 | 120670.2852
C | Xist Rating 7995 | 8 | 2399.14 | 150.3 | 35.7 | 2023.56 | 8134.71 | 10538 | 0.32 | 1.25 | 22.409 | 14.248 | 1 | 1 | 2550 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4854803.7384 | 368995.4821 | 6333.0732 | 34978.3187 | 334017.1634 | 15616.1775 | 0.097157 | -120583.9836 | 120583.9836
C | Xist Rating 7996 | 8.05 | 2400.59 | 150.3 | 35.6 | 2024.05 | 8142.67 | 10538 | 0.32 | 1.25 | 22.396 | 14.258 | 1 | 1 | 2560 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4858914.1895 | 371757.5312 | 6382.8418 | 35115.4886 | 336642.0427 | 15629.2995 | 0.097538 | -120685.3078 | 120685.3078
C | Xist Rating 7997 | 8.04 | 2401.98 | 150.3 | 35.6 | 2023.4 | 8132.13 | 10537.9 | 0.31 | 1.25 | 22.393 | 14.268 | 1 | 1 | 2570 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4860166.332 | 374529.8538 | 6432.8051 | 35252.6584 | 339277.1954 | 15616.9897 | 0.097919 | -120590.2552 | 120590.2552
C | Xist Rating 7998 | 8.05 | 2403.35 | 150.301 | 35.6 | 2022.96 | 8125.12 | 10537.9 | 0.31 | 1.25 | 22.446 | 14.279 | 1 | 1 | 2580 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4861880.916 | 377312.4499 | 6482.9633 | 35389.8283 | 341922.6216 | 15633.425 | 0.0983 | -120717.1637 | 120717.1637
C | Xist Rating 7999 | 8.07 | 2404.71 | 150.301 | 35.6 | 2022.47 | 8117.18 | 10538 | 0.3 | 1.25 | 22.447 | 14.289 | 1 | 1 | 2590 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4863453.8337 | 380105.3195 | 6533.3162 | 35526.9982 | 344578.3213 | 15620.9049 | 0.098681 | -120620.4872 | 120620.4872
C | Xist Rating 8000 | 8.09 | 2405.88 | 150.301 | 35.6 | 2022.68 | 8120.59 | 10537.9 | 0.3 | 1.25 | 22.446 | 14.298 | 1 | 1 | 2600 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4866325.3584 | 382908.4626 | 6583.8639 | 35664.1681 | 347244.2945 | 15633.235 | 0.099062 | -120715.6967 | 120715.6967
C | Xist Rating 8001 | 8.1 | 2407.57 | 150.301 | 35.6 | 2022.05 | 8110.48 | 10537.8 | 0.3 | 1.25 | 22.443 | 14.309 | 1 | 1 | 2610 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4868226.9185 | 385721.8791 | 6634.6064 | 35801.3379 | 349920.5412 | 15647.5716 | 0.099443 | -120826.4 | 120826.4
C | Xist Rating 8002 | 8.09 | 2408.97 | 150.301 | 35.6 | 2021.22 | 8097.09 | 10537.8 | 0.29 | 1.25 | 22.442 | 14.32 | 1 | 1 | 2620 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4869058.3434 | 388545.5692 | 6685.5437 | 35938.5078 | 352607.0614 | 15635.6218 | 0.099824 | -120734.1271 | 120734.1271
C | Xist Rating 8003 | 8.12 | 2410.39 | 150.301 | 35.6 | 2021.04 | 8094.19 | 10537.8 | 0.29 | 1.25 | 22.483 | 14.33 | 1 | 1 | 2630 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4871494.6056 | 391379.5328 | 6736.6758 | 36075.6777 | 355303.8551 | 15650.3258 | 0.10021 | -120847.6671 | 120847.6671
C | Xist Rating 8004 | 8.14 | 2411.64 | 150.301 | 35.6 | 2020.94 | 8092.58 | 10537.8 | 0.28 | 1.25 | 22.482 | 14.339 | 1 | 1 | 2640 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4873779.7416 | 394223.7699 | 6788.0027 | 36212.8476 | 358010.9223 | 15635.956 | 0.10059 | -120736.7075 | 120736.7075
C | Xist Rating 8005 | 8.18 | 2413.14 | 150.301 | 35.6 | 2020.74 | 8089.47 | 10537.8 | 0.28 | 1.25 | 22.486 | 14.35 | 1 | 1 | 2650 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4876328.5236 | 397078.2805 | 6839.5243 | 36350.0175 | 360728.263 | 15650.3342 | 0.10097 | -120847.7323 | 120847.7323
C | Xist Rating 8006 | 8.21 | 2414.48 | 150.301 | 35.6 | 2020.75 | 8089.68 | 10537.8 | 0.28 | 1.25 | 22.485 | 14.36 | 1 | 1 | 2660 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4879060.46 | 399943.0646 | 6891.2408 | 36487.1873 | 363455.8772 | 15663.508 | 0.10135 | -120949.4568 | 120949.4568
C | Xist Rating 8007 | 8.25 | 2415.87 | 150.301 | 35.6 | 2020.9 | 8092.01 | 10537.8 | 0.27 | 1.25 | 22.487 | 14.37 | 1 | 1 | 2670 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4882231.683 | 402818.1221 | 6943.152 | 36624.3572 | 366193.7649 | 15649.8692 | 0.10173 | -120844.1418 | 120844.1418
C | Xist Rating 8008 | 8.29 | 2417.29 | 150.301 | 35.6 | 2020.98 | 8093.28 | 10537.8 | 0.27 | 1.25 | 22.527 | 14.38 | 1 | 1 | 2680 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4885294.7442 | 405703.4532 | 6995.258 | 36761.5271 | 368941.9261 | 15664.2731 | 0.10211 | -120955.365 | 120955.365
C | Xist Rating 8009 | 8.36 | 2418.66 | 150.301 | 35.6 | 2021.59 | 8103.04 | 10537.8 | 0.26 | 1.25 | 22.531 | 14.39 | 1 | 1 | 2690 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4889538.8694 | 408599.0578 | 7047.5588 | 36898.697 | 371700.3608 | 15650.3472 | 0.10249 | -120847.8327 | 120847.8327
C | Xist Rating 8010 | 8.43 | 2419.86 | 150.301 | 35.6 | 2022.62 | 8119.75 | 10537.8 | 0.26 | 1.25 | 22.533 | 14.399 | 1 | 1 | 2700 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4894457.2332 | 411504.9359 | 7100.0544 | 37035.8668 | 374469.0691 | 15662.3825 | 0.10287 | -120940.7659 | 120940.7659
C | Xist Rating 8011 | 8.51 | 2421.52 | 150.301 | 35.6 | 2023.49 | 8133.84 | 10537.7 | 0.26 | 1.25 | 22.533 | 14.41 | 1 | 1 | 2710 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4899921.5048 | 414421.0875 | 7152.7448 | 37173.0367 | 377248.0508 | 15676.4321 | 0.10325 | -121049.253 | 121049.253
C | Xist Rating 8012 | 8.5 | 2422.86 | 150.301 | 35.6 | 2022.62 | 8119.74 | 10537.7 | 0.25 | 1.25 | 22.529 | 14.42 | 1 | 1 | 2720 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4900525.0932 | 417347.5126 | 7205.63 | 37310.2066 | 380037.306 | 15661.8483 | 0.10363 | -120936.641 | 120936.641
C | Xist Rating 8013 | 8.49 | 2424.19 | 150.301 | 35.6 | 2021.93 | 8108.62 | 10537.7 | 0.25 | 1.25 | 22.566 | 14.429 | 1 | 1 | 2730 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4901542.4867 | 420284.2111 | 7258.71 | 37447.3765 | 382836.8347 | 15674.8513 | 0.10402 | -121037.0471 | 121037.0471
C | Xist Rating 8014 | 8.51 | 2425.47 | 150.301 | 35.6 | 2021.84 | 8107.16 | 10537.6 | 0.25 | 1.25 | 22.561 | 14.438 | 1 | 1 | 2740 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4903912.2648 | 423231.1832 | 7311.9847 | 37584.5464 | 385646.6369 | 15686.5731 | 0.1044 | -121127.5593 | 121127.5593
C | Xist Rating 8015 | 8.51 | 2427.02 | 150.301 | 35.6 | 2020.9 | 8092.11 | 10537.7 | 0.25 | 1.25 | 22.558 | 14.449 | 1 | 1 | 2750 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4904764.718 | 426188.4288 | 7365.4543 | 37721.7162 | 388466.7126 | 15700.4323 | 0.10478 | -121234.5768 | 121234.5768
C | Xist Rating 8016 | 8.49 | 2428.44 | 150.301 | 35.6 | 2019.86 | 8075.45 | 10537.7 | 0.24 | 1.25 | 22.553 | 14.459 | 1 | 1 | 2760 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4905108.8184 | 429155.9479 | 7419.1186 | 37858.8861 | 391297.0618 | 15685.2889 | 0.10516 | -121117.6431 | 121117.6431
C | Xist Rating 8017 | 8.47 | 2429.68 | 150.301 | 35.6 | 2019.04 | 8062.26 | 10537.7 | 0.24 | 1.25 | 22.548 | 14.467 | 1 | 1 | 2770 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4905621.1072 | 432133.7405 | 7472.9777 | 37996.056 | 394137.6845 | 15695.8741 | 0.10554 | -121199.3794 | 121199.3794
C | Xist Rating 8018 | 8.47 | 2431.23 | 150.301 | 35.6 | 2018.22 | 8049.28 | 10537.7 | 0.24 | 1.25 | 22.589 | 14.478 | 1 | 1 | 2780 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4906757.0106 | 435121.8066 | 7527.0316 | 38133.2259 | 396988.5807 | 15710.9495 | 0.10592 | -121315.7874 | 121315.7874
C | Xist Rating 8019 | 8.48 | 2432.64 | 150.301 | 35.6 | 2017.79 | 8042.36 | 10537.8 | 0.23 | 1.25 | 22.593 | 14.487 | 1 | 1 | 2790 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4908556.6656 | 438120.1461 | 7581.2803 | 38270.3957 | 399849.7504 | 15694.5911 | 0.1063 | -121189.4727 | 121189.4727
C | Xist Rating 8020 | 8.47 | 2433.61 | 150.301 | 35.6 | 2017.34 | 8035.19 | 10537.8 | 0.23 | 1.25 | 22.588 | 14.495 | 1 | 1 | 2800 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4909418.7974 | 441128.7592 | 7635.7238 | 38407.5656 | 402721.1936 | 15705.0841 | 0.10668 | -121270.4962 | 121270.4962
C | Xist Rating 8021 | 8.48 | 2435.35 | 150.301 | 35.6 | 2016.5 | 8021.99 | 10537.7 | 0.23 | 1.25 | 22.591 | 14.506 | 1 | 1 | 2810 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4910883.275 | 444147.6458 | 7690.3621 | 38544.7355 | 405602.9103 | 15718.9232 | 0.10706 | -121377.3584 | 121377.3584
C | Xist Rating 8022 | 8.52 | 2436.83 | 150.301 | 35.6 | 2016.48 | 8021.55 | 10537.8 | 0.23 | 1.25 | 22.6 | 14.516 | 1 | 1 | 2820 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4913818.9584 | 447176.8059 | 7745.1952 | 38681.9054 | 408494.9005 | 15731.8989 | 0.10744 | -121477.5533 | 121477.5533
C | Xist Rating 8023 | 8.51 | 2438.2 | 150.301 | 35.6 | 2015.9 | 8012.5 | 10537.7 | 0.22 | 1.25 | 22.618 | 14.525 | 1 | 1 | 2830 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4915167.38 | 450216.2395 | 7800.223 | 38819.0752 | 411397.1642 | 15715.4088 | 0.10783 | -121350.2208 | 121350.2208
C | Xist Rating 8024 | 8.55 | 2439.52 | 150.301 | 35.6 | 2016.12 | 8015.94 | 10537.7 | 0.22 | 1.25 | 22.621 | 14.534 | 1 | 1 | 2840 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4918365.0624 | 453265.9465 | 7855.4457 | 38956.2451 | 414309.7014 | 15727.0697 | 0.10821 | -121440.2637 | 121440.2637
C | Xist Rating 8025 | 8.59 | 2440.96 | 150.301 | 35.6 | 2016.37 | 8019.9 | 10537.7 | 0.22 | 1.25 | 22.631 | 14.544 | 1 | 1 | 2850 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4921878.5152 | 456325.9271 | 7910.8631 | 39093.415 | 417232.5121 | 15739.9665 | 0.10859 | -121539.8492 | 121539.8492
C | Xist Rating 8026 | 8.56 | 2442.37 | 150.301 | 35.6 | 2015.21 | 8001.53 | 10537.7 | 0.22 | 1.25 | 22.623 | 14.553 | 1 | 1 | 2860 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4921888.4477 | 459396.1812 | 7966.4753 | 39230.5849 | 420165.5963 | 15751.3191 | 0.10897 | -121627.511 | 121627.511
C | Xist Rating 8027 | 8.68 | 2443.56 | 150.301 | 35.6 | 2016.91 | 8028.43 | 10537.8 | 0.21 | 1.25 | 22.647 | 14.562 | 1 | 1 | 2870 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4928440.5996 | 462476.7088 | 8022.2824 | 39367.7548 | 423108.954 | 15734.4412 | 0.10935 | -121497.184 | 121497.184
C | Xist Rating 8028 | 8.78 | 2445.07 | 150.301 | 35.6 | 2018.11 | 8047.52 | 10537.8 | 0.21 | 1.25 | 22.708 | 14.572 | 1 | 1 | 2880 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4934420.2177 | 465567.5099 | 8078.2842 | 39504.9246 | 426062.5852 | 15748.6117 | 0.10973 | -121606.6048 | 121606.6048
C | Xist Rating 8029 | 8.8 | 2446.41 | 150.301 | 35.6 | 2017.89 | 8043.89 | 10537.8 | 0.21 | 1.25 | 22.708 | 14.581 | 1 | 1 | 2890 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4936586.2749 | 468668.5844 | 8134.4807 | 39642.0945 | 429026.4899 | 15760.0957 | 0.11011 | -121695.2814 | 121695.2814
C | Xist Rating 8030 | 8.98 | 2447.8 | 150.301 | 35.6 | 2020.61 | 8087.31 | 10537.9 | 0.21 | 1.25 | 22.745 | 14.591 | 1 | 1 | 2900 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4946049.158 | 471779.9325 | 8190.8721 | 39779.2644 | 432000.6681 | 15773.6283 | 0.11049 | -121799.7763 | 121799.7763
C | Xist Rating 8031 | 9.45 | 2449.34 | 150.301 | 35.6 | 2028.73 | 8218.91 | 10538 | 0.2 | 1.25 | 22.809 | 14.601 | 1 | 1 | 2910 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4969049.5382 | 474901.5541 | 8247.4583 | 39916.4343 | 434985.1198 | 15758.1554 | 0.11087 | -121680.2988 | 121680.2988
C | Xist Rating 8032 | 10.09 | 2450.73 | 150.301 | 35.6 | 2040.33 | 8412.42 | 10538.2 | 0.2 | 1.25 | 22.884 | 14.612 | 1 | 1 | 2920 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 5000297.9409 | 478033.4492 | 8304.2393 | 40053.6041 | 437979.845 | 15773.587 | 0.11125 | -121799.4577 | 121799.4577
C | Xist Rating 8033 | 9.56 | 2452.11 | 150.302 | 35.6 | 2029.74 | 8235.39 | 10538 | 0.2 | 1.25 | 22.85 | 14.62 | 1 | 1 | 2930 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 4977145.7514 | 481175.6178 | 8361.215 | 40190.774 | 440984.8437 | 15783.0534 | 0.11164 | -121872.555 | 121872.555
C | Xist Rating 8034 | 10.34 | 2453.48 | 150.302 | 35.6 | 2043.96 | 8474.56 | 10538.2 | 0.19 | 1.25 | 22.938 | 14.63 | 1 | 1 | 2940 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 5014814.9808 | 484328.0598 | 8418.3855 | 40327.9439 | 444000.1159 | 15767.5776 | 0.11202 | -121753.0546 | 121753.0546
C | Xist Rating 8035 | 10.87 | 2454.89 | 150.302 | 35.6 | 2053.21 | 8635.77 | 10538.2 | 0.19 | 1.25 | 22.999 | 14.64 | 1 | 1 | 2950 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 5040404.6969 | 487490.7754 | 8475.7509 | 40465.1138 | 447025.6617 | 15781.4487 | 0.1124 | -121860.1637 | 121860.1637
C | Xist Rating 8036 | 11.46 | 2456.26 | 150.301 | 35.6 | 2063.32 | 8817.49 | 10538.3 | 0.19 | 1.25 | 23.067 | 14.65 | 1 | 1 | 2960 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 5068050.3832 | 490663.7645 | 8533.311 | 40602.2837 | 450061.4809 | 15795.5067 | 0.11278 | -121968.7156 | 121968.7156
C | Xist Rating 8037 | 12.08 | 2457.64 | 150.301 | 35.6 | 2074.63 | 9028.04 | 10538.1 | 0.18 | 1.25 | 23.124 | 14.66 | 1 | 1 | 2970 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 5098693.6732 | 493847.0271 | 8591.0659 | 40739.4535 | 453107.5736 | 15778.5132 | 0.11316 | -121837.4965 | 121837.4965
C | Xist Rating 8038 | 12.09 | 2458.87 | 150.302 | 35.6 | 2074.37 | 9023.01 | 10538.1 | 0.18 | 1.25 | 23.149 | 14.669 | 1 | 1 | 2980 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 5100606.1619 | 497040.5632 | 8649.0156 | 40876.6234 | 456163.9398 | 15790.3265 | 0.11354 | -121928.7159 | 121928.7159
C | Xist Rating 8039 | 12.09 | 2460.43 | 150.302 | 35.6 | 2073.59 | 9008.4 | 10538.1 | 0.18 | 1.25 | 23.144 | 14.678 | 1 | 1 | 2990 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 5101923.0437 | 500244.3727 | 8707.16 | 41013.7933 | 459230.5795 | 15801.4202 | 0.11392 | -122014.3779 | 122014.3779
C | Xist Rating 8040 | 12.09 | 2461.86 | 150.302 | 35.6 | 2072.91 | 8995.53 | 10538.1 | 0.18 | 1.25 | 23.138 | 14.687 | 1 | 1 | 3000 | 152.4 | 2 | 4.9 | 19.05 | 1.3333 | 29 | E | Rod | 5103214.2126 | 503458.4558 | 8765.4993 | 41150.9632 | 462307.4927 | 15812.4888 | 0.1143 | -122099.8468 | 122099.8468
C | Xist Rating 8041 | -86.12 | 253.936 | 150.307 | 35.9 | 2349.29 | 6944.97 | 58744.4 | 2.48 | 10.95 | 25.208 | 602.861 | 1 | 1 | 1000 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 596569.3054 | 66412.7417 | 973.9444 | 13996.9262 | 52415.8155 | 628872.446 | 0.038101 | -4855986.3321 | 4855986.3321
C | Xist Rating 8042 | -85.99 | 256.553 | 150.307 | 35.9 | 2346.39 | 6927.13 | 58283.4 | 2.46 | 10.84 | 25.296 | 591.526 | 1 | 1 | 1010 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 601973.3937 | 67606.2689 | 993.5206 | 14136.8955 | 53469.3734 | 617116.0648 | 0.038482 | -4765206.6729 | 4765206.6729
C | Xist Rating 8043 | -84.95 | 276.459 | 150.308 | 35.9 | 2339.58 | 6924.72 | 54967.1 | 2.47 | 10.07 | 25.35 | 512.623 | 1 | 1 | 1020 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 646797.9472 | 68810.2792 | 1013.2917 | 14276.8648 | 54533.4144 | 535220.9815 | 0.038863 | -4132834.5477 | 4132834.5477
C | Xist Rating 8044 | -84.78 | 281.838 | 150.306 | 35.9 | 2323.31 | 6798.18 | 54177.8 | 2.39 | 9.89 | 24.736 | 495.332 | 1 | 1 | 1030 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 654797.0438 | 70024.7727 | 1033.2576 | 14416.834 | 55607.9387 | 517130.9888 | 0.039244 | -3993148.4193 | 3993148.4193
C | Xist Rating 8045 | -84.67 | 284.53 | 150.306 | 35.9 | 2317.55 | 6756 | 53793 | 2.35 | 9.8 | 24.596 | 487.054 | 1 | 1 | 1040 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 659412.5015 | 71249.7493 | 1053.4182 | 14556.8033 | 56692.946 | 508499.3363 | 0.039625 | -3926497.0862 | 3926497.0862
C | Xist Rating 8046 | -84.44 | 289.788 | 150.306 | 35.9 | 2310.76 | 6712.27 | 53042.8 | 2.31 | 9.63 | 24.507 | 470.873 | 1 | 1 | 1050 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 669630.5189 | 72485.2091 | 1073.7737 | 14696.7726 | 57788.4366 | 491665.3207 | 0.040006 | -3796509.2802 | 3796509.2802
C | Xist Rating 8047 | -84.31 | 292.461 | 150.305 | 35.9 | 2309.1 | 6705.04 | 52675.2 | 2.28 | 9.54 | 24.461 | 463.171 | 1 | 1 | 1060 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 675321.6951 | 73731.1521 | 1094.3239 | 14836.7418 | 58894.4103 | 483652.2655 | 0.040387 | -3734634.5919 | 3734634.5919
C | Xist Rating 8048 | -83.28 | 313.83 | 150.305 | 35.9 | 2293.98 | 6632.99 | 49856.6 | 2.26 | 8.9 | 24.225 | 405.237 | 1 | 1 | 1070 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 719919.7434 | 74987.5782 | 1115.0689 | 14976.7111 | 60010.8672 | 423463.8519 | 0.040768 | -3269875.6165 | 3269875.6165
C | Xist Rating 8049 | -83.05 | 317.841 | 150.305 | 35.9 | 2297.24 | 6670.24 | 49379.9 | 2.21 | 8.79 | 24.1 | 396.11 | 1 | 1 | 1080 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 730157.0588 | 76254.4875 | 1136.0087 | 15116.6803 | 61137.8072 | 413938.0069 | 0.041149 | -3196319.566 | 3196319.566
C | Xist Rating 8050 | -82.73 | 323.18 | 150.304 | 35.9 | 2301.74 | 6721.68 | 48760.6 | 2.14 | 8.65 | 23.922 | 384.392 | 1 | 1 | 1090 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 743876.3332 | 77531.88 | 1157.1433 | 15256.6496 | 62275.2304 | 401691.7202 | 0.04153 | -3101756.9867 | 3101756.9867
C | Xist Rating 8051 | -82.46 | 327.16 | 150.304 | 35.9 | 2310.2 | 6804.57 | 48306.8 | 2.1 | 8.55 | 23.924 | 375.93 | 1 | 1 | 1100 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 755805.032 | 78819.7556 | 1178.4727 | 15396.6189 | 63423.1367 | 392879.9198 | 0.041911 | -3033714.5997 | 3033714.5997
C | Xist Rating 8052 | -82.31 | 330.019 | 150.303 | 35.9 | 2311.64 | 6823.93 | 48010.7 | 2.02 | 8.49 | 23.558 | 370.724 | 1 | 1 | 1110 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 762885.1212 | 80118.1144 | 1199.9969 | 15536.5881 | 64581.5263 | 387364.0042 | 0.042292 | -2991122.1615 | 2991122.1615
C | Xist Rating 8053 | -81.08 | 353.83 | 150.304 | 35.9 | 2305.65 | 6834.47 | 45447.6 | 2.06 | 7.92 | 23.876 | 324.376 | 1 | 1 | 1120 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 815808.1395 | 81426.9564 | 1221.7158 | 15676.5574 | 65750.399 | 339333.2055 | 0.042673 | -2620241.0656 | 2620241.0656
C | Xist Rating 8054 | -80.91 | 356.644 | 150.304 | 35.9 | 2308.61 | 6867.36 | 45189.2 | 2 | 7.86 | 23.644 | 320.175 | 1 | 1 | 1130 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 823351.9048 | 82746.2815 | 1243.6296 | 15816.5267 | 66929.7548 | 334896.4562 | 0.043054 | -2585981.6633 | 2585981.6633
C | Xist Rating 8055 | -80.65 | 362.053 | 150.303 | 35.9 | 2306.86 | 6865.58 | 44681.2 | 1.94 | 7.75 | 23.426 | 311.77 | 1 | 1 | 1140 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 835205.5836 | 84076.0897 | 1265.7381 | 15956.4959 | 68119.5938 | 326094.9697 | 0.043435 | -2518018.9181 | 2518018.9181
C | Xist Rating 8056 | -80.36 | 367.399 | 150.303 | 35.8 | 2308.01 | 6889.38 | 44186.1 | 1.9 | 7.64 | 23.195 | 303.647 | 1 | 1 | 1150 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 847960.566 | 85416.3812 | 1288.0414 | 16096.4652 | 69319.916 | 317608.6909 | 0.043816 | -2452490.122 | 2452490.122
C | Xist Rating 8057 | -80.1 | 372.823 | 150.302 | 35.8 | 2305.05 | 6876.67 | 43703.2 | 1.85 | 7.53 | 23.006 | 295.912 | 1 | 1 | 1160 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 859375.6562 | 86767.1558 | 1310.5395 | 16236.4344 | 70530.7213 | 309517.1764 | 0.044197 | -2390009.592 | 2390009.592
C | Xist Rating 8058 | -79.01 | 394.179 | 150.302 | 35.8 | 2300.43 | 6891.16 | 41832.2 | 1.87 | 7.13 | 23.174 | 266.161 | 1 | 1 | 1170 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 906781.197 | 88128.4135 | 1333.2324 | 16376.4037 | 71752.0098 | 278680.4948 | 0.044578 | -2151896.9105 | 2151896.9105
C | Xist Rating 8059 | -78.88 | 395.679 | 150.302 | 35.8 | 2306.45 | 6948.89 | 41724.5 | 1.82 | 7.11 | 23.07 | 264.693 | 1 | 1 | 1180 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 912613.8295 | 89500.1545 | 1356.1201 | 16516.373 | 72983.7815 | 277104.1052 | 0.044959 | -2139724.4481 | 2139724.4481
C | Xist Rating 8060 | -78.38 | 406.356 | 150.302 | 35.8 | 2300.11 | 6918.7 | 40885.5 | 1.77 | 6.92 | 22.871 | 252.236 | 1 | 1 | 1190 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 934663.4992 | 90882.3786 | 1379.2026 | 16656.3422 | 74226.0363 | 264106.0335 | 0.04534 | -2039356.7835 | 2039356.7835
C | Xist Rating 8061 | -78.13 | 409.061 | 150.302 | 35.8 | 2311.88 | 7033.22 | 40681.8 | 1.74 | 6.88 | 22.918 | 249.319 | 1 | 1 | 1200 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 945699.9447 | 92275.0858 | 1402.4799 | 16796.3115 | 75478.7743 | 261062.3716 | 0.045721 | -2015854.4335 | 2015854.4335
C | Xist Rating 8062 | -77.86 | 414.555 | 150.301 | 35.8 | 2310.36 | 7033.08 | 40280.8 | 1.69 | 6.8 | 22.741 | 243.647 | 1 | 1 | 1210 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 957771.2898 | 93678.2762 | 1425.9519 | 16936.2808 | 76741.9955 | 255111.5081 | 0.046102 | -1969903.4433 | 1969903.4433
C | Xist Rating 8063 | -76.69 | 438.72 | 150.301 | 35.8 | 2299.02 | 6991.63 | 38537.6 | 1.69 | 6.43 | 22.747 | 219.063 | 1 | 1 | 1220 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1008626.0544 | 95091.9498 | 1449.6188 | 17076.25 | 78015.6998 | 229598.8447 | 0.046483 | -1772901.4186 | 1772901.4186
C | Xist Rating 8064 | -76.36 | 444.064 | 150.301 | 35.8 | 2304.69 | 7058.07 | 38183.3 | 1.66 | 6.35 | 22.771 | 214.346 | 1 | 1 | 1230 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1023429.8602 | 96516.1065 | 1473.4804 | 17216.2193 | 79299.8873 | 224682.0517 | 0.046864 | -1734935.2463 | 1734935.2463
C | Xist Rating 8065 | -76.07 | 449.548 | 150.301 | 35.8 | 2304.97 | 7074.49 | 37835.7 | 1.62 | 6.28 | 22.654 | 209.848 | 1 | 1 | 1240 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1036194.6536 | 97950.7464 | 1497.5369 | 17356.1885 | 80594.5579 | 219966.6675 | 0.047245 | -1698524.2995 | 1698524.2995
C | Xist Rating 8066 | -75.88 | 452.398 | 150.301 | 35.8 | 2309.97 | 7128.89 | 37664.2 | 1.57 | 6.24 | 22.571 | 207.722 | 1 | 1 | 1250 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1045025.8081 | 99395.8695 | 1521.7881 | 17496.1578 | 81899.7117 | 217704.5028 | 0.047626 | -1681056.4634 | 1681056.4634
C | Xist Rating 8067 | -75.46 | 460.438 | 150.301 | 35.8 | 2310 | 7150.18 | 37161.1 | 1.54 | 6.14 | 22.521 | 201.244 | 1 | 1 | 1260 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1063611.78 | 100851.4757 | 1546.2341 | 17636.1271 | 83215.3487 | 210950.4017 | 0.048007 | -1628903.0855 | 1628903.0855
C | Xist Rating 8068 | -74.33 | 483.319 | 150.301 | 35.8 | 2302.89 | 7143.08 | 35777.4 | 1.55 | 5.85 | 22.592 | 183.757 | 1 | 1 | 1270 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1113030.4919 | 102317.5651 | 1570.8749 | 17776.0963 | 84541.4688 | 192824.8116 | 0.048388 | -1488942.0828 | 1488942.0828
C | Xist Rating 8069 | -74.05 | 488.872 | 150.301 | 35.8 | 2301.91 | 7147.59 | 35477.1 | 1.51 | 5.79 | 22.459 | 180.239 | 1 | 1 | 1280 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1125339.3455 | 103794.1377 | 1595.7105 | 17916.0656 | 85878.0721 | 189123.6988 | 0.048769 | -1460363.0708 | 1460363.0708
C | Xist Rating 8070 | -73.77 | 494.372 | 150.301 | 35.8 | 2301.75 | 7159.93 | 35182.4 | 1.48 | 5.73 | 22.404 | 176.806 | 1 | 1 | 1290 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1137920.751 | 105281.1934 | 1620.7408 | 18056.0349 | 87225.1586 | 185530.0683 | 0.04915 | -1432614.0091 | 1432614.0091
C | Xist Rating 8071 | -73.34 | 502.39 | 150.301 | 35.8 | 2302.86 | 7191.6 | 34750.8 | 1.46 | 5.64 | 22.444 | 171.747 | 1 | 1 | 1300 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1156933.8354 | 106778.7323 | 1645.966 | 18196.0041 | 88582.7282 | 180268.4603 | 0.049531 | -1391985.2666 | 1391985.2666
C | Xist Rating 8072 | -73.1 | 506.594 | 150.3 | 35.8 | 2306 | 7232.87 | 34539.5 | 1.42 | 5.59 | 22.395 | 169.385 | 1 | 1 | 1310 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1168205.764 | 108286.7544 | 1671.3859 | 18335.9734 | 89950.781 | 177773.4128 | 0.049912 | -1372719.1711 | 1372719.1711
C | Xist Rating 8073 | -71.96 | 529.574 | 150.301 | 35.8 | 2299.7 | 7232.21 | 33362.5 | 1.42 | 5.35 | 22.45 | 155.959 | 1 | 1 | 1320 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1217861.3278 | 109805.2596 | 1697.0007 | 18475.9426 | 91329.3169 | 163849.4087 | 0.050293 | -1265201.7026 | 1265201.7026
C | Xist Rating 8074 | -71.56 | 537.808 | 150.3 | 35.8 | 2297.79 | 7234.23 | 32979.5 | 1.39 | 5.28 | 22.333 | 151.859 | 1 | 1 | 1330 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1235769.8443 | 111334.2479 | 1722.8102 | 18615.9119 | 92718.336 | 159556.0075 | 0.050674 | -1232049.1962 | 1232049.1962
C | Xist Rating 8075 | -71.12 | 545.941 | 150.3 | 35.8 | 2299.49 | 7272.13 | 32606.5 | 1.36 | 5.2 | 22.229 | 147.896 | 1 | 1 | 1340 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1255385.8701 | 112873.7195 | 1748.8145 | 18755.8812 | 94117.8383 | 155405.6145 | 0.051055 | -1200000.962 | 1200000.962
C | Xist Rating 8076 | -70.81 | 550.163 | 150.3 | 35.8 | 2306.9 | 7357.54 | 32423.6 | 1.32 | 5.16 | 22.191 | 146.035 | 1 | 1 | 1350 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1269171.0247 | 114423.6742 | 1775.0136 | 18895.8504 | 95527.8237 | 153429.6788 | 0.051436 | -1184743.3099 | 1184743.3099
C | Xist Rating 8077 | -70.5 | 552.815 | 150.3 | 35.8 | 2321.31 | 7513.66 | 32303 | 1.31 | 5.14 | 22.289 | 144.779 | 1 | 1 | 1360 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1283254.9877 | 115984.112 | 1801.4075 | 19035.8197 | 96948.2923 | 152132.7531 | 0.051817 | -1174728.7938 | 1174728.7938
C | Xist Rating 8078 | -69.09 | 585.358 | 150.3 | 35.8 | 2297.35 | 7354.59 | 30902.2 | 1.3 | 4.86 | 22.193 | 130.405 | 1 | 1 | 1370 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1344772.2013 | 117555.0331 | 1827.9962 | 19175.789 | 98379.2441 | 137197.1135 | 0.052198 | -1059399.7432 | 1059399.7432
C | Xist Rating 8079 | -68.96 | 588.272 | 150.3 | 35.8 | 2296.74 | 7355.42 | 30793.8 | 1.28 | 4.84 | 22.146 | 129.412 | 1 | 1 | 1380 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1351107.8333 | 119136.4372 | 1854.7797 | 19315.7582 | 99820.679 | 136147.6392 | 0.052579 | -1051295.9809 | 1051295.9809
C | Xist Rating 8080 | -68.59 | 595.168 | 150.3 | 35.8 | 2298.07 | 7386.85 | 30526.6 | 1.25 | 4.78 | 22.104 | 126.862 | 1 | 1 | 1390 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1367737.7258 | 120728.3246 | 1881.7579 | 19455.7275 | 101272.5971 | 133467.5085 | 0.05296 | -1030600.7221 | 1030600.7221
C | Xist Rating 8081 | -68.21 | 602.06 | 150.3 | 35.8 | 2299.86 | 7423.32 | 30264.9 | 1.22 | 4.73 | 22.07 | 124.39 | 1 | 1 | 1400 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1384653.7116 | 122330.6951 | 1908.931 | 19595.6967 | 102734.9984 | 130868.5086 | 0.053341 | -1010531.9341 | 1010531.9341
C | Xist Rating 8082 | -67.78 | 610.254 | 150.3 | 35.8 | 2300.6 | 7452.6 | 29957.2 | 1.2 | 4.67 | 22.045 | 121.501 | 1 | 1 | 1410 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1403950.3524 | 123943.5488 | 1936.2988 | 19735.666 | 104207.8828 | 127850.5621 | 0.053722 | -987228.1512 | 987228.1512
C | Xist Rating 8083 | -66.57 | 634.662 | 150.3 | 35.8 | 2295.52 | 7465.75 | 29051.6 | 1.21 | 4.49 | 22.122 | 113.027 | 1 | 1 | 1420 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1456879.3142 | 125566.8856 | 1963.8614 | 19875.6353 | 105691.2504 | 119082.1467 | 0.054103 | -919520.7713 | 919520.7713
C | Xist Rating 8084 | -66.37 | 639.124 | 150.3 | 35.8 | 2294.47 | 7465.35 | 28910.4 | 1.17 | 4.47 | 22.023 | 111.851 | 1 | 1 | 1430 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1466450.8443 | 127200.7056 | 1991.6188 | 20015.6045 | 107185.1011 | 117808.7262 | 0.054484 | -909687.7564 | 909687.7564
C | Xist Rating 8085 | -65.82 | 649.97 | 150.3 | 35.7 | 2293.56 | 7484.47 | 28541.6 | 1.15 | 4.39 | 22.004 | 108.59 | 1 | 1 | 1440 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1490745.1932 | 128845.0088 | 2019.571 | 20155.5738 | 108689.435 | 114403.8919 | 0.054865 | -883396.5279 | 883396.5279
C | Xist Rating 8086 | -65.44 | 656.901 | 150.299 | 35.7 | 2295.27 | 7520.72 | 28316.6 | 1.13 | 4.35 | 21.979 | 106.662 | 1 | 1 | 1450 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1507765.1583 | 130499.7951 | 2047.718 | 20295.5431 | 110204.2521 | 112382.5702 | 0.055246 | -867788.4175 | 867788.4175
C | Xist Rating 8087 | -65.14 | 661.004 | 150.3 | 35.7 | 2301.92 | 7603.71 | 28183.4 | 1.12 | 4.32 | 22.013 | 105.531 | 1 | 1 | 1460 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1521578.3277 | 132165.0646 | 2076.0598 | 20435.5123 | 111729.5523 | 111207.2694 | 0.055627 | -858713.0565 | 858713.0565
C | Xist Rating 8088 | -63.93 | 688.492 | 150.299 | 35.7 | 2287.42 | 7520.85 | 27310 | 1.11 | 4.16 | 21.977 | 98.089 | 1 | 1 | 1470 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1574870.3706 | 133840.8173 | 2104.5964 | 20575.4816 | 113265.3357 | 103472.6776 | 0.056008 | -798988.5887 | 798988.5887
C | Xist Rating 8089 | -63.5 | 696.73 | 150.299 | 35.7 | 2287.97 | 7548.44 | 27065.8 | 1.09 | 4.11 | 21.962 | 96.11 | 1 | 1 | 1480 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1594097.3381 | 135527.0531 | 2133.3277 | 20715.4508 | 114811.6023 | 101398.18 | 0.056389 | -782969.8681 | 782969.8681
C | Xist Rating 8090 | -63.12 | 703.662 | 150.299 | 35.7 | 2289.69 | 7585.28 | 26866 | 1.08 | 4.07 | 21.947 | 94.522 | 1 | 1 | 1490 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1611167.8448 | 137223.7721 | 2162.2539 | 20855.4201 | 116368.352 | 99744.0248 | 0.05677 | -770196.9199 | 770196.9199
C | Xist Rating 8091 | -62.77 | 710.686 | 150.299 | 35.7 | 2289.61 | 7602.63 | 26669.5 | 1.05 | 4.03 | 21.912 | 92.988 | 1 | 1 | 1500 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1627193.7725 | 138930.9742 | 2191.3748 | 20995.3894 | 117935.5849 | 98114.8524 | 0.057151 | -757616.8829 | 757616.8829
C | Xist Rating 8092 | -62.31 | 718.951 | 150.299 | 35.7 | 2291.7 | 7647.78 | 26438 | 1.04 | 3.99 | 21.907 | 91.174 | 1 | 1 | 1510 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1647620.0067 | 140648.6595 | 2220.6906 | 21135.3586 | 119513.3009 | 96226.1462 | 0.057532 | -743032.7942 | 743032.7942
C | Xist Rating 8093 | -60.96 | 746.123 | 150.299 | 35.7 | 2288.24 | 7684.41 | 25680.5 | 1.04 | 3.84 | 21.992 | 85.215 | 1 | 1 | 1520 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1707308.4935 | 142376.828 | 2250.2011 | 21275.3279 | 121101.5001 | 90053.9696 | 0.057913 | -695372.8829 | 695372.8829
C | Xist Rating 8094 | -60.63 | 754.731 | 150.299 | 35.7 | 2282.14 | 7637.85 | 25467.6 | 1.02 | 3.8 | 21.857 | 83.676 | 1 | 1 | 1530 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1722401.8043 | 144115.4796 | 2279.9064 | 21415.2972 | 122700.1825 | 88426.364 | 0.058294 | -682804.9439 | 682804.9439
C | Xist Rating 8095 | -60.24 | 759.109 | 150.299 | 35.7 | 2291.54 | 7755.28 | 25363.4 | 0.99 | 3.78 | 21.904 | 82.943 | 1 | 1 | 1540 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1739528.6379 | 145864.6144 | 2309.8065 | 21555.2664 | 124309.348 | 87633.0863 | 0.058675 | -676679.4635 | 676679.4635
C | Xist Rating 8096 | -59.63 | 772.733 | 150.299 | 35.7 | 2287.86 | 7750.47 | 25020 | 0.98 | 3.72 | 21.835 | 80.417 | 1 | 1 | 1550 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1767904.9214 | 147624.2324 | 2339.9013 | 21695.2357 | 125928.9967 | 84999.6429 | 0.059056 | -656344.7114 | 656344.7114
C | Xist Rating 8097 | -59.25 | 776.886 | 150.299 | 35.7 | 2297.8 | 7877.22 | 24919.3 | 0.97 | 3.7 | 21.881 | 79.704 | 1 | 1 | 1560 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1785128.6508 | 149394.3335 | 2370.191 | 21835.2049 | 127559.1286 | 84256.6369 | 0.059437 | -650607.4162 | 650607.4162
C | Xist Rating 8098 | -57.93 | 808.659 | 150.299 | 35.7 | 2280.02 | 7758.44 | 24161.1 | 0.96 | 3.56 | 21.84 | 74.273 | 1 | 1 | 1570 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1843758.6932 | 151174.9178 | 2400.6755 | 21975.1742 | 129199.7436 | 78607.8972 | 0.059818 | -606989.3454 | 606989.3454
C | Xist Rating 8099 | -57.51 | 815.712 | 150.299 | 35.7 | 2283.49 | 7817.46 | 24006.4 | 0.95 | 3.53 | 21.834 | 73.234 | 1 | 1 | 1580 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1862670.1949 | 152965.9853 | 2431.3547 | 22115.1435 | 130850.8418 | 77522.424 | 0.0602 | -598607.6094 | 598607.6094
C | Xist Rating 8100 | -57.11 | 822.8 | 150.299 | 35.7 | 2285.79 | 7863.37 | 23853.9 | 0.93 | 3.5 | 21.822 | 72.222 | 1 | 1 | 1590 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1880748.012 | 154767.5359 | 2462.2288 | 22255.1127 | 132512.4232 | 76448.8432 | 0.060581 | -590317.7028 | 590317.7028
C | Xist Rating 8101 | -56.51 | 832.397 | 150.299 | 35.7 | 2291.26 | 7955.37 | 23644.7 | 0.92 | 3.46 | 21.851 | 70.811 | 1 | 1 | 1600 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1907237.9502 | 156579.5697 | 2493.2976 | 22395.082 | 134184.4877 | 74978.8817 | 0.060962 | -578967.0498 | 578967.0498
C | Xist Rating 8102 | -56.25 | 836.97 | 150.299 | 35.7 | 2293.11 | 7989.35 | 23556 | 0.89 | 3.45 | 21.82 | 70.268 | 1 | 1 | 1610 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1919264.2767 | 158402.0866 | 2524.5612 | 22535.0513 | 135867.0353 | 74374.6889 | 0.061343 | -574301.6334 | 574301.6334
C | Xist Rating 8103 | -54.67 | 872.56 | 150.299 | 35.7 | 2279.46 | 7925.95 | 22804.4 | 0.9 | 3.31 | 21.854 | 65.265 | 1 | 1 | 1620 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 1988965.6176 | 160235.0867 | 2556.0196 | 22675.0205 | 137560.0662 | 69205.8531 | 0.061724 | -534389.2528 | 534389.2528
C | Xist Rating 8104 | -54.29 | 876.788 | 150.299 | 35.7 | 2288.37 | 8046.43 | 22722.7 | 0.89 | 3.29 | 21.882 | 64.765 | 1 | 1 | 1630 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2006415.3556 | 162078.57 | 2587.6728 | 22814.9898 | 139263.5802 | 68681.2735 | 0.062105 | -530338.5888 | 530338.5888
C | Xist Rating 8105 | -53.91 | 884.024 | 150.299 | 35.7 | 2289.13 | 8075.44 | 22588 | 0.87 | 3.27 | 21.856 | 63.947 | 1 | 1 | 1640 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2023645.8591 | 163932.5364 | 2619.5208 | 22954.959 | 140977.5774 | 67806.6766 | 0.062486 | -523585.1831 | 523585.1831
C | Xist Rating 8106 | -53.43 | 893.978 | 150.299 | 35.7 | 2287.93 | 8088.09 | 22402.3 | 0.85 | 3.23 | 21.828 | 62.812 | 1 | 1 | 1650 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2045359.0855 | 165796.986 | 2651.5635 | 23094.9283 | 142702.0577 | 66602.4142 | 0.062867 | -514286.1882 | 514286.1882
C | Xist Rating 8107 | -52.91 | 903.689 | 150.299 | 35.7 | 2289.39 | 8134.13 | 22220.2 | 0.84 | 3.2 | 21.833 | 61.694 | 1 | 1 | 1660 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2068896.5597 | 167671.9187 | 2683.8011 | 23234.8976 | 144437.0212 | 65433.7602 | 0.063248 | -505262.1517 | 505262.1517
C | Xist Rating 8108 | -51.51 | 935.507 | 150.299 | 35.7 | 2277.97 | 8082.56 | 21632.5 | 0.84 | 3.09 | 21.855 | 58.086 | 1 | 1 | 1670 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2131056.8808 | 169557.3347 | 2716.2334 | 23374.8668 | 146182.4678 | 61696.462 | 0.063629 | -476403.7255 | 476403.7255
C | Xist Rating 8109 | -51.19 | 939.846 | 150.299 | 35.7 | 2283.08 | 8159.28 | 21559.9 | 0.83 | 3.08 | 21.865 | 57.68 | 1 | 1 | 1680 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2145743.6057 | 171453.2337 | 2748.8606 | 23514.8361 | 147938.3977 | 61267.2277 | 0.06401 | -473089.2918 | 473089.2918
C | Xist Rating 8110 | -50.64 | 952.569 | 150.299 | 35.7 | 2278.76 | 8139.62 | 21345.6 | 0.81 | 3.04 | 21.83 | 56.444 | 1 | 1 | 1690 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2170676.1344 | 173359.616 | 2781.6825 | 23654.8054 | 149704.8106 | 59956.5037 | 0.064391 | -462968.2286 | 462968.2286
C | Xist Rating 8111 | -50.15 | 960.99 | 150.299 | 35.7 | 2281.56 | 8199.35 | 21205.4 | 0.8 | 3.02 | 21.836 | 55.646 | 1 | 1 | 1700 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2192556.3444 | 175276.4814 | 2814.6992 | 23794.7746 | 151481.7068 | 59119.4389 | 0.064772 | -456504.636 | 456504.636
C | Xist Rating 8112 | -49.66 | 970.894 | 150.299 | 35.7 | 2281.2 | 8222.72 | 21044.3 | 0.79 | 2.99 | 21.825 | 54.74 | 1 | 1 | 1710 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2214803.3928 | 177203.83 | 2847.9107 | 23934.7439 | 153269.0861 | 58168.9862 | 0.065153 | -449165.4925 | 449165.4925
C | Xist Rating 8113 | -48.37 | 1000.15 | 150.299 | 35.7 | 2271.74 | 8185.21 | 20566.8 | 0.78 | 2.9 | 21.852 | 52.019 | 1 | 1 | 1720 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2272080.761 | 179141.6617 | 2881.317 | 24074.7131 | 155066.9486 | 55335.7575 | 0.065534 | -427288.0517 | 427288.0517
C | Xist Rating 8114 | -47.77 | 1012.74 | 150.299 | 35.7 | 2270.32 | 8202.35 | 20374.1 | 0.77 | 2.87 | 21.842 | 50.971 | 1 | 1 | 1730 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2299243.8768 | 181089.9766 | 2914.9181 | 24214.6824 | 156875.2942 | 54237.5087 | 0.065915 | -418807.6657 | 418807.6657
C | Xist Rating 8115 | -47.4 | 1018.53 | 150.299 | 35.7 | 2274.05 | 8267.23 | 20289.7 | 0.76 | 2.85 | 21.845 | 50.534 | 1 | 1 | 1740 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2316188.1465 | 183048.7747 | 2948.714 | 24354.6517 | 158694.123 | 53774.3659 | 0.066296 | -415231.3993 | 415231.3993
C | Xist Rating 8116 | -46.87 | 1029.95 | 150.299 | 35.7 | 2272.05 | 8272.76 | 20123.4 | 0.75 | 2.82 | 21.821 | 49.656 | 1 | 1 | 1750 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2340097.8975 | 185018.0559 | 2982.7046 | 24494.6209 | 160523.435 | 52851.4583 | 0.066677 | -408104.9514 | 408104.9514
C | Xist Rating 8117 | -46.49 | 1038.49 | 150.299 | 35.7 | 2270.27 | 8273.23 | 20000.5 | 0.74 | 2.8 | 21.82 | 49.017 | 1 | 1 | 1760 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2357652.6923 | 186997.8203 | 3016.8901 | 24634.5902 | 162363.2301 | 52177.9204 | 0.067058 | -402904.0705 | 402904.0705
C | Xist Rating 8118 | -44.98 | 1073.16 | 150.299 | 35.7 | 2259.47 | 8230.98 | 19497.1 | 0.74 | 2.71 | 21.856 | 46.341 | 1 | 1 | 1770 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2424772.8252 | 188988.0678 | 3051.2703 | 24774.5595 | 164213.5084 | 49408.25 | 0.067439 | -381517.4097 | 381517.4097
C | Xist Rating 8119 | -44.53 | 1081.81 | 150.299 | 35.7 | 2260.3 | 8265.69 | 19382.7 | 0.73 | 2.69 | 21.846 | 45.776 | 1 | 1 | 1780 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2445215.143 | 190988.7985 | 3085.8453 | 24914.5287 | 166074.2698 | 48810.7272 | 0.06782 | -376903.497 | 376903.497
C | Xist Rating 8120 | -44.46 | 1086.41 | 150.3 | 35.7 | 2254.38 | 8198.58 | 19326.9 | 0.71 | 2.68 | 22.114 | 45.506 | 1 | 1 | 1790 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2449180.9758 | 193000.0124 | 3120.6151 | 25054.498 | 167945.5144 | 48517.6916 | 0.068201 | -374640.754 | 374640.754
C | Xist Rating 8121 | -43.55 | 1101.81 | 150.3 | 35.7 | 2260.34 | 8321.94 | 19121.7 | 0.71 | 2.65 | 21.831 | 44.492 | 1 | 1 | 1800 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2490465.2154 | 195021.7094 | 3155.5797 | 25194.4672 | 169827.2422 | 47455.4802 | 0.068582 | -366438.639 | 366438.639
C | Xist Rating 8122 | -43.35 | 1110.33 | 150.3 | 35.7 | 2250.75 | 8216.64 | 19013 | 0.7 | 2.63 | 22.107 | 43.951 | 1 | 1 | 1810 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2499075.2475 | 197053.8896 | 3190.7391 | 25334.4365 | 171719.4531 | 46898.5631 | 0.068963 | -362138.2731 | 362138.2731
C | Xist Rating 8123 | -41.61 | 1145.26 | 150.3 | 35.7 | 2250.61 | 8315.02 | 18562.5 | 0.7 | 2.55 | 21.863 | 41.735 | 1 | 1 | 1820 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2577533.6086 | 199096.553 | 3226.0933 | 25474.4058 | 173622.1472 | 44590.2532 | 0.069344 | -344314.1156 | 344314.1156
C | Xist Rating 8124 | -41.85 | 1139.72 | 150.3 | 35.6 | 2255.27 | 8363.02 | 18631.3 | 0.69 | 2.56 | 22.162 | 42.071 | 1 | 1 | 1830 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2570376.3244 | 201149.6995 | 3261.6423 | 25614.375 | 175535.3245 | 44945.0381 | 0.069725 | -347053.6704 | 347053.6704
C | Xist Rating 8125 | -41.37 | 1146.74 | 150.3 | 35.6 | 2259.53 | 8442.13 | 18545.3 | 0.68 | 2.55 | 22.19 | 41.667 | 1 | 1 | 1840 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2591093.4322 | 203213.3292 | 3297.386 | 25754.3443 | 177458.9849 | 44515.6309 | 0.070106 | -343737.9023 | 343737.9023
C | Xist Rating 8126 | -40.86 | 1158.27 | 150.3 | 35.6 | 2256.84 | 8437.24 | 18409.2 | 0.67 | 2.52 | 22.175 | 41.038 | 1 | 1 | 1850 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2614030.0668 | 205287.4421 | 3333.3246 | 25894.3136 | 179393.1285 | 43849.9445 | 0.070487 | -338597.6483 | 338597.6483
C | Xist Rating 8127 | -40.3 | 1171.21 | 150.3 | 35.6 | 2253.47 | 8426.69 | 18259.1 | 0.66 | 2.5 | 22.157 | 40.347 | 1 | 1 | 1860 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2639286.5987 | 207372.0381 | 3369.4579 | 26034.2828 | 181337.7553 | 43119.5232 | 0.070868 | -332957.5284 | 332957.5284
C | Xist Rating 8128 | -38.85 | 1203.3 | 150.3 | 35.6 | 2247.06 | 8431.79 | 17879.5 | 0.66 | 2.43 | 22.214 | 38.563 | 1 | 1 | 1870 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2703887.298 | 209467.1173 | 3405.7861 | 26174.2521 | 183292.8652 | 41276.5504 | 0.071249 | -318726.5809 | 318726.5809
C | Xist Rating 8129 | -38.27 | 1216.22 | 150.3 | 35.6 | 2244.76 | 8435.74 | 17738.6 | 0.65 | 2.41 | 22.203 | 37.942 | 1 | 1 | 1880 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2730122.0072 | 211572.6796 | 3442.309 | 26314.2213 | 185258.4583 | 40618.8924 | 0.07163 | -313648.32 | 313648.32
C | Xist Rating 8130 | -37.76 | 1224.79 | 150.3 | 35.6 | 2247.47 | 8498.51 | 17646.5 | 0.64 | 2.39 | 22.222 | 37.54 | 1 | 1 | 1890 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2752678.7813 | 213688.7251 | 3479.0267 | 26454.1906 | 187234.5345 | 40190.1052 | 0.072011 | -310337.3391 | 310337.3391
C | Xist Rating 8131 | -37.37 | 1233.82 | 150.3 | 35.6 | 2245.18 | 8490.24 | 17555.2 | 0.63 | 2.38 | 22.201 | 37.158 | 1 | 1 | 1900 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2770147.9876 | 215815.2538 | 3515.9392 | 26594.1599 | 189221.0939 | 39779.7213 | 0.072392 | -307168.4631 | 307168.4631
C | Xist Rating 8132 | -36.89 | 1242.57 | 150.3 | 35.7 | 2246.46 | 8532.97 | 17465.2 | 0.62 | 2.36 | 22.211 | 36.776 | 1 | 1 | 1910 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2791383.8022 | 217952.2656 | 3553.0464 | 26734.1291 | 191218.1365 | 39370.8077 | 0.072773 | -304010.9412 | 304010.9412
C | Xist Rating 8133 | -35.19 | 1281.54 | 150.3 | 35.7 | 2237.6 | 8521.4 | 17050.3 | 0.62 | 2.29 | 22.254 | 34.942 | 1 | 1 | 1920 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 31 | E | Rod | 2867573.904 | 220099.7606 | 3590.3485 | 26874.0984 | 193225.6622 | 37474.6688 | 0.073154 | -289369.459 | 289369.459
C | Xist Rating 8134 | -34.68 | 1294.53 | 150.3 | 35.7 | 2233.06 | 8492.12 | 16923.8 | 0.61 | 2.27 | 22.246 | 34.419 | 1 | 1 | 1930 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 2890763.1618 | 222257.7388 | 3627.8454 | 27014.0677 | 195243.6711 | 36918.0443 | 0.073535 | -285071.3525 | 285071.3525
C | Xist Rating 8135 | -34.29 | 1298.77 | 150.3 | 35.7 | 2239.41 | 8597.05 | 16882.1 | 0.6 | 2.26 | 22.281 | 34.252 | 1 | 1 | 1940 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 2908478.5257 | 224426.2001 | 3665.537 | 27154.0369 | 197272.1632 | 36733.1789 | 0.073916 | -283643.8706 | 283643.8706
C | Xist Rating 8136 | -33.9 | 1310.88 | 150.3 | 35.7 | 2232.48 | 8528.26 | 16772 | 0.59 | 2.24 | 22.246 | 33.818 | 1 | 1 | 1950 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 2926513.3824 | 226605.1446 | 3703.4235 | 27294.0062 | 199311.1384 | 36267.1827 | 0.074297 | -280045.5711 | 280045.5711
C | Xist Rating 8137 | -33.27 | 1325.15 | 150.3 | 35.7 | 2230.06 | 8533.49 | 16636.7 | 0.58 | 2.22 | 22.264 | 33.266 | 1 | 1 | 1960 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 2955164.009 | 228794.5722 | 3741.5047 | 27433.9754 | 201360.5968 | 35681.1875 | 0.074678 | -275520.6721 | 275520.6721
C | Xist Rating 8138 | -31.74 | 1360.21 | 150.301 | 35.7 | 2222.72 | 8528.75 | 16303 | 0.58 | 2.16 | 22.353 | 31.885 | 1 | 1 | 1970 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3023365.9712 | 230994.4831 | 3779.7807 | 27573.9447 | 203420.5384 | 34257.3678 | 0.075059 | -264526.3132 | 264526.3132
C | Xist Rating 8139 | -31.24 | 1370.34 | 150.301 | 35.7 | 2222.9 | 8559.7 | 16214 | 0.57 | 2.15 | 22.382 | 31.541 | 1 | 1 | 1980 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3046128.786 | 233204.877 | 3818.2515 | 27713.914 | 205490.9631 | 33887.5639 | 0.07544 | -261670.7856 | 261670.7856
C | Xist Rating 8140 | -30.71 | 1383.53 | 150.301 | 35.7 | 2219.21 | 8541.3 | 16101.2 | 0.56 | 2.13 | 22.388 | 31.109 | 1 | 1 | 1990 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3070343.6113 | 235425.7542 | 3856.9171 | 27853.8832 | 207571.8709 | 33424.9859 | 0.075821 | -258098.8811 | 258098.8811
C | Xist Rating 8141 | -30.22 | 1393.79 | 150.301 | 35.7 | 2218.42 | 8557.68 | 16014.8 | 0.56 | 2.12 | 22.394 | 30.783 | 1 | 1 | 2000 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3092011.6118 | 237657.1145 | 3895.7775 | 27993.8525 | 209663.262 | 33092.3564 | 0.076202 | -255530.4045 | 255530.4045
C | Xist Rating 8142 | -29.82 | 1401.27 | 150.301 | 35.7 | 2219.79 | 8598.49 | 15953.6 | 0.55 | 2.11 | 22.402 | 30.56 | 1 | 1 | 2010 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3110525.1333 | 239898.9579 | 3934.8326 | 28133.8218 | 211765.1362 | 32846.6126 | 0.076583 | -253632.8355 | 253632.8355
C | Xist Rating 8143 | -28.21 | 1440.69 | 150.301 | 35.7 | 2209.09 | 8553.04 | 15614.7 | 0.55 | 2.05 | 22.436 | 29.238 | 1 | 1 | 2020 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3182613.8721 | 242151.2846 | 3974.0826 | 28273.791 | 213877.4935 | 31480.9337 | 0.076964 | -243087.4257 | 243087.4257
C | Xist Rating 8144 | -27.52 | 1454.91 | 150.301 | 35.7 | 2209.07 | 8592.9 | 15499.8 | 0.54 | 2.03 | 22.451 | 28.811 | 1 | 1 | 2030 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3213998.0337 | 244414.0943 | 4013.5273 | 28413.7603 | 216000.3341 | 31023.3478 | 0.077345 | -239554.0685 | 239554.0685
C | Xist Rating 8145 | -27.15 | 1464.14 | 150.301 | 35.7 | 2206.78 | 8582.49 | 15431.6 | 0.53 | 2.02 | 22.44 | 28.576 | 1 | 1 | 2040 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3231034.8692 | 246687.3873 | 4053.1669 | 28553.7295 | 218133.6578 | 30763.6722 | 0.077726 | -237548.9223 | 237548.9223
C | Xist Rating 8146 | -26.58 | 1472.55 | 150.301 | 35.7 | 2211.66 | 8681.43 | 15364 | 0.53 | 2.01 | 22.466 | 28.33 | 1 | 1 | 2050 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3256779.933 | 248971.1634 | 4093.0012 | 28693.6988 | 220277.4646 | 30514.7989 | 0.078107 | -235627.1888 | 235627.1888
C | Xist Rating 8147 | -26.09 | 1486.14 | 150.301 | 35.7 | 2206.52 | 8639.15 | 15264.1 | 0.52 | 1.99 | 22.44 | 27.981 | 1 | 1 | 2060 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3279197.6328 | 251265.4227 | 4133.0303 | 28833.6681 | 222431.7546 | 30135.707 | 0.078488 | -232699.9414 | 232699.9414
C | Xist Rating 8148 | -24.36 | 1528.42 | 150.301 | 35.7 | 2196.54 | 8609.09 | 14936 | 0.52 | 1.94 | 22.479 | 26.776 | 1 | 1 | 2070 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3357235.6668 | 253570.1651 | 4173.2542 | 28973.6373 | 224596.5278 | 28891.4286 | 0.078869 | -223091.9536 | 223091.9536
C | Xist Rating 8149 | -23.92 | 1537.45 | 150.301 | 35.7 | 2196.7 | 8635.78 | 14873.3 | 0.51 | 1.93 | 22.48 | 26.568 | 1 | 1 | 2080 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3377316.415 | 255885.3907 | 4213.6729 | 29113.6066 | 226771.7842 | 28659.7497 | 0.07925 | -221302.9906 | 221302.9906
C | Xist Rating 8150 | -23.4 | 1549.19 | 150.301 | 35.7 | 2195.3 | 8646.25 | 14790.9 | 0.5 | 1.91 | 22.487 | 26.287 | 1 | 1 | 2090 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3400936.807 | 258211.0995 | 4254.2864 | 29253.5759 | 228957.5237 | 28352.3386 | 0.079631 | -218929.2431 | 218929.2431
C | Xist Rating 8151 | -22.94 | 1560.93 | 150.301 | 35.7 | 2192.27 | 8631.47 | 14709.3 | 0.5 | 1.9 | 22.488 | 26.012 | 1 | 1 | 2100 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3421980.0111 | 260547.2914 | 4295.0947 | 29393.5451 | 231153.7463 | 28071.8384 | 0.080012 | -216763.2954 | 216763.2954
C | Xist Rating 8152 | -22.49 | 1571.28 | 150.301 | 35.7 | 2190.99 | 8639.7 | 14638.7 | 0.49 | 1.89 | 22.49 | 25.778 | 1 | 1 | 2110 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3442658.7672 | 262893.9665 | 4336.0977 | 29533.5144 | 233360.4522 | 27812.6934 | 0.080393 | -214762.2463 | 214762.2463
C | Xist Rating 8153 | -20.9 | 1611.13 | 150.301 | 35.7 | 2181.26 | 8602.2 | 14359 | 0.49 | 1.84 | 22.524 | 24.81 | 1 | 1 | 2120 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3514293.4238 | 265251.1248 | 4377.2956 | 29673.4836 | 235577.6412 | 26813.9499 | 0.080774 | -207050.2132 | 207050.2132
C | Xist Rating 8154 | -20.3 | 1625.7 | 150.301 | 35.7 | 2178.41 | 8597.33 | 14263.7 | 0.48 | 1.83 | 22.522 | 24.498 | 1 | 1 | 2130 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3541441.137 | 267618.7662 | 4418.6882 | 29813.4529 | 237805.3133 | 26473.2887 | 0.081155 | -204419.7184 | 204419.7184
C | Xist Rating 8155 | -19.79 | 1640.29 | 150.301 | 35.7 | 2173.36 | 8558.24 | 14169.8 | 0.48 | 1.81 | 22.518 | 24.194 | 1 | 1 | 2140 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3564940.6744 | 269996.8908 | 4460.2756 | 29953.4222 | 240043.4686 | 26162.2468 | 0.081536 | -202017.9353 | 202017.9353
C | Xist Rating 8156 | -19.44 | 1647.93 | 150.301 | 35.7 | 2173.43 | 8578.96 | 14123.4 | 0.47 | 1.8 | 22.521 | 24.053 | 1 | 1 | 2150 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3581660.4999 | 272385.4985 | 4502.0578 | 30093.3914 | 242292.1071 | 25999.0981 | 0.081917 | -200758.1441 | 200758.1441
C | Xist Rating 8157 | -18.95 | 1658.22 | 150.301 | 35.7 | 2173.32 | 8604.68 | 14059.1 | 0.47 | 1.79 | 22.527 | 23.85 | 1 | 1 | 2160 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3603842.6904 | 274784.5895 | 4544.0348 | 30233.3607 | 244551.2288 | 25793.3006 | 0.082298 | -199169.0302 | 199169.0302
C | Xist Rating 8158 | -17.32 | 1701.16 | 150.301 | 35.7 | 2161.86 | 8544.65 | 13785.9 | 0.46 | 1.75 | 22.556 | 22.957 | 1 | 1 | 2170 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3677669.7576 | 277194.1635 | 4586.2066 | 30373.33 | 246820.8336 | 24850.0531 | 0.082679 | -191885.523 | 191885.523
C | Xist Rating 8159 | -16.68 | 1715.5 | 150.301 | 35.7 | 2160.78 | 8566.37 | 13699 | 0.46 | 1.74 | 22.567 | 22.686 | 1 | 1 | 2180 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3706818.09 | 279614.2208 | 4628.5732 | 30513.2992 | 249100.9216 | 24573.7654 | 0.08306 | -189752.1024 | 189752.1024
C | Xist Rating 8160 | -16.26 | 1726.02 | 150.301 | 35.7 | 2158.94 | 8564.58 | 13638.9 | 0.45 | 1.73 | 22.564 | 22.507 | 1 | 1 | 2190 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3726373.6188 | 282044.7612 | 4671.1346 | 30653.2685 | 251391.4927 | 24370.2417 | 0.083441 | -188180.5464 | 188180.5464
C | Xist Rating 8161 | -15.86 | 1736.96 | 150.301 | 35.7 | 2156.35 | 8550.91 | 13579.4 | 0.45 | 1.72 | 22.551 | 22.335 | 1 | 1 | 2200 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3745493.696 | 284485.7847 | 4713.8907 | 30793.2377 | 253692.547 | 24195.5945 | 0.083822 | -186831.9669 | 186831.9669
C | Xist Rating 8162 | -15.25 | 1751.55 | 150.301 | 35.7 | 2154.35 | 8557.94 | 13495.3 | 0.44 | 1.7 | 22.553 | 22.08 | 1 | 1 | 2210 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3773451.7425 | 286937.2915 | 4756.8417 | 30933.207 | 256004.0845 | 23913.0737 | 0.084203 | -184650.4168 | 184650.4168
C | Xist Rating 8163 | -13.56 | 1794.36 | 150.301 | 35.7 | 2145.29 | 8531.96 | 13246.2 | 0.44 | 1.66 | 22.591 | 21.306 | 1 | 1 | 2220 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3849422.5644 | 289399.2813 | 4799.9874 | 31073.1763 | 258326.1051 | 23115.3879 | 0.084584 | -178490.898 | 178490.898
C | Xist Rating 8164 | -13.04 | 1806.07 | 150.301 | 35.7 | 2144.83 | 8555.32 | 13182.5 | 0.44 | 1.65 | 22.595 | 21.121 | 1 | 1 | 2230 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3873713.1181 | 291871.7544 | 4843.3279 | 31213.1455 | 260658.6089 | 22927.8972 | 0.084965 | -177043.1446 | 177043.1446
C | Xist Rating 8165 | -12.53 | 1819.62 | 150.301 | 35.7 | 2141.92 | 8543.43 | 13111.7 | 0.43 | 1.64 | 22.589 | 20.919 | 1 | 1 | 2240 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3897480.4704 | 294354.7106 | 4886.8633 | 31353.1148 | 263001.5958 | 22699.6308 | 0.085346 | -175280.5322 | 175280.5322
C | Xist Rating 8166 | -11.96 | 1834.53 | 150.301 | 35.7 | 2138.85 | 8532.75 | 13034 | 0.42 | 1.63 | 22.585 | 20.698 | 1 | 1 | 2250 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3923784.4905 | 296848.15 | 4930.5934 | 31493.0841 | 265355.0659 | 22451.5249 | 0.085727 | -173364.7243 | 173364.7243
C | Xist Rating 8167 | -11.59 | 1842.13 | 150.301 | 35.7 | 2139.49 | 8562.06 | 12995.5 | 0.42 | 1.62 | 22.592 | 20.593 | 1 | 1 | 2260 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 3941218.7137 | 299352.0725 | 4974.5182 | 31633.0533 | 267719.0192 | 22347.0324 | 0.086108 | -172557.8604 | 172557.8604
C | Xist Rating 8168 | -9.86 | 1888.11 | 150.301 | 35.7 | 2128.81 | 8514.35 | 12751.8 | 0.42 | 1.59 | 22.623 | 19.876 | 1 | 1 | 2270 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4019427.4491 | 301866.4782 | 5018.6379 | 31773.0226 | 270093.4557 | 21608.0071 | 0.086489 | -166851.3029 | 166851.3029
C | Xist Rating 8169 | -9.33 | 1901.61 | 150.301 | 35.7 | 2126.55 | 8512.08 | 12686.1 | 0.41 | 1.58 | 22.619 | 19.697 | 1 | 1 | 2280 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4043868.7455 | 304391.3671 | 5062.9524 | 31912.9918 | 272478.3753 | 21403.0866 | 0.08687 | -165268.9612 | 165268.9612
C | Xist Rating 8170 | -8.67 | 1917.66 | 150.301 | 35.7 | 2124.64 | 8522.68 | 12606.8 | 0.41 | 1.56 | 22.62 | 19.477 | 1 | 1 | 2290 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4074337.1424 | 306926.7391 | 5107.4617 | 32052.9611 | 274873.778 | 21178.8159 | 0.087251 | -163537.2029 | 163537.2029
C | Xist Rating 8171 | -8.22 | 1928.35 | 150.301 | 35.7 | 2123.76 | 8534.85 | 12557.1 | 0.4 | 1.56 | 22.624 | 19.346 | 1 | 1 | 2300 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4095352.596 | 309472.5943 | 5152.1657 | 32192.9304 | 277279.664 | 21023.7743 | 0.087632 | -162340.0121 | 162340.0121
| Xist Rating 8172 | -7.82 | 1939.3 | 150.301 | 35.7 | 2121.46 | 8524.07 | 12507.7 | 0.4 | 1.55 | 22.628 | 19.219 | 1 | 1 | 2310 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4114147.378 | 312028.9327 | 5197.0645 | 32332.8996 | 279696.0331 | 20896.1071 | 0.088013 | -161354.2 | 161354.2
| Xist Rating 8173 | -6 | 1986.52 | 150.301 | 35.7 | 2112.47 | 8503.87 | 12277.2 | 0.4 | 1.51 | 22.653 | 18.572 | 1 | 1 | 2320 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4196463.9044 | 314595.7542 | 5242.1582 | 32472.8689 | 282122.8853 | 20229.2957 | 0.088394 | -156205.2593 | 156205.2593
| Xist Rating 8174 | -5.46 | 2000.05 | 150.301 | 35.7 | 2110.71 | 8508.79 | 12216.9 | 0.39 | 1.5 | 22.658 | 18.416 | 1 | 1 | 2330 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4221525.5355 | 317173.0589 | 5287.4466 | 32612.8382 | 284560.2207 | 20047.8962 | 0.088775 | -154804.54 | 154804.54
| Xist Rating 8175 | -4.89 | 2013.56 | 150.301 | 35.7 | 2109.71 | 8525.99 | 12157.2 | 0.39 | 1.49 | 22.662 | 18.262 | 1 | 1 | 2340 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4248027.6676 | 319760.8467 | 5332.9298 | 32752.8074 | 287008.0393 | 19892.092 | 0.089156 | -153601.4617 | 153601.4617
| Xist Rating 8176 | -4.46 | 2025.77 | 150.301 | 35.7 | 2107.14 | 8513.74 | 12104.7 | 0.38 | 1.49 | 22.657 | 18.13 | 1 | 1 | 2350 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4268580.9978 | 322359.1177 | 5378.6078 | 32892.7767 | 289466.3411 | 19734.9001 | 0.089537 | -152387.6672 | 152387.6672
| Xist Rating 8177 | -3.91 | 2040.72 | 150.301 | 35.7 | 2104.16 | 8502.13 | 12039.8 | 0.38 | 1.48 | 22.652 | 17.964 | 1 | 1 | 2360 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4294001.3952 | 324967.8719 | 5424.4805 | 33032.7459 | 291935.126 | 19566.1676 | 0.089918 | -151084.7597 | 151084.7597
| Xist Rating 8178 | -2.25 | 2083.96 | 150.301 | 35.7 | 2096.59 | 8490.59 | 11846.8 | 0.38 | 1.45 | 22.679 | 17.449 | 1 | 1 | 2370 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4369209.6964 | 327587.1092 | 5470.5481 | 33172.7152 | 294414.394 | 19036.2893 | 0.090299 | -146993.1798 | 146993.1798
| Xist Rating 8179 | -1.77 | 2097.7 | 150.301 | 35.7 | 2093.52 | 8473.37 | 11791.2 | 0.38 | 1.44 | 22.671 | 17.313 | 1 | 1 | 2380 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4391576.904 | 330216.8297 | 5516.8105 | 33312.6845 | 296904.1453 | 18898.5922 | 0.09068 | -145929.9193 | 145929.9193
| Xist Rating 8180 | -1.2 | 2112.21 | 150.301 | 35.7 | 2091.86 | 8482.53 | 11730.1 | 0.37 | 1.43 | 22.67 | 17.159 | 1 | 1 | 2390 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4418447.6106 | 332857.0334 | 5563.2676 | 33452.6537 | 299404.3797 | 18718.1978 | 0.091061 | -144536.9615 | 144536.9615
C | Xist Rating 8182 | 9.52 | 2421.68 | 150.301 | 35.7 | 2022.78 | 8121.77 | 10538.3 | 0.4 | 1.25 | 22.651 | 14.228 | 1 | 1 | 2410 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4898525.8704 | 338168.8902 | 5656.7663 | 33732.5923 | 304436.298 | 15754.527 | 0.091823 | -121652.2816 | 121652.2816
C | Xist Rating 8183 | 9.58 | 2423.09 | 150.301 | 35.7 | 2023.68 | 8136.39 | 10538.2 | 0.4 | 1.25 | 22.678 | 14.239 | 1 | 1 | 2420 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4903558.7712 | 340840.5434 | 5703.8078 | 33872.5615 | 306967.9819 | 15771.1833 | 0.092204 | -121780.8972 | 121780.8972
C | Xist Rating 8184 | 9.71 | 2424.44 | 150.301 | 35.7 | 2025.33 | 8163.21 | 10538.2 | 0.39 | 1.25 | 22.68 | 14.25 | 1 | 1 | 2430 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4910291.0652 | 343522.6797 | 5751.0441 | 34012.5308 | 309510.1489 | 15762.0561 | 0.092585 | -121710.4195 | 121710.4195
C | Xist Rating 8185 | 9.78 | 2425.81 | 150.301 | 35.7 | 2025.94 | 8173.18 | 10538.1 | 0.38 | 1.25 | 22.677 | 14.261 | 1 | 1 | 2440 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4914545.5114 | 346215.2992 | 5798.4752 | 34152.5 | 312062.7991 | 15752.5142 | 0.092966 | -121636.7389 | 121636.7389
C | Xist Rating 8186 | 9.82 | 2427.14 | 150.301 | 35.7 | 2026.09 | 8175.54 | 10538.2 | 0.38 | 1.25 | 22.67 | 14.271 | 1 | 1 | 2450 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4917604.0826 | 348918.4018 | 5846.1011 | 34292.4693 | 314625.9325 | 15766.4697 | 0.093347 | -121744.4997 | 121744.4997
C | Xist Rating 8187 | 9.82 | 2428.61 | 150.301 | 35.7 | 2025.49 | 8165.84 | 10538.1 | 0.37 | 1.25 | 22.661 | 14.283 | 1 | 1 | 2460 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4919125.2689 | 351631.9876 | 5893.9217 | 34432.4386 | 317199.549 | 15757.428 | 0.093728 | -121674.6825 | 121674.6825
C | Xist Rating 8188 | 9.82 | 2429.97 | 150.301 | 35.7 | 2024.96 | 8157.33 | 10538.1 | 0.37 | 1.25 | 22.702 | 14.293 | 1 | 1 | 2470 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4920592.0512 | 354356.0566 | 5941.9372 | 34572.4078 | 319783.6487 | 15773.251 | 0.094109 | -121796.8628 | 121796.8628
C | Xist Rating 8189 | 9.82 | 2431.31 | 150.301 | 35.7 | 2024.41 | 8148.36 | 10538.1 | 0.36 | 1.25 | 22.695 | 14.304 | 1 | 1 | 2480 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4921968.2771 | 357090.6087 | 5990.1474 | 34712.3771 | 322378.2316 | 15762.9227 | 0.09449 | -121717.1112 | 121717.1112
C | Xist Rating 8190 | 9.83 | 2432.71 | 150.301 | 35.7 | 2023.78 | 8138.17 | 10538.1 | 0.35 | 1.25 | 22.69 | 14.315 | 1 | 1 | 2490 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4923269.8438 | 359835.644 | 6038.5525 | 34852.3464 | 324983.2976 | 15752.4825 | 0.094871 | -121636.4944 | 121636.4944
C | Xist Rating 8191 | 9.85 | 2433.7 | 150.301 | 35.7 | 2024.01 | 8141.88 | 10538.1 | 0.35 | 1.25 | 22.687 | 14.323 | 1 | 1 | 2500 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4925833.137 | 362591.1625 | 6087.1523 | 34992.3156 | 327598.8468 | 15764.2326 | 0.095252 | -121727.2254 | 121727.2254
C | Xist Rating 8192 | 9.83 | 2435.55 | 150.301 | 35.7 | 2022.45 | 8116.63 | 10538.1 | 0.34 | 1.25 | 22.68 | 14.336 | 1 | 1 | 2510 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4925778.0975 | 365357.1641 | 6135.9469 | 35132.2849 | 330224.8792 | 15755.4995 | 0.095633 | -121659.7905 | 121659.7905
C | Xist Rating 8193 | 9.83 | 2437 | 150.301 | 35.7 | 2021.83 | 8106.67 | 10538.1 | 0.34 | 1.25 | 22.716 | 14.347 | 1 | 1 | 2520 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4927199.71 | 368133.6489 | 6184.9363 | 35272.2541 | 332861.3947 | 15771.7621 | 0.096014 | -121785.366 | 121785.366
C | Xist Rating 8194 | 9.84 | 2438.34 | 150.301 | 35.7 | 2021.3 | 8098.24 | 10538.1 | 0.33 | 1.25 | 22.711 | 14.357 | 1 | 1 | 2530 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4928616.642 | 370920.6168 | 6234.1205 | 35412.2234 | 335508.3934 | 15759.6605 | 0.096395 | -121691.9213 | 121691.9213
C | Xist Rating 8195 | 9.9 | 2439.49 | 150.301 | 35.7 | 2022.23 | 8113.14 | 10538 | 0.33 | 1.25 | 22.701 | 14.367 | 1 | 1 | 2540 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4933209.8627 | 373718.0679 | 6283.4995 | 35552.1927 | 338165.8752 | 15773.0292 | 0.096776 | -121795.1509 | 121795.1509
C | Xist Rating 8196 | 9.93 | 2441.04 | 150.301 | 35.7 | 2022.01 | 8109.6 | 10538 | 0.32 | 1.25 | 22.691 | 14.378 | 1 | 1 | 2550 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4935807.2904 | 376526.0022 | 6333.0732 | 35692.1619 | 340833.8403 | 15761.497 | 0.097157 | -121706.1022 | 121706.1022
C | Xist Rating 8197 | 9.91 | 2442.48 | 150.301 | 35.6 | 2021.17 | 8096.28 | 10538 | 0.32 | 1.25 | 22.687 | 14.388 | 1 | 1 | 2560 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4936667.3016 | 379344.4196 | 6382.8418 | 35832.1312 | 343512.2884 | 15774.9899 | 0.097538 | -121810.2906 | 121810.2906
C | Xist Rating 8198 | 9.87 | 2443.87 | 150.301 | 35.7 | 2019.66 | 8072.02 | 10538 | 0.31 | 1.25 | 22.696 | 14.399 | 1 | 1 | 2570 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4935786.4842 | 382173.3202 | 6432.8051 | 35972.1004 | 346201.2198 | 15763.8537 | 0.097919 | -121724.2999 | 121724.2999
C | Xist Rating 8199 | 9.94 | 2445.24 | 150.301 | 35.6 | 2020.36 | 8083.17 | 10538 | 0.31 | 1.25 | 22.739 | 14.409 | 1 | 1 | 2580 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4940265.0864 | 385012.704 | 6482.9633 | 36112.0697 | 348900.6343 | 15778.934 | 0.0983 | -121840.7461 | 121840.7461
C | Xist Rating 8200 | 9.95 | 2446.6 | 150.301 | 35.6 | 2020.21 | 8080.82 | 10538 | 0.3 | 1.25 | 22.734 | 14.419 | 1 | 1 | 2590 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4942645.786 | 387862.5709 | 6533.3162 | 36252.039 | 351610.5319 | 15765.9056 | 0.098681 | -121740.1438 | 121740.1438
C | Xist Rating 8201 | 9.98 | 2447.78 | 150.302 | 35.6 | 2020.42 | 8084.18 | 10537.9 | 0.3 | 1.25 | 22.734 | 14.428 | 1 | 1 | 2600 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4945543.6676 | 390722.921 | 6583.8639 | 36392.0082 | 354330.9127 | 15778.3092 | 0.099062 | -121835.9212 | 121835.9212
C | Xist Rating 8202 | 9.96 | 2449.46 | 150.302 | 35.6 | 2019.1 | 8063.23 | 10537.9 | 0.3 | 1.25 | 22.735 | 14.44 | 1 | 1 | 2610 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4945704.686 | 393593.7542 | 6634.6064 | 36531.9775 | 357061.7767 | 15793.8634 | 0.099443 | -121956.0267 | 121956.0267
C | Xist Rating 8203 | 9.97 | 2450.86 | 150.302 | 35.6 | 2018.73 | 8057.27 | 10537.9 | 0.29 | 1.25 | 22.735 | 14.45 | 1 | 1 | 2620 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4947624.6078 | 396475.0706 | 6685.5437 | 36671.9468 | 359803.1239 | 15780.6055 | 0.099824 | -121853.653 | 121853.653
C | Xist Rating 8204 | 9.99 | 2452.29 | 150.302 | 35.6 | 2018.4 | 8052.05 | 10537.9 | 0.29 | 1.25 | 22.774 | 14.46 | 1 | 1 | 2630 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4949702.136 | 399366.8702 | 6736.6758 | 36811.916 | 362554.9542 | 15795.2792 | 0.10021 | -121966.9591 | 121966.9591
C | Xist Rating 8205 | 10.02 | 2453.53 | 150.302 | 35.6 | 2018.31 | 8050.55 | 10537.8 | 0.28 | 1.25 | 22.772 | 14.47 | 1 | 1 | 2640 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4951984.1343 | 402269.153 | 6788.0027 | 36951.8853 | 365317.2677 | 15781.6083 | 0.10059 | -121861.3957 | 121861.3957
C | Xist Rating 8206 | 10.05 | 2455.04 | 150.302 | 35.6 | 2018.1 | 8047.21 | 10537.9 | 0.28 | 1.25 | 22.776 | 14.48 | 1 | 1 | 2650 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4954516.224 | 405181.9189 | 6839.5243 | 37091.8545 | 368090.0643 | 15794.9844 | 0.10097 | -121964.6825 | 121964.6825
C | Xist Rating 8207 | 10.07 | 2456.38 | 150.302 | 35.6 | 2017.99 | 8045.52 | 10537.8 | 0.28 | 1.25 | 22.774 | 14.49 | 1 | 1 | 2660 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4956950.2762 | 408105.1679 | 6891.2408 | 37231.8238 | 370873.3441 | 15808.1612 | 0.10135 | -122066.4303 | 122066.4303
C | Xist Rating 8208 | 10.12 | 2457.76 | 150.302 | 35.6 | 2018.19 | 8048.72 | 10537.8 | 0.27 | 1.25 | 22.776 | 14.5 | 1 | 1 | 2670 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4960226.6544 | 411038.9002 | 6943.152 | 37371.7931 | 373667.1071 | 15794.2128 | 0.10173 | -121958.7246 | 121958.7246
C | Xist Rating 8209 | 10.16 | 2459.18 | 150.302 | 35.6 | 2018.27 | 8050.03 | 10537.8 | 0.27 | 1.25 | 22.817 | 14.51 | 1 | 1 | 2680 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4963289.2186 | 413983.1155 | 6995.258 | 37511.7623 | 376471.3532 | 15808.6841 | 0.10211 | -122070.4683 | 122070.4683
C | Xist Rating 8210 | 10.22 | 2460.56 | 150.302 | 35.6 | 2018.84 | 8058.97 | 10537.9 | 0.26 | 1.25 | 22.82 | 14.52 | 1 | 1 | 2690 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4967476.9504 | 416937.8141 | 7047.5588 | 37651.7316 | 379286.0825 | 15794.4123 | 0.10249 | -121960.2649 | 121960.2649
C | Xist Rating 8211 | 10.3 | 2461.76 | 150.302 | 35.6 | 2019.85 | 8075.22 | 10537.8 | 0.26 | 1.25 | 22.823 | 14.529 | 1 | 1 | 2700 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4972385.936 | 419902.9958 | 7100.0544 | 37791.7009 | 382111.295 | 15806.5127 | 0.10287 | -122053.7011 | 122053.7011
C | Xist Rating 8212 | 10.39 | 2463.41 | 150.302 | 35.6 | 2020.97 | 8093.19 | 10537.7 | 0.26 | 1.25 | 22.823 | 14.54 | 1 | 1 | 2710 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4978477.7077 | 422878.6607 | 7152.7448 | 37931.6701 | 384946.9906 | 15820.5961 | 0.10325 | -122162.4492 | 122162.4492
C | Xist Rating 8213 | 10.38 | 2464.76 | 150.302 | 35.6 | 2020.16 | 8080.19 | 10537.7 | 0.25 | 1.25 | 22.82 | 14.55 | 1 | 1 | 2720 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4979209.5616 | 425864.8087 | 7205.63 | 38071.6394 | 387793.1694 | 15805.723 | 0.10363 | -122047.6032 | 122047.6032
C | Xist Rating 8214 | 10.37 | 2466.08 | 150.302 | 35.6 | 2019.35 | 8067.3 | 10537.7 | 0.25 | 1.25 | 22.854 | 14.559 | 1 | 1 | 2730 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4979878.648 | 428861.4399 | 7258.71 | 38211.6086 | 390649.8313 | 15818.6669 | 0.10402 | -122147.5525 | 122147.5525
C | Xist Rating 8215 | 10.36 | 2467.36 | 150.302 | 35.6 | 2018.74 | 8057.45 | 10537.7 | 0.25 | 1.25 | 22.85 | 14.568 | 1 | 1 | 2740 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4980958.3264 | 431868.5543 | 7311.9847 | 38351.5779 | 393516.9764 | 15830.4516 | 0.1044 | -122238.551 | 122238.551
C | Xist Rating 8216 | 10.35 | 2468.91 | 150.302 | 35.6 | 2017.77 | 8042.06 | 10537.8 | 0.25 | 1.25 | 22.848 | 14.579 | 1 | 1 | 2750 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4981692.5307 | 434886.1518 | 7365.4543 | 38491.5472 | 396394.6047 | 15844.3741 | 0.10478 | -122346.0565 | 122346.0565
C | Xist Rating 8217 | 10.32 | 2470.34 | 150.302 | 35.6 | 2016.68 | 8024.83 | 10537.8 | 0.24 | 1.25 | 22.844 | 14.589 | 1 | 1 | 2760 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4981885.2712 | 437914.2325 | 7419.1186 | 38631.5164 | 399282.7161 | 15828.934 | 0.10516 | -122226.8327 | 122226.8327
C | Xist Rating 8218 | 10.34 | 2471.57 | 150.302 | 35.6 | 2016.43 | 8020.86 | 10537.8 | 0.24 | 1.25 | 22.85 | 14.598 | 1 | 1 | 2770 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4983747.8951 | 440952.7964 | 7472.9777 | 38771.4857 | 402181.3107 | 15840.9168 | 0.10554 | -122319.3608 | 122319.3608
C | Xist Rating 8219 | 10.3 | 2473.12 | 150.302 | 35.6 | 2014.98 | 7997.91 | 10537.8 | 0.24 | 1.25 | 22.883 | 14.608 | 1 | 1 | 2780 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4983287.3376 | 444001.8434 | 7527.0316 | 38911.455 | 405090.3885 | 15854.7469 | 0.10592 | -122426.1532 | 122426.1532
C | Xist Rating 8220 | 10.31 | 2474.53 | 150.302 | 35.6 | 2014.5 | 7990.34 | 10537.8 | 0.23 | 1.25 | 22.886 | 14.617 | 1 | 1 | 2790 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4984940.685 | 447061.3736 | 7581.2803 | 39051.4242 | 408009.9494 | 15838.0238 | 0.1063 | -122297.0215 | 122297.0215
C | Xist Rating 8221 | 10.29 | 2475.5 | 150.302 | 35.6 | 2014 | 7982.5 | 10537.8 | 0.23 | 1.25 | 22.881 | 14.625 | 1 | 1 | 2800 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4985657 | 450131.387 | 7635.7238 | 39191.3935 | 410939.9935 | 15848.5469 | 0.10668 | -122378.2783 | 122378.2783
C | Xist Rating 8222 | 10.3 | 2477.25 | 150.302 | 35.6 | 2013.2 | 7969.95 | 10537.8 | 0.23 | 1.25 | 22.883 | 14.636 | 1 | 1 | 2810 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4987199.7 | 453211.8835 | 7690.3621 | 39331.3627 | 413880.5207 | 15862.3873 | 0.10706 | -122485.15 | 122485.15
C | Xist Rating 8223 | 10.36 | 2478.72 | 150.302 | 35.6 | 2013.67 | 7977.32 | 10537.8 | 0.23 | 1.25 | 22.88 | 14.646 | 1 | 1 | 2820 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4991324.1024 | 456302.8631 | 7745.1952 | 39471.332 | 416831.5311 | 15875.0442 | 0.10744 | -122582.8834 | 122582.8834
C | Xist Rating 8224 | 10.32 | 2480.09 | 150.302 | 35.6 | 2012.6 | 7960.65 | 10537.6 | 0.22 | 1.25 | 22.906 | 14.655 | 1 | 1 | 2830 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4991429.134 | 459404.326 | 7800.223 | 39611.3013 | 419793.0247 | 15858.451 | 0.10783 | -122454.7551 | 122454.7551
C | Xist Rating 8225 | 10.35 | 2481.41 | 150.302 | 35.6 | 2012.68 | 7961.87 | 10537.7 | 0.22 | 1.25 | 22.912 | 14.664 | 1 | 1 | 2840 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4994284.2788 | 462516.272 | 7855.4457 | 39751.2705 | 422765.0014 | 15870.2244 | 0.10821 | -122545.6661 | 122545.6661
C | Xist Rating 8226 | 10.4 | 2482.86 | 150.302 | 35.6 | 2012.91 | 7965.42 | 10537.7 | 0.22 | 1.25 | 22.922 | 14.674 | 1 | 1 | 2850 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 4997773.7226 | 465638.7011 | 7910.8631 | 39891.2398 | 425747.4614 | 15883.1499 | 0.10859 | -122645.4732 | 122645.4732
C | Xist Rating 8227 | 10.47 | 2484.26 | 150.302 | 35.6 | 2013.71 | 7978.03 | 10537.8 | 0.22 | 1.25 | 22.939 | 14.683 | 1 | 1 | 2860 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 5002579.2046 | 468771.6135 | 7966.4753 | 40031.2091 | 428740.4044 | 15895.2363 | 0.10897 | -122738.8011 | 122738.8011
C | Xist Rating 8228 | 10.52 | 2485.45 | 150.302 | 35.6 | 2013.91 | 7981.16 | 10537.8 | 0.21 | 1.25 | 22.93 | 14.692 | 1 | 1 | 2870 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 5005472.6095 | 471915.009 | 8022.2824 | 40171.1783 | 431743.8306 | 15877.0914 | 0.10935 | -122598.6916 | 122598.6916
C | Xist Rating 8229 | 10.64 | 2486.96 | 150.302 | 35.6 | 2015.41 | 8004.73 | 10537.8 | 0.21 | 1.25 | 22.995 | 14.702 | 1 | 1 | 2880 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 5012244.0536 | 475068.8876 | 8078.2842 | 40311.1476 | 434757.74 | 15891.397 | 0.10973 | -122709.1554 | 122709.1554
C | Xist Rating 8230 | 10.77 | 2488.3 | 150.302 | 35.6 | 2017.22 | 8033.18 | 10537.9 | 0.21 | 1.25 | 23.02 | 14.711 | 1 | 1 | 2890 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 5019448.526 | 478233.2494 | 8134.4807 | 40451.1168 | 437782.1326 | 15903.5882 | 0.11011 | -122803.2922 | 122803.2922
C | Xist Rating 8231 | 10.79 | 2489.69 | 150.302 | 35.6 | 2016.96 | 8029.21 | 10537.9 | 0.21 | 1.25 | 23.021 | 14.721 | 1 | 1 | 2900 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 5021605.1424 | 481408.0944 | 8190.8721 | 40591.0861 | 440817.0083 | 15916.1674 | 0.11049 | -122900.4254 | 122900.4254
C | Xist Rating 8232 | 11.07 | 2491.23 | 150.302 | 35.6 | 2021.35 | 8099.09 | 10538 | 0.2 | 1.25 | 23.07 | 14.731 | 1 | 1 | 2910 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 5035647.7605 | 484593.4226 | 8247.4583 | 40731.0554 | 443862.3672 | 15899.9691 | 0.11087 | -122775.347 | 122775.347
C | Xist Rating 8233 | 11.81 | 2492.62 | 150.302 | 35.6 | 2034.47 | 8313.82 | 10538.2 | 0.2 | 1.25 | 23.158 | 14.741 | 1 | 1 | 2920 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 5071160.6114 | 487789.2339 | 8304.2393 | 40871.0246 | 446918.2092 | 15914.726 | 0.11125 | -122889.2953 | 122889.2953
C | Xist Rating 8234 | 12.38 | 2494.01 | 150.302 | 35.6 | 2044.46 | 8483.13 | 10538.3 | 0.2 | 1.25 | 23.264 | 14.752 | 1 | 1 | 2930 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 5098903.6846 | 490995.5283 | 8361.215 | 41010.9939 | 449984.5344 | 15931.0099 | 0.11164 | -123015.0353 | 123015.0353
C | Xist Rating 8235 | 12.01 | 2495.37 | 150.302 | 35.6 | 2037.13 | 8358.42 | 10538.2 | 0.19 | 1.25 | 23.207 | 14.76 | 1 | 1 | 2940 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 5083393.0881 | 494212.306 | 8418.3855 | 41150.9632 | 453061.3428 | 15909.3179 | 0.11202 | -122847.5356 | 122847.5356
C | Xist Rating 8236 | 12.69 | 2496.78 | 150.302 | 35.6 | 2049.02 | 8562.23 | 10538.3 | 0.19 | 1.25 | 23.285 | 14.77 | 1 | 1 | 2950 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 5115952.1556 | 497439.5668 | 8475.7509 | 41290.9324 | 456148.6343 | 15923.639 | 0.1124 | -122958.1197 | 122958.1197
C | Xist Rating 8237 | 13.31 | 2498.15 | 150.302 | 35.6 | 2059.85 | 8754.58 | 10538.3 | 0.19 | 1.25 | 23.359 | 14.78 | 1 | 1 | 2960 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 5145814.2775 | 500677.3107 | 8533.311 | 41430.9017 | 459246.409 | 15937.8726 | 0.11278 | -123068.0277 | 123068.0277
C | Xist Rating 8238 | 14.01 | 2499.53 | 150.302 | 35.6 | 2072.15 | 8981.26 | 10538.1 | 0.18 | 1.25 | 23.412 | 14.79 | 1 | 1 | 2970 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 5179401.0895 | 503925.5378 | 8591.0659 | 41570.8709 | 462354.6669 | 15920.4194 | 0.11316 | -122933.2586 | 122933.2586
C | Xist Rating 8239 | 14 | 2500.76 | 150.302 | 35.6 | 2071.54 | 8969.78 | 10538.1 | 0.18 | 1.25 | 23.447 | 14.799 | 1 | 1 | 2980 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 30 | E | Rod | 5180424.3704 | 507184.2481 | 8649.0156 | 41710.8402 | 465473.4079 | 15932.4964 | 0.11354 | -123026.5141 | 123026.5141
C | Xist Rating 8240 | 14 | 2502.32 | 150.302 | 35.6 | 2070.77 | 8955.28 | 10538.1 | 0.18 | 1.25 | 23.44 | 14.808 | 1 | 1 | 2990 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 29 | E | Rod | 5181729.1864 | 510453.4416 | 8707.16 | 41850.8095 | 468602.6321 | 15943.5658 | 0.11392 | -123111.9892 | 123111.9892
C | Xist Rating 8241 | 13.99 | 2503.75 | 150.302 | 35.6 | 2070.08 | 8942.53 | 10538.1 | 0.18 | 1.25 | 23.435 | 14.818 | 1 | 1 | 3000 | 152.4 | 2 | 5 | 19.05 | 1.3333 | 29 | E | Rod | 5182962.8 | 513733.1182 | 8765.4993 | 41990.7787 | 471742.3394 | 15955.721 | 0.1143 | -123205.8484 | 123205.8484
C | Xist Rating 8242 | -85.86 | 258.712 | 150.308 | 35.9 | 2347.56 | 6929.85 | 58745.1 | 2.48 | 10.95 | 25.609 | 610.943 | 1 | 1 | 1000 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 607341.9427 | 67740.9966 | 973.9444 | 14276.8648 | 53464.1318 | 637310.1674 | 0.038101 | -4921140.1804 | 4921140.1804
C | Xist Rating 8243 | -85.74 | 261.377 | 150.308 | 35.9 | 2344.42 | 6910.02 | 58282.7 | 2.46 | 10.84 | 25.694 | 599.427 | 1 | 1 | 1010 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 612777.4663 | 68958.3943 | 993.5206 | 14419.6334 | 54538.7609 | 625365.5666 | 0.038482 | -4828907.139 | 4828907.139
C | Xist Rating 8244 | -84.68 | 281.653 | 150.308 | 35.9 | 2337.26 | 6904.41 | 54967 | 2.48 | 10.07 | 25.749 | 519.481 | 1 | 1 | 1020 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 658296.2908 | 70186.4848 | 1013.2917 | 14562.4021 | 55624.0827 | 542399.836 | 0.038863 | -4188267.7589 | 4188267.7589
C | Xist Rating 8245 | -84.5 | 287.129 | 150.307 | 35.9 | 2321.07 | 6779.01 | 54177.7 | 2.39 | 9.89 | 25.118 | 501.951 | 1 | 1 | 1030 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 666446.508 | 71425.2681 | 1033.2576 | 14705.1707 | 56720.0974 | 524046.9616 | 0.039244 | -4046551.7278 | 4046551.7278
C | Xist Rating 8246 | -84.39 | 289.868 | 150.307 | 35.9 | 2315.32 | 6737.08 | 53793.8 | 2.35 | 9.8 | 24.981 | 493.571 | 1 | 1 | 1040 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 671137.1778 | 72674.7443 | 1053.4182 | 14847.9394 | 57826.805 | 515309.4078 | 0.039625 | -3979082.6532 | 3979082.6532
C | Xist Rating 8247 | -84.15 | 295.222 | 150.307 | 35.9 | 2308.66 | 6694.57 | 53042.8 | 2.31 | 9.63 | 24.884 | 477.159 | 1 | 1 | 1050 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 681567.2225 | 73934.9133 | 1073.7737 | 14990.708 | 58944.2053 | 498234.31 | 0.040006 | -3847233.2745 | 3847233.2745
C | Xist Rating 8248 | -84.03 | 297.943 | 150.306 | 35.9 | 2306.34 | 6681.82 | 52676 | 2.28 | 9.54 | 24.842 | 469.362 | 1 | 1 | 1060 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 687157.8586 | 75205.7752 | 1094.3239 | 15133.4767 | 60072.2985 | 490122.8838 | 0.040387 | -3784598.9911 | 3784598.9911
C | Xist Rating 8249 | -82.98 | 319.707 | 150.306 | 35.9 | 2290.98 | 6607.95 | 49856.8 | 2.26 | 8.9 | 24.593 | 410.642 | 1 | 1 | 1070 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 732442.3429 | 76487.3298 | 1115.0689 | 15276.2453 | 61211.0845 | 429116.8252 | 0.040768 | -3313526.3779 | 3313526.3779
C | Xist Rating 8250 | -82.74 | 323.79 | 150.305 | 35.9 | 2294.33 | 6645.73 | 49380 | 2.21 | 8.79 | 24.464 | 401.389 | 1 | 1 | 1080 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 742881.1107 | 77779.5773 | 1136.0087 | 15419.014 | 62360.5633 | 419459.1834 | 0.041149 | -3238952.6282 | 3238952.6282
C | Xist Rating 8251 | -82.43 | 329.224 | 150.305 | 35.9 | 2298.31 | 6692.51 | 48760.6 | 2.15 | 8.65 | 24.278 | 389.51 | 1 | 1 | 1090 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 756658.8114 | 79082.5176 | 1157.1433 | 15561.7826 | 63520.735 | 407055.8397 | 0.04153 | -3143177.2956 | 3143177.2956
C | Xist Rating 8252 | -82.15 | 333.276 | 150.305 | 35.9 | 2307.28 | 6779.28 | 48306.7 | 2.1 | 8.55 | 24.281 | 380.935 | 1 | 1 | 1100 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 768961.0493 | 80396.1507 | 1178.4727 | 15704.5512 | 64691.5995 | 398114.5699 | 0.041911 | -3074135.1805 | 3074135.1805
C | Xist Rating 8253 | -82 | 336.183 | 150.304 | 35.9 | 2307.73 | 6789.94 | 48009.8 | 2.02 | 8.48 | 23.898 | 375.64 | 1 | 1 | 1110 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 775819.5946 | 81720.4767 | 1199.9969 | 15847.3199 | 65873.1568 | 392503.4344 | 0.042292 | -3030807.4793 | 3030807.4793
C | Xist Rating 8254 | -80.74 | 360.437 | 150.305 | 35.9 | 2302.66 | 6808.29 | 45447.6 | 2.07 | 7.92 | 24.23 | 328.689 | 1 | 1 | 1120 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 829963.8624 | 83055.4955 | 1221.7158 | 15990.0885 | 67065.4069 | 343861.024 | 0.042673 | -2655203.6798 | 2655203.6798
C | Xist Rating 8255 | -80.58 | 363.299 | 150.304 | 35.9 | 2304.5 | 6831.12 | 45189 | 2 | 7.86 | 23.991 | 324.425 | 1 | 1 | 1130 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 837222.5455 | 84401.2071 | 1243.6296 | 16132.8572 | 68268.3499 | 339345.2268 | 0.043054 | -2620333.8911 | 2620333.8911
C | Xist Rating 8256 | -80.3 | 368.803 | 150.304 | 35.9 | 2304.22 | 6842.19 | 44681.2 | 1.94 | 7.75 | 23.617 | 315.909 | 1 | 1 | 1140 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 849803.2487 | 85757.6115 | 1265.7381 | 16275.6258 | 69481.9857 | 330412.2493 | 0.043435 | -2551355.8066 | 2551355.8066
C | Xist Rating 8257 | -80 | 374.245 | 150.303 | 35.9 | 2305.62 | 6868.14 | 44186.2 | 1.9 | 7.64 | 23.533 | 307.675 | 1 | 1 | 1150 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 862866.7569 | 87124.7088 | 1288.0414 | 16418.3945 | 70706.3143 | 321824.8668 | 0.043816 | -2485046.3153 | 2485046.3153
C | Xist Rating 8258 | -79.74 | 379.766 | 150.303 | 35.8 | 2302.62 | 6855.07 | 43703.2 | 1.85 | 7.53 | 23.337 | 299.835 | 1 | 1 | 1160 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 874456.7869 | 88502.4989 | 1310.5395 | 16561.1631 | 71941.3358 | 313623.0458 | 0.044197 | -2421714.0272 | 2421714.0272
C | Xist Rating 8259 | -78.63 | 401.516 | 150.303 | 35.8 | 2297.87 | 6868.28 | 41832.2 | 1.87 | 7.13 | 23.508 | 269.688 | 1 | 1 | 1170 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 922631.5709 | 89890.9818 | 1333.2324 | 16703.9318 | 73187.05 | 282376.0347 | 0.044578 | -2180432.8902 | 2180432.8902
C | Xist Rating 8260 | -78.5 | 403.04 | 150.303 | 35.8 | 2303.58 | 6922.9 | 41724.5 | 1.82 | 7.11 | 23.4 | 268.198 | 1 | 1 | 1180 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 928434.8832 | 91290.1576 | 1356.1201 | 16846.7004 | 74443.4571 | 280775.8097 | 0.044959 | -2168076.3774 | 2168076.3774
C | Xist Rating 8261 | -77.99 | 413.908 | 150.303 | 35.8 | 2297.74 | 6897.21 | 40885.7 | 1.77 | 6.92 | 23.195 | 255.572 | 1 | 1 | 1190 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 951052.9679 | 92700.0261 | 1379.2026 | 16989.4691 | 75710.557 | 267601.0544 | 0.04534 | -2066344.4086 | 2066344.4086
C | Xist Rating 8262 | -77.74 | 416.662 | 150.303 | 35.8 | 2309.18 | 7008.24 | 40681.7 | 1.74 | 6.88 | 23.244 | 252.614 | 1 | 1 | 1200 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 962147.5572 | 94120.5875 | 1402.4799 | 17132.2377 | 76988.3498 | 264514.7355 | 0.045721 | -2042512.6723 | 2042512.6723
C | Xist Rating 8263 | -77.46 | 422.251 | 150.302 | 35.8 | 2307.83 | 7009.69 | 40280.8 | 1.69 | 6.8 | 23.062 | 246.865 | 1 | 1 | 1210 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 974483.5253 | 95551.8417 | 1425.9519 | 17275.0064 | 78276.8354 | 258482.8195 | 0.046102 | -1995935.8162 | 1995935.8162
C | Xist Rating 8264 | -76.27 | 446.86 | 150.302 | 35.8 | 2296.57 | 6968.99 | 38537.6 | 1.69 | 6.43 | 23.067 | 221.953 | 1 | 1 | 1220 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1026245.2702 | 96993.7888 | 1449.6188 | 17417.775 | 79576.0138 | 232629.6793 | 0.046483 | -1796304.7205 | 1796304.7205
C | Xist Rating 8265 | -75.93 | 452.299 | 150.302 | 35.8 | 2302.2 | 7034.77 | 38183.3 | 1.66 | 6.35 | 23.091 | 217.172 | 1 | 1 | 1230 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1041282.7578 | 98446.4287 | 1473.4804 | 17560.5437 | 80885.885 | 227646.1355 | 0.046864 | -1757823.1163 | 1757823.1163
C | Xist Rating 8266 | -75.64 | 457.879 | 150.302 | 35.8 | 2302.5 | 7051.28 | 37835.7 | 1.62 | 6.28 | 22.972 | 212.612 | 1 | 1 | 1240 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1054266.3975 | 99909.7614 | 1497.5369 | 17703.3123 | 82206.4491 | 222865.711 | 0.047245 | -1720909.9453 | 1720909.9453
C | Xist Rating 8267 | -75.44 | 460.777 | 150.302 | 35.8 | 2307.47 | 7105.07 | 37664.1 | 1.58 | 6.24 | 22.887 | 210.456 | 1 | 1 | 1250 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1063229.1042 | 101383.7869 | 1521.7881 | 17846.081 | 83537.7059 | 220584.3792 | 0.047626 | -1703294.106 | 1703294.106
C | Xist Rating 8268 | -75.01 | 468.96 | 150.302 | 35.8 | 2307.63 | 7127.6 | 37161.3 | 1.55 | 6.14 | 22.837 | 203.89 | 1 | 1 | 1260 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1082186.1648 | 102868.5053 | 1546.2341 | 17988.8496 | 84879.6557 | 213738.6517 | 0.048007 | -1650433.2122 | 1650433.2122
C | Xist Rating 8269 | -73.87 | 492.26 | 150.302 | 35.8 | 2299.83 | 7113.72 | 35777.4 | 1.55 | 5.85 | 22.905 | 186.169 | 1 | 1 | 1270 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1132114.3158 | 104363.9164 | 1570.8749 | 18131.6183 | 86232.2982 | 195357.288 | 0.048388 | -1508497.1948 | 1508497.1948
C | Xist Rating 8270 | -73.58 | 497.908 | 150.301 | 35.8 | 2299.46 | 7123.97 | 35477.1 | 1.51 | 5.79 | 22.77 | 182.604 | 1 | 1 | 1280 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1144919.5297 | 105870.0205 | 1595.7105 | 18274.3869 | 87595.6335 | 191606.6917 | 0.048769 | -1479536.0838 | 1479536.0838
C | Xist Rating 8271 | -73.3 | 503.505 | 150.301 | 35.8 | 2299.4 | 7137.2 | 35182.4 | 1.48 | 5.73 | 22.712 | 179.124 | 1 | 1 | 1290 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1157759.397 | 107386.8173 | 1620.7408 | 18417.1556 | 88969.6617 | 187963.6661 | 0.04915 | -1451405.6057 | 1451405.6057
C | Xist Rating 8272 | -72.86 | 511.666 | 150.301 | 35.8 | 2300.57 | 7169.34 | 34750.8 | 1.46 | 5.64 | 22.755 | 173.996 | 1 | 1 | 1300 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1177123.4496 | 108914.3069 | 1645.966 | 18559.9242 | 90354.3827 | 182630.5023 | 0.049531 | -1410224.3284 | 1410224.3284
C | Xist Rating 8273 | -72.61 | 515.942 | 150.301 | 35.8 | 2303.1 | 7204.4 | 34539.6 | 1.42 | 5.59 | 22.704 | 171.602 | 1 | 1 | 1310 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1188266.0202 | 110452.4894 | 1671.3859 | 18702.6928 | 91749.7966 | 180101.5291 | 0.049912 | -1390696.268 | 1390696.268
C | Xist Rating 8274 | -71.45 | 539.341 | 150.301 | 35.8 | 2297.01 | 7205.69 | 33362.5 | 1.43 | 5.35 | 22.759 | 157.997 | 1 | 1 | 1320 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1238871.6704 | 112001.3648 | 1697.0007 | 18845.4615 | 93155.9033 | 166005.2967 | 0.050293 | -1281848.8976 | 1281848.8976
C | Xist Rating 8275 | -71.04 | 547.719 | 150.301 | 35.8 | 2295.17 | 7208.31 | 32979.4 | 1.39 | 5.28 | 22.638 | 153.841 | 1 | 1 | 1330 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1257108.2172 | 113560.9329 | 1722.8102 | 18988.2301 | 94572.7027 | 161639.5859 | 0.050674 | -1248138.0363 | 1248138.0363
C | Xist Rating 8276 | -70.59 | 555.996 | 150.301 | 35.8 | 2297.41 | 7251.41 | 32606.5 | 1.36 | 5.2 | 22.532 | 149.825 | 1 | 1 | 1340 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1277350.7704 | 115131.1939 | 1748.8145 | 19130.9988 | 96000.1951 | 157433.6296 | 0.051055 | -1215660.7567 | 1215660.7567
C | Xist Rating 8277 | -70.29 | 560.289 | 150.301 | 35.8 | 2304.15 | 7329.64 | 32423.6 | 1.33 | 5.16 | 22.492 | 147.937 | 1 | 1 | 1350 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1290989.8994 | 116712.1477 | 1775.0136 | 19273.7674 | 97438.3802 | 155442.5566 | 0.051436 | -1200286.2185 | 1200286.2185
C | Xist Rating 8278 | -69.96 | 562.989 | 150.301 | 35.8 | 2318.83 | 7487.7 | 32303 | 1.31 | 5.14 | 22.594 | 146.664 | 1 | 1 | 1360 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1305475.7829 | 118303.7943 | 1801.4075 | 19416.5361 | 98887.2582 | 154114.6798 | 0.051817 | -1190032.7064 | 1190032.7064
C | Xist Rating 8279 | -68.55 | 596.119 | 150.301 | 35.8 | 2293.78 | 7318.1 | 30902.2 | 1.3 | 4.86 | 22.492 | 132.097 | 1 | 1 | 1370 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1367365.8398 | 119906.1337 | 1827.9962 | 19559.3047 | 100346.829 | 138978.1228 | 0.052198 | -1073152.225 | 1073152.225
C | Xist Rating 8280 | -68.4 | 599.08 | 150.301 | 35.8 | 2294.3 | 7330.4 | 30793.8 | 1.28 | 4.84 | 22.445 | 131.091 | 1 | 1 | 1380 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1374469.244 | 121519.166 | 1854.7797 | 19702.0734 | 101817.0926 | 137914.9523 | 0.052579 | -1064942.7046 | 1064942.7046
C | Xist Rating 8281 | -68.02 | 606.096 | 150.301 | 35.8 | 2295.84 | 7363.82 | 30526.6 | 1.25 | 4.78 | 22.403 | 128.506 | 1 | 1 | 1390 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1391499.4406 | 123142.8911 | 1881.7579 | 19844.842 | 103298.0491 | 135198.0868 | 0.05296 | -1043963.7896 | 1043963.7896
C | Xist Rating 8282 | -67.64 | 613.108 | 150.301 | 35.8 | 2297.51 | 7398.91 | 30264.9 | 1.22 | 4.73 | 22.368 | 126 | 1 | 1 | 1400 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1408621.7611 | 124777.309 | 1908.931 | 19987.6107 | 104789.6983 | 132563.3061 | 0.053341 | -1023618.711 | 1023618.711
C | Xist Rating 8283 | -67.19 | 621.446 | 150.3 | 35.8 | 2298.5 | 7430.6 | 29957.2 | 1.2 | 4.67 | 22.342 | 123.073 | 1 | 1 | 1410 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1428393.631 | 126422.4198 | 1936.2988 | 20130.3793 | 106292.0404 | 129505.6071 | 0.053722 | -1000007.9698 | 1000007.9698
C | Xist Rating 8284 | -66 | 646.296 | 150.3 | 35.8 | 2291.14 | 7419.63 | 29051.3 | 1.21 | 4.49 | 22.401 | 114.486 | 1 | 1 | 1420 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1480754.6174 | 128078.2233 | 1963.8614 | 20273.148 | 107805.0754 | 120618.8038 | 0.054103 | -931386.4304 | 931386.4304
C | Xist Rating 8285 | -65.76 | 650.83 | 150.3 | 35.8 | 2292.13 | 7440.7 | 28910.3 | 1.17 | 4.47 | 22.316 | 113.293 | 1 | 1 | 1430 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1491786.9679 | 129744.7197 | 1991.6188 | 20415.9166 | 109328.8031 | 119328.2148 | 0.054484 | -921420.8445 | 921420.8445
C | Xist Rating 8286 | -65.2 | 661.868 | 150.3 | 35.7 | 2291.46 | 7462.1 | 28541.6 | 1.16 | 4.39 | 22.299 | 109.988 | 1 | 1 | 1440 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1516644.0473 | 131421.909 | 2019.571 | 20558.6853 | 110863.2237 | 115892.0039 | 0.054865 | -894887.3342 | 894887.3342
C | Xist Rating 8287 | -64.81 | 668.918 | 150.3 | 35.7 | 2293.31 | 7499.73 | 28316.4 | 1.13 | 4.35 | 22.274 | 108.034 | 1 | 1 | 1450 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1534036.3386 | 133109.791 | 2047.718 | 20701.4539 | 112408.3371 | 113829.0563 | 0.055246 | -878957.8002 | 878957.8002
C | Xist Rating 8288 | -64.51 | 673.093 | 150.3 | 35.7 | 2299.9 | 7581.7 | 28183.4 | 1.12 | 4.32 | 22.308 | 106.887 | 1 | 1 | 1460 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1548046.5907 | 134808.3659 | 2076.0598 | 20844.2226 | 113964.1434 | 112637.096 | 0.055627 | -869753.7981 | 869753.7981
C | Xist Rating 8289 | -63.27 | 701.072 | 150.3 | 35.7 | 2285.47 | 7499.8 | 27310 | 1.11 | 4.16 | 22.271 | 99.347 | 1 | 1 | 1470 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1602279.0238 | 136517.6336 | 2104.5964 | 20986.9912 | 115530.6424 | 104800.6119 | 0.056008 | -809242.5452 | 809242.5452
C | Xist Rating 8290 | -62.84 | 709.453 | 150.3 | 35.7 | 2286.01 | 7527.17 | 27065.8 | 1.09 | 4.11 | 22.255 | 97.34 | 1 | 1 | 1480 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1621816.6525 | 138237.5942 | 2133.3277 | 21129.7599 | 117107.8343 | 102696.7202 | 0.056389 | -792996.8514 | 792996.8514
C | Xist Rating 8291 | -62.46 | 716.505 | 150.3 | 35.7 | 2287.42 | 7560.44 | 26866 | 1.08 | 4.07 | 22.241 | 95.73 | 1 | 1 | 1490 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1638947.8671 | 139968.2475 | 2162.2539 | 21272.5285 | 118695.719 | 101019.7376 | 0.05677 | -780047.6364 | 780047.6364
C | Xist Rating 8292 | -62.09 | 723.649 | 150.3 | 35.7 | 2287.56 | 7580.06 | 26669.5 | 1.05 | 4.03 | 22.204 | 94.175 | 1 | 1 | 1500 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1655390.5064 | 141709.5937 | 2191.3748 | 21415.2972 | 120294.2966 | 99368.1649 | 0.057151 | -767294.6296 | 767294.6296
C | Xist Rating 8293 | -61.63 | 732.058 | 150.3 | 35.7 | 2289.35 | 7621.67 | 26438 | 1.04 | 3.99 | 22.197 | 92.336 | 1 | 1 | 1510 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1675936.9823 | 143461.6327 | 2220.6906 | 21558.0658 | 121903.5669 | 97453.2952 | 0.057532 | -752508.5137 | 752508.5137
C | Xist Rating 8294 | -60.25 | 759.72 | 150.3 | 35.7 | 2286.13 | 7660.63 | 25680.5 | 1.05 | 3.84 | 22.286 | 86.299 | 1 | 1 | 1520 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1736818.6836 | 145224.3646 | 2250.2011 | 21700.8345 | 123523.5301 | 91215.7186 | 0.057913 | -704343.6008 | 704343.6008
C | Xist Rating 8295 | -59.95 | 768.472 | 150.3 | 35.7 | 2279.27 | 7605.84 | 25467.1 | 1.02 | 3.8 | 22.133 | 84.736 | 1 | 1 | 1530 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1751555.1754 | 146997.7892 | 2279.9064 | 21843.6031 | 125154.1861 | 89546.4795 | 0.058294 | -691454.1785 | 691454.1785
C | Xist Rating 8296 | -59.61 | 772.921 | 150.3 | 35.7 | 2285.94 | 7691.55 | 25362.3 | 1 | 3.78 | 22.126 | 83.991 | 1 | 1 | 1540 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1766851.0307 | 148781.9067 | 2309.8065 | 21986.3717 | 126795.535 | 88751.8776 | 0.058675 | -685318.4735 | 685318.4735
C | Xist Rating 8297 | -58.9 | 786.785 | 150.3 | 35.7 | 2285.69 | 7725.7 | 25019.8 | 0.98 | 3.72 | 22.123 | 81.436 | 1 | 1 | 1550 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1798346.6066 | 150576.7171 | 2339.9013 | 22129.1404 | 128447.5767 | 86077.4823 | 0.059056 | -664667.5017 | 664667.5017
C | Xist Rating 8298 | -58.51 | 791.009 | 150.3 | 35.7 | 2296.09 | 7857.25 | 24919.3 | 0.97 | 3.7 | 22.17 | 80.713 | 1 | 1 | 1560 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 32 | E | Rod | 1816227.8548 | 152382.2202 | 2370.191 | 22271.909 | 130110.3112 | 85324.0843 | 0.059437 | -658849.9619 | 658849.9619
C | Xist Rating 8299 | -57.17 | 823.346 | 150.3 | 35.7 | 2277.89 | 7733.77 | 24161 | 0.96 | 3.56 | 22.106 | 75.209 | 1 | 1 | 1570 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 1875491.6199 | 154198.4162 | 2400.6755 | 22414.6777 | 131783.7385 | 79597.9026 | 0.059818 | -614633.9047 | 614633.9047
C | Xist Rating 8300 | -56.74 | 830.518 | 150.3 | 35.7 | 2281.36 | 7792.47 | 24006.3 | 0.95 | 3.53 | 22.101 | 74.156 | 1 | 1 | 1580 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 1894710.5445 | 156025.305 | 2431.3547 | 22557.4463 | 133467.8586 | 78497.8838 | 0.0602 | -606139.8513 | 606139.8513
C | Xist Rating 8301 | -56.34 | 837.726 | 150.3 | 35.7 | 2283.48 | 7836.1 | 23853.8 | 0.93 | 3.5 | 22.087 | 73.13 | 1 | 1 | 1590 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 1912930.5665 | 157862.8866 | 2462.2288 | 22700.215 | 135162.6716 | 77409.3645 | 0.060581 | -597734.5941 | 597734.5941
C | Xist Rating 8302 | -55.72 | 847.491 | 150.3 | 35.7 | 2289.21 | 7930.72 | 23644.7 | 0.92 | 3.46 | 22.119 | 71.7 | 1 | 1 | 1600 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 1940084.8721 | 159711.1611 | 2493.2976 | 22842.9836 | 136868.1774 | 75919.7899 | 0.060962 | -586232.4938 | 586232.4938
C | Xist Rating 8303 | -55.46 | 852.135 | 150.3 | 35.7 | 2291.04 | 7964.34 | 23555.9 | 0.89 | 3.45 | 22.088 | 71.149 | 1 | 1 | 1610 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 1952275.3704 | 161570.1283 | 2524.5612 | 22985.7523 | 138584.376 | 75306.8195 | 0.061343 | -581499.2984 | 581499.2984
C | Xist Rating 8304 | -53.87 | 888.36 | 150.3 | 35.7 | 2276.28 | 7887.69 | 22804.3 | 0.9 | 3.31 | 22.117 | 66.079 | 1 | 1 | 1620 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2022156.1008 | 163439.7884 | 2556.0196 | 23128.5209 | 140311.2675 | 70068.379 | 0.061724 | -541049.4492 | 541049.4492
C | Xist Rating 8305 | -53.46 | 892.66 | 150.3 | 35.7 | 2286.28 | 8020.69 | 22722.7 | 0.89 | 3.29 | 22.151 | 65.573 | 1 | 1 | 1630 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2040870.7048 | 165320.1414 | 2587.6728 | 23271.2896 | 142048.8518 | 69537.8726 | 0.062105 | -536953.0194 | 536953.0194
C | Xist Rating 8306 | -53.08 | 900.015 | 150.3 | 35.7 | 2287.19 | 8051.45 | 22587.9 | 0.87 | 3.27 | 22.125 | 64.744 | 1 | 1 | 1640 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2058505.3078 | 167211.1871 | 2619.5208 | 23414.0582 | 143797.1289 | 68651.5639 | 0.062486 | -530109.1793 | 530109.1793
C | Xist Rating 8307 | -52.58 | 910.137 | 150.3 | 35.7 | 2286.24 | 8066.99 | 22402.3 | 0.85 | 3.23 | 22.096 | 63.593 | 1 | 1 | 1650 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2080791.6149 | 169112.9257 | 2651.5635 | 23556.8269 | 145556.0988 | 67430.3297 | 0.062867 | -520679.1323 | 520679.1323
C | Xist Rating 8308 | -52.05 | 920.015 | 150.3 | 35.7 | 2287.75 | 8113.46 | 22220.2 | 0.84 | 3.2 | 22.102 | 62.46 | 1 | 1 | 1660 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2104764.3163 | 171025.3571 | 2683.8011 | 23699.5955 | 147325.7616 | 66246.0634 | 0.063248 | -511534.5419 | 511534.5419
C | Xist Rating 8309 | -50.63 | 952.395 | 150.3 | 35.7 | 2276.27 | 8061.26 | 21632.5 | 0.84 | 3.09 | 22.125 | 58.804 | 1 | 1 | 1670 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2167908.1667 | 172948.4814 | 2716.2334 | 23842.3642 | 149106.1172 | 62459.0814 | 0.063629 | -482292.4709 | 482292.4709
C | Xist Rating 8310 | -50.3 | 956.807 | 150.3 | 35.7 | 2281.58 | 8140.06 | 21559.9 | 0.83 | 3.08 | 22.135 | 58.392 | 1 | 1 | 1680 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2183031.7151 | 174882.2984 | 2748.8606 | 23985.1328 | 150897.1656 | 62023.5145 | 0.06401 | -478929.1381 | 478929.1381
C | Xist Rating 8311 | -49.74 | 969.745 | 150.3 | 35.7 | 2277.13 | 8118.86 | 21345.6 | 0.81 | 3.04 | 22.101 | 57.14 | 1 | 1 | 1690 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2208235.4319 | 176826.8083 | 2781.6825 | 24127.9015 | 152698.9068 | 60695.9273 | 0.064391 | -468677.8616 | 468677.8616
C | Xist Rating 8312 | -49.26 | 978.31 | 150.3 | 35.7 | 2279.22 | 8169.27 | 21205.3 | 0.8 | 3.02 | 22.105 | 56.331 | 1 | 1 | 1700 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2229783.7182 | 178782.011 | 2814.6992 | 24270.6701 | 154511.3409 | 59847.2089 | 0.064772 | -462124.2836 | 462124.2836
C | Xist Rating 8313 | -48.75 | 988.381 | 150.3 | 35.7 | 2279.36 | 8198.89 | 21044.4 | 0.79 | 2.99 | 22.095 | 55.413 | 1 | 1 | 1710 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2252876.1162 | 180747.9066 | 2847.9107 | 24413.4388 | 156334.4678 | 58884.2451 | 0.065153 | -454688.5323 | 454688.5323
C | Xist Rating 8314 | -47.43 | 1018.15 | 150.3 | 35.7 | 2270.02 | 8162.91 | 20566.9 | 0.78 | 2.9 | 22.123 | 52.656 | 1 | 1 | 1720 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2311220.863 | 182724.4949 | 2881.317 | 24556.2074 | 158168.2875 | 56013.5781 | 0.065534 | -432522.0023 | 432522.0023
C | Xist Rating 8315 | -46.82 | 1030.96 | 150.3 | 35.7 | 2268.68 | 8180.9 | 20374.1 | 0.77 | 2.87 | 22.119 | 51.594 | 1 | 1 | 1730 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2338918.3328 | 184711.7761 | 2914.9181 | 24698.9761 | 160012.8001 | 54901.0332 | 0.065915 | -423931.2256 | 423931.2256
C | Xist Rating 8316 | -46.41 | 1036.85 | 150.3 | 35.7 | 2273.51 | 8260.05 | 20290 | 0.76 | 2.85 | 22.122 | 51.15 | 1 | 1 | 1740 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2357288.8435 | 186709.7501 | 2948.714 | 24841.7447 | 161868.0054 | 54430.5004 | 0.066296 | -420297.8961 | 420297.8961
C | Xist Rating 8317 | -45.91 | 1048.46 | 150.3 | 35.7 | 2270.46 | 8251.71 | 20123.4 | 0.75 | 2.82 | 22.098 | 50.261 | 1 | 1 | 1750 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2380486.4916 | 188718.417 | 2982.7046 | 24984.5133 | 163733.9036 | 53496.0464 | 0.066677 | -413082.2899 | 413082.2899
C | Xist Rating 8318 | -45.52 | 1057.14 | 150.3 | 35.7 | 2268.77 | 8253.35 | 20000.5 | 0.74 | 2.8 | 22.092 | 49.612 | 1 | 1 | 1760 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2398407.5178 | 190737.7767 | 3016.8901 | 25127.282 | 165610.4947 | 52811.7062 | 0.067058 | -407797.9966 | 407797.9966
C | Xist Rating 8319 | -43.98 | 1092.42 | 150.3 | 35.7 | 2257.88 | 8209.85 | 19497.2 | 0.74 | 2.71 | 22.127 | 46.901 | 1 | 1 | 1770 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2466553.2696 | 192767.8292 | 3051.2703 | 25270.0506 | 167497.7785 | 50005.7199 | 0.067439 | -386130.9138 | 386130.9138
C | Xist Rating 8320 | -43.53 | 1101.21 | 150.3 | 35.7 | 2258.62 | 8243.33 | 19382.7 | 0.73 | 2.69 | 22.117 | 46.328 | 1 | 1 | 1780 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2487214.9302 | 194808.5745 | 3085.8453 | 25412.8193 | 169395.7552 | 49399.7627 | 0.06782 | -381451.8734 | 381451.8734
C | Xist Rating 8321 | -43.45 | 1105.88 | 150.301 | 35.7 | 2253.05 | 8181.01 | 19326.9 | 0.71 | 2.68 | 22.392 | 46.055 | 1 | 1 | 1790 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2491602.934 | 196860.0127 | 3120.6151 | 25555.5879 | 171304.4247 | 49103.6643 | 0.068201 | -379165.4794 | 379165.4794
C | Xist Rating 8322 | -42.52 | 1121.55 | 150.301 | 35.7 | 2258.91 | 8302.67 | 19121.7 | 0.71 | 2.65 | 22.103 | 45.026 | 1 | 1 | 1800 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2533480.5105 | 198922.1436 | 3155.5797 | 25698.3566 | 173223.787 | 48025.6201 | 0.068582 | -370841.1084 | 370841.1084
C | Xist Rating 8323 | -42.05 | 1130.21 | 150.301 | 35.7 | 2260.62 | 8349.81 | 19012.2 | 0.7 | 2.63 | 22.108 | 44.487 | 1 | 1 | 1810 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2554975.3302 | 200994.9674 | 3190.7391 | 25841.1252 | 175153.8422 | 47455.2551 | 0.068963 | -366436.9007 | 366436.9007
C | Xist Rating 8324 | -40.81 | 1165.75 | 150.301 | 35.7 | 2238.87 | 8156.75 | 18563.3 | 0.69 | 2.55 | 22.413 | 42.225 | 1 | 1 | 1820 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2609962.7025 | 203078.4841 | 3226.0933 | 25983.8939 | 177094.5902 | 45112.2413 | 0.069344 | -348344.7697 | 348344.7697
C | Xist Rating 8325 | -40.79 | 1160.12 | 150.301 | 35.6 | 2253.86 | 8343.63 | 18631.3 | 0.69 | 2.56 | 22.439 | 42.574 | 1 | 1 | 1830 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2614748.0632 | 205172.6935 | 3261.6423 | 26126.6625 | 179046.031 | 45483.081 | 0.069725 | -351208.2953 | 351208.2953
C | Xist Rating 8326 | -40.3 | 1167.25 | 150.301 | 35.6 | 2258.05 | 8421.59 | 18545.3 | 0.69 | 2.55 | 22.468 | 42.164 | 1 | 1 | 1840 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2635708.8625 | 207277.5958 | 3297.386 | 26269.4312 | 181008.1646 | 45065.8872 | 0.070106 | -347986.8352 | 347986.8352
C | Xist Rating 8327 | -39.78 | 1178.98 | 150.301 | 35.6 | 2255.49 | 8418.46 | 18409.3 | 0.67 | 2.52 | 22.453 | 41.526 | 1 | 1 | 1850 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2659177.6002 | 209393.1909 | 3333.3246 | 26412.1998 | 182980.9911 | 44372.1775 | 0.070487 | -342630.1927 | 342630.1927
C | Xist Rating 8328 | -39.21 | 1192.13 | 150.301 | 35.6 | 2252.19 | 8408.81 | 18259.1 | 0.66 | 2.5 | 22.434 | 40.825 | 1 | 1 | 1860 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2684903.2647 | 211519.4789 | 3369.4579 | 26554.9685 | 184964.5104 | 43631.1678 | 0.070868 | -336908.3128 | 336908.3128
C | Xist Rating 8329 | -37.74 | 1224.79 | 150.301 | 35.6 | 2245.9 | 8415.46 | 17879.5 | 0.66 | 2.43 | 22.489 | 39.019 | 1 | 1 | 1870 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2750755.861 | 213656.4596 | 3405.7861 | 26697.7371 | 186958.7225 | 41765.3194 | 0.071249 | -322500.7255 | 322500.7255
C | Xist Rating 8330 | -37.17 | 1237.92 | 150.301 | 35.6 | 2242.83 | 8408.47 | 17738.6 | 0.65 | 2.41 | 22.479 | 38.388 | 1 | 1 | 1880 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2776444.1136 | 215804.1332 | 3442.309 | 26840.5058 | 188963.6274 | 41097.1808 | 0.07163 | -317341.5362 | 317341.5362
C | Xist Rating 8331 | -36.65 | 1246.64 | 150.301 | 35.6 | 2245.78 | 8474.41 | 17646.3 | 0.64 | 2.39 | 22.494 | 37.981 | 1 | 1 | 1890 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2799679.1792 | 217962.4996 | 3479.0267 | 26983.2744 | 190979.2252 | 40662.8308 | 0.072011 | -313987.6009 | 313987.6009
C | Xist Rating 8332 | -36.23 | 1255.81 | 150.301 | 35.7 | 2243.57 | 8467.13 | 17555.4 | 0.63 | 2.38 | 22.484 | 37.595 | 1 | 1 | 1900 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2817497.6417 | 220131.5589 | 3515.9392 | 27126.0431 | 193005.5158 | 40248.7295 | 0.072392 | -310790.0202 | 310790.0202
C | Xist Rating 8333 | -35.75 | 1264.7 | 150.301 | 35.7 | 2245.11 | 8513.62 | 17465.1 | 0.62 | 2.36 | 22.489 | 37.206 | 1 | 1 | 1910 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2839390.617 | 222311.3109 | 3553.0464 | 27268.8117 | 195042.4992 | 39832.1187 | 0.072773 | -307573.062 | 307573.062
C | Xist Rating 8334 | -34.02 | 1304.35 | 150.301 | 35.7 | 2236.13 | 8500.18 | 17050.3 | 0.62 | 2.29 | 22.54 | 35.348 | 1 | 1 | 1920 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2916696.1655 | 224501.7558 | 3590.3485 | 27411.5804 | 197090.1755 | 37911.5599 | 0.073154 | -292743.0164 | 292743.0164
C | Xist Rating 8335 | -33.5 | 1317.56 | 150.301 | 35.7 | 2231.7 | 8472.51 | 16923.8 | 0.61 | 2.27 | 22.534 | 34.819 | 1 | 1 | 1930 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2940398.652 | 226702.8936 | 3627.8454 | 27554.349 | 199148.5446 | 37348.6421 | 0.073535 | -288396.3139 | 288396.3139
C | Xist Rating 8336 | -33.1 | 1321.87 | 150.301 | 35.7 | 2237.99 | 8576.23 | 16882 | 0.61 | 2.26 | 22.57 | 34.65 | 1 | 1 | 1940 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2958331.8413 | 228914.7241 | 3665.537 | 27697.1177 | 201217.6065 | 37181.2069 | 0.073916 | -287103.4244 | 287103.4244
C | Xist Rating 8337 | -32.71 | 1334.17 | 150.301 | 35.7 | 2231.07 | 8507.75 | 16771.9 | 0.59 | 2.24 | 22.534 | 34.209 | 1 | 1 | 1950 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 2976626.6619 | 231137.2475 | 3703.4235 | 27839.8863 | 203297.3612 | 36688.0879 | 0.074297 | -283295.6899 | 283295.6899
C | Xist Rating 8338 | -32.07 | 1348.68 | 150.301 | 35.7 | 2228.68 | 8513.33 | 16636.6 | 0.58 | 2.22 | 22.551 | 33.65 | 1 | 1 | 1960 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3005776.1424 | 233370.4637 | 3741.5047 | 27982.6549 | 205387.8087 | 36094.5955 | 0.074678 | -278712.8987 | 278712.8987
C | Xist Rating 8339 | -30.51 | 1384.36 | 150.301 | 35.7 | 2221.34 | 8508.43 | 16303 | 0.58 | 2.16 | 22.64 | 32.251 | 1 | 1 | 1970 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3075134.2424 | 235614.3727 | 3779.7807 | 28125.4236 | 207488.9491 | 34652.1574 | 0.075059 | -267574.7738 | 267574.7738
C | Xist Rating 8340 | -30 | 1394.65 | 150.301 | 35.7 | 2221.49 | 8538.74 | 16214 | 0.58 | 2.15 | 22.67 | 31.902 | 1 | 1 | 1980 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3098201.0285 | 237868.9746 | 3818.2515 | 28268.1922 | 209600.7823 | 34297.1517 | 0.07544 | -264833.5144 | 264833.5144
C | Xist Rating 8341 | -29.46 | 1408.06 | 150.301 | 35.7 | 2217.65 | 8518.18 | 16101.2 | 0.56 | 2.13 | 22.683 | 31.464 | 1 | 1 | 1990 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3122584.259 | 240134.2692 | 3856.9171 | 28410.9609 | 211723.3084 | 33808.3889 | 0.075821 | -261059.4171 | 261059.4171
C | Xist Rating 8342 | -28.97 | 1418.48 | 150.301 | 35.7 | 2217.04 | 8537.23 | 16014.7 | 0.56 | 2.12 | 22.684 | 31.133 | 1 | 1 | 2000 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3144826.8992 | 242410.2568 | 3895.7775 | 28553.7295 | 213856.5272 | 33470.3899 | 0.076202 | -258449.4789 | 258449.4789
C | Xist Rating 8343 | -28.58 | 1426.09 | 150.301 | 35.7 | 2217.39 | 8562.54 | 15953.5 | 0.55 | 2.11 | 22.689 | 30.906 | 1 | 1 | 2010 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3162197.7051 | 244696.9371 | 3934.8326 | 28696.4982 | 216000.4389 | 33220.1549 | 0.076583 | -256517.2305 | 256517.2305
C | Xist Rating 8344 | -26.91 | 1466.19 | 150.301 | 35.7 | 2208.1 | 8538.22 | 15614.7 | 0.55 | 2.05 | 22.725 | 29.568 | 1 | 1 | 2020 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3237494.139 | 246994.3102 | 3974.0826 | 28839.2668 | 218155.0434 | 31838.0305 | 0.076964 | -245844.832 | 245844.832
C | Xist Rating 8345 | -26.2 | 1480.65 | 150.301 | 35.7 | 2207.92 | 8575.57 | 15499.7 | 0.54 | 2.03 | 22.738 | 29.135 | 1 | 1 | 2030 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3269156.748 | 249302.3762 | 4013.5273 | 28982.0355 | 220320.3408 | 31373.9236 | 0.077345 | -242261.1215 | 242261.1215
C | Xist Rating 8346 | -25.79 | 1490.02 | 150.301 | 35.7 | 2206.87 | 8583.79 | 15431.5 | 0.53 | 2.02 | 22.733 | 28.897 | 1 | 1 | 2040 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3288280.4374 | 251621.135 | 4053.1669 | 29124.8041 | 222496.3309 | 31111.2303 | 0.077726 | -240232.6735 | 240232.6735
C | Xist Rating 8347 | -25.25 | 1498.57 | 150.301 | 35.7 | 2210.67 | 8666.15 | 15364.1 | 0.53 | 2.01 | 22.757 | 28.648 | 1 | 1 | 2050 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3312843.7419 | 253950.5867 | 4093.0012 | 29267.5728 | 224683.0139 | 30859.2137 | 0.078107 | -238286.6684 | 238286.6684
C | Xist Rating 8348 | -24.78 | 1512.37 | 150.301 | 35.7 | 2204.77 | 8612.38 | 15264.2 | 0.52 | 1.99 | 22.732 | 28.294 | 1 | 1 | 2060 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3334428.0049 | 256290.7311 | 4133.0303 | 29410.3414 | 226880.3897 | 30474.7777 | 0.078488 | -235318.1557 | 235318.1557
C | Xist Rating 8349 | -23 | 1555.39 | 150.302 | 35.7 | 2194.69 | 8580.75 | 14936.2 | 0.52 | 1.94 | 22.774 | 27.073 | 1 | 1 | 2070 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3413598.8791 | 258641.5684 | 4173.2542 | 29553.1101 | 229088.4584 | 29214.0962 | 0.078869 | -225583.507 | 225583.507
C | Xist Rating 8350 | -22.56 | 1564.56 | 150.301 | 35.7 | 2194.84 | 8607.05 | 14873.4 | 0.51 | 1.93 | 22.773 | 26.862 | 1 | 1 | 2080 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3433958.8704 | 261003.0986 | 4213.6729 | 29695.8787 | 231307.2198 | 28979.0004 | 0.07925 | -223768.1598 | 223768.1598
C | Xist Rating 8351 | -22.03 | 1576.49 | 150.301 | 35.7 | 2193.62 | 8620.31 | 14790.8 | 0.5 | 1.91 | 22.775 | 26.577 | 1 | 1 | 2090 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3458219.9938 | 263375.3215 | 4254.2864 | 29838.6474 | 233536.6741 | 28666.9935 | 0.079631 | -221358.9254 | 221358.9254
C | Xist Rating 8352 | -21.55 | 1588.42 | 150.301 | 35.7 | 2190.8 | 8608.71 | 14709.3 | 0.5 | 1.9 | 22.781 | 26.299 | 1 | 1 | 2100 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3479910.536 | 265758.2373 | 4295.0947 | 29981.416 | 235776.8213 | 28383.6778 | 0.080012 | -219171.2362 | 219171.2362
C | Xist Rating 8353 | -21.1 | 1598.94 | 150.301 | 35.7 | 2189.51 | 8616.78 | 14638.6 | 0.49 | 1.89 | 22.784 | 26.061 | 1 | 1 | 2110 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3500895.1194 | 268151.8459 | 4336.0977 | 30124.1847 | 238027.6612 | 28120.2137 | 0.080393 | -217136.8362 | 217136.8362
C | Xist Rating 8354 | -19.47 | 1639.48 | 150.302 | 35.7 | 2179.86 | 8580.44 | 14359 | 0.49 | 1.84 | 22.818 | 25.08 | 1 | 1 | 2120 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3573836.8728 | 270556.1473 | 4377.2956 | 30266.9533 | 240289.194 | 27108.0342 | 0.080774 | -209321.0545 | 209321.0545
C | Xist Rating 8355 | -18.86 | 1654.28 | 150.302 | 35.7 | 2177.29 | 8579.92 | 14263.7 | 0.48 | 1.83 | 22.815 | 24.765 | 1 | 1 | 2130 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3601847.3012 | 272971.1415 | 4418.6882 | 30409.722 | 242561.4196 | 26763.9956 | 0.081155 | -206664.48 | 206664.48
C | Xist Rating 8356 | -18.34 | 1669.11 | 150.302 | 35.7 | 2172.21 | 8540.35 | 14169.8 | 0.48 | 1.81 | 22.812 | 24.456 | 1 | 1 | 2140 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3625657.4331 | 275396.8286 | 4460.2756 | 30552.4906 | 244844.338 | 26447.8703 | 0.081536 | -204223.4442 | 204223.4442
C | Xist Rating 8357 | -17.98 | 1676.87 | 150.302 | 35.7 | 2172.19 | 8559.67 | 14123.4 | 0.47 | 1.8 | 22.814 | 24.313 | 1 | 1 | 2150 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3642480.2453 | 277833.2085 | 4502.0578 | 30695.2593 | 247137.9493 | 26282.3792 | 0.081917 | -202945.5658 | 202945.5658
C | Xist Rating 8358 | -17.49 | 1687.33 | 150.302 | 35.7 | 2172.13 | 8586.01 | 14059.1 | 0.47 | 1.79 | 22.82 | 24.107 | 1 | 1 | 2160 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3665100.1129 | 280280.2812 | 4544.0348 | 30838.0279 | 249442.2533 | 26073.528 | 0.082298 | -201332.8715 | 201332.8715
C | Xist Rating 8359 | -15.84 | 1731 | 150.302 | 35.7 | 2160.2 | 8518.65 | 13785.9 | 0.46 | 1.75 | 22.847 | 23.203 | 1 | 1 | 2170 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3739306.2 | 282738.0468 | 4586.2066 | 30980.7966 | 251757.2503 | 25118.5442 | 0.082679 | -193958.7401 | 193958.7401
C | Xist Rating 8360 | -15.2 | 1745.58 | 150.302 | 35.7 | 2159.11 | 8540.19 | 13699 | 0.46 | 1.74 | 22.858 | 22.927 | 1 | 1 | 2180 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3768899.2338 | 285206.5052 | 4628.5732 | 31123.5652 | 254082.94 | 24837.124 | 0.08306 | -191785.6878 | 191785.6878
C | Xist Rating 8361 | -14.75 | 1756.27 | 150.302 | 35.7 | 2157.81 | 8546.85 | 13638.9 | 0.45 | 1.73 | 22.857 | 22.746 | 1 | 1 | 2190 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3789696.9687 | 287685.6564 | 4671.1346 | 31266.3338 | 256419.3225 | 24631.386 | 0.083441 | -190197.0335 | 190197.0335
C | Xist Rating 8362 | -14.34 | 1767.37 | 150.302 | 35.7 | 2155.24 | 8533.42 | 13579.4 | 0.45 | 1.72 | 22.844 | 22.572 | 1 | 1 | 2200 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3809106.5188 | 290175.5004 | 4713.8907 | 31409.1025 | 258766.3979 | 24454.7209 | 0.083822 | -188832.8724 | 188832.8724
C | Xist Rating 8363 | -13.72 | 1782.21 | 150.302 | 35.7 | 2153.22 | 8540.19 | 13495.3 | 0.44 | 1.7 | 22.846 | 22.313 | 1 | 1 | 2210 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3837490.2162 | 292676.0373 | 4756.8417 | 31551.8711 | 261124.1661 | 24167.815 | 0.084203 | -186617.4613 | 186617.4613
C | Xist Rating 8364 | -12 | 1825.74 | 150.302 | 35.7 | 2144.16 | 8514.16 | 13246.2 | 0.44 | 1.66 | 22.884 | 21.529 | 1 | 1 | 2220 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3914678.6784 | 295187.267 | 4799.9874 | 31694.6398 | 263492.6272 | 23359.802 | 0.084584 | -180378.1987 | 180378.1987
C | Xist Rating 8365 | -11.47 | 1837.64 | 150.302 | 35.7 | 2143.75 | 8538.1 | 13182.5 | 0.44 | 1.65 | 22.889 | 21.342 | 1 | 1 | 2230 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3939440.75 | 297709.1895 | 4843.3279 | 31837.4084 | 265871.781 | 23170.336 | 0.084965 | -178915.1931 | 178915.1931
C | Xist Rating 8366 | -10.95 | 1851.41 | 150.302 | 35.7 | 2140.7 | 8524.12 | 13111.7 | 0.43 | 1.64 | 22.883 | 21.138 | 1 | 1 | 2240 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3963313.387 | 300241.8048 | 4886.8633 | 31980.1771 | 268261.6277 | 22939.7555 | 0.085346 | -177134.711 | 177134.711
C | Xist Rating 8367 | -10.38 | 1866.56 | 150.302 | 35.7 | 2137.61 | 8513.05 | 13034 | 0.42 | 1.63 | 22.879 | 20.913 | 1 | 1 | 2250 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 3989977.3216 | 302785.113 | 4930.5934 | 32122.9457 | 270662.1673 | 22687.2557 | 0.085727 | -175184.975 | 175184.975
C | Xist Rating 8368 | -10 | 1874.27 | 150.302 | 35.7 | 2138.24 | 8541.98 | 12995.5 | 0.42 | 1.62 | 22.886 | 20.807 | 1 | 1 | 2260 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4007639.0848 | 305339.114 | 4974.5182 | 32265.7144 | 273073.3996 | 22581.78 | 0.086108 | -174370.5195 | 174370.5195
C | Xist Rating 8369 | -8.23 | 1921.04 | 150.302 | 35.7 | 2127.69 | 8496.5 | 12751.8 | 0.42 | 1.59 | 22.916 | 20.08 | 1 | 1 | 2270 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4087377.5976 | 307903.8078 | 5018.6379 | 32408.483 | 275495.3248 | 21832.3823 | 0.086489 | -168583.8693 | 168583.8693
C | Xist Rating 8370 | -7.71 | 1934.75 | 150.302 | 35.7 | 2125.24 | 8491.08 | 12686.1 | 0.41 | 1.58 | 22.914 | 19.899 | 1 | 1 | 2280 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4111808.09 | 310479.1944 | 5062.9524 | 32551.2517 | 277927.9428 | 21625.2244 | 0.08687 | -166984.2503 | 166984.2503
C | Xist Rating 8371 | -7.03 | 1951.06 | 150.302 | 35.7 | 2123.4 | 8502.87 | 12606.8 | 0.41 | 1.56 | 22.915 | 19.676 | 1 | 1 | 2290 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4142880.804 | 313065.2739 | 5107.4617 | 32694.0203 | 280371.2536 | 21397.8925 | 0.087251 | -165228.8536 | 165228.8536
C | Xist Rating 8372 | -6.59 | 1961.92 | 150.302 | 35.7 | 2122.24 | 8510.4 | 12557 | 0.4 | 1.56 | 22.916 | 19.543 | 1 | 1 | 2300 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4163665.1008 | 315662.0462 | 5152.1657 | 32836.789 | 282825.2572 | 21240.4001 | 0.087632 | -164012.7397 | 164012.7397
| Xist Rating 8373 | -6.16 | 1973.04 | 150.302 | 35.7 | 2120.41 | 8507.13 | 12507.7 | 0.4 | 1.55 | 22.922 | 19.414 | 1 | 1 | 2310 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4183653.7464 | 318269.5113 | 5197.0645 | 32979.5576 | 285289.9537 | 21110.7912 | 0.088013 | -163011.9335 | 163011.9335
| Xist Rating 8374 | -4.31 | 2021.06 | 150.302 | 35.7 | 2111.39 | 8486.29 | 12277.2 | 0.4 | 1.51 | 22.945 | 18.758 | 1 | 1 | 2320 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4267245.8734 | 320887.6693 | 5242.1582 | 33122.3263 | 287765.343 | 20434.6028 | 0.088394 | -157790.5864 | 157790.5864
| Xist Rating 8375 | -3.76 | 2034.81 | 150.302 | 35.7 | 2109.62 | 8491.09 | 12216.9 | 0.39 | 1.5 | 22.95 | 18.6 | 1 | 1 | 2330 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4292675.8722 | 323516.5201 | 5287.4466 | 33265.0949 | 290251.4252 | 20250.8737 | 0.088775 | -156371.8784 | 156371.8784
| Xist Rating 8376 | -3.18 | 2048.53 | 150.302 | 35.7 | 2108.74 | 8510.13 | 12157.2 | 0.39 | 1.49 | 22.954 | 18.445 | 1 | 1 | 2340 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4319817.1522 | 326156.0637 | 5332.9298 | 33407.8636 | 292748.2001 | 20094.0821 | 0.089156 | -155161.1753 | 155161.1753
| Xist Rating 8377 | -2.71 | 2060.93 | 150.302 | 35.7 | 2106.59 | 8504.78 | 12104.7 | 0.38 | 1.49 | 22.951 | 18.31 | 1 | 1 | 2350 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4341534.5287 | 328806.3001 | 5378.6078 | 33550.6322 | 295255.6679 | 19933.5981 | 0.089537 | -153921.9611 | 153921.9611
| Xist Rating 8378 | -2.15 | 2076.13 | 150.302 | 35.7 | 2103.74 | 8495.32 | 12039.9 | 0.38 | 1.48 | 22.946 | 18.142 | 1 | 1 | 2360 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4367637.7262 | 331467.2294 | 5424.4805 | 33693.4009 | 297773.8285 | 19762.8387 | 0.089918 | -152603.4022 | 152603.4022
| Xist Rating 8379 | -0.49 | 2120.09 | 150.302 | 35.7 | 2095.6 | 8474.43 | 11846.8 | 0.38 | 1.45 | 22.972 | 17.621 | 1 | 1 | 2370 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4442860.604 | 334138.8514 | 5470.5481 | 33836.1695 | 300302.6819 | 19226.7391 | 0.090299 | -148463.7832 | 148463.7832
| Xist Rating 8380 | -0.0275 | 2134.05 | 150.302 | 35.7 | 2092.14 | 8450.65 | 11791.2 | 0.38 | 1.44 | 22.963 | 17.483 | 1 | 1 | 2380 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4464731.367 | 336821.1663 | 5516.8105 | 33978.9382 | 302842.2282 | 19086.9744 | 0.09068 | -147384.557 | 147384.557
| Xist Rating 8381 | 0.54 | 2148.8 | 150.302 | 35.7 | 2090.03 | 8452.64 | 11730.1 | 0.37 | 1.43 | 22.962 | 17.327 | 1 | 1 | 2390 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4491056.464 | 339514.1741 | 5563.2676 | 34121.7068 | 305392.4673 | 18904.2399 | 0.091061 | -145973.5297 | 145973.5297
C | Xist Rating 8383 | 11.4 | 2463.58 | 150.302 | 35.7 | 2020.27 | 8081.61 | 10538.3 | 0.4 | 1.25 | 22.941 | 14.358 | 1 | 1 | 2410 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4977096.7666 | 344932.268 | 5656.7663 | 34407.2441 | 310525.0239 | 15902.063 | 0.091823 | -122791.5153 | 122791.5153
C | Xist Rating 8384 | 11.47 | 2464.98 | 150.302 | 35.7 | 2021.23 | 8096.95 | 10538.3 | 0.4 | 1.25 | 22.968 | 14.369 | 1 | 1 | 2420 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4982291.5254 | 347657.3542 | 5703.8078 | 34550.0127 | 313107.3415 | 15918.7713 | 0.092204 | -122920.5324 | 122920.5324
C | Xist Rating 8385 | 11.6 | 2466.34 | 150.302 | 35.7 | 2022.9 | 8123.96 | 10538.2 | 0.39 | 1.25 | 22.972 | 14.38 | 1 | 1 | 2430 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4989159.186 | 350393.1333 | 5751.0441 | 34692.7814 | 315700.3519 | 15909.4652 | 0.092585 | -122848.6731 | 122848.6731
C | Xist Rating 8386 | 11.67 | 2467.71 | 150.302 | 35.7 | 2023.62 | 8135.55 | 10538.2 | 0.38 | 1.25 | 22.968 | 14.391 | 1 | 1 | 2440 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4993707.3102 | 353139.6051 | 5798.4752 | 34835.55 | 318304.0551 | 15899.6133 | 0.092966 | -122772.5997 | 122772.5997
C | Xist Rating 8387 | 11.72 | 2469.03 | 150.302 | 35.7 | 2023.84 | 8139 | 10538.2 | 0.38 | 1.25 | 22.96 | 14.402 | 1 | 1 | 2450 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4996921.6752 | 355896.7698 | 5846.1011 | 34978.3187 | 320918.4512 | 15914.6152 | 0.093347 | -122888.44 | 122888.44
C | Xist Rating 8388 | 11.71 | 2470.51 | 150.302 | 35.7 | 2023.14 | 8127.8 | 10538.2 | 0.37 | 1.25 | 22.951 | 14.413 | 1 | 1 | 2460 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4998187.6014 | 358664.6274 | 5893.9217 | 35121.0873 | 323543.54 | 15904.2647 | 0.093728 | -122808.5159 | 122808.5159
C | Xist Rating 8389 | 11.71 | 2471.86 | 150.302 | 35.7 | 2022.61 | 8119.22 | 10538.2 | 0.37 | 1.25 | 22.992 | 14.423 | 1 | 1 | 2470 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 4999608.7546 | 361443.1777 | 5941.9372 | 35263.856 | 326179.3217 | 15920.1357 | 0.094109 | -122931.0677 | 122931.0677
C | Xist Rating 8390 | 11.72 | 2473.21 | 150.302 | 35.7 | 2022.05 | 8110.2 | 10538.2 | 0.36 | 1.25 | 22.986 | 14.434 | 1 | 1 | 2480 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5000954.2805 | 364232.4209 | 5990.1474 | 35406.6246 | 328825.7962 | 15909.5732 | 0.09449 | -122849.5071 | 122849.5071
C | Xist Rating 8391 | 11.72 | 2474.6 | 150.302 | 35.7 | 2021.42 | 8100.11 | 10538.2 | 0.35 | 1.25 | 22.98 | 14.445 | 1 | 1 | 2490 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5002205.932 | 367032.3569 | 6038.5525 | 35549.3933 | 331482.9636 | 15898.8161 | 0.094871 | -122766.4433 | 122766.4433
C | Xist Rating 8392 | 11.75 | 2475.59 | 150.302 | 35.7 | 2021.65 | 8103.78 | 10538.2 | 0.35 | 1.25 | 22.977 | 14.454 | 1 | 1 | 2500 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5004776.5235 | 369842.9857 | 6087.1523 | 35692.1619 | 334150.8238 | 15911.6501 | 0.095252 | -122865.5446 | 122865.5446
C | Xist Rating 8393 | 11.72 | 2477.44 | 150.302 | 35.7 | 2020.08 | 8078.56 | 10538.2 | 0.34 | 1.25 | 22.97 | 14.466 | 1 | 1 | 2510 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5004626.9952 | 372664.3074 | 6135.9469 | 35834.9306 | 336829.3768 | 15901.5977 | 0.095633 | -122787.9226 | 122787.9226
C | Xist Rating 8394 | 11.76 | 2478.89 | 150.302 | 35.7 | 2020.16 | 8079.88 | 10538.1 | 0.34 | 1.25 | 23.003 | 14.477 | 1 | 1 | 2520 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5007754.4224 | 375496.3218 | 6184.9363 | 35977.6992 | 339518.6226 | 15917.7893 | 0.096014 | -122912.9497 | 122912.9497
C | Xist Rating 8395 | 11.77 | 2480.23 | 150.302 | 35.7 | 2019.89 | 8075.61 | 10538.1 | 0.33 | 1.25 | 22.995 | 14.487 | 1 | 1 | 2530 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5009791.7747 | 378339.0291 | 6234.1205 | 36120.4679 | 342218.5613 | 15905.2938 | 0.096395 | -122816.4626 | 122816.4626
C | Xist Rating 8396 | 11.82 | 2481.38 | 150.302 | 35.7 | 2020.36 | 8083.22 | 10538.1 | 0.33 | 1.25 | 22.988 | 14.497 | 1 | 1 | 2540 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5013280.8968 | 381192.4293 | 6283.4995 | 36263.2365 | 344929.1927 | 15918.8172 | 0.096776 | -122920.8869 | 122920.8869
C | Xist Rating 8397 | 11.8 | 2482.93 | 150.302 | 35.7 | 2019.38 | 8067.46 | 10538 | 0.32 | 1.25 | 22.982 | 14.508 | 1 | 1 | 2550 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5013979.1834 | 384056.5222 | 6333.0732 | 36406.0052 | 347650.5171 | 15907.1457 | 0.097157 | -122830.7626 | 122830.7626
C | Xist Rating 8398 | 11.75 | 2484.38 | 150.302 | 35.7 | 2017.66 | 8040.11 | 10538.1 | 0.32 | 1.25 | 22.991 | 14.519 | 1 | 1 | 2560 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5012634.1508 | 386931.308 | 6382.8418 | 36548.7738 | 350382.5342 | 15922.1962 | 0.097538 | -122946.9784 | 122946.9784
C | Xist Rating 8399 | 11.81 | 2485.77 | 150.302 | 35.7 | 2018.14 | 8047.76 | 10538.1 | 0.31 | 1.25 | 22.976 | 14.529 | 1 | 1 | 2570 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5016631.8678 | 389816.7866 | 6432.8051 | 36691.5425 | 353125.2442 | 15908.8578 | 0.097919 | -122843.9831 | 122843.9831
C | Xist Rating 8400 | 11.83 | 2487.13 | 150.302 | 35.6 | 2018.22 | 8049.02 | 10538 | 0.31 | 1.25 | 23.028 | 14.539 | 1 | 1 | 2580 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5019575.5086 | 392712.958 | 6482.9633 | 36834.3111 | 355878.6469 | 15924.2997 | 0.0983 | -122963.2212 | 122963.2212
C | Xist Rating 8401 | 11.85 | 2488.49 | 150.302 | 35.6 | 2018.02 | 8045.95 | 10538 | 0.3 | 1.25 | 23.023 | 14.549 | 1 | 1 | 2590 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5021822.5898 | 395619.8223 | 6533.3162 | 36977.0798 | 358642.7426 | 15910.9759 | 0.098681 | -122860.3382 | 122860.3382
C | Xist Rating 8402 | 11.84 | 2489.67 | 150.302 | 35.6 | 2017.59 | 8039.05 | 10537.9 | 0.3 | 1.25 | 23.026 | 14.558 | 1 | 1 | 2600 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5023133.2953 | 398537.3794 | 6583.8639 | 37119.8484 | 361417.531 | 15923.5232 | 0.099062 | -122957.2257 | 122957.2257
C | Xist Rating 8403 | 11.84 | 2491.36 | 150.302 | 35.6 | 2016.68 | 8024.64 | 10537.9 | 0.3 | 1.25 | 23.025 | 14.57 | 1 | 1 | 2610 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 31 | E | Rod | 5024275.8848 | 401465.6293 | 6634.6064 | 37262.617 | 364203.0123 | 15939.0465 | 0.099443 | -123077.0923 | 123077.0923
C | Xist Rating 8404 | 11.85 | 2492.75 | 150.302 | 35.6 | 2016.32 | 8019.06 | 10537.9 | 0.29 | 1.25 | 23.023 | 14.58 | 1 | 1 | 2620 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5026181.68 | 404404.5721 | 6685.5437 | 37405.3857 | 366999.1864 | 15925.419 | 0.099824 | -122971.8639 | 122971.8639
C | Xist Rating 8405 | 11.87 | 2494.18 | 150.302 | 35.6 | 2015.96 | 8013.26 | 10537.9 | 0.29 | 1.25 | 23.061 | 14.59 | 1 | 1 | 2630 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5028167.1128 | 407354.2076 | 6736.6758 | 37548.1543 | 369806.0533 | 15940.0959 | 0.10021 | -123085.1951 | 123085.1951
C | Xist Rating 8406 | 11.9 | 2495.43 | 150.302 | 35.6 | 2015.98 | 8013.59 | 10537.9 | 0.28 | 1.25 | 23.062 | 14.6 | 1 | 1 | 2640 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5030736.9714 | 410314.536 | 6788.0027 | 37690.923 | 372623.613 | 15926.222 | 0.10059 | -122978.0648 | 122978.0648
C | Xist Rating 8407 | 11.93 | 2496.93 | 150.302 | 35.6 | 2015.63 | 8008.18 | 10537.9 | 0.28 | 1.25 | 23.064 | 14.61 | 1 | 1 | 2650 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5032887.0159 | 413285.5572 | 6839.5243 | 37833.6916 | 375451.8656 | 15939.568 | 0.10097 | -123081.1191 | 123081.1191
C | Xist Rating 8408 | 11.95 | 2498.27 | 150.302 | 35.6 | 2015.49 | 8005.89 | 10537.9 | 0.28 | 1.25 | 23.062 | 14.62 | 1 | 1 | 2660 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5035238.2023 | 416267.2713 | 6891.2408 | 37976.4603 | 378290.811 | 15952.781 | 0.10135 | -123183.146 | 123183.146
C | Xist Rating 8409 | 12 | 2499.66 | 150.302 | 35.6 | 2015.68 | 8008.87 | 10537.9 | 0.27 | 1.25 | 23.064 | 14.63 | 1 | 1 | 2670 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5038514.6688 | 419259.6782 | 6943.152 | 38119.2289 | 381140.4492 | 15938.524 | 0.10173 | -123073.0578 | 123073.0578
C | Xist Rating 8410 | 12.06 | 2501.07 | 150.303 | 35.6 | 2016.22 | 8017.35 | 10537.9 | 0.27 | 1.25 | 23.109 | 14.64 | 1 | 1 | 2680 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5042707.3554 | 422262.7779 | 6995.258 | 38261.9976 | 384000.7803 | 15953.16 | 0.10211 | -123186.0725 | 123186.0725
C | Xist Rating 8411 | 12.11 | 2502.45 | 150.303 | 35.6 | 2016.58 | 8023.04 | 10537.9 | 0.26 | 1.25 | 23.111 | 14.65 | 1 | 1 | 2690 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5046390.621 | 425276.5704 | 7047.5588 | 38404.7662 | 386871.8041 | 15938.54 | 0.10249 | -123073.1811 | 123073.1811
C | Xist Rating 8412 | 12.18 | 2503.65 | 150.303 | 35.6 | 2017.28 | 8034.24 | 10537.9 | 0.26 | 1.25 | 23.111 | 14.659 | 1 | 1 | 2700 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5050563.072 | 428301.0557 | 7100.0544 | 38547.5349 | 389753.5209 | 15950.5799 | 0.10287 | -123166.1503 | 123166.1503
C | Xist Rating 8413 | 12.28 | 2505.31 | 150.303 | 35.6 | 2018.55 | 8054.41 | 10537.8 | 0.26 | 1.25 | 23.111 | 14.67 | 1 | 1 | 2710 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5057093.5005 | 431336.2339 | 7152.7448 | 38690.3035 | 392645.9304 | 15964.6969 | 0.10325 | -123275.1575 | 123275.1575
C | Xist Rating 8414 | 12.26 | 2506.65 | 150.303 | 35.6 | 2017.74 | 8041.49 | 10537.8 | 0.25 | 1.25 | 23.108 | 14.68 | 1 | 1 | 2720 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5057767.971 | 434382.1049 | 7205.63 | 38833.0722 | 395549.0327 | 15949.5062 | 0.10363 | -123157.8594 | 123157.8594
C | Xist Rating 8415 | 12.25 | 2507.97 | 150.303 | 35.6 | 2016.92 | 8028.63 | 10537.8 | 0.25 | 1.25 | 23.142 | 14.689 | 1 | 1 | 2730 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5058374.8524 | 437438.6687 | 7258.71 | 38975.8408 | 398462.8279 | 15962.4824 | 0.10402 | -123258.0579 | 123258.0579
C | Xist Rating 8416 | 12.25 | 2509.26 | 150.303 | 35.6 | 2016.39 | 8020.09 | 10537.8 | 0.25 | 1.25 | 23.139 | 14.699 | 1 | 1 | 2740 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5059646.7714 | 440505.9254 | 7311.9847 | 39118.6095 | 401387.3159 | 15975.3686 | 0.1044 | -123357.5617 | 123357.5617
C | Xist Rating 8417 | 12.23 | 2510.8 | 150.303 | 35.6 | 2015.3 | 8003.01 | 10537.8 | 0.25 | 1.25 | 23.134 | 14.709 | 1 | 1 | 2750 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5060015.24 | 443583.8749 | 7365.4543 | 39261.3781 | 404322.4968 | 15988.1925 | 0.10478 | -123456.5844 | 123456.5844
C | Xist Rating 8418 | 12.21 | 2512.23 | 150.303 | 35.6 | 2014.46 | 7989.65 | 10537.8 | 0.24 | 1.25 | 23.134 | 14.719 | 1 | 1 | 2760 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5060786.8458 | 446672.5172 | 7419.1186 | 39404.1468 | 407268.3704 | 15972.5494 | 0.10516 | -123335.7929 | 123335.7929
C | Xist Rating 8419 | 12.21 | 2513.46 | 150.303 | 35.6 | 2013.92 | 7981.21 | 10537.8 | 0.24 | 1.25 | 23.136 | 14.728 | 1 | 1 | 2770 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5061907.3632 | 449771.8523 | 7472.9777 | 39546.9154 | 410224.9369 | 15984.4443 | 0.10554 | -123427.6416 | 123427.6416
C | Xist Rating 8420 | 12.18 | 2515.01 | 150.303 | 35.6 | 2012.69 | 7961.91 | 10537.8 | 0.24 | 1.25 | 23.171 | 14.738 | 1 | 1 | 2780 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5061935.4769 | 452881.8803 | 7527.0316 | 39689.6841 | 413192.1962 | 15998.3649 | 0.10592 | -123535.1334 | 123535.1334
C | Xist Rating 8421 | 12.18 | 2516.42 | 150.303 | 35.6 | 2012.07 | 7952.23 | 10537.8 | 0.23 | 1.25 | 23.173 | 14.748 | 1 | 1 | 2790 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5063213.1894 | 456002.6011 | 7581.2803 | 39832.4527 | 416170.1484 | 15982.3223 | 0.1063 | -123411.2567 | 123411.2567
C | Xist Rating 8422 | 12.16 | 2517.4 | 150.303 | 35.6 | 2011.48 | 7943.13 | 10537.8 | 0.23 | 1.25 | 23.167 | 14.755 | 1 | 1 | 2800 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5063699.752 | 459134.0147 | 7635.7238 | 39975.2214 | 419158.7933 | 15991.8077 | 0.10668 | -123484.5 | 123484.5
C | Xist Rating 8423 | 12.2 | 2519.14 | 150.303 | 35.6 | 2011.29 | 7940.17 | 10537.8 | 0.23 | 1.25 | 23.154 | 14.766 | 1 | 1 | 2810 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5066721.0906 | 462276.1211 | 7690.3621 | 40117.99 | 422158.1311 | 16005.243 | 0.10706 | -123588.2439 | 123588.2439
C | Xist Rating 8424 | 12.22 | 2520.61 | 150.303 | 35.6 | 2011.17 | 7938.32 | 10537.7 | 0.23 | 1.25 | 23.159 | 14.776 | 1 | 1 | 2820 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5069375.2137 | 465428.9204 | 7745.1952 | 40260.7587 | 425168.1618 | 16018.1605 | 0.10744 | -123687.9891 | 123687.9891
C | Xist Rating 8425 | 12.24 | 2521.99 | 150.303 | 35.6 | 2011.1 | 7937.17 | 10537.8 | 0.22 | 1.25 | 23.204 | 14.785 | 1 | 1 | 2830 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5071974.089 | 468592.4125 | 7800.223 | 40403.5273 | 428188.8852 | 16001.7723 | 0.10783 | -123561.4444 | 123561.4444
C | Xist Rating 8426 | 12.21 | 2523.3 | 150.303 | 35.6 | 2010.01 | 7920.25 | 10537.7 | 0.22 | 1.25 | 23.195 | 14.794 | 1 | 1 | 2840 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5071858.233 | 471766.5974 | 7855.4457 | 40546.2959 | 431220.3015 | 16013.155 | 0.10821 | -123649.3384 | 123649.3384
C | Xist Rating 8427 | 12.25 | 2524.75 | 150.303 | 35.6 | 2010.19 | 7922.97 | 10537.7 | 0.22 | 1.25 | 23.205 | 14.804 | 1 | 1 | 2850 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5075227.2025 | 474951.4752 | 7910.8631 | 40689.0646 | 434262.4106 | 16026.1084 | 0.10859 | -123749.3611 | 123749.3611
C | Xist Rating 8428 | 12.33 | 2526.15 | 150.303 | 35.6 | 2010.9 | 7934.07 | 10537.8 | 0.22 | 1.25 | 23.221 | 14.814 | 1 | 1 | 2860 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5079835.035 | 478147.0457 | 7966.4753 | 40831.8332 | 437315.2125 | 16039.233 | 0.10897 | -123850.7056 | 123850.7056
C | Xist Rating 8429 | 12.33 | 2527.34 | 150.303 | 35.6 | 2010.53 | 7928.35 | 10537.8 | 0.21 | 1.25 | 23.22 | 14.822 | 1 | 1 | 2870 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5081292.8902 | 481353.3091 | 8022.2824 | 40974.6019 | 440378.7073 | 16019.9308 | 0.10935 | -123701.6594 | 123701.6594
C | Xist Rating 8430 | 12.44 | 2528.85 | 150.303 | 35.6 | 2011.85 | 7948.84 | 10537.8 | 0.21 | 1.25 | 23.283 | 14.832 | 1 | 1 | 2880 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5087666.8725 | 484570.2654 | 8078.2842 | 41117.3705 | 443452.8948 | 16034.2095 | 0.10973 | -123811.9154 | 123811.9154
C | Xist Rating 8431 | 12.6 | 2530.2 | 150.303 | 35.6 | 2014.19 | 7985.44 | 10537.9 | 0.21 | 1.25 | 23.314 | 14.841 | 1 | 1 | 2890 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5096303.538 | 487797.9144 | 8134.4807 | 41260.1392 | 446537.7752 | 16046.591 | 0.11011 | -123907.5219 | 123907.5219
C | Xist Rating 8432 | 12.63 | 2531.58 | 150.303 | 35.6 | 2014.06 | 7983.35 | 10537.9 | 0.21 | 1.25 | 23.318 | 14.851 | 1 | 1 | 2900 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5098754.0148 | 491036.2563 | 8190.8721 | 41402.9078 | 449633.3485 | 16059.2797 | 0.11049 | -124005.5012 | 124005.5012
C | Xist Rating 8433 | 12.76 | 2533.12 | 150.303 | 35.6 | 2015.68 | 8008.86 | 10538 | 0.2 | 1.25 | 23.346 | 14.861 | 1 | 1 | 2910 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5105959.3216 | 494285.291 | 8247.4583 | 41545.6765 | 452739.6145 | 16042.1742 | 0.11087 | -123873.4168 | 123873.4168
C | Xist Rating 8434 | 13.53 | 2534.51 | 150.303 | 35.6 | 2028.9 | 8221.51 | 10538.2 | 0.2 | 1.25 | 23.431 | 14.871 | 1 | 1 | 2920 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5142267.339 | 497545.0185 | 8304.2393 | 41688.4451 | 455856.5734 | 16056.8772 | 0.11125 | -123986.9498 | 123986.9498
C | Xist Rating 8435 | 14.11 | 2535.9 | 150.303 | 35.6 | 2038.93 | 8388.77 | 10538.3 | 0.2 | 1.25 | 23.538 | 14.881 | 1 | 1 | 2930 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5170522.587 | 500815.4389 | 8361.215 | 41831.2138 | 458984.2251 | 16072.1734 | 0.11164 | -124105.0626 | 124105.0626
C | Xist Rating 8436 | 13.77 | 2537.26 | 150.303 | 35.6 | 2032.3 | 8277.67 | 10538.2 | 0.19 | 1.25 | 23.486 | 14.89 | 1 | 1 | 2940 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5156473.498 | 504096.5521 | 8418.3855 | 41973.9824 | 462122.5697 | 16051.3086 | 0.11202 | -123943.9501 | 123943.9501
C | Xist Rating 8437 | 14.45 | 2538.67 | 150.303 | 35.6 | 2044.04 | 8475.95 | 10538.3 | 0.19 | 1.25 | 23.564 | 14.9 | 1 | 1 | 2950 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5189143.0268 | 507388.3581 | 8475.7509 | 42116.7511 | 465271.607 | 16065.6535 | 0.1124 | -124054.7176 | 124054.7176
C | Xist Rating 8438 | 15.08 | 2540.04 | 150.303 | 35.6 | 2054.88 | 8665.41 | 10538.3 | 0.19 | 1.25 | 23.639 | 14.91 | 1 | 1 | 2960 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5219477.3952 | 510690.8569 | 8533.311 | 42259.5197 | 468431.3372 | 16079.936 | 0.11278 | -124165.0037 | 124165.0037
C | Xist Rating 8439 | 15.91 | 2541.43 | 150.303 | 35.6 | 2069.37 | 8929.18 | 10538.2 | 0.18 | 1.25 | 23.708 | 14.921 | 1 | 1 | 2970 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5259158.9991 | 514004.0486 | 8591.0659 | 42402.2884 | 471601.7602 | 16063.5558 | 0.11316 | -124038.5201 | 124038.5201
C | Xist Rating 8440 | 15.91 | 2542.65 | 150.303 | 35.6 | 2068.74 | 8917.53 | 10538.2 | 0.18 | 1.25 | 23.743 | 14.929 | 1 | 1 | 2980 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5260081.761 | 517327.9331 | 8649.0156 | 42545.057 | 474782.8761 | 16074.6182 | 0.11354 | -124123.941 | 124123.941
C | Xist Rating 8441 | 15.9 | 2544.21 | 150.303 | 35.6 | 2067.96 | 8902.93 | 10538.2 | 0.18 | 1.25 | 23.737 | 14.939 | 1 | 1 | 2990 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5261324.5116 | 520662.5104 | 8707.16 | 42687.8257 | 477974.6847 | 16086.7741 | 0.11392 | -124217.8058 | 124217.8058
C | Xist Rating 8442 | 15.9 | 2545.64 | 150.303 | 35.6 | 2067.27 | 8890.23 | 10538.1 | 0.18 | 1.25 | 23.732 | 14.948 | 1 | 1 | 3000 | 152.4 | 2 | 5.1 | 19.05 | 1.3333 | 30 | E | Rod | 5262525.2028 | 524007.7805 | 8765.4993 | 42830.5943 | 481177.1862 | 16097.9148 | 0.1143 | -124303.8311 | 124303.8311
C | Xist Rating 8443 | -85.6 | 263.487 | 150.309 | 35.9 | 2345.3 | 6910.23 | 58745.1 | 2.49 | 10.95 | 26.005 | 619.011 | 1 | 1 | 1000 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 617956.0611 | 69069.2514 | 973.9444 | 14556.8033 | 54512.4481 | 645744.4507 | 0.038101 | -4986267.4803 | 4986267.4803
C | Xist Rating 8444 | -85.48 | 266.2 | 150.309 | 35.9 | 2342.16 | 6890.38 | 58282.7 | 2.47 | 10.84 | 26.094 | 607.34 | 1 | 1 | 1010 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 623482.992 | 70310.5196 | 993.5206 | 14702.3713 | 55608.1483 | 633639.5666 | 0.038482 | -4892796.774 | 4892796.774
C | Xist Rating 8445 | -84.4 | 286.848 | 150.309 | 35.9 | 2334.93 | 6884.14 | 54967 | 2.48 | 10.07 | 26.148 | 526.338 | 1 | 1 | 1020 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 669770.0006 | 71562.6904 | 1013.2917 | 14847.9394 | 56714.751 | 549566.0616 | 0.038863 | -4243603.4538 | 4243603.4538
C | Xist Rating 8446 | -84.22 | 292.419 | 150.308 | 35.9 | 2318.87 | 6760.29 | 54177.7 | 2.39 | 9.89 | 25.499 | 508.571 | 1 | 1 | 1030 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 678081.6465 | 72825.7636 | 1033.2576 | 14993.5074 | 57832.2562 | 530963.8625 | 0.039244 | -4099962.2032 | 4099962.2032
C | Xist Rating 8447 | -84.11 | 295.207 | 150.308 | 35.9 | 2313.22 | 6719.32 | 53793.8 | 2.35 | 9.8 | 25.36 | 500.077 | 1 | 1 | 1040 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 682878.7365 | 74099.7393 | 1053.4182 | 15139.0754 | 58960.6639 | 522107.3985 | 0.039625 | -4031574.9355 | 4031574.9355
C | Xist Rating 8448 | -83.87 | 300.656 | 150.307 | 35.9 | 2306.57 | 6676.99 | 53042.8 | 2.31 | 9.63 | 25.261 | 483.445 | 1 | 1 | 1050 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 693484.1099 | 75384.6175 | 1073.7737 | 15284.6435 | 60099.974 | 504803.2993 | 0.040006 | -3897957.2689 | 3897957.2689
C | Xist Rating 8449 | -83.74 | 303.424 | 150.307 | 35.9 | 2303.73 | 6659.98 | 52676 | 2.28 | 9.54 | 25.217 | 475.543 | 1 | 1 | 1060 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 699006.9715 | 76680.3982 | 1094.3239 | 15430.2115 | 61250.1867 | 496582.4671 | 0.040387 | -3834478.1812 | 3834478.1812
C | Xist Rating 8450 | -82.67 | 325.583 | 150.307 | 35.9 | 2288.62 | 6588.41 | 49856.6 | 2.26 | 8.9 | 24.958 | 416.044 | 1 | 1 | 1070 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 745135.7655 | 77987.0814 | 1115.0689 | 15575.7795 | 62411.3018 | 434766.3578 | 0.040768 | -3357150.5712 | 3357150.5712
C | Xist Rating 8451 | -82.44 | 329.739 | 150.306 | 35.9 | 2291.21 | 6619.61 | 49379.9 | 2.21 | 8.79 | 24.825 | 406.668 | 1 | 1 | 1080 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 755501.2942 | 79304.667 | 1136.0087 | 15721.3476 | 63583.3195 | 424980.0391 | 0.041149 | -3281583.212 | 3281583.212
C | Xist Rating 8452 | -82.12 | 335.269 | 150.306 | 35.9 | 2295.27 | 6666.76 | 48760.6 | 2.15 | 8.65 | 24.634 | 394.629 | 1 | 1 | 1090 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 769532.8776 | 80633.1552 | 1157.1433 | 15866.9156 | 64766.2396 | 412409.3097 | 0.04153 | -3184515.3718 | 3184515.3718
C | Xist Rating 8453 | -81.83 | 339.392 | 150.306 | 35.9 | 2304.18 | 6752.64 | 48306.7 | 2.11 | 8.55 | 24.638 | 385.938 | 1 | 1 | 1100 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 782020.2586 | 81972.5458 | 1178.4727 | 16012.4836 | 65960.0622 | 403359.2914 | 0.041911 | -3114633.5291 | 3114633.5291
C | Xist Rating 8454 | -81.68 | 342.347 | 150.305 | 35.9 | 2304.76 | 6764.33 | 48009.6 | 2.02 | 8.48 | 24.244 | 380.569 | 1 | 1 | 1110 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 789027.6717 | 83322.839 | 1199.9969 | 16158.0517 | 67164.7873 | 397656.9681 | 0.042292 | -3070601.7007 | 3070601.7007
C | Xist Rating 8455 | -80.41 | 367.044 | 150.306 | 35.9 | 2299.24 | 6778.48 | 45447.6 | 2.07 | 7.92 | 24.586 | 333.002 | 1 | 1 | 1120 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 843922.2466 | 84684.0346 | 1221.7158 | 16303.6197 | 68380.4149 | 348377.0637 | 0.042673 | -2690075.3415 | 2690075.3415
C | Xist Rating 8456 | -80.24 | 369.953 | 150.305 | 35.9 | 2301.62 | 6805.94 | 45188.5 | 2 | 7.86 | 24.338 | 328.678 | 1 | 1 | 1130 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 851491.2239 | 86056.1327 | 1243.6296 | 16449.1877 | 69606.945 | 343797.113 | 0.043054 | -2654710.176 | 2654710.176
C | Xist Rating 8457 | -79.96 | 375.554 | 150.305 | 35.9 | 2300.15 | 6806.45 | 44681 | 1.95 | 7.75 | 23.952 | 320.043 | 1 | 1 | 1140 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 863830.5331 | 87439.1333 | 1265.7381 | 16594.7558 | 70844.3776 | 334750.8512 | 0.043435 | -2584857.3406 | 2584857.3406
C | Xist Rating 8458 | -79.65 | 381.092 | 150.304 | 35.9 | 2302.32 | 6838.94 | 44185.8 | 1.9 | 7.64 | 23.868 | 311.704 | 1 | 1 | 1150 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 877395.7334 | 88833.0364 | 1288.0414 | 16740.3238 | 72092.7126 | 326041.7875 | 0.043816 | -2517608.2588 | 2517608.2588
C | Xist Rating 8459 | -79.38 | 386.708 | 150.304 | 35.8 | 2300.08 | 6832.66 | 43703.2 | 1.85 | 7.53 | 23.668 | 303.758 | 1 | 1 | 1160 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 889459.3366 | 90237.842 | 1310.5395 | 16885.8918 | 73351.9502 | 317728.9152 | 0.044197 | -2453418.4625 | 2453418.4625
C | Xist Rating 8460 | -78.25 | 408.853 | 150.304 | 35.8 | 2295.16 | 6844.09 | 41832.2 | 1.87 | 7.13 | 23.842 | 273.215 | 1 | 1 | 1170 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 938383.0515 | 91653.5501 | 1333.2324 | 17031.4599 | 74622.0902 | 286071.5746 | 0.044578 | -2208968.8699 | 2208968.8699
C | Xist Rating 8461 | -78.12 | 410.401 | 150.304 | 35.8 | 2300.64 | 6896.44 | 41724.5 | 1.82 | 7.11 | 23.731 | 271.702 | 1 | 1 | 1180 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 944184.9566 | 93080.1606 | 1356.1201 | 17177.0279 | 75903.1328 | 284446.5721 | 0.044959 | -2196421.0309 | 2196421.0309
C | Xist Rating 8462 | -77.6 | 421.461 | 150.303 | 35.8 | 2294.79 | 6870.73 | 40885.6 | 1.77 | 6.92 | 23.519 | 258.907 | 1 | 1 | 1190 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 33 | E | Rod | 967164.4882 | 94517.6737 | 1379.2026 | 17322.5959 | 77195.0778 | 271095.0368 | 0.04534 | -2093324.0146 | 2093324.0146
C | Xist Rating 8463 | -77.34 | 424.262 | 150.303 | 35.8 | 2306.58 | 6984.43 | 40681.7 | 1.74 | 6.88 | 23.503 | 255.91 | 1 | 1 | 1200 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 978594.244 | 95966.0892 | 1402.4799 | 17468.164 | 78497.9253 | 267961.8671 | 0.045721 | -2069130.5088 | 2069130.5088
C | Xist Rating 8464 | -77.06 | 429.948 | 150.303 | 35.8 | 2305.38 | 6987.09 | 40280.8 | 1.69 | 6.8 | 23.321 | 250.082 | 1 | 1 | 1210 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 991193.5202 | 97425.4073 | 1425.9519 | 17613.732 | 79811.6753 | 261847.4094 | 0.046102 | -2021916.2872 | 2021916.2872
C | Xist Rating 8465 | -75.85 | 454.999 | 150.303 | 35.8 | 2294.17 | 6946.93 | 38537.5 | 1.69 | 6.43 | 23.327 | 224.843 | 1 | 1 | 1220 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1043845.0558 | 98895.6278 | 1449.6188 | 17759.3 | 81136.3278 | 235654.9688 | 0.046483 | -1819665.204 | 1819665.204
C | Xist Rating 8466 | -75.5 | 460.534 | 150.303 | 35.8 | 2299.76 | 7012.03 | 38183.3 | 1.66 | 6.35 | 23.352 | 219.998 | 1 | 1 | 1230 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1059117.6718 | 100376.7508 | 1473.4804 | 17904.8681 | 82471.8828 | 230604.8196 | 0.046864 | -1780669.2901 | 1780669.2901
C | Xist Rating 8467 | -75.21 | 466.21 | 150.303 | 35.8 | 2300.07 | 7028.56 | 37835.7 | 1.62 | 6.28 | 23.232 | 215.376 | 1 | 1 | 1240 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1072315.6347 | 101868.7763 | 1497.5369 | 18050.4361 | 83818.3402 | 225759.532 | 0.047245 | -1743255.2641 | 1743255.2641
C | Xist Rating 8468 | -75.01 | 469.155 | 150.302 | 35.8 | 2304.44 | 7076.49 | 37664.2 | 1.58 | 6.24 | 23.145 | 213.188 | 1 | 1 | 1250 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1081139.5482 | 103371.7043 | 1521.7881 | 18196.0041 | 85175.7002 | 223444.3973 | 0.047626 | -1725378.4075 | 1725378.4075
C | Xist Rating 8469 | -74.58 | 477.482 | 150.302 | 35.8 | 2304.59 | 7098.61 | 37161.2 | 1.55 | 6.14 | 23.095 | 206.535 | 1 | 1 | 1260 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1100400.2424 | 104885.5348 | 1546.2341 | 18341.5722 | 86543.9626 | 216508.0659 | 0.048007 | -1671817.8953 | 1671817.8953
C | Xist Rating 8470 | -73.4 | 501.201 | 150.302 | 35.8 | 2297.45 | 7091 | 35777.4 | 1.56 | 5.85 | 23.166 | 188.583 | 1 | 1 | 1270 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1151484.2374 | 106410.2677 | 1570.8749 | 18487.1402 | 87923.1276 | 197900.441 | 0.048388 | -1528134.7474 | 1528134.7474
C | Xist Rating 8471 | -73.12 | 506.945 | 150.302 | 35.8 | 2296.8 | 7098.56 | 35477.1 | 1.51 | 5.79 | 23.031 | 184.968 | 1 | 1 | 1280 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1164351.276 | 107945.9032 | 1595.7105 | 18632.7082 | 89313.195 | 194084.3142 | 0.048769 | -1498667.6283 | 1498667.6283
C | Xist Rating 8472 | -72.82 | 512.637 | 150.302 | 35.8 | 2297.32 | 7117.19 | 35182.5 | 1.48 | 5.73 | 22.977 | 181.442 | 1 | 1 | 1290 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1177691.2328 | 109492.4412 | 1620.7408 | 18778.2763 | 90714.1649 | 190393.5839 | 0.04915 | -1470168.7871 | 1470168.7871
C | Xist Rating 8473 | -72.38 | 520.942 | 150.302 | 35.8 | 2298.27 | 7146.98 | 34750.8 | 1.46 | 5.64 | 23.016 | 176.246 | 1 | 1 | 1300 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1197265.3703 | 111049.8816 | 1645.966 | 18923.8443 | 92126.0373 | 184989.3288 | 0.049531 | -1428438.5621 | 1428438.5621
C | Xist Rating 8474 | -72.13 | 525.29 | 150.302 | 35.8 | 2300.57 | 7179.7 | 34539.4 | 1.42 | 5.59 | 22.967 | 173.818 | 1 | 1 | 1310 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1208466.4153 | 112618.2245 | 1671.3859 | 19069.4123 | 93548.8122 | 182424.7713 | 0.049912 | -1408635.7282 | 1408635.7282
C | Xist Rating 8475 | -70.95 | 549.107 | 150.302 | 35.8 | 2294.34 | 7179.45 | 33362.4 | 1.43 | 5.35 | 23.021 | 160.035 | 1 | 1 | 1320 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1259838.1544 | 114197.4699 | 1697.0007 | 19214.9803 | 94982.4896 | 168143.9245 | 0.050293 | -1298362.8151 | 1298362.8151
C | Xist Rating 8476 | -70.53 | 557.629 | 150.302 | 35.8 | 2292.56 | 7182.71 | 32979.3 | 1.39 | 5.28 | 22.9 | 155.822 | 1 | 1 | 1330 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1278397.9402 | 115787.6179 | 1722.8102 | 19360.5484 | 96427.0695 | 163718.5625 | 0.050674 | -1264191.3426 | 1264191.3426
C | Xist Rating 8477 | -70.07 | 566.05 | 150.301 | 35.8 | 2294.75 | 7224.97 | 32606.5 | 1.36 | 5.2 | 22.794 | 151.753 | 1 | 1 | 1340 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1298943.2375 | 117388.6682 | 1748.8145 | 19506.1164 | 97882.5518 | 159457.2569 | 0.051055 | -1231286.6704 | 1231286.6704
C | Xist Rating 8478 | -69.78 | 570.415 | 150.301 | 35.8 | 2300.44 | 7292.25 | 32423.5 | 1.33 | 5.16 | 22.754 | 149.837 | 1 | 1 | 1350 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1312205.4826 | 119000.6211 | 1775.0136 | 19651.6844 | 99348.9367 | 157436.79 | 0.051436 | -1215685.1606 | 1215685.1606
C | Xist Rating 8479 | -69.43 | 573.163 | 150.302 | 35.8 | 2316.26 | 7461.03 | 32303 | 1.32 | 5.14 | 22.857 | 148.549 | 1 | 1 | 1360 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1327594.5304 | 120623.4765 | 1801.4075 | 19797.2525 | 100826.224 | 156107.1864 | 0.051817 | -1205418.3139 | 1205418.3139
C | Xist Rating 8480 | -67.98 | 606.879 | 150.301 | 35.8 | 2291.85 | 7298.5 | 30902.1 | 1.31 | 4.86 | 22.755 | 133.791 | 1 | 1 | 1370 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1390875.6361 | 122257.2344 | 1827.9962 | 19942.8205 | 102314.4139 | 140772.3089 | 0.052198 | -1087006.4546 | 1087006.4546
C | Xist Rating 8481 | -67.84 | 609.889 | 150.301 | 35.8 | 2291.85 | 7305.42 | 30793.8 | 1.28 | 4.84 | 22.708 | 132.771 | 1 | 1 | 1380 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1397774.1046 | 123901.8947 | 1854.7797 | 20088.3885 | 103813.5062 | 139680.4535 | 0.052579 | -1078575.4371 | 1078575.4371
C | Xist Rating 8482 | -67.45 | 617.024 | 150.301 | 35.8 | 2293.42 | 7339.02 | 30526.7 | 1.25 | 4.78 | 22.666 | 130.151 | 1 | 1 | 1390 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1415095.1821 | 125557.4576 | 1881.7579 | 20233.9566 | 105323.501 | 136926.8999 | 0.05296 | -1057313.2259 | 1057313.2259
C | Xist Rating 8483 | -67.06 | 624.156 | 150.301 | 35.8 | 2295.07 | 7373.64 | 30264.7 | 1.23 | 4.73 | 22.631 | 127.611 | 1 | 1 | 1400 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1432481.7109 | 127223.9229 | 1908.931 | 20379.5246 | 106844.3983 | 134270.6644 | 0.053341 | -1036802.4795 | 1036802.4795
C | Xist Rating 8484 | -66.61 | 632.637 | 150.301 | 35.8 | 2296.2 | 7406.67 | 29957.2 | 1.2 | 4.67 | 22.606 | 124.644 | 1 | 1 | 1410 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1452661.0794 | 128901.2907 | 1936.2988 | 20525.0926 | 108376.1981 | 131157.1107 | 0.053722 | -1012760.4432 | 1012760.4432
C | Xist Rating 8485 | -65.4 | 657.93 | 150.301 | 35.8 | 2288.75 | 7394.55 | 29051.3 | 1.21 | 4.49 | 22.664 | 115.945 | 1 | 1 | 1420 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1505837.2875 | 130589.5611 | 1963.8614 | 20670.6607 | 109918.9004 | 122154.2286 | 0.054103 | -943242.5741 | 943242.5741
C | Xist Rating 8486 | -65.15 | 662.536 | 150.301 | 35.8 | 2289.95 | 7417.72 | 28910.3 | 1.17 | 4.47 | 22.581 | 114.735 | 1 | 1 | 1430 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1517174.3132 | 132288.7339 | 1991.6188 | 20816.2287 | 111472.5051 | 120845.6035 | 0.054484 | -933137.7178 | 933137.7178
C | Xist Rating 8487 | -64.58 | 673.765 | 150.301 | 35.8 | 2289.36 | 7439.93 | 28541.6 | 1.16 | 4.39 | 22.564 | 111.387 | 1 | 1 | 1440 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1542490.6404 | 133998.8092 | 2019.571 | 20961.7967 | 113037.0124 | 117364.705 | 0.054865 | -906259.1424 | 906259.1424
C | Xist Rating 8488 | -64.19 | 680.935 | 150.301 | 35.7 | 2291.34 | 7478.75 | 28316.4 | 1.13 | 4.35 | 22.539 | 109.406 | 1 | 1 | 1450 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1560253.6029 | 135719.7869 | 2047.718 | 21107.3648 | 114612.4222 | 115273.3391 | 0.055246 | -890110.1692 | 890110.1692
C | Xist Rating 8489 | -63.87 | 685.182 | 150.301 | 35.7 | 2298.05 | 7561.64 | 28183.4 | 1.12 | 4.32 | 22.575 | 108.243 | 1 | 1 | 1460 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1574582.4951 | 137451.6672 | 2076.0598 | 21252.9328 | 116198.7344 | 114064.8702 | 0.055627 | -880778.6922 | 880778.6922
C | Xist Rating 8490 | -62.62 | 713.651 | 150.301 | 35.7 | 2283.53 | 7478.98 | 27310 | 1.11 | 4.16 | 22.536 | 100.604 | 1 | 1 | 1470 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1629643.468 | 139194.45 | 2104.5964 | 21398.5008 | 117795.9491 | 106125.3866 | 0.056008 | -819472.1044 | 819472.1044
C | Xist Rating 8491 | -62.17 | 722.176 | 150.301 | 35.7 | 2284.08 | 7506.27 | 27065.8 | 1.09 | 4.11 | 22.521 | 98.571 | 1 | 1 | 1480 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1649507.7581 | 140948.1352 | 2133.3277 | 21544.0689 | 119404.0663 | 103994.3465 | 0.056389 | -803016.7779 | 803016.7779
C | Xist Rating 8492 | -61.79 | 729.348 | 150.301 | 35.7 | 2285.48 | 7539.35 | 26866 | 1.08 | 4.07 | 22.507 | 96.939 | 1 | 1 | 1490 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1666910.267 | 142712.723 | 2162.2539 | 21689.6369 | 121023.0861 | 102294.4693 | 0.05677 | -789890.7763 | 789890.7763
C | Xist Rating 8493 | -61.43 | 736.612 | 150.301 | 35.7 | 2284.93 | 7551.33 | 26669.5 | 1.06 | 4.03 | 22.468 | 95.362 | 1 | 1 | 1500 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1683106.8572 | 144488.2132 | 2191.3748 | 21835.2049 | 122653.0083 | 100634.6074 | 0.057151 | -777073.763 | 777073.763
C | Xist Rating 8494 | -60.96 | 745.164 | 150.301 | 35.7 | 2287.03 | 7596.04 | 26438 | 1.04 | 3.99 | 22.462 | 93.499 | 1 | 1 | 1510 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1704212.4229 | 146274.6059 | 2220.6906 | 21980.773 | 124293.8329 | 98679.7229 | 0.057532 | -761978.6634 | 761978.6634
C | Xist Rating 8495 | -59.55 | 773.317 | 150.301 | 35.7 | 2283.77 | 7634.19 | 25680.5 | 1.05 | 3.84 | 22.551 | 87.383 | 1 | 1 | 1520 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1766078.1651 | 148071.9011 | 2250.2011 | 22126.341 | 125945.5601 | 92360.4091 | 0.057913 | -713182.5968 | 713182.5968
C | Xist Rating 8496 | -59.25 | 782.213 | 150.3 | 35.7 | 2276.43 | 7574.32 | 25467.1 | 1.02 | 3.8 | 22.394 | 85.798 | 1 | 1 | 1530 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1780653.1396 | 149880.0988 | 2279.9064 | 22271.909 | 127608.1898 | 90667.6226 | 0.058294 | -700111.3487 | 700111.3487
C | Xist Rating 8497 | -58.9 | 786.734 | 150.3 | 35.7 | 2283.43 | 7663.32 | 25362.2 | 1 | 3.78 | 22.389 | 85.043 | 1 | 1 | 1540 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1796452.0176 | 151699.199 | 2309.8065 | 22417.4771 | 129281.7219 | 89862.5328 | 0.058675 | -693894.6586 | 693894.6586
C | Xist Rating 8498 | -58.18 | 800.837 | 150.3 | 35.7 | 2283.38 | 7699.36 | 25019.8 | 0.98 | 3.72 | 22.386 | 82.454 | 1 | 1 | 1550 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1828615.1891 | 153529.2017 | 2339.9013 | 22563.0451 | 130966.1566 | 87152.581 | 0.059056 | -672969.1289 | 672969.1289
C | Xist Rating 8499 | -57.78 | 805.133 | 150.301 | 35.7 | 2293.86 | 7831.13 | 24919.4 | 0.97 | 3.7 | 22.437 | 81.722 | 1 | 1 | 1560 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1846862.3834 | 155370.1069 | 2370.191 | 22708.6131 | 132661.4937 | 86390.0394 | 0.059437 | -667080.9851 | 667080.9851
C | Xist Rating 8500 | -56.41 | 838.032 | 150.3 | 35.7 | 2275.75 | 7709.15 | 24161 | 0.96 | 3.56 | 22.392 | 76.145 | 1 | 1 | 1570 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1907151.324 | 157221.9145 | 2400.6755 | 22854.1812 | 134367.7334 | 80589.2592 | 0.059818 | -622288.8976 | 622288.8976
C | Xist Rating 8501 | -55.98 | 845.324 | 150.3 | 35.7 | 2279.26 | 7768.03 | 24006.3 | 0.95 | 3.53 | 22.386 | 75.078 | 1 | 1 | 1580 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1926713.1802 | 159084.6247 | 2431.3547 | 22999.7492 | 136084.8755 | 79474.5547 | 0.0602 | -613681.4447 | 613681.4447
C | Xist Rating 8502 | -55.56 | 852.652 | 150.3 | 35.7 | 2282.03 | 7818.97 | 23853.9 | 0.93 | 3.5 | 22.375 | 74.038 | 1 | 1 | 1590 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1945777.4436 | 160958.2373 | 2462.2288 | 23145.3172 | 137812.9201 | 78371.4104 | 0.060581 | -605163.257 | 605163.257
C | Xist Rating 8503 | -54.98 | 862.584 | 150.3 | 35.7 | 2285.52 | 7886.67 | 23644.1 | 0.92 | 3.46 | 22.394 | 72.586 | 1 | 1 | 1600 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1971452.9837 | 162842.7524 | 2493.2976 | 23290.8853 | 139551.8672 | 76858.0446 | 0.060962 | -593477.4473 | 593477.4473
C | Xist Rating 8504 | -54.67 | 867.3 | 150.3 | 35.7 | 2289.04 | 7940.16 | 23556 | 0.9 | 3.45 | 22.373 | 72.03 | 1 | 1 | 1610 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 1985284.392 | 164738.1701 | 2524.5612 | 23436.4533 | 141301.7168 | 76256.188 | 0.061343 | -588830.0704 | 588830.0704
C | Xist Rating 8505 | -53.06 | 904.159 | 150.3 | 35.7 | 2274.13 | 7861.86 | 22804.3 | 0.9 | 3.31 | 22.403 | 66.894 | 1 | 1 | 1620 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2056175.1067 | 166644.4902 | 2556.0196 | 23582.0213 | 143062.4688 | 70933.4465 | 0.061724 | -547729.2715 | 547729.2715
C | Xist Rating 8506 | -52.64 | 908.531 | 150.3 | 35.7 | 2284.32 | 7996.59 | 22722.7 | 0.89 | 3.29 | 22.437 | 66.381 | 1 | 1 | 1630 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2075375.5339 | 168561.7128 | 2587.6728 | 23727.5894 | 144834.1234 | 70395.577 | 0.062105 | -543575.986 | 543575.986
C | Xist Rating 8507 | -52.25 | 916.006 | 150.3 | 35.7 | 2285.15 | 8026.18 | 22588 | 0.87 | 3.27 | 22.41 | 65.54 | 1 | 1 | 1640 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2093211.1109 | 170489.8379 | 2619.5208 | 23873.1574 | 146616.6804 | 69496.4361 | 0.062486 | -536633.058 | 536633.058
C | Xist Rating 8508 | -51.75 | 926.295 | 150.3 | 35.7 | 2284.03 | 8039.61 | 22402.3 | 0.85 | 3.23 | 22.381 | 64.375 | 1 | 1 | 1650 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2115685.5688 | 172428.8654 | 2651.5635 | 24018.7254 | 148410.14 | 68260.3525 | 0.062867 | -527088.3479 | 527088.3479
C | Xist Rating 8509 | -51.2 | 936.341 | 150.3 | 35.7 | 2286.1 | 8092.7 | 22220.1 | 0.84 | 3.2 | 22.388 | 63.226 | 1 | 1 | 1660 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2140569.1601 | 174378.7955 | 2683.8011 | 24164.2935 | 150214.502 | 67059.4292 | 0.063248 | -517815.1369 | 517815.1369
C | Xist Rating 8510 | -49.74 | 969.284 | 150.3 | 35.7 | 2274.58 | 8040.14 | 21632.5 | 0.84 | 3.09 | 22.411 | 59.523 | 1 | 1 | 1670 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2204714.0007 | 176339.628 | 2716.2334 | 24309.8615 | 152029.7665 | 63223.7455 | 0.063629 | -488197.0039 | 488197.0039
C | Xist Rating 8511 | -49.41 | 973.767 | 150.3 | 35.7 | 2279.93 | 8119.15 | 21559.9 | 0.83 | 3.08 | 22.421 | 59.105 | 1 | 1 | 1680 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2220120.5963 | 178311.3631 | 2748.8606 | 24455.4295 | 153855.9336 | 62781.8398 | 0.06401 | -484784.7256 | 484784.7256
C | Xist Rating 8512 | -48.83 | 986.921 | 150.3 | 35.7 | 2275.58 | 8099.17 | 21345.7 | 0.81 | 3.04 | 22.387 | 57.836 | 1 | 1 | 1690 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2245817.6892 | 180294.0006 | 2781.6825 | 24600.9976 | 155693.0031 | 61436.2713 | 0.064391 | -474394.6016 | 474394.6016
C | Xist Rating 8513 | -48.35 | 995.629 | 150.3 | 35.7 | 2277.6 | 8148.48 | 21205.5 | 0.8 | 3.02 | 22.391 | 57.016 | 1 | 1 | 1700 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2267644.6104 | 182287.5407 | 2814.6992 | 24746.5656 | 157540.975 | 60576.0153 | 0.064772 | -467751.9335 | 467751.9335
C | Xist Rating 8514 | -47.82 | 1005.87 | 150.3 | 35.7 | 2278.12 | 8182.76 | 21044.6 | 0.79 | 2.99 | 22.386 | 56.086 | 1 | 1 | 1710 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2291492.5644 | 184291.9832 | 2847.9107 | 24892.1336 | 159399.8495 | 59600.7757 | 0.065153 | -460221.3912 | 460221.3912
C | Xist Rating 8515 | -46.51 | 1036.15 | 150.301 | 35.7 | 2267.87 | 8135.22 | 20566.8 | 0.79 | 2.9 | 22.412 | 53.293 | 1 | 1 | 1720 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2349853.5005 | 186307.3282 | 2881.317 | 25037.7017 | 161269.6265 | 56709.7604 | 0.065534 | -437897.7376 | 437897.7376
C | Xist Rating 8516 | -45.88 | 1049.17 | 150.3 | 35.7 | 2266.98 | 8158.89 | 20374.1 | 0.77 | 2.87 | 22.403 | 52.216 | 1 | 1 | 1730 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2378447.4066 | 188333.5757 | 2914.9181 | 25183.2697 | 163150.306 | 55563.9371 | 0.065915 | -429049.9939 | 429049.9939
C | Xist Rating 8517 | -45.5 | 1055.16 | 150.301 | 35.7 | 2270.51 | 8220.66 | 20289.7 | 0.76 | 2.85 | 22.405 | 51.767 | 1 | 1 | 1740 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2395751.3316 | 190370.7256 | 2948.714 | 25328.8377 | 165041.8879 | 55088.0291 | 0.066296 | -425375.1582 | 425375.1582
C | Xist Rating 8518 | -44.94 | 1066.96 | 150.301 | 35.7 | 2268.96 | 8231.9 | 20123.4 | 0.75 | 2.82 | 22.383 | 50.865 | 1 | 1 | 1750 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2420889.5616 | 192418.7781 | 2982.7046 | 25474.4058 | 166944.3723 | 54140.0666 | 0.066677 | -418055.2436 | 418055.2436
C | Xist Rating 8519 | -44.55 | 1075.79 | 150.301 | 35.7 | 2267.03 | 8230.31 | 20000.5 | 0.74 | 2.8 | 22.375 | 50.207 | 1 | 1 | 1760 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2438848.2037 | 194477.7331 | 3016.8901 | 25619.9738 | 168857.7593 | 53446.1342 | 0.067058 | -412696.8814 | 412696.8814
C | Xist Rating 8520 | -42.98 | 1111.68 | 150.301 | 35.7 | 2256.35 | 8189.71 | 19497.2 | 0.74 | 2.71 | 22.411 | 47.461 | 1 | 1 | 1770 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2508339.168 | 196547.5905 | 3051.2703 | 25765.5418 | 170782.0487 | 50603.953 | 0.067439 | -390750.3114 | 390750.3114
C | Xist Rating 8521 | -42.53 | 1120.62 | 150.301 | 35.7 | 2257 | 8221.71 | 19382.7 | 0.73 | 2.69 | 22.4 | 46.881 | 1 | 1 | 1780 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2529239.34 | 198628.3505 | 3085.8453 | 25911.1099 | 172717.2406 | 49990.5357 | 0.06782 | -386013.666 | 386013.666
C | Xist Rating 8522 | -42.44 | 1125.36 | 150.301 | 35.7 | 2251.64 | 8162.42 | 19326.9 | 0.71 | 2.68 | 22.679 | 46.603 | 1 | 1 | 1790 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2533905.5904 | 200720.0129 | 3120.6151 | 26056.6779 | 174663.335 | 49689.1111 | 0.068201 | -383686.1448 | 383686.1448
C | Xist Rating 8523 | -41.5 | 1141.28 | 150.301 | 35.7 | 2257.38 | 8282.02 | 19121.7 | 0.71 | 2.65 | 22.386 | 45.561 | 1 | 1 | 1800 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2576302.6464 | 202822.5778 | 3155.5797 | 26202.2459 | 176620.3319 | 48597.4287 | 0.068582 | -375256.4625 | 375256.4625
C | Xist Rating 8524 | -41.02 | 1150.09 | 150.301 | 35.7 | 2259.09 | 8329 | 19012.2 | 0.7 | 2.63 | 22.392 | 45.014 | 1 | 1 | 1810 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2598156.8181 | 204936.0452 | 3190.7391 | 26347.814 | 178588.2313 | 48018.6729 | 0.068963 | -370787.4639 | 370787.4639
C | Xist Rating 8525 | -39.76 | 1186.24 | 150.301 | 35.7 | 2237.48 | 8138.35 | 18563.3 | 0.69 | 2.55 | 22.7 | 42.723 | 1 | 1 | 1820 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2654188.2752 | 207060.4151 | 3226.0933 | 26493.382 | 180567.0331 | 45645.569 | 0.069344 | -352462.9846 | 352462.9846
C | Xist Rating 8526 | -39.74 | 1180.51 | 150.302 | 35.6 | 2252.42 | 8323.83 | 18631.3 | 0.69 | 2.56 | 22.726 | 43.076 | 1 | 1 | 1830 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2659004.3342 | 209195.6875 | 3261.6423 | 26638.95 | 182556.7375 | 46020.6514 | 0.069725 | -355359.2717 | 355359.2717
C | Xist Rating 8527 | -39.24 | 1187.77 | 150.302 | 35.6 | 2256.54 | 8400.66 | 18545.3 | 0.69 | 2.55 | 22.756 | 42.661 | 1 | 1 | 1840 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2680250.5158 | 211341.8624 | 3297.386 | 26784.5181 | 184557.3443 | 45598.4108 | 0.070106 | -352098.8414 | 352098.8414
C | Xist Rating 8528 | -38.71 | 1199.68 | 150.302 | 35.6 | 2254.08 | 8398.85 | 18409.3 | 0.67 | 2.52 | 22.741 | 42.015 | 1 | 1 | 1850 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2704174.6944 | 213498.9398 | 3333.3246 | 26930.0861 | 186568.8537 | 44896.0045 | 0.070487 | -346675.0463 | 346675.0463
C | Xist Rating 8529 | -38.13 | 1213.05 | 150.302 | 35.6 | 2250.88 | 8390.58 | 18259 | 0.66 | 2.5 | 22.722 | 41.304 | 1 | 1 | 1860 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2730429.984 | 215666.9196 | 3369.4579 | 27075.6541 | 188591.2655 | 44144.4563 | 0.070868 | -340871.7901 | 340871.7901
C | Xist Rating 8530 | -36.63 | 1246.27 | 150.302 | 35.6 | 2244.52 | 8396.16 | 17879.5 | 0.66 | 2.43 | 22.777 | 39.474 | 1 | 1 | 1870 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2797277.9404 | 217845.802 | 3405.7861 | 27221.2222 | 190624.5798 | 42253.7691 | 0.071249 | -326272.4045 | 326272.4045
C | Xist Rating 8531 | -36.05 | 1259.62 | 150.302 | 35.6 | 2241.66 | 8392.07 | 17738.5 | 0.65 | 2.41 | 22.766 | 38.835 | 1 | 1 | 1880 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2823639.7692 | 220035.5868 | 3442.309 | 27366.7902 | 192668.7966 | 41577.1102 | 0.07163 | -321047.424 | 321047.424
C | Xist Rating 8532 | -35.51 | 1268.48 | 150.302 | 35.6 | 2244.44 | 8455.38 | 17646.3 | 0.64 | 2.39 | 22.78 | 38.422 | 1 | 1 | 1890 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2847027.2512 | 222236.2741 | 3479.0267 | 27512.3582 | 194723.9159 | 41136.3155 | 0.072011 | -317643.7242 | 317643.7242
C | Xist Rating 8533 | -35.1 | 1277.79 | 150.302 | 35.7 | 2242.11 | 8446.43 | 17555.4 | 0.63 | 2.38 | 22.77 | 38.03 | 1 | 1 | 1900 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2864945.7369 | 224447.864 | 3515.9392 | 27657.9263 | 196789.9377 | 40715.8216 | 0.072392 | -314396.7821 | 314396.7821
C | Xist Rating 8534 | -34.61 | 1286.83 | 150.302 | 35.7 | 2243.63 | 8492.34 | 17465 | 0.62 | 2.36 | 22.775 | 37.637 | 1 | 1 | 1910 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2887170.3929 | 226670.3563 | 3553.0464 | 27803.4943 | 198866.862 | 40294.8928 | 0.072773 | -311146.4808 | 311146.4808
C | Xist Rating 8535 | -32.85 | 1327.16 | 150.302 | 35.7 | 2234.82 | 8481.31 | 17050.2 | 0.62 | 2.29 | 22.829 | 35.755 | 1 | 1 | 1920 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2965963.7112 | 228903.7511 | 3590.3485 | 27949.0623 | 200954.6887 | 38349.6496 | 0.073154 | -296125.8288 | 296125.8288
C | Xist Rating 8536 | -32.32 | 1340.59 | 150.302 | 35.7 | 2230.37 | 8453.37 | 16923.8 | 0.61 | 2.27 | 22.822 | 35.218 | 1 | 1 | 1930 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 2990011.7183 | 231148.0483 | 3627.8454 | 28094.6304 | 203053.418 | 37778.2013 | 0.073535 | -291713.2564 | 291713.2564
C | Xist Rating 8537 | -31.91 | 1344.97 | 150.302 | 35.7 | 2236.61 | 8556.03 | 16882 | 0.61 | 2.26 | 22.859 | 35.047 | 1 | 1 | 1940 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3008173.3517 | 233403.2481 | 3665.537 | 28240.1984 | 205163.0497 | 37608.821 | 0.073916 | -290405.3465 | 290405.3465
C | Xist Rating 8538 | -31.52 | 1357.46 | 150.302 | 35.7 | 2229.74 | 8488.43 | 16771.8 | 0.59 | 2.24 | 22.822 | 34.6 | 1 | 1 | 1950 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3026782.8604 | 235669.3504 | 3703.4235 | 28385.7664 | 207283.584 | 37108.9932 | 0.074297 | -286545.8088 | 286545.8088
C | Xist Rating 8539 | -30.86 | 1372.22 | 150.302 | 35.7 | 2227.32 | 8493.46 | 16636.6 | 0.58 | 2.22 | 22.837 | 34.033 | 1 | 1 | 1960 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3056373.0504 | 237946.3551 | 3741.5047 | 28531.3345 | 209415.0207 | 36506.914 | 0.074678 | -281896.7129 | 281896.7129
C | Xist Rating 8540 | -29.27 | 1408.5 | 150.302 | 35.7 | 2219.98 | 8488.49 | 16303 | 0.58 | 2.16 | 22.927 | 32.616 | 1 | 1 | 1970 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3126841.83 | 240234.2624 | 3779.7807 | 28676.9025 | 211557.3599 | 35045.9085 | 0.075059 | -270615.2154 | 270615.2154
C | Xist Rating 8541 | -28.75 | 1418.96 | 150.302 | 35.7 | 2220.12 | 8518.51 | 16214 | 0.58 | 2.15 | 22.957 | 32.263 | 1 | 1 | 1980 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3150261.4752 | 242533.0721 | 3818.2515 | 28822.4705 | 213710.6016 | 34686.8234 | 0.07544 | -267842.4561 | 267842.4561
C | Xist Rating 8542 | -28.2 | 1432.58 | 150.302 | 35.7 | 2216.47 | 8500.89 | 16101.1 | 0.57 | 2.13 | 22.964 | 31.819 | 1 | 1 | 1990 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3175270.5926 | 244842.7843 | 3856.9171 | 28968.0386 | 215874.7458 | 34211.5766 | 0.075821 | -264172.726 | 264172.726
C | Xist Rating 8543 | -27.71 | 1443.17 | 150.302 | 35.7 | 2215.69 | 8517.35 | 16014.6 | 0.56 | 2.12 | 22.974 | 31.484 | 1 | 1 | 2000 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3197617.3373 | 247163.399 | 3895.7775 | 29113.6066 | 218049.7925 | 33849.4619 | 0.076202 | -261376.5724 | 261376.5724
C | Xist Rating 8544 | -27.31 | 1450.9 | 150.302 | 35.7 | 2216.39 | 8547.76 | 15953.5 | 0.55 | 2.11 | 22.978 | 31.254 | 1 | 1 | 2010 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3215760.251 | 249494.9162 | 3934.8326 | 29259.1746 | 220235.7416 | 33595.8734 | 0.076583 | -259418.4289 | 259418.4289
C | Xist Rating 8545 | -25.61 | 1491.68 | 150.302 | 35.7 | 2206.82 | 8519.12 | 15614.7 | 0.55 | 2.05 | 23.018 | 29.897 | 1 | 1 | 2020 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3291869.2576 | 251837.3359 | 3974.0826 | 29404.7427 | 222432.5933 | 32194.2879 | 0.076964 | -248595.7575 | 248595.7575
C | Xist Rating 8546 | -24.93 | 1506.38 | 150.302 | 35.7 | 2205.57 | 8540.35 | 15499.6 | 0.54 | 2.03 | 23.026 | 29.459 | 1 | 1 | 2030 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3322426.5366 | 254190.6581 | 4013.5273 | 29550.3107 | 224640.3474 | 31724.5485 | 0.077345 | -244968.5539 | 244968.5539
C | Xist Rating 8547 | -24.49 | 1515.89 | 150.302 | 35.7 | 2204.93 | 8554.6 | 15431.6 | 0.53 | 2.02 | 23.024 | 29.218 | 1 | 1 | 2040 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3342431.3377 | 256554.8828 | 4053.1669 | 29695.8787 | 226859.0041 | 31458.6914 | 0.077726 | -242915.6763 | 242915.6763
C | Xist Rating 8548 | -23.91 | 1524.59 | 150.302 | 35.7 | 2209.57 | 8649.32 | 15364 | 0.53 | 2.01 | 23.049 | 28.965 | 1 | 1 | 2050 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3368688.3263 | 258930.01 | 4093.0012 | 29841.4468 | 229088.5632 | 31202.6387 | 0.078107 | -240938.5051 | 240938.5051
C | Xist Rating 8549 | -23.44 | 1538.61 | 150.302 | 35.7 | 2203.44 | 8592.18 | 15264.2 | 0.52 | 1.99 | 23.027 | 28.607 | 1 | 1 | 2060 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3390234.8184 | 261316.0396 | 4133.0303 | 29987.0148 | 231329.0248 | 30813.9925 | 0.078488 | -237937.4822 | 237937.4822
C | Xist Rating 8550 | -21.63 | 1582.36 | 150.302 | 35.7 | 2193.56 | 8563.49 | 14936.1 | 0.52 | 1.94 | 23.065 | 27.37 | 1 | 1 | 2070 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3471001.6016 | 263712.9717 | 4173.2542 | 30132.5828 | 233580.3889 | 29536.5708 | 0.078869 | -228073.5701 | 228073.5701
C | Xist Rating 8551 | -21.21 | 1591.67 | 150.302 | 35.7 | 2192.82 | 8576.05 | 14873.4 | 0.51 | 1.93 | 23.065 | 27.156 | 1 | 1 | 2080 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3490245.8094 | 266120.8064 | 4213.6729 | 30278.1509 | 235842.6555 | 29298.2036 | 0.07925 | -226232.9617 | 226232.9617
C | Xist Rating 8552 | -20.68 | 1603.79 | 150.302 | 35.7 | 2191.33 | 8584.92 | 14790.9 | 0.5 | 1.91 | 23.074 | 26.868 | 1 | 1 | 2090 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3514433.1407 | 268539.5435 | 4254.2864 | 30423.7189 | 238115.8246 | 28983.2023 | 0.079631 | -223800.6053 | 223800.6053
C | Xist Rating 8553 | -20.16 | 1615.92 | 150.302 | 35.7 | 2189.48 | 8588.3 | 14709.2 | 0.5 | 1.9 | 23.075 | 26.585 | 1 | 1 | 2100 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3538024.5216 | 270969.1831 | 4295.0947 | 30569.2869 | 240399.8962 | 28694.5257 | 0.080012 | -221571.5214 | 221571.5214
C | Xist Rating 8554 | -19.69 | 1626.6 | 150.302 | 35.7 | 2188.4 | 8599.63 | 14638.7 | 0.49 | 1.89 | 23.077 | 26.344 | 1 | 1 | 2110 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3559651.44 | 273409.7252 | 4336.0977 | 30714.855 | 242694.8702 | 28427.6876 | 0.080393 | -219511.0682 | 219511.0682
C | Xist Rating 8555 | -18.04 | 1667.82 | 150.302 | 35.7 | 2178.7 | 8562.53 | 14359 | 0.49 | 1.84 | 23.112 | 25.351 | 1 | 1 | 2120 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3633679.434 | 275861.1698 | 4377.2956 | 30860.423 | 245000.7468 | 27403.157 | 0.080774 | -211599.9149 | 211599.9149
C | Xist Rating 8556 | -17.42 | 1682.86 | 150.302 | 35.7 | 2176.06 | 8560.83 | 14263.7 | 0.48 | 1.83 | 23.109 | 25.031 | 1 | 1 | 2130 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3662004.3316 | 278323.5169 | 4418.6882 | 31005.991 | 247317.5258 | 27053.7099 | 0.081155 | -208901.5764 | 208901.5764
C | Xist Rating 8557 | -16.9 | 1697.93 | 150.302 | 35.7 | 2171.01 | 8521.85 | 14169.8 | 0.48 | 1.81 | 23.105 | 24.718 | 1 | 1 | 2140 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3686223.0093 | 280796.7664 | 4460.2756 | 31151.5591 | 249645.2074 | 26733.4478 | 0.081536 | -206428.5975 | 206428.5975
C | Xist Rating 8558 | -16.53 | 1705.81 | 150.302 | 35.7 | 2171 | 8541.12 | 14123.3 | 0.47 | 1.8 | 23.107 | 24.573 | 1 | 1 | 2150 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3703313.51 | 283280.9185 | 4502.0578 | 31297.1271 | 251983.7914 | 26565.6603 | 0.081917 | -205132.9874 | 205132.9874
C | Xist Rating 8559 | -16.03 | 1716.44 | 150.302 | 35.7 | 2171.08 | 8569.65 | 14059 | 0.47 | 1.79 | 23.115 | 24.364 | 1 | 1 | 2160 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3726528.5552 | 285775.973 | 4544.0348 | 31442.6951 | 254333.2779 | 26353.8463 | 0.082298 | -203497.4156 | 203497.4156
C | Xist Rating 8560 | -14.35 | 1760.84 | 150.302 | 35.7 | 2159.05 | 8500.87 | 13785.8 | 0.46 | 1.75 | 23.139 | 23.448 | 1 | 1 | 2170 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3801741.602 | 288281.9301 | 4586.2066 | 31588.2631 | 256693.6669 | 25386.0415 | 0.082679 | -196024.2837 | 196024.2837
C | Xist Rating 8561 | -13.69 | 1775.66 | 150.302 | 35.7 | 2157.96 | 8522.3 | 13699 | 0.46 | 1.74 | 23.151 | 23.169 | 1 | 1 | 2180 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3831803.2536 | 290798.7896 | 4628.5732 | 31733.8312 | 259064.9584 | 25101.611 | 0.08306 | -193827.9864 | 193827.9864
C | Xist Rating 8562 | -13.24 | 1786.52 | 150.302 | 35.7 | 2156.67 | 8528.98 | 13638.9 | 0.45 | 1.73 | 23.15 | 22.985 | 1 | 1 | 2190 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3852934.0884 | 293326.5516 | 4671.1346 | 31879.3992 | 261447.1524 | 24892.5303 | 0.083441 | -192213.5206 | 192213.5206
C | Xist Rating 8563 | -12.82 | 1797.78 | 150.302 | 35.7 | 2154.11 | 8515.74 | 13579.4 | 0.45 | 1.72 | 23.137 | 22.809 | 1 | 1 | 2200 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3872615.8758 | 295865.2161 | 4713.8907 | 32024.9672 | 263840.2489 | 24713.8473 | 0.083822 | -190833.7778 | 190833.7778
C | Xist Rating 8564 | -12.19 | 1812.86 | 150.302 | 35.7 | 2152.1 | 8522.56 | 13495.3 | 0.44 | 1.7 | 23.139 | 22.547 | 1 | 1 | 2210 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3901456.006 | 298414.7831 | 4756.8417 | 32170.5353 | 266244.2478 | 24423.5948 | 0.084203 | -188592.5249 | 188592.5249
C | Xist Rating 8565 | -10.45 | 1857.13 | 150.302 | 35.7 | 2142.94 | 8494.94 | 13246.2 | 0.44 | 1.66 | 23.178 | 21.753 | 1 | 1 | 2220 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 3979718.1622 | 300975.2526 | 4799.9874 | 32316.1033 | 268659.1493 | 23605.2983 | 0.084584 | -182273.8564 | 182273.8564
C | Xist Rating 8566 | -9.9 | 1869.21 | 150.302 | 35.7 | 2142.53 | 8518.83 | 13182.5 | 0.44 | 1.65 | 23.182 | 21.562 | 1 | 1 | 2230 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 4004838.5013 | 303546.6246 | 4843.3279 | 32461.6713 | 271084.9532 | 23411.6924 | 0.084965 | -180778.8829 | 180778.8829
C | Xist Rating 8567 | -9.38 | 1883.2 | 150.302 | 35.7 | 2139.62 | 8507.01 | 13111.7 | 0.43 | 1.64 | 23.176 | 21.356 | 1 | 1 | 2240 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 4029332.384 | 306128.899 | 4886.8633 | 32607.2394 | 273521.6597 | 23178.7984 | 0.085346 | -178980.5374 | 178980.5374
C | Xist Rating 8568 | -8.79 | 1898.59 | 150.302 | 35.7 | 2136.52 | 8495.68 | 13034 | 0.42 | 1.63 | 23.172 | 21.128 | 1 | 1 | 2250 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 32 | E | Rod | 4056375.5068 | 308722.076 | 4930.5934 | 32752.8074 | 275969.2686 | 22922.9442 | 0.085727 | -177004.8986 | 177004.8986
C | Xist Rating 8569 | -8.41 | 1906.42 | 150.302 | 35.7 | 2137.16 | 8524.83 | 12995.5 | 0.42 | 1.62 | 23.175 | 21.02 | 1 | 1 | 2260 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4074324.5672 | 311326.1554 | 4974.5182 | 32898.3754 | 278427.78 | 22815.2764 | 0.086108 | -176173.5168 | 176173.5168
C | Xist Rating 8570 | -6.62 | 1953.96 | 150.302 | 35.7 | 2126.47 | 8477.13 | 12751.8 | 0.42 | 1.59 | 23.205 | 20.284 | 1 | 1 | 2270 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4155037.3212 | 313941.1374 | 5018.6379 | 33043.9435 | 280897.1939 | 22056.5867 | 0.086489 | -170315.1157 | 170315.1157
C | Xist Rating 8571 | -6.07 | 1967.89 | 150.302 | 35.7 | 2124.24 | 8475.17 | 12686.1 | 0.41 | 1.58 | 23.201 | 20.1 | 1 | 1 | 2280 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4180270.6536 | 316567.0218 | 5062.9524 | 33189.5115 | 283377.5103 | 21845.9884 | 0.08687 | -168688.932 | 168688.932
C | Xist Rating 8572 | -5.39 | 1984.47 | 150.302 | 35.7 | 2122.35 | 8486.05 | 12606.8 | 0.41 | 1.56 | 23.202 | 19.875 | 1 | 1 | 2290 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4211739.9045 | 319203.8087 | 5107.4617 | 33335.0795 | 285868.7292 | 21616.6323 | 0.087251 | -166917.9046 | 166917.9046
C | Xist Rating 8573 | -4.93 | 1995.49 | 150.302 | 35.7 | 2121.21 | 8493.87 | 12557 | 0.4 | 1.56 | 23.204 | 19.74 | 1 | 1 | 2300 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4232853.3429 | 321851.4981 | 5152.1657 | 33480.6476 | 288370.8505 | 21456.8611 | 0.087632 | -165684.1936 | 165684.1936
| Xist Rating 8574 | -4.51 | 2006.79 | 150.302 | 35.7 | 2119.31 | 8489.38 | 12507.7 | 0.4 | 1.55 | 23.21 | 19.609 | 1 | 1 | 2310 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4253010.1149 | 324510.09 | 5197.0645 | 33626.2156 | 290883.8744 | 21325.2267 | 0.088013 | -164667.7481 | 164667.7481
| Xist Rating 8575 | -2.61 | 2055.61 | 150.302 | 35.7 | 2110.42 | 8470.67 | 12277.2 | 0.4 | 1.51 | 23.232 | 18.945 | 1 | 1 | 2320 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4338200.4562 | 327179.5844 | 5242.1582 | 33771.7836 | 293407.8007 | 20640.7404 | 0.088394 | -159382.3265 | 159382.3265
| Xist Rating 8576 | -2.06 | 2069.57 | 150.302 | 35.7 | 2108.67 | 8475.64 | 12216.9 | 0.39 | 1.5 | 23.238 | 18.785 | 1 | 1 | 2330 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4364040.1719 | 329859.9812 | 5287.4466 | 33917.3517 | 295942.6296 | 20454.7267 | 0.088775 | -157945.9778 | 157945.9778
| Xist Rating 8577 | -1.47 | 2083.51 | 150.302 | 35.7 | 2107.67 | 8492.67 | 12157.2 | 0.39 | 1.49 | 23.24 | 18.627 | 1 | 1 | 2340 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4391351.5217 | 332551.2806 | 5332.9298 | 34062.9197 | 298488.3609 | 20294.7882 | 0.089156 | -156710.9746 | 156710.9746
| Xist Rating 8578 | -0.98 | 2096.1 | 150.302 | 35.7 | 2105.93 | 8494.06 | 12104.8 | 0.38 | 1.49 | 23.241 | 18.491 | 1 | 1 | 2350 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4414239.873 | 335253.4825 | 5378.6078 | 34208.4877 | 301044.9947 | 20133.1746 | 0.089537 | -155463.0375 | 155463.0375
| Xist Rating 8579 | -0.43 | 2111.53 | 150.302 | 35.7 | 2102.67 | 8477.84 | 12039.9 | 0.38 | 1.48 | 23.235 | 18.32 | 1 | 1 | 2360 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4439850.7851 | 337966.5868 | 5424.4805 | 34354.0558 | 303612.531 | 19959.3089 | 0.089918 | -154120.4927 | 154120.4927
| Xist Rating 8580 | 1.21 | 2156.23 | 150.302 | 35.7 | 2093.38 | 8438.15 | 11846.9 | 0.38 | 1.45 | 23.26 | 17.792 | 1 | 1 | 2370 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4513808.7574 | 340690.5936 | 5470.5481 | 34499.6238 | 306190.9698 | 19415.9487 | 0.090299 | -149924.809 | 149924.809
| Xist Rating 8581 | 1.68 | 2170.4 | 150.302 | 35.7 | 2089.85 | 8413.53 | 11791.3 | 0.38 | 1.44 | 23.251 | 17.653 | 1 | 1 | 2380 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4535810.44 | 343425.5029 | 5516.8105 | 34645.1918 | 308780.3111 | 19275.1945 | 0.09068 | -148837.9426 | 148837.9426
| Xist Rating 8582 | 2.25 | 2185.39 | 150.302 | 35.7 | 2087.71 | 8414.66 | 11730.1 | 0.37 | 1.43 | 23.249 | 17.495 | 1 | 1 | 2390 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 4562460.5569 | 346171.3147 | 5563.2676 | 34790.7599 | 311380.5549 | 19090.0839 | 0.091061 | -147408.5675 | 147408.5675
C | Xist Rating 8584 | 13.26 | 2505.47 | 150.302 | 35.7 | 2017.83 | 8042.66 | 10538.2 | 0.41 | 1.25 | 23.215 | 14.488 | 1 | 1 | 2410 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5055612.5301 | 351695.6458 | 5656.7663 | 35081.8959 | 316613.7499 | 16073.9862 | 0.091823 | -124119.0603 | 124119.0603
C | Xist Rating 8585 | 13.36 | 2506.87 | 150.303 | 35.7 | 2018.9 | 8059.62 | 10538.3 | 0.4 | 1.25 | 23.254 | 14.499 | 1 | 1 | 2420 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5061119.843 | 354474.1651 | 5703.8078 | 35227.464 | 319246.7011 | 16066.1857 | 0.092204 | -124058.8274 | 124058.8274
C | Xist Rating 8586 | 13.47 | 2508.23 | 150.303 | 35.7 | 2020.34 | 8082.66 | 10538.2 | 0.39 | 1.25 | 23.255 | 14.51 | 1 | 1 | 2430 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5067477.3982 | 357263.5869 | 5751.0441 | 35373.032 | 321890.5549 | 16056.4919 | 0.092585 | -123983.9745 | 123983.9745
C | Xist Rating 8587 | 13.57 | 2509.6 | 150.302 | 35.7 | 2021.34 | 8098.8 | 10538.2 | 0.38 | 1.25 | 23.255 | 14.521 | 1 | 1 | 2440 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5072754.864 | 360063.9111 | 5798.4752 | 35518.6 | 324545.3111 | 16046.5463 | 0.092966 | -123907.1767 | 123907.1767
C | Xist Rating 8588 | 13.61 | 2510.93 | 150.302 | 35.7 | 2021.54 | 8101.9 | 10538.3 | 0.38 | 1.25 | 23.246 | 14.532 | 1 | 1 | 2450 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5075945.4322 | 362875.1379 | 5846.1011 | 35664.1681 | 327210.9698 | 16061.5553 | 0.093347 | -124023.0723 | 124023.0723
C | Xist Rating 8589 | 13.6 | 2512.4 | 150.302 | 35.7 | 2020.8 | 8090.13 | 10538.2 | 0.37 | 1.25 | 23.237 | 14.543 | 1 | 1 | 2460 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5077057.92 | 365697.2671 | 5893.9217 | 35809.7361 | 329887.531 | 16050.9381 | 0.093728 | -123941.0892 | 123941.0892
C | Xist Rating 8590 | 13.6 | 2513.75 | 150.303 | 35.7 | 2020.29 | 8081.94 | 10538.2 | 0.37 | 1.25 | 23.279 | 14.554 | 1 | 1 | 2470 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5078503.9875 | 368530.2988 | 5941.9372 | 35955.3041 | 332574.9947 | 16067.936 | 0.094109 | -124072.3426 | 124072.3426
C | Xist Rating 8591 | 13.61 | 2515.1 | 150.302 | 35.7 | 2019.75 | 8073.34 | 10538.2 | 0.36 | 1.25 | 23.273 | 14.564 | 1 | 1 | 2480 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5079873.225 | 371374.2331 | 5990.1474 | 36100.8722 | 335273.3609 | 16056.0636 | 0.09449 | -123980.6669 | 123980.6669
C | Xist Rating 8592 | 13.61 | 2516.5 | 150.302 | 35.7 | 2019.09 | 8062.85 | 10538.2 | 0.35 | 1.25 | 23.267 | 14.575 | 1 | 1 | 2490 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5081039.985 | 374229.0698 | 6038.5525 | 36246.4402 | 337982.6296 | 16045.0324 | 0.094871 | -123895.4873 | 123895.4873
C | Xist Rating 8593 | 13.63 | 2517.48 | 150.302 | 35.7 | 2019.31 | 8066.36 | 10538.2 | 0.35 | 1.25 | 23.264 | 14.584 | 1 | 1 | 2500 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5083572.5388 | 377094.8089 | 6087.1523 | 36392.0082 | 340702.8007 | 16057.9115 | 0.095252 | -123994.9363 | 123994.9363
C | Xist Rating 8594 | 13.63 | 2519.33 | 150.302 | 35.7 | 2018.39 | 8051.65 | 10538.2 | 0.34 | 1.25 | 23.253 | 14.596 | 1 | 1 | 2510 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5084990.4787 | 379971.4506 | 6135.9469 | 36537.5763 | 343433.8744 | 16047.4282 | 0.095633 | -123913.987 | 123913.987
C | Xist Rating 8595 | 13.64 | 2520.78 | 150.302 | 35.7 | 2017.9 | 8043.82 | 10538.1 | 0.34 | 1.25 | 23.288 | 14.607 | 1 | 1 | 2520 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5086681.962 | 382858.9948 | 6184.9363 | 36683.1443 | 346175.8505 | 16063.7397 | 0.096014 | -124039.9403 | 124039.9403
C | Xist Rating 8596 | 13.68 | 2522.12 | 150.302 | 35.7 | 2018.06 | 8046.39 | 10538.1 | 0.33 | 1.25 | 23.279 | 14.617 | 1 | 1 | 2530 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5089789.4872 | 385757.4415 | 6234.1205 | 36828.7123 | 348928.7291 | 16050.927 | 0.096395 | -123941.0038 | 123941.0038
C | Xist Rating 8597 | 13.62 | 2523.27 | 150.302 | 35.7 | 2016.98 | 8029.33 | 10538 | 0.33 | 1.25 | 23.277 | 14.627 | 1 | 1 | 2540 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5089385.1246 | 388666.7906 | 6283.4995 | 36974.2804 | 351692.5103 | 16064.6803 | 0.096776 | -124047.2032 | 124047.2032
C | Xist Rating 8598 | 13.64 | 2524.82 | 150.302 | 35.7 | 2015.98 | 8013.48 | 10538.1 | 0.32 | 1.25 | 23.277 | 14.638 | 1 | 1 | 2550 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5089986.6236 | 391587.0423 | 6333.0732 | 37119.8484 | 354467.1939 | 16052.9407 | 0.097157 | -123956.5529 | 123956.5529
C | Xist Rating 8599 | 13.69 | 2526.27 | 150.302 | 35.7 | 2016.29 | 8018.41 | 10538.1 | 0.32 | 1.25 | 23.267 | 14.649 | 1 | 1 | 2560 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5093692.9383 | 394518.1964 | 6382.8418 | 37265.4164 | 357252.78 | 16067.3358 | 0.097538 | -124067.7081 | 124067.7081
C | Xist Rating 8600 | 13.7 | 2527.66 | 150.302 | 35.7 | 2016.02 | 8014.2 | 10538.1 | 0.31 | 1.25 | 23.261 | 14.659 | 1 | 1 | 2570 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5095813.1132 | 397460.253 | 6432.8051 | 37410.9845 | 360049.2685 | 16054.0405 | 0.097919 | -123965.0451 | 123965.0451
C | Xist Rating 8601 | 13.72 | 2529.02 | 150.303 | 35.6 | 2016.1 | 8015.52 | 10538 | 0.31 | 1.25 | 23.313 | 14.669 | 1 | 1 | 2580 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5098757.222 | 400413.2121 | 6482.9633 | 37556.5525 | 362856.6596 | 16069.522 | 0.0983 | -124084.589 | 124084.589
C | Xist Rating 8602 | 13.7 | 2530.38 | 150.303 | 35.6 | 2015.22 | 8001.6 | 10538 | 0.3 | 1.25 | 23.313 | 14.679 | 1 | 1 | 2590 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5099272.3836 | 403377.0737 | 6533.3162 | 37702.1205 | 365674.9532 | 16056.081 | 0.098681 | -123980.8016 | 123980.8016
C | Xist Rating 8603 | 13.73 | 2531.56 | 150.303 | 35.6 | 2015.28 | 8002.55 | 10538 | 0.3 | 1.25 | 23.317 | 14.688 | 1 | 1 | 2600 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5101802.2368 | 406351.8378 | 6583.8639 | 37847.6886 | 368504.1492 | 16068.7023 | 0.099062 | -124078.2601 | 124078.2601
C | Xist Rating 8604 | 13.72 | 2533.25 | 150.303 | 35.6 | 2014.26 | 7986.39 | 10538 | 0.3 | 1.25 | 23.313 | 14.7 | 1 | 1 | 2610 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5102624.145 | 409337.5044 | 6634.6064 | 37993.2566 | 371344.2478 | 16084.1595 | 0.099443 | -124197.6159 | 124197.6159
C | Xist Rating 8605 | 13.73 | 2534.65 | 150.303 | 35.6 | 2013.9 | 7980.92 | 10537.9 | 0.29 | 1.25 | 23.313 | 14.71 | 1 | 1 | 2620 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5104531.635 | 412334.0735 | 6685.5437 | 38138.8246 | 374195.2488 | 16070.3005 | 0.099824 | -124090.6008 | 124090.6008
C | Xist Rating 8606 | 13.76 | 2536.07 | 150.303 | 35.6 | 2013.74 | 7978.35 | 10537.9 | 0.29 | 1.25 | 23.354 | 14.721 | 1 | 1 | 2630 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5106985.6018 | 415341.545 | 6736.6758 | 38284.3927 | 377057.1524 | 16086.1562 | 0.10021 | -124213.0341 | 124213.0341
C | Xist Rating 8607 | 13.79 | 2537.32 | 150.303 | 35.6 | 2013.75 | 7978.47 | 10537.9 | 0.28 | 1.25 | 23.355 | 14.73 | 1 | 1 | 2640 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5109528.15 | 418359.9191 | 6788.0027 | 38429.9607 | 379929.9584 | 16070.9352 | 0.10059 | -124095.5016 | 124095.5016
C | Xist Rating 8608 | 13.81 | 2538.82 | 150.303 | 35.6 | 2013.28 | 7971.18 | 10537.9 | 0.28 | 1.25 | 23.354 | 14.741 | 1 | 1 | 2650 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5111355.5296 | 421389.1956 | 6839.5243 | 38575.5287 | 382813.6669 | 16085.2567 | 0.10097 | -124206.0883 | 124206.0883
C | Xist Rating 8609 | 13.85 | 2540.16 | 150.303 | 35.6 | 2013.49 | 7974.41 | 10537.9 | 0.28 | 1.25 | 23.357 | 14.75 | 1 | 1 | 2660 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5114586.7584 | 424429.3746 | 6891.2408 | 38721.0968 | 385708.2779 | 16097.6345 | 0.10135 | -124301.6662 | 124301.6662
C | Xist Rating 8610 | 13.88 | 2541.55 | 150.303 | 35.6 | 2013.46 | 7973.89 | 10537.9 | 0.27 | 1.25 | 23.356 | 14.76 | 1 | 1 | 2670 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5117309.263 | 427480.4562 | 6943.152 | 38866.6648 | 388613.7914 | 16082.9646 | 0.10173 | -124188.3892 | 124188.3892
C | Xist Rating 8611 | 13.94 | 2542.97 | 150.303 | 35.6 | 2013.76 | 7978.57 | 10537.9 | 0.27 | 1.25 | 23.399 | 14.771 | 1 | 1 | 2680 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5120931.2672 | 430542.4402 | 6995.258 | 39012.2328 | 391530.2073 | 16098.6094 | 0.10211 | -124309.1948 | 124309.1948
C | Xist Rating 8612 | 13.99 | 2544.34 | 150.303 | 35.6 | 2014.08 | 7983.58 | 10538 | 0.26 | 1.25 | 23.4 | 14.78 | 1 | 1 | 2690 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5124504.3072 | 433615.3267 | 7047.5588 | 39157.8009 | 394457.5258 | 16082.6051 | 0.10249 | -124185.6133 | 124185.6133
C | Xist Rating 8613 | 14.05 | 2545.54 | 150.303 | 35.6 | 2014.74 | 7994.05 | 10537.9 | 0.26 | 1.25 | 23.4 | 14.789 | 1 | 1 | 2700 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5128601.2596 | 436699.1156 | 7100.0544 | 39303.3689 | 397395.7467 | 16094.6787 | 0.10287 | -124278.8425 | 124278.8425
C | Xist Rating 8614 | 14.16 | 2547.2 | 150.303 | 35.6 | 2016.24 | 8017.85 | 10537.8 | 0.26 | 1.25 | 23.402 | 14.801 | 1 | 1 | 2710 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5135766.528 | 439793.8071 | 7152.7448 | 39448.9369 | 400344.8702 | 16109.931 | 0.10325 | -124396.6166 | 124396.6166
C | Xist Rating 8615 | 14.14 | 2548.54 | 150.303 | 35.6 | 2015.35 | 8003.78 | 10537.8 | 0.25 | 1.25 | 23.398 | 14.81 | 1 | 1 | 2720 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5136200.089 | 442899.4011 | 7205.63 | 39594.505 | 403304.8961 | 16093.3505 | 0.10363 | -124268.5863 | 124268.5863
C | Xist Rating 8616 | 14.13 | 2549.86 | 150.303 | 35.6 | 2014.53 | 7990.77 | 10537.8 | 0.25 | 1.25 | 23.432 | 14.82 | 1 | 1 | 2730 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5136769.4658 | 446015.8975 | 7258.71 | 39740.073 | 406275.8245 | 16107.3976 | 0.10402 | -124377.0548 | 124377.0548
C | Xist Rating 8617 | 14.12 | 2551.15 | 150.303 | 35.6 | 2013.98 | 7982.16 | 10537.9 | 0.25 | 1.25 | 23.429 | 14.829 | 1 | 1 | 2740 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5137965.077 | 449143.2965 | 7311.9847 | 39885.641 | 409257.6555 | 16119.2778 | 0.1044 | -124468.7905 | 124468.7905
C | Xist Rating 8618 | 14.1 | 2552.7 | 150.303 | 35.6 | 2012.88 | 7964.9 | 10537.9 | 0.25 | 1.25 | 23.424 | 14.839 | 1 | 1 | 2750 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5138278.776 | 452281.5979 | 7365.4543 | 40031.2091 | 412250.3889 | 16132.1342 | 0.10478 | -124568.0642 | 124568.0642
C | Xist Rating 8619 | 14.09 | 2554.12 | 150.303 | 35.6 | 2012.02 | 7951.47 | 10537.9 | 0.24 | 1.25 | 23.421 | 14.849 | 1 | 1 | 2760 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5138940.5224 | 455430.8018 | 7419.1186 | 40176.7771 | 415254.0248 | 16116.0758 | 0.10516 | -124444.0654 | 124444.0654
C | Xist Rating 8620 | 14.09 | 2555.36 | 150.303 | 35.6 | 2011.58 | 7944.59 | 10537.9 | 0.24 | 1.25 | 23.425 | 14.858 | 1 | 1 | 2770 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5140311.0688 | 458590.9083 | 7472.9777 | 40322.3451 | 418268.5631 | 16128.0611 | 0.10554 | -124536.6127 | 124536.6127
C | Xist Rating 8621 | 14.05 | 2556.9 | 150.303 | 35.6 | 2010.25 | 7923.82 | 10537.8 | 0.24 | 1.25 | 23.459 | 14.868 | 1 | 1 | 2780 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5140008.225 | 461761.9172 | 7527.0316 | 40467.9132 | 421294.004 | 16141.983 | 0.10592 | -124644.1136 | 124644.1136
C | Xist Rating 8622 | 14.05 | 2558.31 | 150.303 | 35.6 | 2009.62 | 7914.08 | 10537.9 | 0.23 | 1.25 | 23.461 | 14.878 | 1 | 1 | 2790 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5141230.9422 | 464943.8286 | 7581.2803 | 40613.4812 | 424330.3474 | 16125.6112 | 0.1063 | -124517.695 | 124517.695
C | Xist Rating 8623 | 14.09 | 2559.29 | 150.303 | 35.6 | 2010.02 | 7920.32 | 10537.9 | 0.23 | 1.25 | 23.469 | 14.885 | 1 | 1 | 2800 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5144224.0858 | 468136.6424 | 7635.7238 | 40759.0492 | 427377.5932 | 16135.5303 | 0.10668 | -124594.2882 | 124594.2882
C | Xist Rating 8624 | 14.05 | 2561.03 | 150.303 | 35.6 | 2008.86 | 7902.36 | 10537.7 | 0.23 | 1.25 | 23.435 | 14.896 | 1 | 1 | 2810 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5144750.7258 | 471340.3588 | 7690.3621 | 40904.6173 | 430435.7416 | 16148.3884 | 0.10706 | -124693.5749 | 124693.5749
C | Xist Rating 8625 | 14.08 | 2562.51 | 150.303 | 35.6 | 2008.67 | 7899.42 | 10537.8 | 0.23 | 1.25 | 23.443 | 14.906 | 1 | 1 | 2820 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5147236.9617 | 474554.9777 | 7745.1952 | 41050.1853 | 433504.7924 | 16161.4221 | 0.10744 | -124794.2172 | 124794.2172
C | Xist Rating 8626 | 14.1 | 2563.88 | 150.303 | 35.6 | 2008.56 | 7897.7 | 10537.8 | 0.22 | 1.25 | 23.489 | 14.916 | 1 | 1 | 2830 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5149706.8128 | 477780.499 | 7800.223 | 41195.7533 | 436584.7457 | 16145.7694 | 0.10783 | -124673.3513 | 124673.3513
C | Xist Rating 8627 | 14.07 | 2565.2 | 150.303 | 35.6 | 2007.44 | 7880.44 | 10537.7 | 0.22 | 1.25 | 23.479 | 14.924 | 1 | 1 | 2840 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5149485.088 | 481016.9229 | 7855.4457 | 41341.3214 | 439675.6015 | 16156.1136 | 0.10821 | -124753.227 | 124753.227
C | Xist Rating 8628 | 14.11 | 2566.64 | 150.303 | 35.6 | 2007.5 | 7881.35 | 10537.8 | 0.22 | 1.25 | 23.489 | 14.934 | 1 | 1 | 2850 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5152529.8 | 484264.2492 | 7910.8631 | 41486.8894 | 442777.3598 | 16169.095 | 0.10859 | -124853.4659 | 124853.4659
C | Xist Rating 8629 | 14.18 | 2568.05 | 150.303 | 35.6 | 2008.16 | 7891.52 | 10537.8 | 0.22 | 1.25 | 23.504 | 14.944 | 1 | 1 | 2860 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5157055.288 | 487522.478 | 7966.4753 | 41632.4574 | 445890.0206 | 16182.2194 | 0.10897 | -124954.809 | 124954.809
C | Xist Rating 8630 | 14.17 | 2569.24 | 150.303 | 35.6 | 2007.7 | 7884.38 | 10537.8 | 0.21 | 1.25 | 23.503 | 14.952 | 1 | 1 | 2870 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5158263.148 | 490791.6093 | 8022.2824 | 41778.0255 | 449013.5839 | 16162.5811 | 0.10935 | -124803.167 | 124803.167
C | Xist Rating 8631 | 14.28 | 2570.74 | 150.304 | 35.6 | 2008.83 | 7901.83 | 10537.9 | 0.21 | 1.25 | 23.565 | 14.962 | 1 | 1 | 2880 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5164179.6342 | 494071.6431 | 8078.2842 | 41923.5935 | 452148.0496 | 16176.8593 | 0.10973 | -124913.4193 | 124913.4193
C | Xist Rating 8632 | 14.43 | 2572.09 | 150.304 | 35.6 | 2011.05 | 7936.3 | 10537.9 | 0.21 | 1.25 | 23.594 | 14.972 | 1 | 1 | 2890 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5172601.5945 | 497362.5794 | 8134.4807 | 42069.1615 | 455293.4179 | 16190.2514 | 0.11011 | -125016.8297 | 125016.8297
C | Xist Rating 8633 | 14.62 | 2573.47 | 150.304 | 35.6 | 2013.77 | 7978.71 | 10538 | 0.21 | 1.25 | 23.634 | 14.981 | 1 | 1 | 2900 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5182376.6819 | 500664.4182 | 8190.8721 | 42214.7296 | 458449.6886 | 16202.9108 | 0.11049 | -125114.5819 | 125114.5819
C | Xist Rating 8634 | 14.59 | 2575.01 | 150.304 | 35.6 | 2012.64 | 7961.03 | 10538 | 0.2 | 1.25 | 23.628 | 14.991 | 1 | 1 | 2910 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5182568.1264 | 503977.1595 | 8247.4583 | 42360.2976 | 461616.8619 | 16184.5358 | 0.11087 | -124972.6953 | 124972.6953
C | Xist Rating 8635 | 15.19 | 2576.4 | 150.304 | 35.6 | 2022.82 | 8122.54 | 10538.2 | 0.2 | 1.25 | 23.707 | 15.001 | 1 | 1 | 2920 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5211593.448 | 507300.8032 | 8304.2393 | 42505.8656 | 464794.9376 | 16199.107 | 0.11125 | -125085.2107 | 125085.2107
C | Xist Rating 8636 | 15.91 | 2577.79 | 150.304 | 35.6 | 2035.05 | 8323.41 | 10538.3 | 0.2 | 1.25 | 23.831 | 15.011 | 1 | 1 | 2930 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5245931.5395 | 510635.3495 | 8361.215 | 42651.4337 | 467983.9158 | 16214.8745 | 0.11164 | -125206.9626 | 125206.9626
C | Xist Rating 8637 | 15.85 | 2579.16 | 150.304 | 35.6 | 2033.43 | 8296.38 | 10538.3 | 0.19 | 1.25 | 23.814 | 15.02 | 1 | 1 | 2940 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5244541.3188 | 513980.7982 | 8418.3855 | 42797.0017 | 471183.7965 | 16194.5262 | 0.11202 | -125049.8384 | 125049.8384
C | Xist Rating 8638 | 16.17 | 2580.57 | 150.304 | 35.6 | 2038.39 | 8379.48 | 10538.3 | 0.19 | 1.25 | 23.839 | 15.03 | 1 | 1 | 2950 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5260208.0823 | 517337.1494 | 8475.7509 | 42942.5697 | 474394.5797 | 16207.5674 | 0.1124 | -125150.5395 | 125150.5395
C | Xist Rating 8639 | 16.95 | 2581.94 | 150.304 | 35.6 | 2051.67 | 8608.66 | 10538.4 | 0.19 | 1.25 | 23.933 | 15.04 | 1 | 1 | 2960 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5297288.8398 | 520704.4031 | 8533.311 | 43088.1378 | 477616.2654 | 16222.3524 | 0.11278 | -125264.7051 | 125264.7051
C | Xist Rating 8640 | 17.82 | 2583.32 | 150.304 | 35.6 | 2066.62 | 8878.18 | 10538.2 | 0.18 | 1.25 | 24.007 | 15.051 | 1 | 1 | 2970 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5338740.7784 | 524082.5594 | 8591.0659 | 43233.7058 | 480848.8536 | 16205.7256 | 0.11316 | -125136.3177 | 125136.3177
C | Xist Rating 8641 | 17.81 | 2584.54 | 150.304 | 35.6 | 2065.98 | 8866.39 | 10538.2 | 0.18 | 1.25 | 24.041 | 15.059 | 1 | 1 | 2980 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5339607.9492 | 527471.618 | 8649.0156 | 43379.2738 | 484092.3442 | 16216.7881 | 0.11354 | -125221.7392 | 125221.7392
C | Xist Rating 8642 | 17.8 | 2586.1 | 150.304 | 35.6 | 2065.2 | 8852.06 | 10538.2 | 0.18 | 1.25 | 24.036 | 15.069 | 1 | 1 | 2990 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5340813.72 | 530871.5792 | 8707.16 | 43524.8419 | 487346.7374 | 16228.9922 | 0.11392 | -125315.9759 | 125315.9759
C | Xist Rating 8643 | 17.8 | 2587.53 | 150.304 | 35.6 | 2064.5 | 8839.14 | 10538.2 | 0.18 | 1.25 | 24.03 | 15.078 | 1 | 1 | 3000 | 152.4 | 2 | 5.2 | 19.05 | 1.3333 | 31 | E | Rod | 5341955.685 | 534282.4429 | 8765.4993 | 43670.4099 | 490612.033 | 16240.1328 | 0.1143 | -125402.0006 | 125402.0006
C | Xist Rating 8644 | -85.35 | 268.263 | 150.31 | 35.9 | 2343.1 | 6891.18 | 58745 | 2.49 | 10.95 | 26.268 | 627.077 | 1 | 1 | 1000 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 628567.0353 | 70397.5062 | 973.9444 | 14836.7418 | 55560.7644 | 654150.3333 | 0.038101 | -5051175.4773 | 5051175.4773
C | Xist Rating 8645 | -85.22 | 271.024 | 150.31 | 35.9 | 2339.8 | 6869.97 | 58283.5 | 2.47 | 10.84 | 26.361 | 615.266 | 1 | 1 | 1010 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 634141.9552 | 71662.645 | 993.5206 | 14985.1092 | 56677.5358 | 641900.5621 | 0.038482 | -4956585.9915 | 4956585.9915
C | Xist Rating 8646 | -84.13 | 292.043 | 150.31 | 35.9 | 2332.63 | 6864.24 | 54967 | 2.48 | 10.07 | 26.412 | 533.196 | 1 | 1 | 1020 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 681228.2631 | 72938.896 | 1013.2917 | 15133.4767 | 57805.4193 | 556718.0183 | 0.038863 | -4298828.9677 | 4298828.9677
C | Xist Rating 8647 | -83.94 | 297.71 | 150.309 | 35.9 | 2316.66 | 6741.52 | 54178.5 | 2.39 | 9.89 | 25.767 | 515.203 | 1 | 1 | 1030 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 689692.8486 | 74226.2591 | 1033.2576 | 15281.8441 | 58944.415 | 537880.7564 | 0.039244 | -4153372.6247 | 4153372.6247
C | Xist Rating 8648 | -83.83 | 300.545 | 150.308 | 35.9 | 2311.14 | 6701.83 | 53793.7 | 2.35 | 9.8 | 25.621 | 506.583 | 1 | 1 | 1040 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 694601.5713 | 75524.7343 | 1053.4182 | 15430.2115 | 60094.5228 | 528892.4621 | 0.039625 | -4083967.3985 | 4083967.3985
C | Xist Rating 8649 | -83.58 | 306.091 | 150.308 | 35.9 | 2304.59 | 6660.44 | 53042.8 | 2.32 | 9.63 | 25.522 | 489.732 | 1 | 1 | 1050 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 705414.2577 | 76834.3217 | 1073.7737 | 15578.5789 | 61255.7428 | 511372.7275 | 0.040006 | -3948684.6521 | 3948684.6521
C | Xist Rating 8650 | -83.46 | 308.906 | 150.308 | 35.9 | 2301.22 | 6639.03 | 52676 | 2.28 | 9.54 | 25.477 | 481.723 | 1 | 1 | 1060 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 710860.6653 | 78155.0212 | 1094.3239 | 15726.9463 | 62428.0749 | 503028.5537 | 0.040387 | -3884253.1533 | 3884253.1533
C | Xist Rating 8651 | -82.37 | 331.46 | 150.307 | 35.9 | 2286.24 | 6568.68 | 49856.6 | 2.26 | 8.9 | 25.217 | 421.448 | 1 | 1 | 1070 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 757797.1104 | 79486.8329 | 1115.0689 | 15875.3137 | 63611.5192 | 440406.4776 | 0.040768 | -3400702.0809 | 3400702.0809
C | Xist Rating 8652 | -82.14 | 335.687 | 150.307 | 35.9 | 2287.69 | 6590.39 | 49379.9 | 2.21 | 8.79 | 25.082 | 411.944 | 1 | 1 | 1080 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 767947.793 | 80829.7568 | 1136.0087 | 16023.6812 | 64806.0756 | 430486.6525 | 0.041149 | -3324103.8213 | 3324103.8213
C | Xist Rating 8653 | -81.81 | 341.313 | 150.307 | 35.9 | 2292.15 | 6640.5 | 48760.5 | 2.15 | 8.65 | 24.891 | 399.748 | 1 | 1 | 1090 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 782340.5929 | 82183.7928 | 1157.1433 | 16172.0486 | 66011.7442 | 417752.3801 | 0.04153 | -3225773.1449 | 3225773.1449
C | Xist Rating 8654 | -81.52 | 345.508 | 150.307 | 35.9 | 2300.98 | 6725.22 | 48306.7 | 2.11 | 8.55 | 24.895 | 390.942 | 1 | 1 | 1100 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 795006.9978 | 83548.941 | 1178.4727 | 16320.416 | 67228.525 | 408582.6752 | 0.041911 | -3154967.1146 | 3154967.1146
C | Xist Rating 8655 | -81.36 | 348.511 | 150.306 | 35.9 | 2302.47 | 6744.66 | 48009.4 | 2.03 | 8.48 | 24.502 | 385.5 | 1 | 1 | 1110 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 802436.1222 | 84925.2013 | 1199.9969 | 16468.7834 | 68456.4178 | 402815.9254 | 0.042292 | -3110437.8012 | 3110437.8012
C | Xist Rating 8656 | -80.07 | 373.651 | 150.306 | 35.9 | 2296.21 | 6752.19 | 45447.6 | 2.07 | 7.92 | 24.844 | 337.315 | 1 | 1 | 1120 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 857981.1627 | 86312.5737 | 1221.7158 | 16617.1508 | 69695.4229 | 352882.9191 | 0.042673 | -2724868.3626 | 2724868.3626
C | Xist Rating 8657 | -79.89 | 376.608 | 150.306 | 35.9 | 2299.02 | 6783.27 | 45188.5 | 2.01 | 7.86 | 24.597 | 332.933 | 1 | 1 | 1130 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 865829.3242 | 87711.0583 | 1243.6296 | 16765.5183 | 70945.5401 | 348254.6203 | 0.043054 | -2689129.8656 | 2689129.8656
C | Xist Rating 8658 | -79.61 | 382.305 | 150.305 | 35.9 | 2297.5 | 6783.29 | 44681 | 1.95 | 7.75 | 24.211 | 324.182 | 1 | 1 | 1140 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 878345.7375 | 89120.6551 | 1265.7381 | 16913.8857 | 72206.7694 | 339075.0043 | 0.043435 | -2618247.3043 | 2618247.3043
C | Xist Rating 8659 | -79.31 | 387.938 | 150.305 | 35.9 | 2298.64 | 6806.63 | 44185.8 | 1.91 | 7.64 | 24.126 | 315.73 | 1 | 1 | 1150 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 891729.8043 | 90541.364 | 1288.0414 | 17062.2531 | 73479.111 | 330260.4877 | 0.043816 | -2550183.9434 | 2550183.9434
C | Xist Rating 8660 | -79.02 | 393.65 | 150.304 | 35.8 | 2297.58 | 6810.6 | 43703.2 | 1.85 | 7.53 | 23.926 | 307.68 | 1 | 1 | 1160 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 904442.367 | 91973.1851 | 1310.5395 | 17210.6205 | 74762.5646 | 321826.724 | 0.044197 | -2485060.6556 | 2485060.6556
C | Xist Rating 8661 | -77.88 | 416.19 | 150.305 | 35.9 | 2291.43 | 6811 | 41832 | 1.88 | 7.13 | 24.098 | 276.737 | 1 | 1 | 1170 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 953670.2517 | 93416.1183 | 1333.2324 | 17358.9879 | 76057.1304 | 289766.9106 | 0.044578 | -2237503.2749 | 2237503.2749
C | Xist Rating 8662 | -77.75 | 417.762 | 150.304 | 35.8 | 2297.62 | 6869.32 | 41724.5 | 1.83 | 7.11 | 23.989 | 275.206 | 1 | 1 | 1180 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 959858.3264 | 94870.1637 | 1356.1201 | 17507.3553 | 77362.8084 | 288122.9955 | 0.044959 | -2224809.3984 | 2224809.3984
C | Xist Rating 8663 | -77.21 | 429.014 | 150.304 | 35.8 | 2291.86 | 6844.52 | 40885.6 | 1.78 | 6.92 | 23.776 | 262.242 | 1 | 1 | 1190 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 983240.026 | 96335.3213 | 1379.2026 | 17655.7228 | 78679.5985 | 274595.3759 | 0.04534 | -2120352.7054 | 2120352.7054
C | Xist Rating 8664 | -76.95 | 431.863 | 150.304 | 35.8 | 2304.01 | 6960.86 | 40681.7 | 1.75 | 6.88 | 23.829 | 259.206 | 1 | 1 | 1200 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 995016.6706 | 97811.591 | 1402.4799 | 17804.0902 | 80007.5008 | 271428.087 | 0.045721 | -2095895.7402 | 2095895.7402
C | Xist Rating 8665 | -76.66 | 437.644 | 150.304 | 35.8 | 2302.81 | 6963.56 | 40280.7 | 1.69 | 6.8 | 23.642 | 253.3 | 1 | 1 | 1210 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1007810.9796 | 99298.9728 | 1425.9519 | 17952.4576 | 81346.5152 | 265218.7208 | 0.046102 | -2047948.6601 | 2047948.6601
C | Xist Rating 8666 | -75.43 | 463.138 | 150.304 | 35.8 | 2291.52 | 6922.74 | 38537.5 | 1.69 | 6.43 | 23.646 | 227.733 | 1 | 1 | 1220 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1061289.9898 | 100797.4668 | 1449.6188 | 18100.825 | 82696.6418 | 238685.7111 | 0.046483 | -1843067.7922 | 1843067.7922
C | Xist Rating 8667 | -75.07 | 468.769 | 150.304 | 35.8 | 2297.27 | 6988.98 | 38183.2 | 1.66 | 6.35 | 23.672 | 222.824 | 1 | 1 | 1230 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1076888.9606 | 102307.0729 | 1473.4804 | 18249.1924 | 84057.8805 | 233568.9035 | 0.046864 | -1803557.1601 | 1803557.1601
C | Xist Rating 8668 | -74.77 | 474.54 | 150.303 | 35.8 | 2297.58 | 7005.4 | 37835.7 | 1.62 | 6.28 | 23.55 | 218.14 | 1 | 1 | 1240 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1090293.6132 | 103827.7912 | 1497.5369 | 18397.5599 | 85430.2314 | 228658.5756 | 0.047245 | -1765640.9099 | 1765640.9099
C | Xist Rating 8669 | -74.58 | 477.534 | 150.303 | 35.8 | 2302.02 | 7053.66 | 37664.2 | 1.58 | 6.24 | 23.461 | 215.922 | 1 | 1 | 1250 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1099292.8187 | 105359.6217 | 1521.7881 | 18545.9273 | 86813.6944 | 226311.6271 | 0.047626 | -1747518.3955 | 1747518.3955
C | Xist Rating 8670 | -74.14 | 486.004 | 150.303 | 35.8 | 2302.12 | 7075.3 | 37161.2 | 1.55 | 6.14 | 23.409 | 209.181 | 1 | 1 | 1260 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1118839.5285 | 106902.5643 | 1546.2341 | 18694.2947 | 88208.2696 | 219283.4211 | 0.048007 | -1693248.4523 | 1693248.4523
C | Xist Rating 8671 | -72.94 | 510.142 | 150.303 | 35.8 | 2295.03 | 7068 | 35777.4 | 1.56 | 5.85 | 23.481 | 190.996 | 1 | 1 | 1270 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1170791.1943 | 108456.6191 | 1570.8749 | 18842.6621 | 89613.9569 | 200434.3117 | 0.048388 | -1547700.6258 | 1547700.6258
C | Xist Rating 8672 | -72.65 | 515.982 | 150.303 | 35.8 | 2294.59 | 7077.49 | 35477.1 | 1.51 | 5.79 | 23.343 | 187.333 | 1 | 1 | 1280 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1183967.1374 | 110021.786 | 1595.7105 | 18991.0295 | 91030.7564 | 196567.3938 | 0.048769 | -1517841.3103 | 1517841.3103
C | Xist Rating 8673 | -72.35 | 521.77 | 150.303 | 35.8 | 2294.55 | 7090.73 | 35182.4 | 1.48 | 5.73 | 23.282 | 183.758 | 1 | 1 | 1290 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1197227.3535 | 111598.065 | 1620.7408 | 19139.3969 | 92458.6681 | 192824.8479 | 0.04915 | -1488942.3633 | 1488942.3633
C | Xist Rating 8674 | -71.9 | 530.218 | 150.303 | 35.8 | 2295.95 | 7124.63 | 34750.8 | 1.46 | 5.64 | 23.324 | 178.495 | 1 | 1 | 1300 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1217354.0171 | 113185.4562 | 1645.966 | 19287.7644 | 93897.6919 | 187351.1156 | 0.049531 | -1446675.6531 | 1446675.6531
C | Xist Rating 8675 | -71.65 | 534.638 | 150.302 | 35.8 | 2297.89 | 7153.72 | 34539.4 | 1.42 | 5.59 | 23.275 | 176.034 | 1 | 1 | 1310 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1228539.3138 | 114783.9596 | 1671.3859 | 19436.1318 | 95347.8278 | 184751.7657 | 0.049912 | -1426604.1622 | 1426604.1622
C | Xist Rating 8676 | -70.45 | 558.874 | 150.303 | 35.8 | 2291.69 | 7153.57 | 33362.4 | 1.43 | 5.35 | 23.329 | 162.073 | 1 | 1 | 1320 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1280765.9571 | 116393.5751 | 1697.0007 | 19584.4992 | 96809.0759 | 170286.4445 | 0.050293 | -1314906.7864 | 1314906.7864
C | Xist Rating 8677 | -70.02 | 567.54 | 150.302 | 35.8 | 2289.99 | 7157.51 | 32979.3 | 1.39 | 5.28 | 23.205 | 157.804 | 1 | 1 | 1330 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1299660.9246 | 118014.3028 | 1722.8102 | 19732.8666 | 98281.4362 | 165802.1409 | 0.050674 | -1280280.1827 | 1280280.1827
C | Xist Rating 8678 | -69.55 | 576.104 | 150.302 | 35.8 | 2292.16 | 7199.41 | 32606.1 | 1.36 | 5.2 | 23.096 | 153.681 | 1 | 1 | 1340 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1320522.5446 | 119646.1426 | 1748.8145 | 19881.234 | 99764.9086 | 161484.1518 | 0.051055 | -1246937.8153 | 1246937.8153
C | Xist Rating 8679 | -69.25 | 580.541 | 150.302 | 35.8 | 2298.37 | 7271.46 | 32423.4 | 1.33 | 5.16 | 23.055 | 151.74 | 1 | 1 | 1350 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1334298.0182 | 121289.0946 | 1775.0136 | 20029.6015 | 101259.4932 | 159437.2778 | 0.051436 | -1231132.3969 | 1231132.3969
C | Xist Rating 8680 | -68.9 | 583.336 | 150.302 | 35.8 | 2314.03 | 7437.87 | 32302.9 | 1.32 | 5.14 | 23.161 | 150.435 | 1 | 1 | 1360 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1349857.0041 | 122943.1588 | 1801.4075 | 20177.9689 | 102765.1899 | 158090.2571 | 0.051817 | -1220731.0599 | 1220731.0599
C | Xist Rating 8681 | -67.43 | 617.64 | 150.302 | 35.8 | 2289.68 | 7276.52 | 30901.9 | 1.31 | 4.86 | 23.055 | 135.485 | 1 | 1 | 1370 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1414197.9552 | 124608.335 | 1827.9962 | 20326.3363 | 104281.9987 | 142555.6592 | 0.052198 | -1100777.0134 | 1100777.0134
C | Xist Rating 8682 | -67.3 | 620.697 | 150.302 | 35.8 | 2287.93 | 7265.86 | 30793.6 | 1.28 | 4.84 | 23.002 | 134.448 | 1 | 1 | 1380 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1420111.2872 | 126284.6235 | 1854.7797 | 20474.7037 | 105809.9198 | 141445.2938 | 0.052579 | -1092203.0657 | 1092203.0657
C | Xist Rating 8683 | -66.89 | 627.952 | 150.302 | 35.8 | 2291.05 | 7314.76 | 30526.7 | 1.25 | 4.78 | 22.964 | 131.795 | 1 | 1 | 1390 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1438669.4296 | 127972.0241 | 1881.7579 | 20623.0711 | 107348.9529 | 138657.4004 | 0.05296 | -1070675.692 | 1070675.692
C | Xist Rating 8684 | -66.49 | 635.203 | 150.302 | 35.8 | 2292.74 | 7349.66 | 30264.7 | 1.23 | 4.73 | 22.928 | 129.221 | 1 | 1 | 1400 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1456355.3262 | 129670.5368 | 1908.931 | 20771.4385 | 108899.0983 | 135965.5717 | 0.053341 | -1049890.1045 | 1049890.1045
C | Xist Rating 8685 | -66.07 | 643.828 | 150.301 | 35.8 | 2291.64 | 7359.44 | 29956.7 | 1.21 | 4.67 | 22.882 | 126.215 | 1 | 1 | 1410 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1475421.9979 | 131380.1617 | 1936.2988 | 20919.806 | 110460.3558 | 132823.9866 | 0.053722 | -1025631.6165 | 1025631.6165
C | Xist Rating 8686 | -64.8 | 669.565 | 150.302 | 35.8 | 2286.4 | 7370.16 | 29051.3 | 1.22 | 4.49 | 22.961 | 117.404 | 1 | 1 | 1420 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1530893.416 | 133100.8988 | 1963.8614 | 21068.1734 | 112032.7254 | 123706.887 | 0.054103 | -955231.7904 | 955231.7904
C | Xist Rating 8687 | -64.55 | 674.242 | 150.302 | 35.8 | 2287.55 | 7392.59 | 28910.3 | 1.18 | 4.47 | 22.875 | 116.177 | 1 | 1 | 1430 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1542362.2871 | 134832.748 | 1991.6188 | 21216.5408 | 113616.2072 | 122379.8298 | 0.054484 | -944984.6064 | 944984.6064
C | Xist Rating 8688 | -63.97 | 685.663 | 150.302 | 35.8 | 2287.04 | 7415.4 | 28541.6 | 1.16 | 4.39 | 22.858 | 112.785 | 1 | 1 | 1440 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1568138.7075 | 136575.7093 | 2019.571 | 21364.9082 | 115210.8011 | 118838.5391 | 0.054865 | -917639.6984 | 917639.6984
C | Xist Rating 8689 | -63.59 | 692.952 | 150.301 | 35.7 | 2287.63 | 7439.4 | 28316.2 | 1.14 | 4.35 | 22.817 | 110.777 | 1 | 1 | 1450 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1585217.7838 | 138329.7828 | 2047.718 | 21513.2756 | 116816.5072 | 116732.3683 | 0.055246 | -901376.4057 | 901376.4057
C | Xist Rating 8690 | -63.24 | 697.271 | 150.302 | 35.7 | 2296.01 | 7539.6 | 28183.4 | 1.12 | 4.32 | 22.871 | 109.6 | 1 | 1 | 1460 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1600941.1887 | 140094.9685 | 2076.0598 | 21661.6431 | 118433.3254 | 115495.8085 | 0.055627 | -891828.0188 | 891828.0188
C | Xist Rating 8691 | -61.96 | 726.231 | 150.301 | 35.7 | 2281.61 | 7458.38 | 27310 | 1.11 | 4.16 | 22.83 | 101.861 | 1 | 1 | 1470 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1656975.9119 | 141871.2663 | 2104.5964 | 21810.0105 | 120061.2558 | 107452.2824 | 0.056008 | -829718.0419 | 829718.0419
C | Xist Rating 8692 | -61.51 | 734.9 | 150.301 | 35.7 | 2282.28 | 7486.78 | 27065.8 | 1.1 | 4.11 | 22.815 | 99.801 | 1 | 1 | 1480 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1677247.572 | 143658.6763 | 2133.3277 | 21958.3779 | 121700.2984 | 105308.0946 | 0.056389 | -813161.1925 | 813161.1925
C | Xist Rating 8693 | -61.12 | 742.191 | 150.301 | 35.7 | 2283.51 | 7517.87 | 26866 | 1.08 | 4.07 | 22.8 | 98.147 | 1 | 1 | 1490 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1694800.5704 | 145457.1984 | 2162.2539 | 22106.7453 | 123350.4531 | 103570.11 | 0.05677 | -799740.9358 | 799740.9358
C | Xist Rating 8694 | -60.75 | 749.575 | 150.301 | 35.7 | 2283.07 | 7531 | 26669.5 | 1.06 | 4.03 | 22.759 | 96.549 | 1 | 1 | 1500 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1711332.1953 | 147266.8327 | 2191.3748 | 22255.1127 | 125011.72 | 101888.0449 | 0.057151 | -786752.4755 | 786752.4755
C | Xist Rating 8695 | -60.29 | 758.27 | 150.301 | 35.7 | 2284.06 | 7563.32 | 26438 | 1.04 | 3.99 | 22.751 | 94.661 | 1 | 1 | 1510 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1731934.1762 | 149087.5791 | 2220.6906 | 22403.4801 | 126684.099 | 99906.8016 | 0.057532 | -771453.8393 | 771453.8393
C | Xist Rating 8696 | -58.93 | 786.914 | 150.301 | 35.7 | 2278 | 7570.23 | 25679.6 | 1.05 | 3.84 | 22.806 | 88.464 | 1 | 1 | 1520 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1792590.092 | 150919.4377 | 2250.2011 | 22551.8476 | 128367.5901 | 93501.2686 | 0.057913 | -721992.0116 | 721992.0116
C | Xist Rating 8697 | -58.54 | 795.954 | 150.301 | 35.7 | 2274.3 | 7550.76 | 25467.1 | 1.02 | 3.8 | 22.681 | 86.86 | 1 | 1 | 1530 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1810238.1822 | 152762.4084 | 2279.9064 | 22700.215 | 130062.1934 | 91790.5846 | 0.058294 | -708782.5631 | 708782.5631
C | Xist Rating 8698 | -58.19 | 800.547 | 150.301 | 35.7 | 2281.23 | 7638.51 | 25362.2 | 1 | 3.78 | 22.676 | 86.095 | 1 | 1 | 1540 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1826231.8328 | 154616.4913 | 2309.8065 | 22848.5824 | 131767.9089 | 90974.8448 | 0.058675 | -702483.6366 | 702483.6366
C | Xist Rating 8699 | -57.45 | 814.889 | 150.301 | 35.7 | 2281.29 | 7675.64 | 25019.8 | 0.99 | 3.72 | 22.673 | 83.472 | 1 | 1 | 1550 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1858998.1268 | 156481.6863 | 2339.9013 | 22996.9498 | 133484.7365 | 88245.0666 | 0.059056 | -681405.0133 | 681405.0133
C | Xist Rating 8700 | -57.05 | 819.257 | 150.301 | 35.7 | 2291.6 | 7804.89 | 24919.2 | 0.97 | 3.7 | 22.724 | 82.73 | 1 | 1 | 1560 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1877409.3412 | 158357.9935 | 2370.191 | 23145.3172 | 135212.6763 | 87456.3127 | 0.059437 | -675314.4644 | 675314.4644
C | Xist Rating 8701 | -55.65 | 852.718 | 150.301 | 35.7 | 2273.69 | 7685.59 | 24160.9 | 0.96 | 3.56 | 22.679 | 77.081 | 1 | 1 | 1570 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1938816.3894 | 160245.4129 | 2400.6755 | 23293.6847 | 136951.7282 | 81580.6833 | 0.059818 | -629944.4122 | 629944.4122
C | Xist Rating 8702 | -55.21 | 860.13 | 150.301 | 35.7 | 2277.1 | 7743.09 | 24006.3 | 0.95 | 3.53 | 22.672 | 76 | 1 | 1 | 1580 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1958602.023 | 162143.9444 | 2431.3547 | 23442.0521 | 138701.8923 | 80451.2928 | 0.0602 | -621223.5577 | 621223.5577
C | Xist Rating 8703 | -54.79 | 867.577 | 150.301 | 35.7 | 2279.9 | 7794.09 | 23853.9 | 0.93 | 3.5 | 22.661 | 74.946 | 1 | 1 | 1590 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 1977988.8023 | 164053.588 | 2462.2288 | 23590.4195 | 140463.1685 | 79333.3237 | 0.060581 | -612590.8964 | 612590.8964
C | Xist Rating 8704 | -54.18 | 877.677 | 150.301 | 35.7 | 2283.7 | 7864.96 | 23644.6 | 0.92 | 3.46 | 22.689 | 73.477 | 1 | 1 | 1600 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2004350.9649 | 165974.3438 | 2493.2976 | 23738.7869 | 142235.5569 | 77802.8113 | 0.060962 | -600772.6857 | 600772.6857
C | Xist Rating 8705 | -53.88 | 882.466 | 150.301 | 35.7 | 2287.06 | 7916.39 | 23556 | 0.9 | 3.45 | 22.659 | 72.911 | 1 | 1 | 1610 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2018252.69 | 167906.2118 | 2524.5612 | 23887.1543 | 144019.0575 | 77189.6811 | 0.061343 | -596038.2565 | 596038.2565
C | Xist Rating 8706 | -52.23 | 919.959 | 150.301 | 35.7 | 2272.68 | 7844.56 | 22804.4 | 0.9 | 3.31 | 22.691 | 67.71 | 1 | 1 | 1620 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2090772.4201 | 169849.1919 | 2556.0196 | 24035.5217 | 145813.6702 | 71799.6833 | 0.061724 | -554418.1222 | 554418.1222
C | Xist Rating 8707 | -51.82 | 924.402 | 150.301 | 35.7 | 2282.24 | 7971.13 | 22722.7 | 0.89 | 3.29 | 22.724 | 67.189 | 1 | 1 | 1630 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2109707.2205 | 171803.2842 | 2587.6728 | 24183.8892 | 147619.395 | 71253.3465 | 0.062105 | -550199.4548 | 550199.4548
C | Xist Rating 8708 | -51.42 | 931.997 | 150.301 | 35.7 | 2283.2 | 8002.15 | 22588 | 0.87 | 3.27 | 22.697 | 66.337 | 1 | 1 | 1640 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2127935.5504 | 173768.4886 | 2619.5208 | 24332.2566 | 149436.232 | 70342.4746 | 0.062486 | -543165.9435 | 543165.9435
C | Xist Rating 8709 | -50.91 | 942.454 | 150.301 | 35.7 | 2281.81 | 8012.14 | 22402.4 | 0.85 | 3.23 | 22.666 | 65.156 | 1 | 1 | 1650 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2150500.9617 | 175744.8051 | 2651.5635 | 24480.624 | 151264.1811 | 69089.3367 | 0.062867 | -533489.5444 | 533489.5444
C | Xist Rating 8710 | -50.34 | 952.668 | 150.301 | 35.7 | 2284.38 | 8071.22 | 22220.2 | 0.84 | 3.2 | 22.674 | 63.992 | 1 | 1 | 1660 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2176255.7258 | 177732.2339 | 2683.8011 | 24628.9914 | 153103.2424 | 67872.795 | 0.063248 | -524095.7319 | 524095.7319
C | Xist Rating 8711 | -48.85 | 986.173 | 150.301 | 35.7 | 2273.14 | 8022.13 | 21632.8 | 0.84 | 3.09 | 22.703 | 60.242 | 1 | 1 | 1670 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2241709.2932 | 179730.7747 | 2716.2334 | 24777.3588 | 154953.4159 | 63988.7868 | 0.063629 | -494104.4503 | 494104.4503
C | Xist Rating 8712 | -48.52 | 990.728 | 150.301 | 35.7 | 2278.35 | 8099.12 | 21560.1 | 0.83 | 3.08 | 22.709 | 59.818 | 1 | 1 | 1680 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2257225.1388 | 181740.4278 | 2748.8606 | 24925.7263 | 156814.7015 | 63540.2902 | 0.06401 | -490641.2784 | 490641.2784
C | Xist Rating 8713 | -47.95 | 1004.1 | 150.301 | 35.7 | 2273.87 | 8077.63 | 21345.7 | 0.81 | 3.04 | 22.677 | 58.532 | 1 | 1 | 1690 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2283192.867 | 183761.1929 | 2781.6825 | 25074.0937 | 158687.0993 | 62176.8607 | 0.064391 | -480113.2369 | 480113.2369
C | Xist Rating 8714 | -47.45 | 1012.95 | 150.301 | 35.7 | 2275.99 | 8127.88 | 21205.4 | 0.8 | 3.02 | 22.681 | 57.701 | 1 | 1 | 1700 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2305464.0705 | 185793.0703 | 2814.6992 | 25222.4611 | 160570.6092 | 61305.0656 | 0.064772 | -473381.4663 | 473381.4663
C | Xist Rating 8715 | -46.94 | 1023.36 | 150.301 | 35.7 | 2275.51 | 8149.18 | 21044.4 | 0.79 | 2.99 | 22.67 | 56.758 | 1 | 1 | 1710 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2328665.9136 | 187836.0598 | 2847.9107 | 25370.8285 | 162465.2313 | 60315.8438 | 0.065153 | -465742.958 | 465742.958
C | Xist Rating 8716 | -45.58 | 1054.15 | 150.301 | 35.7 | 2266.29 | 8114.92 | 20566.9 | 0.79 | 2.9 | 22.696 | 53.929 | 1 | 1 | 1720 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2389009.6035 | 189890.1614 | 2881.317 | 25519.1959 | 164370.9655 | 57387.5432 | 0.065534 | -443131.3966 | 443131.3966
C | Xist Rating 8717 | -44.95 | 1067.39 | 150.301 | 35.7 | 2264.77 | 8130.35 | 20374.1 | 0.77 | 2.87 | 22.685 | 52.838 | 1 | 1 | 1730 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2417392.8503 | 191955.3752 | 2914.9181 | 25667.5633 | 166287.8118 | 56226.7216 | 0.065915 | -434167.8401 | 434167.8401
C | Xist Rating 8718 | -44.55 | 1073.47 | 150.301 | 35.7 | 2268.89 | 8199.46 | 20289.7 | 0.76 | 2.85 | 22.689 | 52.383 | 1 | 1 | 1740 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2435585.3483 | 194031.7011 | 2948.714 | 25815.9308 | 168215.7704 | 55744.5785 | 0.066296 | -430444.8589 | 430444.8589
C | Xist Rating 8719 | -44.01 | 1085.46 | 150.301 | 35.7 | 2266.45 | 8199.06 | 20123.3 | 0.75 | 2.82 | 22.666 | 51.469 | 1 | 1 | 1750 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2460140.817 | 196119.1392 | 2982.7046 | 25964.2982 | 170154.841 | 54783.9692 | 0.066677 | -423027.2888 | 423027.2888
C | Xist Rating 8720 | -43.59 | 1094.43 | 150.301 | 35.7 | 2265.42 | 8209.22 | 20000.5 | 0.74 | 2.8 | 22.658 | 50.802 | 1 | 1 | 1760 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2479343.6106 | 198217.6895 | 3016.8901 | 26112.6656 | 172105.0239 | 54080.5622 | 0.067058 | -417595.7661 | 417595.7661
C | Xist Rating 8721 | -42.01 | 1130.94 | 150.301 | 35.7 | 2254.12 | 8160.42 | 19497.1 | 0.74 | 2.71 | 22.695 | 48.021 | 1 | 1 | 1770 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2549274.4728 | 200327.3519 | 3051.2703 | 26261.033 | 174066.3189 | 51202.1861 | 0.067439 | -395369.7091 | 395369.7091
C | Xist Rating 8722 | -41.53 | 1140.02 | 150.301 | 35.7 | 2255.42 | 8200.77 | 19382.7 | 0.73 | 2.69 | 22.683 | 47.433 | 1 | 1 | 1780 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2571223.9084 | 202448.1264 | 3085.8453 | 26409.4004 | 176038.726 | 50580.2702 | 0.06782 | -390567.4395 | 390567.4395
C | Xist Rating 8723 | -41.2 | 1144.83 | 150.301 | 35.7 | 2259.21 | 8263.07 | 19326 | 0.72 | 2.68 | 22.679 | 47.161 | 1 | 1 | 1790 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2586411.3843 | 204580.0131 | 3120.6151 | 26557.7679 | 178022.2453 | 50286.79 | 0.068201 | -388301.2626 | 388301.2626
C | Xist Rating 8724 | -40.48 | 1161.02 | 150.302 | 35.7 | 2256.01 | 8263.6 | 19121.6 | 0.71 | 2.65 | 22.67 | 46.096 | 1 | 1 | 1800 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2619272.7302 | 206723.012 | 3155.5797 | 26706.1353 | 180016.8767 | 49169.2945 | 0.068582 | -379672.259 | 379672.259
C | Xist Rating 8725 | -39.99 | 1169.97 | 150.302 | 35.7 | 2257.64 | 8309.42 | 19012.1 | 0.7 | 2.63 | 22.675 | 45.542 | 1 | 1 | 1810 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2641371.0708 | 208877.123 | 3190.7391 | 26854.5027 | 182022.6203 | 48583.0725 | 0.068963 | -375145.6075 | 375145.6075
C | Xist Rating 8726 | -38.71 | 1206.73 | 150.302 | 35.6 | 2237.73 | 8141.83 | 18562.7 | 0.7 | 2.55 | 22.975 | 43.218 | 1 | 1 | 1820 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2700335.9229 | 211042.3462 | 3226.0933 | 27002.8701 | 184039.4761 | 46193.8489 | 0.069344 | -356696.6566 | 356696.6566
C | Xist Rating 8727 | -38.71 | 1200.91 | 150.302 | 35.6 | 2249.73 | 8287.22 | 18631.2 | 0.69 | 2.56 | 23.013 | 43.578 | 1 | 1 | 1830 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2701723.2543 | 213218.6815 | 3261.6423 | 27151.2375 | 186067.444 | 46558.2219 | 0.069725 | -359510.248 | 359510.248
C | Xist Rating 8728 | -38.19 | 1208.28 | 150.302 | 35.6 | 2254.96 | 8378.79 | 18545.3 | 0.69 | 2.55 | 23.044 | 43.158 | 1 | 1 | 1840 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2724623.0688 | 215406.129 | 3297.386 | 27299.6049 | 188106.524 | 46130.9344 | 0.070106 | -356210.8476 | 356210.8476
C | Xist Rating 8729 | -37.64 | 1220.39 | 150.302 | 35.6 | 2252.71 | 8379.81 | 18409.2 | 0.67 | 2.52 | 23.029 | 42.503 | 1 | 1 | 1850 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2749184.7569 | 217604.6886 | 3333.3246 | 27447.9724 | 190156.7162 | 45418.7931 | 0.070487 | -350711.881 | 350711.881
C | Xist Rating 8730 | -37.05 | 1233.97 | 150.302 | 35.6 | 2249.54 | 8371.94 | 18259 | 0.66 | 2.5 | 23.009 | 41.783 | 1 | 1 | 1860 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2775864.8738 | 219814.3604 | 3369.4579 | 27596.3398 | 192218.0206 | 44657.6897 | 0.070868 | -344834.8425 | 344834.8425
C | Xist Rating 8731 | -35.52 | 1267.76 | 150.302 | 35.6 | 2243.23 | 8378.09 | 17879.5 | 0.66 | 2.43 | 23.065 | 39.929 | 1 | 1 | 1870 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2843877.2648 | 222035.1443 | 3405.7861 | 27744.7072 | 194290.4371 | 42742.2187 | 0.071249 | -330044.0834 | 330044.0834
C | Xist Rating 8732 | -34.93 | 1281.32 | 150.302 | 35.6 | 2240.37 | 8373.99 | 17738.5 | 0.65 | 2.41 | 23.053 | 39.282 | 1 | 1 | 1880 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2870630.8884 | 224267.0404 | 3442.309 | 27893.0746 | 196373.9658 | 42057.0396 | 0.07163 | -324753.3118 | 324753.3118
C | Xist Rating 8733 | -34.38 | 1290.32 | 150.302 | 35.7 | 2242.9 | 8433.4 | 17646.5 | 0.64 | 2.39 | 23.072 | 38.864 | 1 | 1 | 1890 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 33 | E | Rod | 2894058.728 | 226510.0486 | 3479.0267 | 28041.442 | 198468.6066 | 41611.164 | 0.072011 | -321310.3786 | 321310.3786
C | Xist Rating 8734 | -33.97 | 1299.78 | 150.302 | 35.7 | 2240.78 | 8427.52 | 17555.2 | 0.63 | 2.38 | 23.044 | 38.466 | 1 | 1 | 1900 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 2912521.0284 | 228764.169 | 3515.9392 | 28189.8095 | 200574.3596 | 41183.3084 | 0.072392 | -318006.5913 | 318006.5913
C | Xist Rating 8735 | -33.47 | 1308.96 | 150.302 | 35.7 | 2242.46 | 8475.62 | 17464.9 | 0.62 | 2.36 | 23.057 | 38.067 | 1 | 1 | 1910 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 2935290.4416 | 231029.4016 | 3553.0464 | 28338.1769 | 202691.2247 | 40756.416 | 0.072773 | -314710.2411 | 314710.2411
C | Xist Rating 8736 | -31.68 | 1349.97 | 150.302 | 35.7 | 2233.49 | 8462.15 | 17050.1 | 0.62 | 2.29 | 23.108 | 36.161 | 1 | 1 | 1920 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3015144.4953 | 233305.7463 | 3590.3485 | 28486.5443 | 204819.202 | 38786.1672 | 0.073154 | -299496.5019 | 299496.5019
C | Xist Rating 8737 | -31.14 | 1363.62 | 150.302 | 35.7 | 2229.07 | 8434.75 | 16923.7 | 0.61 | 2.27 | 23.1 | 35.617 | 1 | 1 | 1930 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3039604.4334 | 235593.2031 | 3627.8454 | 28634.9117 | 206958.2914 | 38207.2328 | 0.073535 | -295026.1239 | 295026.1239
C | Xist Rating 8738 | -30.72 | 1368.07 | 150.302 | 35.7 | 2235.41 | 8538.48 | 16882 | 0.61 | 2.26 | 23.141 | 35.444 | 1 | 1 | 1940 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3058197.3587 | 237891.7721 | 3665.537 | 28783.2791 | 209108.493 | 38036.0637 | 0.073916 | -293704.4014 | 293704.4014
C | Xist Rating 8739 | -30.33 | 1380.75 | 150.302 | 35.7 | 2228.39 | 8469 | 16771.8 | 0.59 | 2.24 | 23.101 | 34.991 | 1 | 1 | 1950 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3076849.4925 | 240201.4533 | 3703.4235 | 28931.6465 | 211269.8067 | 37529.4343 | 0.074297 | -289792.3437 | 289792.3437
C | Xist Rating 8740 | -29.66 | 1395.75 | 150.302 | 35.7 | 2225.92 | 8473.25 | 16636.6 | 0.58 | 2.22 | 23.114 | 34.417 | 1 | 1 | 1960 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3106827.84 | 242522.2466 | 3741.5047 | 29080.014 | 213442.2326 | 36919.8124 | 0.074678 | -285085.0048 | 285085.0048
C | Xist Rating 8741 | -28.04 | 1432.64 | 150.302 | 35.7 | 2218.58 | 8468.16 | 16302.9 | 0.58 | 2.16 | 23.205 | 32.982 | 1 | 1 | 1970 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3178426.4512 | 244854.152 | 3779.7807 | 29228.3814 | 215625.7707 | 35440.2371 | 0.075059 | -273660.1167 | 273660.1167
C | Xist Rating 8742 | -27.52 | 1443.27 | 150.303 | 35.7 | 2218.73 | 8498.12 | 16213.9 | 0.58 | 2.15 | 23.236 | 32.623 | 1 | 1 | 1980 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3202226.4471 | 247197.1696 | 3818.2515 | 29376.7488 | 217820.4208 | 35075.0449 | 0.07544 | -270840.199 | 270840.199
C | Xist Rating 8743 | -26.96 | 1457.11 | 150.303 | 35.7 | 2214.94 | 8478.34 | 16101.2 | 0.57 | 2.13 | 23.255 | 32.174 | 1 | 1 | 1990 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3227411.2234 | 249551.2994 | 3856.9171 | 29525.1162 | 220026.1832 | 34595.0393 | 0.075821 | -267133.7235 | 267133.7235
C | Xist Rating 8744 | -26.48 | 1467.87 | 150.303 | 35.7 | 2214 | 8492.41 | 16014.5 | 0.56 | 2.12 | 23.256 | 31.834 | 1 | 1 | 2000 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3249864.18 | 251916.5413 | 3895.7775 | 29673.4836 | 222243.0577 | 34227.0938 | 0.076202 | -264292.5455 | 264292.5455
C | Xist Rating 8745 | -26.08 | 1475.71 | 150.303 | 35.7 | 2214.15 | 8514.57 | 15953.5 | 0.55 | 2.11 | 23.266 | 31.601 | 1 | 1 | 2010 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3267443.2965 | 254292.8954 | 3934.8326 | 29821.8511 | 224471.0443 | 33970.5038 | 0.076583 | -262311.2255 | 262311.2255
C | Xist Rating 8746 | -24.35 | 1517.18 | 150.303 | 35.7 | 2204.35 | 8482.51 | 15614.7 | 0.55 | 2.05 | 23.304 | 30.228 | 1 | 1 | 2020 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3344395.733 | 256680.3616 | 3974.0826 | 29970.2185 | 226710.1432 | 32552.2737 | 0.076964 | -251360.0292 | 251360.0292
C | Xist Rating 8747 | -23.65 | 1532.12 | 150.303 | 35.7 | 2203.3 | 8506.35 | 15499.7 | 0.54 | 2.03 | 23.319 | 29.784 | 1 | 1 | 2030 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3375719.996 | 259078.94 | 4013.5273 | 30118.5859 | 228960.3541 | 32076.4575 | 0.077345 | -247685.9024 | 247685.9024
C | Xist Rating 8748 | -23.19 | 1541.77 | 150.303 | 35.7 | 2203.38 | 8531.27 | 15431.6 | 0.53 | 2.02 | 23.307 | 29.539 | 1 | 1 | 2040 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3397105.1826 | 261488.6305 | 4053.1669 | 30266.9533 | 231221.6772 | 31805.7648 | 0.077726 | -245595.6853 | 245595.6853
C | Xist Rating 8749 | -22.62 | 1550.61 | 150.303 | 35.7 | 2207.25 | 8613.81 | 15364.1 | 0.53 | 2.01 | 23.337 | 29.283 | 1 | 1 | 2050 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3422583.9225 | 263909.4332 | 4093.0012 | 30415.3207 | 233494.1125 | 31546.9074 | 0.078107 | -243596.8565 | 243596.8565
C | Xist Rating 8750 | -22.11 | 1564.85 | 150.303 | 35.7 | 2201.97 | 8569.7 | 15264.3 | 0.52 | 1.99 | 23.313 | 28.92 | 1 | 1 | 2060 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3445752.7545 | 266341.3481 | 4133.0303 | 30563.6881 | 235777.6599 | 31152.7751 | 0.078488 | -240553.4719 | 240553.4719
C | Xist Rating 8751 | -20.28 | 1609.32 | 150.303 | 35.7 | 2192 | 8539.77 | 14936.1 | 0.52 | 1.94 | 23.35 | 27.667 | 1 | 1 | 2070 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3527629.44 | 268784.375 | 4173.2542 | 30712.0556 | 238072.3195 | 29858.7558 | 0.078869 | -230561.3978 | 230561.3978
C | Xist Rating 8752 | -19.85 | 1618.78 | 150.303 | 35.7 | 2191.34 | 8553.4 | 14873.4 | 0.51 | 1.93 | 23.351 | 27.45 | 1 | 1 | 2080 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3547297.3652 | 271238.5142 | 4213.6729 | 30860.423 | 240378.0912 | 29617.1214 | 0.07925 | -228695.5607 | 228695.5607
C | Xist Rating 8753 | -19.3 | 1631.09 | 150.303 | 35.7 | 2189.97 | 8564.22 | 14790.9 | 0.5 | 1.91 | 23.361 | 27.158 | 1 | 1 | 2090 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3572038.1673 | 273703.7655 | 4254.2864 | 31008.7904 | 242694.9751 | 29297.8104 | 0.079631 | -226229.9259 | 226229.9259
C | Xist Rating 8754 | -18.77 | 1643.41 | 150.303 | 35.7 | 2188.23 | 8569.14 | 14709.3 | 0.5 | 1.9 | 23.361 | 26.871 | 1 | 1 | 2100 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3596159.0643 | 276180.1289 | 4295.0947 | 31157.1578 | 245022.9711 | 29004.9971 | 0.080012 | -223968.8992 | 223968.8992
C | Xist Rating 8755 | -18.3 | 1654.26 | 150.303 | 35.7 | 2187.13 | 8579.95 | 14638.7 | 0.49 | 1.89 | 23.364 | 26.627 | 1 | 1 | 2110 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3618081.6738 | 278667.6045 | 4336.0977 | 31305.5252 | 247362.0793 | 28734.8834 | 0.080393 | -221883.153 | 221883.153
C | Xist Rating 8756 | -16.62 | 1696.16 | 150.303 | 35.7 | 2177.44 | 8543.12 | 14359 | 0.49 | 1.84 | 23.398 | 25.621 | 1 | 1 | 2120 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3693286.6304 | 281166.1923 | 4377.2956 | 31453.8927 | 249712.2996 | 27696.8689 | 0.080774 | -213867.8798 | 213867.8798
C | Xist Rating 8757 | -15.99 | 1711.45 | 150.303 | 35.7 | 2174.83 | 8541.96 | 14263.7 | 0.48 | 1.83 | 23.395 | 25.297 | 1 | 1 | 2130 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3722112.8035 | 283675.8922 | 4418.6882 | 31602.2601 | 252073.6321 | 27343.0575 | 0.081155 | -211135.8418 | 211135.8418
C | Xist Rating 8758 | -15.48 | 1726.76 | 150.303 | 35.7 | 2169.2 | 8494.1 | 14169.8 | 0.48 | 1.81 | 23.388 | 24.98 | 1 | 1 | 2140 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3745687.792 | 286196.7042 | 4460.2756 | 31750.6275 | 254446.0768 | 27018.5648 | 0.081536 | -208630.1954 | 208630.1954
C | Xist Rating 8759 | -15.08 | 1734.75 | 150.303 | 35.7 | 2169.6 | 8519.44 | 14123.5 | 0.47 | 1.8 | 23.391 | 24.833 | 1 | 1 | 2150 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3763713.6 | 288728.6285 | 4502.0578 | 31898.9949 | 256829.6335 | 26848.5338 | 0.081917 | -207317.2613 | 207317.2613
C | Xist Rating 8760 | -14.58 | 1745.55 | 150.303 | 35.7 | 2169.38 | 8543.28 | 14059 | 0.47 | 1.79 | 23.396 | 24.621 | 1 | 1 | 2160 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3786761.259 | 291271.6648 | 4544.0348 | 32047.3623 | 259224.3025 | 26633.5276 | 0.082298 | -205657.0403 | 205657.0403
C | Xist Rating 8761 | -12.86 | 1790.68 | 150.303 | 35.7 | 2157.89 | 8482.87 | 13785.9 | 0.46 | 1.75 | 23.426 | 23.694 | 1 | 1 | 2170 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3864090.4652 | 293825.8133 | 4586.2066 | 32195.7297 | 261630.0836 | 25654.3537 | 0.082679 | -198096.1189 | 198096.1189
C | Xist Rating 8762 | -12.19 | 1805.73 | 150.303 | 35.7 | 2156.8 | 8504.22 | 13699 | 0.46 | 1.74 | 23.438 | 23.411 | 1 | 1 | 2180 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3894598.464 | 296391.074 | 4628.5732 | 32344.0972 | 264046.9768 | 25365.8283 | 0.08306 | -195868.2025 | 195868.2025
C | Xist Rating 8763 | -11.73 | 1816.76 | 150.303 | 35.7 | 2155.5 | 8510.74 | 13638.8 | 0.45 | 1.73 | 23.438 | 23.225 | 1 | 1 | 2190 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3916026.18 | 298967.4468 | 4671.1346 | 32492.4646 | 266474.9823 | 25154.4922 | 0.083441 | -194236.3212 | 194236.3212
C | Xist Rating 8764 | -11.31 | 1828.2 | 150.303 | 35.7 | 2152.84 | 8496.07 | 13579.3 | 0.45 | 1.72 | 23.424 | 23.046 | 1 | 1 | 2200 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3935822.088 | 301554.9318 | 4713.8907 | 32640.832 | 268914.0998 | 24972.7074 | 0.083822 | -192832.6273 | 192832.6273
C | Xist Rating 8765 | -10.67 | 1843.51 | 150.303 | 35.7 | 2150.84 | 8502.89 | 13495.3 | 0.44 | 1.7 | 23.426 | 22.78 | 1 | 1 | 2210 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 3965095.0484 | 304153.5289 | 4756.8417 | 32789.1994 | 271364.3295 | 24678.0745 | 0.084203 | -190557.55 | 190557.55
C | Xist Rating 8766 | -8.89 | 1888.51 | 150.303 | 35.7 | 2141.83 | 8477.44 | 13246.2 | 0.44 | 1.66 | 23.465 | 21.976 | 1 | 1 | 2220 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4044867.3733 | 306763.2382 | 4799.9874 | 32937.5668 | 273825.6714 | 23849.4497 | 0.084584 | -184159.1285 | 184159.1285
C | Xist Rating 8767 | -8.34 | 1900.79 | 150.303 | 35.7 | 2141.39 | 8500.76 | 13182.5 | 0.44 | 1.65 | 23.471 | 21.783 | 1 | 1 | 2230 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4070332.6981 | 309384.0597 | 4843.3279 | 33085.9343 | 276298.1254 | 23653.9113 | 0.084965 | -182649.2333 | 182649.2333
C | Xist Rating 8768 | -7.81 | 1914.99 | 150.303 | 35.7 | 2138.27 | 8485.67 | 13111.7 | 0.43 | 1.64 | 23.466 | 21.574 | 1 | 1 | 2240 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4094765.6673 | 312015.9932 | 4886.8633 | 33234.3017 | 278781.6916 | 23417.7119 | 0.085346 | -180825.3636 | 180825.3636
C | Xist Rating 8769 | -7.22 | 1930.62 | 150.303 | 35.7 | 2135.23 | 8475.35 | 13034 | 0.42 | 1.63 | 23.462 | 21.343 | 1 | 1 | 2250 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4122317.7426 | 314659.039 | 4930.5934 | 33382.6691 | 281276.3699 | 23158.5055 | 0.085727 | -178823.841 | 178823.841
C | Xist Rating 8770 | -6.83 | 1938.57 | 150.303 | 35.7 | 2135.88 | 8504.42 | 12995.5 | 0.42 | 1.62 | 23.469 | 21.234 | 1 | 1 | 2260 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4140552.8916 | 317313.1969 | 4974.5182 | 33531.0365 | 283782.1604 | 23050.0241 | 0.086108 | -177986.1759 | 177986.1759
C | Xist Rating 8771 | -4.99 | 1986.89 | 150.303 | 35.7 | 2125.4 | 8460.09 | 12751.8 | 0.42 | 1.59 | 23.497 | 20.488 | 1 | 1 | 2270 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4222936.006 | 319978.4669 | 5018.6379 | 33679.4039 | 286299.063 | 22280.9192 | 0.086489 | -172047.352 | 172047.352
C | Xist Rating 8772 | -4.44 | 2001.04 | 150.303 | 35.7 | 2123.21 | 8458.79 | 12686.1 | 0.41 | 1.58 | 23.494 | 20.302 | 1 | 1 | 2280 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4248628.1384 | 322654.8491 | 5062.9524 | 33827.7713 | 288827.0778 | 22068.0424 | 0.08687 | -170403.5741 | 170403.5741
C | Xist Rating 8773 | -3.74 | 2017.88 | 150.303 | 35.7 | 2121.37 | 8470.38 | 12606.8 | 0.41 | 1.56 | 23.495 | 20.073 | 1 | 1 | 2290 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4280670.0956 | 325342.3435 | 5107.4617 | 33976.1388 | 291366.2047 | 21834.5861 | 0.087251 | -168600.8864 | 168600.8864
C | Xist Rating 8774 | -3.28 | 2029.07 | 150.303 | 35.7 | 2120.32 | 8479.56 | 12557 | 0.4 | 1.56 | 23.497 | 19.937 | 1 | 1 | 2300 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4302277.7024 | 328040.95 | 5152.1657 | 34124.5062 | 293916.4438 | 21673.5282 | 0.087632 | -167357.2397 | 167357.2397
| Xist Rating 8775 | -2.85 | 2040.53 | 150.303 | 35.7 | 2118.27 | 8472.85 | 12507.7 | 0.4 | 1.55 | 23.502 | 19.804 | 1 | 1 | 2310 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4322393.4831 | 330750.6686 | 5197.0645 | 34272.8736 | 296477.795 | 21539.828 | 0.088013 | -166324.842 | 166324.842
| Xist Rating 8776 | -0.94 | 2090.15 | 150.303 | 35.7 | 2109.11 | 8449.51 | 12277.3 | 0.4 | 1.51 | 23.53 | 19.132 | 1 | 1 | 2320 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4408356.2665 | 333471.4995 | 5242.1582 | 34421.241 | 299050.2584 | 20847.3356 | 0.088394 | -160977.5998 | 160977.5998
| Xist Rating 8777 | -0.39 | 2104.33 | 150.303 | 35.7 | 2107.1 | 8450.27 | 12216.9 | 0.39 | 1.5 | 23.528 | 18.969 | 1 | 1 | 2330 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4434033.743 | 336203.4424 | 5287.4466 | 34569.6084 | 301633.834 | 20657.6228 | 0.088775 | -159512.6872 | 159512.6872
| Xist Rating 8778 | 0.19 | 2118.48 | 150.303 | 35.7 | 2105.6 | 8459.18 | 12157.3 | 0.39 | 1.49 | 23.531 | 18.809 | 1 | 1 | 2340 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4460671.488 | 338946.4975 | 5332.9298 | 34717.9759 | 304228.5217 | 20495.6988 | 0.089156 | -158262.3534 | 158262.3534
| Xist Rating 8779 | 0.69 | 2131.26 | 150.303 | 35.7 | 2103.91 | 8461.23 | 12104.8 | 0.38 | 1.49 | 23.533 | 18.672 | 1 | 1 | 2350 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4483979.2266 | 341700.6648 | 5378.6078 | 34866.3433 | 306834.3215 | 20332.8311 | 0.089537 | -157004.7322 | 157004.7322
| Xist Rating 8780 | 1.24 | 2146.94 | 150.303 | 35.7 | 2100.38 | 8440.77 | 12039.9 | 0.38 | 1.48 | 23.527 | 18.499 | 1 | 1 | 2360 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4509389.8372 | 344465.9442 | 5424.4805 | 35014.7107 | 309451.2335 | 20156.9382 | 0.089918 | -155646.5334 | 155646.5334
| Xist Rating 8781 | 2.89 | 2192.36 | 150.303 | 35.7 | 2090.96 | 8399.01 | 11846.9 | 0.38 | 1.45 | 23.551 | 17.964 | 1 | 1 | 2370 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4584137.0656 | 347242.3358 | 5470.5481 | 35163.0781 | 312079.2577 | 19606.3178 | 0.090299 | -151394.789 | 151394.789
| Xist Rating 8782 | 3.37 | 2206.76 | 150.303 | 35.7 | 2087.44 | 8374.56 | 11791.3 | 0.38 | 1.44 | 23.542 | 17.822 | 1 | 1 | 2380 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4606479.0944 | 350029.8395 | 5516.8105 | 35311.4455 | 314718.394 | 19462.4977 | 0.09068 | -150284.2483 | 150284.2483
| Xist Rating 8783 | 3.95 | 2221.98 | 150.303 | 35.7 | 2085.31 | 8375.89 | 11730.2 | 0.37 | 1.43 | 23.54 | 17.662 | 1 | 1 | 2390 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 4633517.1138 | 352828.4554 | 5563.2676 | 35459.8129 | 317368.6425 | 19275.0479 | 0.091061 | -148836.8107 | 148836.8107
C | Xist Rating 8785 | 15.14 | 2547.36 | 150.303 | 35.7 | 2015.41 | 8004.39 | 10538.3 | 0.41 | 1.25 | 23.505 | 14.618 | 1 | 1 | 2410 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5133974.8176 | 358459.0236 | 5656.7663 | 35756.5478 | 322702.4758 | 16221.8354 | 0.091823 | -125260.7131 | 125260.7131
C | Xist Rating 8786 | 15.24 | 2548.76 | 150.303 | 35.7 | 2016.47 | 8021.03 | 10538.3 | 0.4 | 1.25 | 23.544 | 14.63 | 1 | 1 | 2420 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5139498.0772 | 361290.976 | 5703.8078 | 35904.9152 | 325386.0608 | 16214.8122 | 0.092204 | -125206.4816 | 125206.4816
C | Xist Rating 8787 | 15.35 | 2550.12 | 150.303 | 35.7 | 2017.93 | 8044.32 | 10538.3 | 0.39 | 1.25 | 23.547 | 14.64 | 1 | 1 | 2430 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5145963.6516 | 364134.0405 | 5751.0441 | 36053.2826 | 328080.7578 | 16203.901 | 0.092585 | -125122.2281 | 125122.2281
C | Xist Rating 8788 | 15.45 | 2551.49 | 150.303 | 35.7 | 2019.01 | 8061.43 | 10538.2 | 0.38 | 1.25 | 23.546 | 14.651 | 1 | 1 | 2440 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5151483.8249 | 366988.2171 | 5798.4752 | 36201.65 | 330786.5671 | 16193.6454 | 0.092966 | -125043.0375 | 125043.0375
C | Xist Rating 8789 | 15.49 | 2552.82 | 150.303 | 35.7 | 2019.23 | 8064.93 | 10538.3 | 0.38 | 1.25 | 23.536 | 14.662 | 1 | 1 | 2450 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5154730.7286 | 369853.5059 | 5846.1011 | 36350.0175 | 333503.4885 | 16208.6623 | 0.093347 | -125158.9936 | 125158.9936
C | Xist Rating 8790 | 15.49 | 2554.29 | 150.303 | 35.7 | 2018.47 | 8052.8 | 10538.3 | 0.37 | 1.25 | 23.529 | 14.673 | 1 | 1 | 2460 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5155757.7363 | 372729.9069 | 5893.9217 | 36498.3849 | 336231.522 | 16197.8563 | 0.093728 | -125075.5528 | 125075.5528
C | Xist Rating 8791 | 15.49 | 2555.64 | 150.303 | 35.7 | 2017.92 | 8044.07 | 10538.3 | 0.37 | 1.25 | 23.57 | 14.684 | 1 | 1 | 2470 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5157077.0688 | 375617.42 | 5941.9372 | 36646.7523 | 338970.6677 | 16214.8617 | 0.094109 | -125206.8637 | 125206.8637
C | Xist Rating 8792 | 15.49 | 2556.99 | 150.303 | 35.7 | 2017.37 | 8035.42 | 10538.3 | 0.36 | 1.25 | 23.563 | 14.694 | 1 | 1 | 2480 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5158394.9163 | 378516.0452 | 5990.1474 | 36795.1197 | 341720.9255 | 16202.674 | 0.09449 | -125112.7538 | 125112.7538
C | Xist Rating 8793 | 15.48 | 2558.39 | 150.303 | 35.7 | 2016.7 | 8024.79 | 10538.3 | 0.35 | 1.25 | 23.557 | 14.705 | 1 | 1 | 2490 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5159505.113 | 381425.7826 | 6038.5525 | 36943.4871 | 344482.2955 | 16191.366 | 0.094871 | -125025.4362 | 125025.4362
C | Xist Rating 8794 | 15.53 | 2559.37 | 150.303 | 35.7 | 2017.37 | 8035.41 | 10538.2 | 0.35 | 1.25 | 23.551 | 14.714 | 1 | 1 | 2500 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5163196.2569 | 384346.6322 | 6087.1523 | 37091.8545 | 347254.7776 | 16204.1729 | 0.095252 | -125124.3279 | 125124.3279
C | Xist Rating 8795 | 15.51 | 2561.22 | 150.303 | 35.7 | 2015.98 | 8013.42 | 10538.2 | 0.34 | 1.25 | 23.542 | 14.727 | 1 | 1 | 2510 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5163368.2956 | 387278.5939 | 6135.9469 | 37240.222 | 350038.3719 | 16194.5267 | 0.095633 | -125049.8427 | 125049.8427
C | Xist Rating 8796 | 15.55 | 2562.68 | 150.303 | 35.7 | 2015.99 | 8013.55 | 10538.2 | 0.34 | 1.25 | 23.575 | 14.737 | 1 | 1 | 2520 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5166337.2532 | 390221.6678 | 6184.9363 | 37388.5894 | 352833.0784 | 16209.767 | 0.096014 | -125167.524 | 125167.524
C | Xist Rating 8797 | 15.49 | 2564.02 | 150.303 | 35.7 | 2014.33 | 7987.33 | 10538.2 | 0.33 | 1.25 | 23.577 | 14.748 | 1 | 1 | 2530 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5164782.4066 | 393175.8538 | 6234.1205 | 37536.9568 | 355638.897 | 16198.1227 | 0.096395 | -125077.6098 | 125077.6098
C | Xist Rating 8798 | 15.51 | 2565.17 | 150.303 | 35.7 | 2014.3 | 7987 | 10538.2 | 0.33 | 1.25 | 23.573 | 14.757 | 1 | 1 | 2540 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5167021.931 | 396141.152 | 6283.4995 | 37685.3242 | 358455.8278 | 16210.8064 | 0.096776 | -125175.5503 | 125175.5503
C | Xist Rating 8799 | 15.57 | 2566.71 | 150.303 | 35.7 | 2014.44 | 7989.08 | 10538.2 | 0.32 | 1.25 | 23.563 | 14.768 | 1 | 1 | 2550 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5170483.2924 | 399117.5623 | 6333.0732 | 37833.6916 | 361283.8707 | 16198.4065 | 0.097157 | -125079.8012 | 125079.8012
C | Xist Rating 8800 | 15.56 | 2568.16 | 150.303 | 35.7 | 2014.12 | 7984.17 | 10538.1 | 0.32 | 1.25 | 23.554 | 14.779 | 1 | 1 | 2560 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5172582.4192 | 402105.0848 | 6382.8418 | 37982.0591 | 364123.0257 | 16212.8793 | 0.097538 | -125191.5567 | 125191.5567
C | Xist Rating 8801 | 15.59 | 2569.55 | 150.303 | 35.7 | 2014.1 | 7983.82 | 10538.1 | 0.31 | 1.25 | 23.564 | 14.789 | 1 | 1 | 2570 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5175330.655 | 405103.7194 | 6432.8051 | 38130.4265 | 366973.2929 | 16199.8659 | 0.097919 | -125091.0707 | 125091.0707
C | Xist Rating 8802 | 15.56 | 2570.92 | 150.303 | 35.6 | 2013.16 | 7969.14 | 10538 | 0.31 | 1.25 | 23.606 | 14.799 | 1 | 1 | 2580 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5175673.3072 | 408113.4662 | 6482.9633 | 38278.7939 | 369834.6723 | 16215.031 | 0.0983 | -125208.1715 | 125208.1715
C | Xist Rating 8803 | 15.57 | 2572.28 | 150.303 | 35.6 | 2012.74 | 7962.52 | 10538 | 0.3 | 1.25 | 23.605 | 14.809 | 1 | 1 | 2590 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5177330.8472 | 411134.3251 | 6533.3162 | 38427.1613 | 372707.1638 | 16201.2558 | 0.098681 | -125101.8028 | 125101.8028
C | Xist Rating 8804 | 15.6 | 2573.45 | 150.304 | 35.6 | 2012.77 | 7963.01 | 10538 | 0.3 | 1.25 | 23.607 | 14.819 | 1 | 1 | 2600 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5179762.9565 | 414166.2962 | 6583.8639 | 38575.5287 | 375590.7675 | 16214.885 | 0.099062 | -125207.0436 | 125207.0436
C | Xist Rating 8805 | 15.6 | 2575.14 | 150.304 | 35.6 | 2011.92 | 7949.75 | 10538 | 0.3 | 1.25 | 23.606 | 14.83 | 1 | 1 | 2610 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5180975.6688 | 417209.3795 | 6634.6064 | 38723.8961 | 378485.4833 | 16229.4479 | 0.099443 | -125319.4946 | 125319.4946
C | Xist Rating 8806 | 15.61 | 2576.54 | 150.304 | 35.6 | 2011.56 | 7944.19 | 10538 | 0.29 | 1.25 | 23.606 | 14.84 | 1 | 1 | 2620 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5182864.8024 | 420263.5749 | 6685.5437 | 38872.2636 | 381391.3113 | 16215.2842 | 0.099824 | -125210.1267 | 125210.1267
C | Xist Rating 8807 | 15.63 | 2577.96 | 150.304 | 35.6 | 2011.25 | 7939.34 | 10538 | 0.29 | 1.25 | 23.644 | 14.851 | 1 | 1 | 2630 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5184922.05 | 423328.8824 | 6736.6758 | 39020.631 | 384308.2514 | 16231.0754 | 0.10021 | -125332.0621 | 125332.0621
C | Xist Rating 8808 | 15.68 | 2579.21 | 150.304 | 35.6 | 2011.49 | 7943.12 | 10538 | 0.28 | 1.25 | 23.649 | 14.86 | 1 | 1 | 2640 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5188055.1229 | 426405.3021 | 6788.0027 | 39168.9984 | 387236.3037 | 16215.6815 | 0.10059 | -125213.1941 | 125213.1941
C | Xist Rating 8809 | 15.68 | 2580.71 | 150.304 | 35.6 | 2010.81 | 7932.51 | 10538 | 0.28 | 1.25 | 23.643 | 14.871 | 1 | 1 | 2650 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5189317.4751 | 429492.834 | 6839.5243 | 39317.3658 | 390175.4682 | 16229.8736 | 0.10097 | -125322.7817 | 125322.7817
C | Xist Rating 8810 | 15.73 | 2582.05 | 150.304 | 35.6 | 2011.16 | 7937.86 | 10538 | 0.28 | 1.25 | 23.646 | 14.881 | 1 | 1 | 2660 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5192915.678 | 432591.478 | 6891.2408 | 39465.7332 | 393125.7448 | 16243.3261 | 0.10135 | -125426.6587 | 125426.6587
C | Xist Rating 8811 | 15.74 | 2583.44 | 150.304 | 35.6 | 2010.87 | 7933.5 | 10537.9 | 0.27 | 1.25 | 23.646 | 14.891 | 1 | 1 | 2670 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5194961.9928 | 435701.2342 | 6943.152 | 39614.1007 | 396087.1335 | 16228.3789 | 0.10173 | -125311.2405 | 125311.2405
C | Xist Rating 8812 | 15.8 | 2584.86 | 150.304 | 35.6 | 2011.14 | 7937.71 | 10538 | 0.27 | 1.25 | 23.688 | 14.901 | 1 | 1 | 2680 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5198515.3404 | 438822.1025 | 6995.258 | 39762.4681 | 399059.6344 | 16242.988 | 0.10211 | -125424.0477 | 125424.0477
C | Xist Rating 8813 | 15.85 | 2586.23 | 150.304 | 35.6 | 2011.39 | 7941.48 | 10538 | 0.26 | 1.25 | 23.69 | 14.911 | 1 | 1 | 2690 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5201917.1597 | 441954.0829 | 7047.5588 | 39910.8355 | 402043.2474 | 16227.74 | 0.10249 | -125306.3065 | 125306.3065
C | Xist Rating 8814 | 15.92 | 2587.43 | 150.304 | 35.6 | 2012.26 | 7955.19 | 10538 | 0.26 | 1.25 | 23.689 | 14.92 | 1 | 1 | 2700 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5206581.8918 | 445097.1756 | 7100.0544 | 40059.2029 | 405037.9726 | 16239.8159 | 0.10287 | -125399.5537 | 125399.5537
C | Xist Rating 8815 | 16.02 | 2589.09 | 150.304 | 35.6 | 2013.42 | 7973.33 | 10537.9 | 0.26 | 1.25 | 23.691 | 14.931 | 1 | 1 | 2710 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5212925.5878 | 448251.3803 | 7152.7448 | 40207.5703 | 408043.81 | 16254.0634 | 0.10325 | -125509.5689 | 125509.5689
C | Xist Rating 8816 | 16.02 | 2590.43 | 150.304 | 35.6 | 2013.01 | 7966.85 | 10537.9 | 0.25 | 1.25 | 23.687 | 14.94 | 1 | 1 | 2720 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5214561.4943 | 451416.6973 | 7205.63 | 40355.9377 | 411060.7595 | 16237.1642 | 0.10363 | -125379.0779 | 125379.0779
C | Xist Rating 8817 | 16.02 | 2591.76 | 150.304 | 35.6 | 2012.38 | 7957.04 | 10537.9 | 0.25 | 1.25 | 23.725 | 14.95 | 1 | 1 | 2730 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5215605.9888 | 454593.1263 | 7258.71 | 40504.3052 | 414088.8212 | 16251.3661 | 0.10402 | -125488.7413 | 125488.7413
C | Xist Rating 8818 | 16.01 | 2593.04 | 150.304 | 35.6 | 2011.72 | 7946.66 | 10537.9 | 0.25 | 1.25 | 23.72 | 14.959 | 1 | 1 | 2740 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5216470.4288 | 457780.6676 | 7311.9847 | 40652.6726 | 417127.995 | 16263.2177 | 0.1044 | -125580.2564 | 125580.2564
C | Xist Rating 8819 | 15.99 | 2594.59 | 150.304 | 35.6 | 2010.72 | 7931.16 | 10537.9 | 0.25 | 1.25 | 23.716 | 14.969 | 1 | 1 | 2750 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5216994.0048 | 460979.321 | 7365.4543 | 40801.04 | 420178.281 | 16276.1375 | 0.10478 | -125680.0198 | 125680.0198
C | Xist Rating 8820 | 15.98 | 2596.01 | 150.304 | 35.6 | 2009.94 | 7918.98 | 10537.9 | 0.24 | 1.25 | 23.714 | 14.979 | 1 | 1 | 2760 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5217824.3394 | 464189.0865 | 7419.1186 | 40949.4074 | 423239.6791 | 16259.7803 | 0.10516 | -125553.7135 | 125553.7135
C | Xist Rating 8821 | 15.95 | 2597.25 | 150.304 | 35.6 | 2009.12 | 7906.34 | 10537.9 | 0.24 | 1.25 | 23.711 | 14.988 | 1 | 1 | 2770 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5218186.92 | 467409.9642 | 7472.9777 | 41097.7748 | 426312.1893 | 16271.5885 | 0.10554 | -125644.8935 | 125644.8935
C | Xist Rating 8822 | 15.96 | 2598.8 | 150.304 | 35.6 | 2008.47 | 7896.27 | 10537.9 | 0.24 | 1.25 | 23.756 | 14.998 | 1 | 1 | 2780 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5219611.836 | 470641.954 | 7527.0316 | 41246.1423 | 429395.8118 | 16285.8701 | 0.10592 | -125755.1723 | 125755.1723
C | Xist Rating 8823 | 15.97 | 2600.2 | 150.304 | 35.6 | 2007.84 | 7886.5 | 10537.9 | 0.23 | 1.25 | 23.738 | 15.008 | 1 | 1 | 2790 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5220785.568 | 473885.056 | 7581.2803 | 41394.5097 | 432490.5464 | 16268.5836 | 0.1063 | -125621.6901 | 125621.6901
C | Xist Rating 8824 | 16 | 2601.18 | 150.304 | 35.6 | 2008.32 | 7893.98 | 10537.9 | 0.23 | 1.25 | 23.739 | 15.015 | 1 | 1 | 2800 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5224001.8176 | 477139.2702 | 7635.7238 | 41542.8771 | 435596.3931 | 16278.3292 | 0.10668 | -125696.9435 | 125696.9435
C | Xist Rating 8825 | 15.92 | 2602.92 | 150.304 | 35.6 | 2006.55 | 7866.68 | 10537.8 | 0.23 | 1.25 | 23.721 | 15.026 | 1 | 1 | 2810 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5222889.126 | 480404.5965 | 7690.3621 | 41691.2445 | 438713.352 | 16291.6787 | 0.10706 | -125800.0243 | 125800.0243
C | Xist Rating 8826 | 15.93 | 2604.4 | 150.304 | 35.6 | 2006.14 | 7860.41 | 10537.8 | 0.23 | 1.25 | 23.727 | 15.036 | 1 | 1 | 2820 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5224791.016 | 483681.0349 | 7745.1952 | 41839.6119 | 441841.423 | 16304.6837 | 0.10744 | -125900.4453 | 125900.4453
C | Xist Rating 8827 | 15.96 | 2605.77 | 150.304 | 35.6 | 2005.99 | 7858.08 | 10537.8 | 0.22 | 1.25 | 23.774 | 15.046 | 1 | 1 | 2830 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5227148.5623 | 486968.5855 | 7800.223 | 41987.9794 | 444980.6062 | 16288.7279 | 0.10783 | -125777.2391 | 125777.2391
C | Xist Rating 8828 | 15.94 | 2607.09 | 150.304 | 35.6 | 2005.23 | 7846.43 | 10537.8 | 0.22 | 1.25 | 23.769 | 15.055 | 1 | 1 | 2840 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5227815.0807 | 490267.2483 | 7855.4457 | 42136.3468 | 448130.9015 | 16300.2788 | 0.10821 | -125866.4322 | 125866.4322
C | Xist Rating 8829 | 15.96 | 2608.53 | 150.304 | 35.6 | 2004.85 | 7840.72 | 10537.8 | 0.22 | 1.25 | 23.772 | 15.064 | 1 | 1 | 2850 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5229711.3705 | 493577.0232 | 7910.8631 | 42284.7142 | 451292.309 | 16312.0536 | 0.10859 | -125957.3538 | 125957.3538
C | Xist Rating 8830 | 16.02 | 2609.94 | 150.304 | 35.6 | 2005.44 | 7849.72 | 10537.8 | 0.22 | 1.25 | 23.788 | 15.074 | 1 | 1 | 2860 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5234078.0736 | 496897.9103 | 7966.4753 | 42433.0816 | 454464.8287 | 16325.2341 | 0.10897 | -126059.1301 | 126059.1301
C | Xist Rating 8831 | 16.02 | 2611.13 | 150.304 | 35.6 | 2004.98 | 7842.67 | 10537.8 | 0.21 | 1.25 | 23.786 | 15.082 | 1 | 1 | 2870 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5235263.4274 | 500229.9095 | 8022.2824 | 42581.449 | 457648.4605 | 16305.2314 | 0.10935 | -125904.6746 | 125904.6746
C | Xist Rating 8832 | 16.12 | 2612.64 | 150.304 | 35.6 | 2006.09 | 7859.64 | 10537.9 | 0.21 | 1.25 | 23.848 | 15.092 | 1 | 1 | 2880 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5241190.9776 | 503573.0209 | 8078.2842 | 42729.8164 | 460843.2044 | 16319.5362 | 0.10973 | -126015.1326 | 126015.1326
C | Xist Rating 8833 | 16.26 | 2613.98 | 150.304 | 35.6 | 2008.05 | 7889.78 | 10538 | 0.21 | 1.25 | 23.876 | 15.102 | 1 | 1 | 2890 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5249002.539 | 506927.2444 | 8134.4807 | 42878.1839 | 464049.0605 | 16332.9277 | 0.11011 | -126118.5386 | 126118.5386
C | Xist Rating 8834 | 16.44 | 2615.37 | 150.304 | 35.6 | 2010.47 | 7927.2 | 10538 | 0.21 | 1.25 | 23.91 | 15.111 | 1 | 1 | 2900 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5258122.9239 | 510292.5801 | 8190.8721 | 43026.5513 | 467266.0288 | 16345.4499 | 0.11049 | -126215.2311 | 126215.2311
C | Xist Rating 8835 | 16.62 | 2616.91 | 150.304 | 35.6 | 2013.03 | 7967.11 | 10538.1 | 0.2 | 1.25 | 23.949 | 15.121 | 1 | 1 | 2910 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5267918.3373 | 513669.0279 | 8247.4583 | 43174.9187 | 470494.1092 | 16327.9148 | 0.11087 | -126079.8302 | 126079.8302
C | Xist Rating 8836 | 16.83 | 2618.3 | 150.304 | 35.6 | 2016.04 | 8014.44 | 10538.2 | 0.2 | 1.25 | 23.97 | 15.131 | 1 | 1 | 2920 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5278597.532 | 517056.5879 | 8304.2393 | 43323.2861 | 473733.3018 | 16340.9965 | 0.11125 | -126180.8438 | 126180.8438
C | Xist Rating 8837 | 17.62 | 2619.68 | 150.304 | 35.6 | 2029.48 | 8230.97 | 10538.3 | 0.2 | 1.25 | 24.104 | 15.141 | 1 | 1 | 2930 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5316588.1664 | 520455.26 | 8361.215 | 43471.6535 | 476983.6065 | 16357.0502 | 0.11164 | -126304.8061 | 126304.8061
C | Xist Rating 8838 | 18.1 | 2621.05 | 150.304 | 35.6 | 2037.33 | 8361.56 | 10538.4 | 0.19 | 1.25 | 24.157 | 15.151 | 1 | 1 | 2940 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 32 | E | Rod | 5339943.7965 | 523865.0443 | 8418.3855 | 43620.021 | 480245.0234 | 16339.1579 | 0.11202 | -126166.646 | 126166.646
C | Xist Rating 8839 | 17.69 | 2622.46 | 150.304 | 35.6 | 2029.68 | 8234.38 | 10538.3 | 0.19 | 1.25 | 24.095 | 15.16 | 1 | 1 | 2950 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 31 | E | Rod | 5322754.6128 | 527285.9408 | 8475.7509 | 43768.3884 | 483517.5524 | 16349.004 | 0.1124 | -126242.6754 | 126242.6754
C | Xist Rating 8840 | 18.89 | 2623.83 | 150.304 | 35.6 | 2049.72 | 8574.35 | 10538.4 | 0.19 | 1.25 | 24.235 | 15.171 | 1 | 1 | 2960 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 31 | E | Rod | 5378116.8276 | 530717.9494 | 8533.311 | 43916.7558 | 486801.1936 | 16366.0089 | 0.11278 | -126373.9827 | 126373.9827
C | Xist Rating 8841 | 19.7 | 2625.21 | 150.304 | 35.6 | 2063.54 | 8821.51 | 10538.3 | 0.18 | 1.25 | 24.315 | 15.181 | 1 | 1 | 2970 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 31 | E | Rod | 5417225.8434 | 534161.0701 | 8591.0659 | 44065.1232 | 490095.9469 | 16348.1111 | 0.11316 | -126235.7806 | 126235.7806
C | Xist Rating 8842 | 19.7 | 2626.44 | 150.304 | 35.6 | 2062.88 | 8809.52 | 10538.3 | 0.18 | 1.25 | 24.349 | 15.189 | 1 | 1 | 2980 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 31 | E | Rod | 5418030.5472 | 537615.303 | 8649.0156 | 44213.4906 | 493401.8124 | 16359.1984 | 0.11354 | -126321.394 | 126321.394
C | Xist Rating 8843 | 19.71 | 2627.99 | 150.304 | 35.6 | 2062.49 | 8802.38 | 10538.2 | 0.18 | 1.25 | 24.333 | 15.199 | 1 | 1 | 2990 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 31 | E | Rod | 5420203.0951 | 541080.6481 | 8707.16 | 44361.858 | 496718.79 | 16371.162 | 0.11392 | -126413.7735 | 126413.7735
C | Xist Rating 8844 | 19.7 | 2629.43 | 150.304 | 35.6 | 2061.77 | 8789.27 | 10538.2 | 0.18 | 1.25 | 24.328 | 15.208 | 1 | 1 | 3000 | 152.4 | 2 | 5.3 | 19.05 | 1.3333 | 31 | E | Rod | 5421279.8911 | 544557.1053 | 8765.4993 | 44510.2255 | 500046.8798 | 16382.3508 | 0.1143 | -126500.1701 | 126500.1701
C | Xist Rating 8845 | -85.09 | 273.039 | 150.311 | 35.9 | 2340.9 | 6872.2 | 58745.1 | 2.49 | 10.95 | 26.664 | 635.144 | 1 | 1 | 1000 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 639156.9951 | 71725.7611 | 973.9444 | 15116.6803 | 56609.0807 | 662572.0989 | 0.038101 | -5116206.1192 | 5116206.1192
C | Xist Rating 8846 | -84.96 | 275.848 | 150.311 | 35.9 | 2337.57 | 6850.81 | 58283.5 | 2.47 | 10.84 | 26.761 | 623.178 | 1 | 1 | 1010 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 644814.0094 | 73014.7704 | 993.5206 | 15267.8471 | 57746.9233 | 650161.8912 | 0.038482 | -5020377.785 | 5020377.785
C | Xist Rating 8847 | -83.85 | 297.237 | 150.311 | 35.9 | 2330.33 | 6844.33 | 54967 | 2.48 | 10.07 | 26.811 | 540.053 | 1 | 1 | 1020 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 692660.2982 | 74315.1015 | 1013.2917 | 15419.014 | 58896.0876 | 563884.2439 | 0.038863 | -4354164.6625 | 4354164.6625
C | Xist Rating 8848 | -83.66 | 303 | 150.309 | 35.9 | 2314.29 | 6721.56 | 54177.9 | 2.39 | 9.89 | 26.145 | 521.809 | 1 | 1 | 1030 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 701229.87 | 75626.7545 | 1033.2576 | 15570.1808 | 60056.5738 | 544782.7873 | 0.039244 | -4206668.2778 | 4206668.2778
C | Xist Rating 8849 | -83.54 | 305.883 | 150.309 | 35.9 | 2309.14 | 6685.06 | 53793.8 | 2.35 | 9.8 | 26.001 | 513.089 | 1 | 1 | 1040 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 706326.6706 | 76949.7293 | 1053.4182 | 15721.3476 | 61228.3817 | 535690.5624 | 0.039625 | -4136460.5267 | 4136460.5267
C | Xist Rating 8850 | -83.3 | 311.525 | 150.309 | 35.9 | 2302 | 6638.87 | 53042.8 | 2.32 | 9.63 | 25.898 | 496.016 | 1 | 1 | 1050 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 717130.55 | 78284.0259 | 1073.7737 | 15872.5144 | 62411.5115 | 517939.7081 | 0.040006 | -3999393.1354 | 3999393.1354
C | Xist Rating 8851 | -83.17 | 314.388 | 150.309 | 35.9 | 2298.63 | 6617.53 | 52676 | 2.28 | 9.54 | 25.852 | 487.903 | 1 | 1 | 1060 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 722661.6884 | 79629.6443 | 1094.3239 | 16023.6812 | 63605.9631 | 509487.0985 | 0.040387 | -3934124.3243 | 3934124.3243
C | Xist Rating 8852 | -82.06 | 337.337 | 150.308 | 35.9 | 2284.21 | 6551.97 | 49856.6 | 2.27 | 8.9 | 25.584 | 426.854 | 1 | 1 | 1070 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 770548.5488 | 80986.5845 | 1115.0689 | 16174.848 | 64811.7365 | 446072.6517 | 0.040768 | -3444454.7754 | 3444454.7754
C | Xist Rating 8853 | -81.84 | 341.636 | 150.308 | 35.9 | 2284.81 | 6566.5 | 49379.9 | 2.22 | 8.79 | 25.444 | 417.223 | 1 | 1 | 1080 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 780573.3492 | 82354.8465 | 1136.0087 | 16326.0148 | 66028.8318 | 436019.9327 | 0.041149 | -3366830.3444 | 3366830.3444
C | Xist Rating 8854 | -81.5 | 347.358 | 150.307 | 35.9 | 2289.15 | 6615.44 | 48760.6 | 2.15 | 8.65 | 25.248 | 404.866 | 1 | 1 | 1090 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 795154.5657 | 83734.4304 | 1157.1433 | 16477.1816 | 67257.2488 | 423104.9166 | 0.04153 | -3267104.0132 | 3267104.0132
C | Xist Rating 8855 | -81.21 | 351.625 | 150.307 | 35.9 | 2297.96 | 6699.44 | 48306.7 | 2.11 | 8.55 | 25.252 | 395.945 | 1 | 1 | 1100 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 808020.185 | 85125.3361 | 1178.4727 | 16628.3484 | 68496.9877 | 413815.4244 | 0.041911 | -3195373.0166 | 3195373.0166
C | Xist Rating 8856 | -81.05 | 354.676 | 150.306 | 35.9 | 2299.06 | 6715.43 | 48009.4 | 2.03 | 8.48 | 24.847 | 390.428 | 1 | 1 | 1110 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 815421.4046 | 86527.5636 | 1199.9969 | 16779.5152 | 69748.0484 | 407968.4918 | 0.042292 | -3150224.553 | 3150224.553
C | Xist Rating 8857 | -79.73 | 380.258 | 150.307 | 35.9 | 2292.99 | 6724.45 | 45447.6 | 2.07 | 7.92 | 25.198 | 341.628 | 1 | 1 | 1120 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 871927.7914 | 87941.1129 | 1221.7158 | 16930.682 | 71010.4309 | 357398.751 | 0.042673 | -2759738.4194 | 2759738.4194
C | Xist Rating 8858 | -79.55 | 383.263 | 150.307 | 35.9 | 2296.23 | 6759 | 45188.5 | 2.01 | 7.86 | 24.945 | 337.187 | 1 | 1 | 1130 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 880059.9985 | 89365.984 | 1243.6296 | 17081.8488 | 72284.1352 | 352707.8225 | 0.043054 | -2723516.3128 | 2723516.3128
C | Xist Rating 8859 | -79.26 | 389.055 | 150.306 | 35.9 | 2295.34 | 6764.56 | 44680.7 | 1.95 | 7.75 | 24.549 | 328.321 | 1 | 1 | 1140 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 893013.5037 | 90802.1769 | 1265.7381 | 17233.0156 | 73569.1613 | 343407.0293 | 0.043435 | -2651698.0533 | 2651698.0533
C | Xist Rating 8860 | -78.95 | 394.784 | 150.305 | 35.9 | 2295.94 | 6783 | 44185.8 | 1.91 | 7.64 | 24.46 | 319.757 | 1 | 1 | 1150 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 906400.377 | 92249.6917 | 1288.0414 | 17384.1824 | 74865.5093 | 334475.4056 | 0.043816 | -2582730.4221 | 2582730.4221
C | Xist Rating 8861 | -78.66 | 400.592 | 150.305 | 35.9 | 2294.88 | 6786.95 | 43703.2 | 1.85 | 7.53 | 24.256 | 311.603 | 1 | 1 | 1160 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 919310.569 | 93708.5282 | 1310.5395 | 17535.3492 | 76173.179 | 325932.4972 | 0.044197 | -2516764.3481 | 2516764.3481
C | Xist Rating 8862 | -77.5 | 423.527 | 150.305 | 35.9 | 2288.97 | 6789.33 | 41832.1 | 1.88 | 7.13 | 24.434 | 280.263 | 1 | 1 | 1170 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 969440.5972 | 95178.6866 | 1333.2324 | 17686.516 | 77492.1706 | 293461.7844 | 0.044578 | -2266034.1108 | 2266034.1108
C | Xist Rating 8863 | -77.37 | 425.123 | 150.305 | 35.8 | 2294.42 | 6840.87 | 41724.5 | 1.83 | 7.11 | 24.317 | 278.71 | 1 | 1 | 1180 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 975410.7137 | 96660.1668 | 1356.1201 | 17837.6828 | 78822.484 | 291793.6425 | 0.044959 | -2253153.1616 | 2253153.1616
C | Xist Rating 8864 | -76.83 | 436.566 | 150.305 | 35.8 | 2288.97 | 6818.84 | 40885.5 | 1.78 | 6.92 | 24.1 | 265.577 | 1 | 1 | 1190 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 999286.477 | 98152.9688 | 1379.2026 | 17988.8496 | 80164.1192 | 278089.5311 | 0.04534 | -2147333.6459 | 2147333.6459
C | Xist Rating 8865 | -76.56 | 439.463 | 150.305 | 35.8 | 2301.36 | 6936.72 | 40681.7 | 1.75 | 6.88 | 24.155 | 262.502 | 1 | 1 | 1200 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1011362.5697 | 99657.0927 | 1402.4799 | 18140.0164 | 81517.0763 | 274881.6647 | 0.045721 | -2122563.3521 | 2122563.3521
C | Xist Rating 8866 | -76.26 | 445.34 | 150.304 | 35.8 | 2300.35 | 6941.12 | 40280.7 | 1.69 | 6.8 | 23.964 | 256.517 | 1 | 1 | 1210 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1024437.869 | 101172.5383 | 1425.9519 | 18291.1832 | 82881.3551 | 268589.0853 | 0.046102 | -2073973.7219 | 2073973.7219
C | Xist Rating 8867 | -75.01 | 471.277 | 150.304 | 35.8 | 2288.83 | 6898.17 | 38537.5 | 1.69 | 6.43 | 23.965 | 230.623 | 1 | 1 | 1220 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1078672.9359 | 102699.3058 | 1449.6188 | 18442.35 | 84256.9558 | 241716.4533 | 0.046483 | -1866470.3804 | 1866470.3804
C | Xist Rating 8868 | -74.65 | 477.004 | 150.304 | 35.8 | 2294.85 | 6966.58 | 38183.2 | 1.67 | 6.35 | 23.993 | 225.65 | 1 | 1 | 1230 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1094652.6294 | 104237.3951 | 1473.4804 | 18593.5168 | 85643.8782 | 236546.3072 | 0.046864 | -1826547.8829 | 1826547.8829
C | Xist Rating 8869 | -74.34 | 482.871 | 150.304 | 35.8 | 2295.18 | 6983.13 | 37835.8 | 1.62 | 6.28 | 23.867 | 220.904 | 1 | 1 | 1240 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1108275.8618 | 105786.8062 | 1497.5369 | 18744.6836 | 87042.1225 | 231557.5291 | 0.047245 | -1788025.8604 | 1788025.8604
C | Xist Rating 8870 | -74.14 | 485.912 | 150.304 | 35.8 | 2299.54 | 7030.45 | 37664.2 | 1.58 | 6.24 | 23.776 | 218.655 | 1 | 1 | 1250 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1117374.0805 | 107347.5391 | 1521.7881 | 18895.8504 | 88451.6886 | 229177.7298 | 0.047626 | -1769649.681 | 1769649.681
C | Xist Rating 8871 | -73.69 | 494.526 | 150.304 | 35.8 | 2299.67 | 7052.19 | 37161.2 | 1.55 | 6.14 | 23.723 | 211.827 | 1 | 1 | 1260 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1137246.6064 | 108919.5938 | 1546.2341 | 19047.0172 | 89872.5766 | 222058.7763 | 0.048007 | -1714679.0092 | 1714679.0092
C | Xist Rating 8872 | -72.48 | 519.083 | 150.304 | 35.8 | 2292.6 | 7044.98 | 35777.4 | 1.56 | 5.85 | 23.795 | 193.41 | 1 | 1 | 1270 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1190049.6858 | 110502.9704 | 1570.8749 | 19198.184 | 91304.7863 | 202969.1322 | 0.048388 | -1567273.8374 | 1567273.8374
C | Xist Rating 8873 | -72.18 | 525.019 | 150.304 | 35.8 | 2292.33 | 7055.96 | 35477.1 | 1.52 | 5.79 | 23.654 | 189.698 | 1 | 1 | 1280 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1203516.8043 | 112097.6687 | 1595.7105 | 19349.3508 | 92748.3179 | 199063.9583 | 0.048769 | -1537119.1196 | 1537119.1196
C | Xist Rating 8874 | -71.88 | 530.902 | 150.303 | 35.8 | 2292.33 | 7069.57 | 35182.4 | 1.48 | 5.73 | 23.59 | 186.076 | 1 | 1 | 1290 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1217002.5817 | 113703.6889 | 1620.7408 | 19500.5176 | 94203.1712 | 195258.4456 | 0.04915 | -1507733.9599 | 1507733.9599
C | Xist Rating 8875 | -71.42 | 539.494 | 150.303 | 35.8 | 2293.21 | 7098.34 | 34750.8 | 1.46 | 5.64 | 23.63 | 180.743 | 1 | 1 | 1300 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1237173.0357 | 115321.0309 | 1645.966 | 19651.6844 | 95669.3464 | 189711.6936 | 0.049531 | -1464903.4112 | 1464903.4112
C | Xist Rating 8876 | -71.17 | 543.986 | 150.303 | 35.8 | 2295.27 | 7128.42 | 34539.4 | 1.43 | 5.59 | 23.583 | 178.251 | 1 | 1 | 1310 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1248594.7462 | 116949.6947 | 1671.3859 | 19802.8513 | 97146.8434 | 187093.6466 | 0.049912 | -1444687.5458 | 1444687.5458
C | Xist Rating 8877 | -69.95 | 568.641 | 150.303 | 35.8 | 2288.51 | 7122.74 | 33362.4 | 1.43 | 5.35 | 23.635 | 164.11 | 1 | 1 | 1320 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1301340.6149 | 118589.6803 | 1697.0007 | 19954.0181 | 98635.6623 | 172427.7567 | 0.050293 | -1331441.4319 | 1331441.4319
C | Xist Rating 8878 | -69.52 | 577.45 | 150.303 | 35.8 | 2286.86 | 7127.01 | 32979.3 | 1.39 | 5.28 | 23.508 | 159.785 | 1 | 1 | 1330 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1320547.307 | 120240.9878 | 1722.8102 | 20105.1849 | 100135.8029 | 167884.5151 | 0.050674 | -1296359.7241 | 1296359.7241
C | Xist Rating 8879 | -69.04 | 586.158 | 150.303 | 35.8 | 2289.57 | 7173.9 | 32606.1 | 1.36 | 5.2 | 23.397 | 155.609 | 1 | 1 | 1340 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1342049.7721 | 121903.617 | 1748.8145 | 20256.3517 | 101647.2654 | 163510.965 | 0.051055 | -1262588.3294 | 1262588.3294
C | Xist Rating 8880 | -68.73 | 590.667 | 150.303 | 35.8 | 2295.75 | 7245.35 | 32423.4 | 1.33 | 5.16 | 23.356 | 153.642 | 1 | 1 | 1350 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1356023.7653 | 123577.5681 | 1775.0136 | 20407.5185 | 103170.0496 | 161436.7271 | 0.051436 | -1246571.6142 | 1246571.6142
C | Xist Rating 8881 | -68.37 | 593.51 | 150.303 | 35.8 | 2311.51 | 7411.9 | 32302.9 | 1.32 | 5.14 | 23.464 | 152.32 | 1 | 1 | 1360 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1371904.3001 | 125262.841 | 1801.4075 | 20558.6853 | 104704.1557 | 160072.2088 | 0.051817 | -1236035.1655 | 1236035.1655
C | Xist Rating 8882 | -66.87 | 628.4 | 150.303 | 35.8 | 2287.29 | 7252.47 | 30901.8 | 1.31 | 4.86 | 23.355 | 137.178 | 1 | 1 | 1370 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1437333.036 | 126959.4357 | 1827.9962 | 20709.8521 | 106249.5836 | 144337.9711 | 0.052198 | -1114539.5531 | 1114539.5531
C | Xist Rating 8883 | -66.73 | 631.505 | 150.303 | 35.8 | 2286.36 | 7250.05 | 30793.6 | 1.28 | 4.84 | 23.304 | 136.128 | 1 | 1 | 1380 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1443847.7718 | 128667.3522 | 1854.7797 | 20861.0189 | 107806.3333 | 143213.883 | 0.052579 | -1105859.6426 | 1105859.6426
C | Xist Rating 8884 | -66.34 | 638.88 | 150.303 | 35.8 | 2287.39 | 7277.64 | 30526.6 | 1.25 | 4.78 | 23.259 | 133.438 | 1 | 1 | 1390 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1461367.7232 | 130386.5906 | 1881.7579 | 21012.1857 | 109374.4049 | 140386.6288 | 0.05296 | -1084028.3348 | 1084028.3348
C | Xist Rating 8885 | -65.93 | 646.251 | 150.302 | 35.8 | 2290.1 | 7322.61 | 30264.7 | 1.23 | 4.73 | 23.222 | 130.832 | 1 | 1 | 1400 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1479979.4151 | 132117.1507 | 1908.931 | 21163.3525 | 110953.7982 | 137661.286 | 0.053341 | -1062983.9603 | 1062983.9603
C | Xist Rating 8886 | -65.49 | 655.019 | 150.302 | 35.8 | 2289.33 | 7335.66 | 29956.8 | 1.21 | 4.67 | 23.178 | 127.787 | 1 | 1 | 1410 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1499554.6473 | 133859.0327 | 1936.2988 | 21314.5193 | 112544.5134 | 134479.1428 | 0.053722 | -1038412.2941 | 1038412.2941
C | Xist Rating 8887 | -64.2 | 681.199 | 150.302 | 35.8 | 2284.09 | 7346.19 | 29051.4 | 1.22 | 4.49 | 23.258 | 118.863 | 1 | 1 | 1420 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1555919.8239 | 135612.2365 | 1963.8614 | 21465.6861 | 114146.5504 | 125245.1195 | 0.054103 | -967109.614 | 967109.614
C | Xist Rating 8888 | -63.94 | 685.948 | 150.302 | 35.8 | 2285.25 | 7368.66 | 28910.3 | 1.18 | 4.47 | 23.17 | 117.62 | 1 | 1 | 1430 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1567562.667 | 137376.7621 | 1991.6188 | 21616.8529 | 115759.9092 | 123900.696 | 0.054484 | -956728.3319 | 956728.3319
C | Xist Rating 8889 | -63.35 | 697.56 | 150.302 | 35.8 | 2284.7 | 7390.9 | 28541.5 | 1.16 | 4.39 | 23.152 | 114.183 | 1 | 1 | 1440 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1593715.332 | 139152.6095 | 2019.571 | 21768.0197 | 117384.5898 | 120312.3732 | 0.054865 | -929020.2544 | 929020.2544
C | Xist Rating 8890 | -62.97 | 704.969 | 150.302 | 35.7 | 2285.56 | 7417.53 | 28316.2 | 1.14 | 4.35 | 23.11 | 112.149 | 1 | 1 | 1450 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1611248.9476 | 140939.7787 | 2047.718 | 21919.1865 | 119020.5922 | 118178.898 | 0.055246 | -912546.1247 | 912546.1247
C | Xist Rating 8891 | -62.61 | 709.36 | 150.302 | 35.7 | 2294.03 | 7518.26 | 28183.4 | 1.12 | 4.32 | 23.166 | 110.956 | 1 | 1 | 1460 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1627293.1208 | 142738.2698 | 2076.0598 | 22070.3533 | 120667.9165 | 116925.6351 | 0.055627 | -902868.7605 | 902868.7605
C | Xist Rating 8892 | -61.31 | 738.811 | 150.302 | 35.7 | 2279.64 | 7437.4 | 27310 | 1.11 | 4.16 | 23.123 | 103.118 | 1 | 1 | 1470 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1684223.108 | 144548.0827 | 2104.5964 | 22221.5201 | 122326.5626 | 108779.105 | 0.056008 | -839963.4147 | 839963.4147
C | Xist Rating 8893 | -60.85 | 747.623 | 150.302 | 35.7 | 2280.37 | 7466.34 | 27065.8 | 1.1 | 4.11 | 23.108 | 101.031 | 1 | 1 | 1480 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1704857.0605 | 146369.2173 | 2133.3277 | 22372.6869 | 123996.5304 | 106606.8292 | 0.056389 | -823189.6768 | 823189.6768
C | Xist Rating 8894 | -60.45 | 755.034 | 150.302 | 35.7 | 2281.6 | 7497.3 | 26866 | 1.08 | 4.07 | 23.092 | 99.356 | 1 | 1 | 1490 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1722685.5744 | 148201.6739 | 2162.2539 | 22523.8537 | 125677.8201 | 104846.7171 | 0.05677 | -809598.5573 | 809598.5573
C | Xist Rating 8895 | -60.08 | 762.537 | 150.302 | 35.7 | 2281.17 | 7510.31 | 26669.5 | 1.06 | 4.03 | 23.049 | 97.736 | 1 | 1 | 1500 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1739476.5283 | 150045.4522 | 2191.3748 | 22675.0205 | 127370.4317 | 103141.4112 | 0.057151 | -796430.6376 | 796430.6376
C | Xist Rating 8896 | -59.62 | 771.377 | 150.302 | 35.7 | 2281.99 | 7540.67 | 26437.9 | 1.04 | 3.99 | 23.038 | 95.823 | 1 | 1 | 1510 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1760274.6002 | 151900.5523 | 2220.6906 | 22826.1873 | 129074.365 | 101133.7394 | 0.057532 | -780927.9282 | 780927.9282
C | Xist Rating 8897 | -58.23 | 800.511 | 150.302 | 35.7 | 2275.86 | 7546.57 | 25679.6 | 1.05 | 3.84 | 23.095 | 89.548 | 1 | 1 | 1520 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 34 | E | Rod | 1821850.9645 | 153766.9743 | 2250.2011 | 22977.3541 | 130789.6201 | 94647.676 | 0.057913 | -730844.2656 | 730844.2656
C | Xist Rating 8898 | -57.84 | 809.694 | 150.302 | 35.7 | 2272.15 | 7527.1 | 25466.9 | 1.02 | 3.8 | 22.946 | 87.923 | 1 | 1 | 1530 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 1839746.2221 | 155644.718 | 2279.9064 | 23128.5209 | 132516.1971 | 92913.046 | 0.058294 | -717449.9129 | 717449.9129
C | Xist Rating 8899 | -57.48 | 814.359 | 150.302 | 35.7 | 2278.91 | 7612.6 | 25362.2 | 1 | 3.78 | 22.939 | 87.147 | 1 | 1 | 1540 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 1855850.8687 | 157533.7836 | 2309.8065 | 23279.6877 | 134254.0959 | 92085.5 | 0.058675 | -711059.8217 | 711059.8217
C | Xist Rating 8900 | -56.73 | 828.941 | 150.302 | 35.7 | 2279.22 | 7652.2 | 25019.9 | 0.99 | 3.72 | 22.938 | 84.49 | 1 | 1 | 1550 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 1889338.906 | 159434.171 | 2339.9013 | 23430.8545 | 136003.3165 | 89320.4856 | 0.059056 | -689709.1138 | 689709.1138
C | Xist Rating 8901 | -56.32 | 833.381 | 150.302 | 35.7 | 2289.41 | 7779.58 | 24919.2 | 0.97 | 3.7 | 22.988 | 83.739 | 1 | 1 | 1560 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 1907950.7952 | 161345.8802 | 2370.191 | 23582.0213 | 137763.8589 | 88522.0643 | 0.059437 | -683543.9163 | 683543.9163
C | Xist Rating 8902 | -54.9 | 867.405 | 150.302 | 35.7 | 2271.57 | 7661.42 | 24160.8 | 0.97 | 3.56 | 22.945 | 78.018 | 1 | 1 | 1570 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 1970371.1758 | 163268.9112 | 2400.6755 | 23733.1881 | 139535.7231 | 82587.8747 | 0.059818 | -637721.677 | 637721.677
C | Xist Rating 8903 | -54.45 | 874.936 | 150.302 | 35.7 | 2274.97 | 7718.46 | 24006.2 | 0.95 | 3.53 | 22.939 | 76.922 | 1 | 1 | 1580 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 1990453.1519 | 165203.2641 | 2431.3547 | 23884.3549 | 141318.9091 | 81426.7526 | 0.0602 | -628755.7996 | 628755.7996
C | Xist Rating 8904 | -54.01 | 882.503 | 150.302 | 35.7 | 2277.81 | 7769.76 | 23854 | 0.93 | 3.5 | 22.93 | 75.855 | 1 | 1 | 1590 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2010174.1584 | 167148.9388 | 2462.2288 | 24035.5217 | 143113.417 | 80295.1486 | 0.060581 | -620017.8539 | 620017.8539
C | Xist Rating 8905 | -53.41 | 892.77 | 150.302 | 35.7 | 2281.76 | 7842.05 | 23644.1 | 0.92 | 3.46 | 22.949 | 74.365 | 1 | 1 | 1600 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2037086.8752 | 169105.9352 | 2493.2976 | 24186.6886 | 144919.2467 | 78742.1532 | 0.060962 | -608026.0347 | 608026.0347
C | Xist Rating 8906 | -53.12 | 897.631 | 150.302 | 35.7 | 2283.68 | 7876.1 | 23555.9 | 0.9 | 3.45 | 22.924 | 73.791 | 1 | 1 | 1610 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2049901.9621 | 171074.2535 | 2524.5612 | 24337.8554 | 146736.3982 | 78120.7717 | 0.061343 | -603227.8913 | 603227.8913
C | Xist Rating 8907 | -51.42 | 935.758 | 150.302 | 35.7 | 2270.53 | 7818.98 | 22804.4 | 0.9 | 3.31 | 22.965 | 68.526 | 1 | 1 | 1620 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2124666.6117 | 173053.8936 | 2556.0196 | 24489.0222 | 148564.8715 | 72665.0051 | 0.061724 | -561099.9077 | 561099.9077
C | Xist Rating 8908 | -51.02 | 940.273 | 150.302 | 35.7 | 2278.94 | 7931.08 | 22722.6 | 0.89 | 3.29 | 22.988 | 67.996 | 1 | 1 | 1630 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2142825.7506 | 175044.8556 | 2587.6728 | 24640.189 | 150404.6666 | 72108.5819 | 0.062105 | -556803.3557 | 556803.3557
C | Xist Rating 8909 | -50.58 | 947.988 | 150.302 | 35.7 | 2281.22 | 7977.85 | 22588.1 | 0.87 | 3.27 | 22.967 | 67.134 | 1 | 1 | 1640 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2162569.1854 | 177047.1393 | 2619.5208 | 24791.3558 | 152255.7835 | 71187.426 | 0.062486 | -549690.4335 | 549690.4335
C | Xist Rating 8910 | -50.08 | 958.612 | 150.302 | 35.7 | 2279.66 | 7985.73 | 22402.4 | 0.85 | 3.23 | 22.94 | 65.938 | 1 | 1 | 1650 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2185309.4319 | 179060.7449 | 2651.5635 | 24942.5226 | 154118.2223 | 69918.6679 | 0.062867 | -539893.4201 | 539893.4201
C | Xist Rating 8911 | -49.47 | 968.994 | 150.302 | 35.7 | 2282.96 | 8053.47 | 22220.4 | 0.84 | 3.2 | 22.95 | 64.759 | 1 | 1 | 1660 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2212174.5422 | 181085.6722 | 2683.8011 | 25093.6894 | 155991.9829 | 68686.5743 | 0.063248 | -530379.5196 | 530379.5196
C | Xist Rating 8912 | -48 | 1003.06 | 150.302 | 35.7 | 2270.81 | 7993.15 | 21632.6 | 0.84 | 3.09 | 22.971 | 60.96 | 1 | 1 | 1670 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2277758.6786 | 183121.9214 | 2716.2334 | 25244.8562 | 157877.0653 | 64751.2805 | 0.063629 | -499992.2246 | 499992.2246
C | Xist Rating 8913 | -47.64 | 1007.69 | 150.302 | 35.7 | 2276.58 | 8076.86 | 21560 | 0.83 | 3.08 | 22.984 | 60.531 | 1 | 1 | 1680 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2294086.9002 | 185169.4924 | 2748.8606 | 25396.023 | 159773.4695 | 64297.9281 | 0.06401 | -496491.5569 | 496491.5569
C | Xist Rating 8914 | -47.05 | 1021.27 | 150.302 | 35.7 | 2272.39 | 8058.88 | 21345.7 | 0.81 | 3.04 | 22.947 | 59.228 | 1 | 1 | 1690 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2320723.7353 | 187228.3853 | 2781.6825 | 25547.1898 | 161681.1955 | 62916.2229 | 0.064391 | -485822.3961 | 485822.3961
C | Xist Rating 8915 | -46.55 | 1030.27 | 150.302 | 35.7 | 2274.37 | 8107.33 | 21205.4 | 0.8 | 3.02 | 22.951 | 58.386 | 1 | 1 | 1700 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2343215.1799 | 189298.5999 | 2814.6992 | 25698.3566 | 163600.2433 | 62032.8966 | 0.064772 | -479001.5846 | 479001.5846
C | Xist Rating 8916 | -46.03 | 1040.84 | 150.302 | 35.7 | 2273.93 | 8129.04 | 21044.4 | 0.79 | 2.99 | 22.94 | 57.431 | 1 | 1 | 1710 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2366797.3012 | 191380.1364 | 2847.9107 | 25849.5234 | 165530.613 | 61031.1027 | 0.065153 | -471265.9977 | 471265.9977
C | Xist Rating 8917 | -44.64 | 1072.15 | 150.302 | 35.7 | 2264.68 | 8094.34 | 20566.8 | 0.79 | 2.9 | 22.966 | 54.566 | 1 | 1 | 1720 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2428076.662 | 193472.9946 | 2881.317 | 26000.6902 | 167472.3044 | 58065.5118 | 0.065534 | -448366.4903 | 448366.4903
C | Xist Rating 8918 | -44 | 1085.61 | 150.302 | 35.7 | 2263.18 | 8109.83 | 20374.1 | 0.78 | 2.87 | 22.955 | 53.461 | 1 | 1 | 1730 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2456930.8398 | 195577.1747 | 2914.9181 | 26151.857 | 169425.3177 | 56907.6289 | 0.065915 | -439425.6257 | 439425.6257
C | Xist Rating 8919 | -43.6 | 1091.79 | 150.302 | 35.7 | 2267.21 | 8177.48 | 20289.7 | 0.76 | 2.85 | 22.96 | 52.999 | 1 | 1 | 1740 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2475317.2059 | 197692.6766 | 2948.714 | 26303.0238 | 171389.6528 | 56400.3574 | 0.066296 | -435508.6094 | 435508.6094
C | Xist Rating 8920 | -43.05 | 1103.97 | 150.302 | 35.7 | 2264.79 | 8177.29 | 20123.3 | 0.75 | 2.82 | 22.936 | 52.073 | 1 | 1 | 1750 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2500260.2163 | 199819.5003 | 2982.7046 | 26454.1906 | 173365.3097 | 55427.107 | 0.066677 | -427993.4283 | 427993.4283
C | Xist Rating 8921 | -42.62 | 1113.08 | 150.302 | 35.7 | 2263.9 | 8189.22 | 20000.6 | 0.74 | 2.8 | 22.931 | 51.398 | 1 | 1 | 1760 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2519901.812 | 201957.6459 | 3016.8901 | 26605.3574 | 175352.2885 | 54715.4449 | 0.067058 | -422498.162 | 422498.162
C | Xist Rating 8922 | -41.02 | 1150.2 | 150.302 | 35.7 | 2252.21 | 8135.45 | 19497.1 | 0.74 | 2.71 | 22.965 | 48.581 | 1 | 1 | 1770 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2590491.942 | 204107.1132 | 3051.2703 | 26756.5242 | 177350.589 | 51799.5973 | 0.067439 | -399982.7598 | 399982.7598
C | Xist Rating 8923 | -40.53 | 1159.42 | 150.302 | 35.7 | 2253.84 | 8179.95 | 19382.8 | 0.73 | 2.69 | 22.955 | 47.985 | 1 | 1 | 1780 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2613147.1728 | 206267.9024 | 3085.8453 | 26907.691 | 179360.2114 | 51169.3641 | 0.06782 | -395116.2657 | 395116.2657
C | Xist Rating 8924 | -40.2 | 1164.31 | 150.303 | 35.7 | 2257.6 | 8241.6 | 19325.9 | 0.72 | 2.68 | 22.95 | 47.709 | 1 | 1 | 1790 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2628546.256 | 208440.0134 | 3120.6151 | 27058.8578 | 181381.1556 | 50871.5428 | 0.068201 | -392816.5687 | 392816.5687
C | Xist Rating 8925 | -39.46 | 1180.76 | 150.303 | 35.7 | 2254.51 | 8243.48 | 19121.6 | 0.71 | 2.65 | 22.941 | 46.63 | 1 | 1 | 1800 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2662035.2276 | 210623.4462 | 3155.5797 | 27210.0246 | 183413.4216 | 49739.3772 | 0.068582 | -384074.286 | 384074.286
C | Xist Rating 8926 | -39.24 | 1189.85 | 150.303 | 35.7 | 2245.8 | 8150.96 | 19012.9 | 0.7 | 2.63 | 23.235 | 46.06 | 1 | 1 | 1810 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2672165.13 | 212818.2008 | 3190.7391 | 27361.1914 | 185457.0094 | 49152.8186 | 0.068963 | -379545.0364 | 379545.0364
C | Xist Rating 8927 | -37.38 | 1227.23 | 150.303 | 35.7 | 2244.74 | 8235.46 | 18562.3 | 0.7 | 2.55 | 22.971 | 43.727 | 1 | 1 | 1820 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2754812.2702 | 215024.2772 | 3226.0933 | 27512.3582 | 187511.919 | 46722.2162 | 0.069344 | -360776.5685 | 360776.5685
C | Xist Rating 8928 | -37.66 | 1221.31 | 150.303 | 35.6 | 2249.05 | 8278.11 | 18631 | 0.69 | 2.56 | 23.286 | 44.08 | 1 | 1 | 1830 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2746787.2555 | 217241.6755 | 3261.6423 | 27663.525 | 189578.1505 | 47094.9999 | 0.069725 | -363655.1057 | 363655.1057
C | Xist Rating 8929 | -37.13 | 1228.8 | 150.303 | 35.6 | 2253.35 | 8356.55 | 18545.2 | 0.69 | 2.55 | 23.32 | 43.655 | 1 | 1 | 1840 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2768916.48 | 219470.3956 | 3297.386 | 27814.6918 | 191655.7037 | 46662.7751 | 0.070106 | -360317.5805 | 360317.5805
C | Xist Rating 8930 | -36.57 | 1241.1 | 150.303 | 35.6 | 2251.17 | 8358.57 | 18409.2 | 0.67 | 2.52 | 23.306 | 42.991 | 1 | 1 | 1850 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2793927.087 | 221710.4374 | 3333.3246 | 27965.8586 | 193744.5788 | 45940.9705 | 0.070487 | -354743.9964 | 354743.9964
C | Xist Rating 8931 | -35.97 | 1254.9 | 150.303 | 35.6 | 2248.18 | 8353.15 | 18259 | 0.66 | 2.5 | 23.286 | 42.261 | 1 | 1 | 1860 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2821241.082 | 223961.8011 | 3369.4579 | 28117.0254 | 195844.7757 | 45169.3344 | 0.070868 | -348785.6268 | 348785.6268
C | Xist Rating 8932 | -34.41 | 1289.24 | 150.303 | 35.6 | 2241.92 | 8359.8 | 17879.5 | 0.66 | 2.43 | 23.342 | 40.385 | 1 | 1 | 1870 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2890372.9408 | 226224.4867 | 3405.7861 | 28268.1922 | 197956.2944 | 43231.0984 | 0.071249 | -333819.0824 | 333819.0824
C | Xist Rating 8933 | -33.8 | 1303.02 | 150.303 | 35.6 | 2239 | 8354.89 | 17738.6 | 0.65 | 2.41 | 23.329 | 39.729 | 1 | 1 | 1880 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2917461.78 | 228498.494 | 3442.309 | 28419.359 | 200079.1349 | 42536.3665 | 0.07163 | -328454.547 | 328454.547
C | Xist Rating 8934 | -33.27 | 1312.17 | 150.303 | 35.7 | 2240.96 | 8406.11 | 17646.5 | 0.64 | 2.39 | 23.348 | 39.305 | 1 | 1 | 1890 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2940520.4832 | 230783.8231 | 3479.0267 | 28570.5259 | 202213.2973 | 42084.1065 | 0.072011 | -324962.3151 | 324962.3151
C | Xist Rating 8935 | -32.86 | 1321.77 | 150.303 | 35.6 | 2239.31 | 8406.9 | 17555 | 0.63 | 2.38 | 23.332 | 38.901 | 1 | 1 | 1900 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2959852.7787 | 233080.4741 | 3515.9392 | 28721.6927 | 204358.7814 | 41650.5079 | 0.072392 | -321614.1819 | 321614.1819
C | Xist Rating 8936 | -32.33 | 1331.09 | 150.303 | 35.7 | 2241.12 | 8456.64 | 17464.9 | 0.62 | 2.36 | 23.344 | 38.497 | 1 | 1 | 1910 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 2983132.4208 | 235388.4469 | 3553.0464 | 28872.8595 | 206515.5874 | 41218.2047 | 0.072773 | -318276.0508 | 318276.0508
C | Xist Rating 8937 | -30.55 | 1372.79 | 150.303 | 35.7 | 2230.76 | 8423.09 | 17050.1 | 0.62 | 2.29 | 23.397 | 36.568 | 1 | 1 | 1920 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3062365.0204 | 237707.7415 | 3590.3485 | 29024.0263 | 208683.7152 | 39224.2569 | 0.073154 | -302879.3143 | 302879.3143
C | Xist Rating 8938 | -29.96 | 1386.65 | 150.303 | 35.7 | 2227.74 | 8415.78 | 16923.7 | 0.61 | 2.27 | 23.388 | 36.017 | 1 | 1 | 1930 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3089095.671 | 240038.3579 | 3627.8454 | 29175.1931 | 210863.1648 | 38637.8305 | 0.073535 | -298351.0854 | 298351.0854
C | Xist Rating 8939 | -29.54 | 1391.17 | 150.303 | 35.7 | 2234.04 | 8518.46 | 16881.9 | 0.61 | 2.26 | 23.43 | 35.841 | 1 | 1 | 1940 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3107929.4268 | 242380.2961 | 3665.537 | 29326.3599 | 213053.9362 | 38463.6777 | 0.073916 | -297006.3235 | 297006.3235
C | Xist Rating 8940 | -29.13 | 1404.04 | 150.303 | 35.7 | 2227.02 | 8449.13 | 16771.8 | 0.59 | 2.24 | 23.388 | 35.382 | 1 | 1 | 1950 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3126825.1608 | 244733.5562 | 3703.4235 | 29477.5267 | 215256.0295 | 37950.288 | 0.074297 | -293042.0643 | 293042.0643
C | Xist Rating 8941 | -28.45 | 1419.28 | 150.303 | 35.7 | 2224.56 | 8453.51 | 16636.8 | 0.58 | 2.22 | 23.419 | 34.801 | 1 | 1 | 1960 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3157273.5168 | 247098.138 | 3741.5047 | 29628.6935 | 217469.4445 | 37334.1375 | 0.074678 | -288284.314 | 288284.314
C | Xist Rating 8942 | -26.81 | 1456.78 | 150.303 | 35.7 | 2217.27 | 8448.97 | 16302.9 | 0.58 | 2.16 | 23.492 | 33.347 | 1 | 1 | 1970 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3230074.5906 | 249474.0417 | 3779.7807 | 29779.8603 | 219694.1814 | 35833.9882 | 0.075059 | -276700.5584 | 276700.5584
C | Xist Rating 8943 | -26.28 | 1467.58 | 150.303 | 35.7 | 2217.38 | 8478.33 | 16213.9 | 0.58 | 2.15 | 23.523 | 32.984 | 1 | 1 | 1980 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3254182.5404 | 251861.2672 | 3818.2515 | 29931.0271 | 221930.2401 | 35464.7166 | 0.07544 | -273849.1407 | 273849.1407
C | Xist Rating 8944 | -25.75 | 1481.63 | 150.303 | 35.7 | 2212.47 | 8442.32 | 16101.2 | 0.57 | 2.13 | 23.549 | 32.529 | 1 | 1 | 1990 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3278061.9261 | 254259.8145 | 3856.9171 | 30082.1939 | 224177.6206 | 34978.6546 | 0.075821 | -270095.8987 | 270095.8987
C | Xist Rating 8945 | -25.23 | 1492.56 | 150.303 | 35.7 | 2211.69 | 8458.4 | 16014.7 | 0.56 | 2.12 | 23.552 | 32.185 | 1 | 1 | 2000 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3301080.0264 | 256669.6836 | 3895.7775 | 30233.3607 | 226436.3229 | 34606.467 | 0.076202 | -267221.9649 | 267221.9649
C | Xist Rating 8946 | -24.8 | 1500.52 | 150.303 | 35.7 | 2212.9 | 8495.95 | 15953.7 | 0.55 | 2.11 | 23.558 | 31.948 | 1 | 1 | 2010 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3320500.708 | 259090.8746 | 3934.8326 | 30384.5275 | 228706.3471 | 34345.3324 | 0.076583 | -265205.5528 | 265205.5528
C | Xist Rating 8947 | -23.07 | 1542.67 | 150.303 | 35.7 | 2202.66 | 8457.58 | 15614.6 | 0.55 | 2.05 | 23.596 | 30.558 | 1 | 1 | 2020 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3397977.5022 | 261523.3873 | 3974.0826 | 30535.6943 | 230987.693 | 32909.5199 | 0.076964 | -254118.5891 | 254118.5891
C | Xist Rating 8948 | -22.33 | 1557.85 | 150.304 | 35.7 | 2201.98 | 8486.65 | 15499.9 | 0.54 | 2.03 | 23.61 | 30.108 | 1 | 1 | 2030 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3430354.543 | 263967.2219 | 4013.5273 | 30686.8611 | 233280.3608 | 32427.2298 | 0.077345 | -250394.473 | 250394.473
C | Xist Rating 8949 | -21.91 | 1567.65 | 150.303 | 35.7 | 2200.92 | 8494.56 | 15431.6 | 0.53 | 2.02 | 23.594 | 29.859 | 1 | 1 | 2040 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3450272.238 | 266422.3783 | 4053.1669 | 30838.0279 | 235584.3504 | 32151.9936 | 0.077726 | -248269.1722 | 248269.1722
C | Xist Rating 8950 | -21.28 | 1576.63 | 150.304 | 35.7 | 2206.25 | 8598.56 | 15364.3 | 0.53 | 2.01 | 23.628 | 29.601 | 1 | 1 | 2050 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3478439.9375 | 268888.8565 | 4093.0012 | 30989.1947 | 237899.6618 | 31891.3221 | 0.078107 | -246256.3361 | 246256.3361
C | Xist Rating 8951 | -20.78 | 1591.08 | 150.303 | 35.7 | 2200.59 | 8548.97 | 15264.2 | 0.52 | 1.99 | 23.605 | 29.232 | 1 | 1 | 2060 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3501314.7372 | 271366.6565 | 4133.0303 | 31140.3615 | 240226.295 | 31490.8074 | 0.078488 | -243163.6671 | 243163.6671
C | Xist Rating 8952 | -18.92 | 1636.29 | 150.304 | 35.7 | 2190.44 | 8516.15 | 14936.2 | 0.52 | 1.94 | 23.643 | 27.964 | 1 | 1 | 2070 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3584195.0676 | 273855.7783 | 4173.2542 | 31291.5283 | 242564.25 | 30181.3269 | 0.078869 | -233052.206 | 233052.206
C | Xist Rating 8953 | -18.47 | 1645.89 | 150.304 | 35.7 | 2190.14 | 8535.19 | 14873.4 | 0.51 | 1.93 | 23.643 | 27.744 | 1 | 1 | 2080 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3604729.5246 | 276356.222 | 4213.6729 | 31442.6951 | 244913.5269 | 29936.3245 | 0.07925 | -231160.3627 | 231160.3627
C | Xist Rating 8954 | -17.92 | 1658.39 | 150.304 | 35.7 | 2188.7 | 8544.83 | 14790.9 | 0.5 | 1.91 | 23.655 | 27.448 | 1 | 1 | 2090 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3629718.193 | 278867.9875 | 4254.2864 | 31593.8619 | 247274.1256 | 29612.7464 | 0.079631 | -228661.7784 | 228661.7784
C | Xist Rating 8955 | -17.38 | 1670.9 | 150.304 | 35.7 | 2186.97 | 8549.89 | 14709.3 | 0.5 | 1.9 | 23.655 | 27.158 | 1 | 1 | 2100 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3654208.173 | 281391.0748 | 4295.0947 | 31745.0287 | 249646.046 | 29316.8835 | 0.080012 | -226377.2034 | 226377.2034
C | Xist Rating 8956 | -16.9 | 1681.92 | 150.304 | 35.7 | 2185.9 | 8561.07 | 14638.7 | 0.49 | 1.89 | 23.657 | 26.91 | 1 | 1 | 2110 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3676508.928 | 283925.4839 | 4336.0977 | 31896.1955 | 252029.2883 | 29042.3573 | 0.080393 | -224257.385 | 224257.385
C | Xist Rating 8957 | -15.19 | 1724.51 | 150.304 | 35.7 | 2176.37 | 8526.62 | 14358.9 | 0.49 | 1.84 | 23.688 | 25.891 | 1 | 1 | 2120 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3753171.8287 | 286471.2148 | 4377.2956 | 32047.3623 | 254423.8524 | 27990.767 | 0.080774 | -216137.2829 | 216137.2829
C | Xist Rating 8958 | -14.57 | 1740.03 | 150.304 | 35.7 | 2173.14 | 8515.91 | 14263.7 | 0.48 | 1.83 | 23.685 | 25.563 | 1 | 1 | 2130 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3781328.7942 | 289028.2675 | 4418.6882 | 32198.5291 | 256829.7384 | 27632.5884 | 0.081155 | -213371.5228 | 213371.5228
C | Xist Rating 8959 | -14.03 | 1755.58 | 150.304 | 35.7 | 2168.06 | 8476.62 | 14169.8 | 0.48 | 1.81 | 23.68 | 25.242 | 1 | 1 | 2140 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3806202.7748 | 291596.6421 | 4460.2756 | 32349.6959 | 259246.9461 | 27304.0962 | 0.081536 | -210834.9932 | 210834.9932
C | Xist Rating 8960 | -13.63 | 1763.69 | 150.304 | 35.7 | 2168.46 | 8502 | 14123.5 | 0.47 | 1.8 | 23.684 | 25.093 | 1 | 1 | 2150 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3824491.2174 | 294176.3384 | 4502.0578 | 32500.8627 | 261675.4757 | 27131.8149 | 0.081917 | -209504.683 | 209504.683
C | Xist Rating 8961 | -13.12 | 1774.66 | 150.304 | 35.7 | 2168.25 | 8525.77 | 14059 | 0.47 | 1.79 | 23.689 | 24.879 | 1 | 1 | 2160 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3847906.545 | 296767.3566 | 4544.0348 | 32652.0295 | 264115.3271 | 26914.7934 | 0.082298 | -207828.9006 | 207828.9006
C | Xist Rating 8962 | -11.38 | 1820.52 | 150.304 | 35.7 | 2156.72 | 8464.88 | 13785.9 | 0.46 | 1.75 | 23.719 | 23.939 | 1 | 1 | 2170 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3926351.8944 | 299369.6966 | 4586.2066 | 32803.1963 | 266566.5003 | 25921.8958 | 0.082679 | -200162.008 | 200162.008
C | Xist Rating 8963 | -10.69 | 1835.81 | 150.304 | 35.7 | 2155.63 | 8486.03 | 13699 | 0.46 | 1.74 | 23.732 | 23.653 | 1 | 1 | 2180 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3957327.1103 | 301983.3584 | 4628.5732 | 32954.3632 | 269028.9953 | 25630.3603 | 0.08306 | -197910.8482 | 197910.8482
C | Xist Rating 8964 | -10.23 | 1847.01 | 150.304 | 35.7 | 2154.31 | 8492.23 | 13638.8 | 0.45 | 1.73 | 23.731 | 23.464 | 1 | 1 | 2190 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3979032.1131 | 304608.3421 | 4671.1346 | 33105.53 | 271502.8121 | 25415.6365 | 0.083441 | -196252.8084 | 196252.8084
C | Xist Rating 8965 | -9.79 | 1858.61 | 150.304 | 35.7 | 2151.76 | 8479.11 | 13579.3 | 0.45 | 1.72 | 23.717 | 23.283 | 1 | 1 | 2200 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 3999282.6536 | 307244.6475 | 4713.8907 | 33256.6968 | 273987.9508 | 25231.8338 | 0.083822 | -194833.5328 | 194833.5328
C | Xist Rating 8966 | -9.14 | 1874.17 | 150.304 | 35.7 | 2149.74 | 8485.77 | 13495.3 | 0.44 | 1.7 | 23.72 | 23.014 | 1 | 1 | 2210 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4028978.2158 | 309892.2748 | 4756.8417 | 33407.8636 | 276484.4112 | 24933.8979 | 0.084203 | -192532.9501 | 192532.9501
C | Xist Rating 8967 | -7.34 | 1919.89 | 150.304 | 35.7 | 2140.55 | 8457.48 | 13246.2 | 0.44 | 1.66 | 23.76 | 22.199 | 1 | 1 | 2220 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4109620.5395 | 312551.2239 | 4799.9874 | 33559.0304 | 278992.1935 | 24093.9513 | 0.084584 | -186047.1054 | 186047.1054
C | Xist Rating 8968 | -6.78 | 1932.37 | 150.304 | 35.7 | 2140.14 | 8481.17 | 13182.5 | 0.44 | 1.65 | 23.765 | 22.004 | 1 | 1 | 2230 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4135542.3318 | 315221.4947 | 4843.3279 | 33710.1972 | 281511.2976 | 23896.3502 | 0.084965 | -184521.2818 | 184521.2818
C | Xist Rating 8969 | -6.24 | 1946.78 | 150.304 | 35.7 | 2137.26 | 8469.76 | 13111.7 | 0.43 | 1.64 | 23.759 | 21.792 | 1 | 1 | 2240 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4160775.0228 | 317903.0875 | 4886.8633 | 33861.364 | 284041.7235 | 23656.7548 | 0.085346 | -182671.19 | 182671.19
C | Xist Rating 8970 | -5.63 | 1962.65 | 150.304 | 35.7 | 2134.21 | 8459.29 | 13034 | 0.42 | 1.63 | 23.755 | 21.558 | 1 | 1 | 2250 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4188707.2565 | 320596.002 | 4930.5934 | 34012.5308 | 286583.4712 | 23394.194 | 0.085727 | -180643.7646 | 180643.7646
C | Xist Rating 8971 | -5.23 | 1970.72 | 150.304 | 35.7 | 2134.84 | 8487.98 | 12995.5 | 0.42 | 1.62 | 23.763 | 21.448 | 1 | 1 | 2260 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4207171.8848 | 323300.2383 | 4974.5182 | 34163.6976 | 289136.5408 | 23284.7717 | 0.086108 | -179798.835 | 179798.835
C | Xist Rating 8972 | -3.36 | 2019.82 | 150.304 | 35.7 | 2124.57 | 8446.97 | 12751.8 | 0.42 | 1.59 | 23.789 | 20.693 | 1 | 1 | 2270 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4291248.9774 | 326015.7965 | 5018.6379 | 34314.8644 | 291700.9321 | 22506.2902 | 0.086489 | -173787.6074 | 173787.6074
C | Xist Rating 8973 | -2.8 | 2034.18 | 150.304 | 35.7 | 2122.36 | 8445.27 | 12686.1 | 0.41 | 1.58 | 23.786 | 20.504 | 1 | 1 | 2280 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4317262.2648 | 328742.6765 | 5062.9524 | 34466.0312 | 294276.6453 | 22290.0545 | 0.08687 | -172117.8926 | 172117.8926
C | Xist Rating 8974 | -2.09 | 2051.28 | 150.304 | 35.7 | 2120.5 | 8456.49 | 12606.9 | 0.41 | 1.56 | 23.788 | 20.272 | 1 | 1 | 2290 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4349739.24 | 331480.8783 | 5107.4617 | 34617.198 | 296863.6803 | 22053.5785 | 0.087251 | -170291.8873 | 170291.8873
C | Xist Rating 8975 | -1.62 | 2062.64 | 150.304 | 35.7 | 2119.4 | 8464.82 | 12557 | 0.4 | 1.56 | 23.789 | 20.133 | 1 | 1 | 2300 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4371559.216 | 334230.4019 | 5152.1657 | 34768.3648 | 299462.0371 | 21889.1156 | 0.087632 | -169021.9483 | 169021.9483
| Xist Rating 8976 | -1.19 | 2074.27 | 150.304 | 35.7 | 2117.22 | 8456.01 | 12507.8 | 0.4 | 1.55 | 23.794 | 19.999 | 1 | 1 | 2310 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4391685.9294 | 336991.2473 | 5197.0645 | 34919.5316 | 302071.7157 | 21754.4292 | 0.088013 | -167981.9359 | 167981.9359
| Xist Rating 8977 | 0.7 | 2124.69 | 150.304 | 35.7 | 2107.03 | 8416.19 | 12277.3 | 0.4 | 1.51 | 23.82 | 19.318 | 1 | 1 | 2320 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4476785.5707 | 339763.4145 | 5242.1582 | 35070.6984 | 304692.7161 | 21052.5596 | 0.088394 | -162562.2844 | 162562.2844
| Xist Rating 8978 | 1.25 | 2139.09 | 150.304 | 35.7 | 2104.84 | 8413.99 | 12217 | 0.39 | 1.5 | 23.819 | 19.154 | 1 | 1 | 2330 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4502442.1956 | 342546.9036 | 5287.4466 | 35221.8652 | 307325.0384 | 20861.598 | 0.088775 | -161087.7301 | 161087.7301
| Xist Rating 8979 | 1.83 | 2153.46 | 150.304 | 35.7 | 2103.15 | 8419.7 | 12157.3 | 0.39 | 1.49 | 23.822 | 18.992 | 1 | 1 | 2340 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4529049.399 | 345341.7145 | 5332.9298 | 35373.032 | 309968.6825 | 20697.6479 | 0.089156 | -159821.7511 | 159821.7511
| Xist Rating 8980 | 2.34 | 2166.43 | 150.304 | 35.7 | 2101.61 | 8424.05 | 12104.8 | 0.38 | 1.49 | 23.825 | 18.852 | 1 | 1 | 2350 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4552990.9523 | 348147.8472 | 5378.6078 | 35524.1988 | 312623.6484 | 20531.4491 | 0.089537 | -158538.4078 | 158538.4078
| Xist Rating 8981 | 2.9 | 2182.34 | 150.304 | 35.7 | 2098.08 | 8403.67 | 12040 | 0.38 | 1.48 | 23.819 | 18.677 | 1 | 1 | 2360 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4578723.9072 | 350965.3017 | 5424.4805 | 35675.3656 | 315289.9361 | 20353.5289 | 0.089918 | -157164.5551 | 157164.5551
| Xist Rating 8982 | 4.58 | 2228.5 | 150.304 | 35.7 | 2088.67 | 8362.21 | 11847 | 0.38 | 1.45 | 23.842 | 18.135 | 1 | 1 | 2370 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4654601.095 | 353794.078 | 5470.5481 | 35826.5324 | 317967.5456 | 19795.6484 | 0.090299 | -152856.7499 | 152856.7499
| Xist Rating 8983 | 5.06 | 2243.11 | 150.304 | 35.7 | 2085.12 | 8337.34 | 11791.3 | 0.38 | 1.44 | 23.833 | 17.992 | 1 | 1 | 2380 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4677153.5232 | 356634.1761 | 5516.8105 | 35977.6992 | 320656.4769 | 19650.8394 | 0.09068 | -151738.5729 | 151738.5729
| Xist Rating 8984 | 5.65 | 2258.57 | 150.304 | 35.7 | 2082.96 | 8338.02 | 11730.2 | 0.37 | 1.43 | 23.831 | 17.83 | 1 | 1 | 2390 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 4704510.9672 | 359485.5961 | 5563.2676 | 36128.866 | 323356.7301 | 19461.0504 | 0.091061 | -150273.0728 | 150273.0728
C | Xist Rating 8986 | 17.02 | 2589.26 | 150.304 | 35.7 | 2013.11 | 7968.29 | 10538.3 | 0.41 | 1.25 | 23.795 | 14.748 | 1 | 1 | 2410 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5212465.1986 | 365222.4014 | 5656.7663 | 36431.1996 | 328791.2018 | 16369.6847 | 0.091823 | -126402.3658 | 126402.3658
C | Xist Rating 8987 | 17.12 | 2590.66 | 150.304 | 35.7 | 2014.16 | 7984.63 | 10538.4 | 0.4 | 1.25 | 23.835 | 14.76 | 1 | 1 | 2420 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5218003.7456 | 368107.7868 | 5703.8078 | 36582.3664 | 331525.4204 | 16362.4435 | 0.092204 | -126346.4518 | 126346.4518
C | Xist Rating 8988 | 17.23 | 2592.01 | 150.304 | 35.7 | 2015.56 | 8006.75 | 10538.3 | 0.39 | 1.25 | 23.837 | 14.771 | 1 | 1 | 2430 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5224351.6756 | 371004.4941 | 5751.0441 | 36733.5332 | 334270.9608 | 16352.2636 | 0.092585 | -126267.8447 | 126267.8447
C | Xist Rating 8989 | 17.34 | 2593.38 | 150.304 | 35.7 | 2016.82 | 8026.64 | 10538.3 | 0.38 | 1.25 | 23.837 | 14.782 | 1 | 1 | 2440 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5230380.6516 | 373912.5231 | 5798.4752 | 36884.7 | 337027.8231 | 16341.7831 | 0.092966 | -126186.9173 | 126186.9173
C | Xist Rating 8990 | 17.38 | 2594.71 | 150.304 | 35.7 | 2016.99 | 8029.28 | 10538.3 | 0.38 | 1.25 | 23.827 | 14.792 | 1 | 1 | 2450 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5233504.1229 | 376831.8739 | 5846.1011 | 37035.8668 | 339796.0071 | 16355.811 | 0.093347 | -126295.2371 | 126295.2371
C | Xist Rating 8991 | 17.37 | 2596.18 | 150.304 | 35.7 | 2016.21 | 8017.01 | 10538.3 | 0.37 | 1.25 | 23.819 | 14.803 | 1 | 1 | 2460 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5234444.0778 | 379762.5466 | 5893.9217 | 37187.0336 | 342575.513 | 16344.6929 | 0.093728 | -126209.3862 | 126209.3862
C | Xist Rating 8992 | 17.37 | 2597.54 | 150.304 | 35.7 | 2015.67 | 8008.44 | 10538.3 | 0.37 | 1.25 | 23.86 | 14.814 | 1 | 1 | 2470 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5235783.4518 | 382704.5411 | 5941.9372 | 37338.2005 | 345366.3406 | 16361.7464 | 0.094109 | -126341.0686 | 126341.0686
C | Xist Rating 8993 | 17.38 | 2598.88 | 150.304 | 35.7 | 2015.27 | 8002.17 | 10538.2 | 0.36 | 1.25 | 23.853 | 14.824 | 1 | 1 | 2480 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5237444.8976 | 385657.8574 | 5990.1474 | 37489.3673 | 348168.4901 | 16349.2844 | 0.09449 | -126244.8408 | 126244.8408
C | Xist Rating 8994 | 17.38 | 2600.28 | 150.304 | 35.7 | 2014.81 | 7994.97 | 10538.2 | 0.35 | 1.25 | 23.845 | 14.835 | 1 | 1 | 2490 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5239070.1468 | 388622.4955 | 6038.5525 | 37640.5341 | 350981.9615 | 16337.6214 | 0.094871 | -126154.7818 | 126154.7818
C | Xist Rating 8995 | 17.41 | 2601.27 | 150.304 | 35.7 | 2015.09 | 7999.33 | 10538.2 | 0.35 | 1.25 | 23.842 | 14.844 | 1 | 1 | 2500 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5241793.1643 | 391598.4554 | 6087.1523 | 37791.7009 | 353806.7546 | 16350.5912 | 0.095252 | -126254.931 | 126254.931
C | Xist Rating 8996 | 17.34 | 2603.12 | 150.304 | 35.7 | 2013.06 | 7967.52 | 10538.2 | 0.34 | 1.25 | 23.836 | 14.857 | 1 | 1 | 2510 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5240236.7472 | 394585.7372 | 6135.9469 | 37942.8677 | 356642.8695 | 16340.778 | 0.095633 | -126179.1563 | 126179.1563
C | Xist Rating 8997 | 17.36 | 2604.57 | 150.304 | 35.7 | 2012.42 | 7957.51 | 10538.3 | 0.34 | 1.25 | 23.874 | 14.868 | 1 | 1 | 2520 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5241488.7594 | 397584.3408 | 6184.9363 | 38094.0345 | 359490.3063 | 16357.2936 | 0.096014 | -126306.6854 | 126306.6854
C | Xist Rating 8998 | 17.37 | 2605.91 | 150.304 | 35.7 | 2012.02 | 7951.15 | 10538.3 | 0.33 | 1.25 | 23.868 | 14.878 | 1 | 1 | 2530 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5243143.0382 | 400594.2661 | 6234.1205 | 38245.2013 | 362349.0649 | 16344.0179 | 0.096395 | -126204.1739 | 126204.1739
C | Xist Rating 8999 | 17.46 | 2607.06 | 150.304 | 35.7 | 2012.5 | 7958.52 | 10538.4 | 0.33 | 1.25 | 23.864 | 14.887 | 1 | 1 | 2540 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5246708.25 | 403615.5133 | 6283.4995 | 38396.3681 | 365219.1453 | 16356.7447 | 0.096776 | -126302.4468 | 126302.4468
C | Xist Rating 9000 | 17.44 | 2608.61 | 150.304 | 35.7 | 2012.48 | 7958.4 | 10538.2 | 0.32 | 1.25 | 23.848 | 14.898 | 1 | 1 | 2550 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5249775.4528 | 406648.0823 | 6333.0732 | 38547.5349 | 368100.5475 | 16343.8357 | 0.097157 | -126202.767 | 126202.767
C | Xist Rating 9001 | 17.45 | 2610.05 | 150.304 | 35.7 | 2012.04 | 7951.53 | 10538.2 | 0.32 | 1.25 | 23.842 | 14.909 | 1 | 1 | 2560 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5251525.002 | 409691.9732 | 6382.8418 | 38698.7017 | 370993.2715 | 16358.4596 | 0.097538 | -126315.6888 | 126315.6888
C | Xist Rating 9002 | 17.42 | 2611.44 | 150.304 | 35.7 | 2011.05 | 7936.17 | 10538.1 | 0.31 | 1.25 | 23.86 | 14.919 | 1 | 1 | 2570 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5251736.412 | 412747.1858 | 6432.8051 | 38849.8685 | 373897.3173 | 16345.4414 | 0.097919 | -126215.166 | 126215.166
C | Xist Rating 9003 | 17.44 | 2612.81 | 150.304 | 35.7 | 2010.8 | 7932.32 | 10538.1 | 0.31 | 1.25 | 23.899 | 14.929 | 1 | 1 | 2580 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 33 | E | Rod | 5253838.348 | 415813.7203 | 6482.9633 | 39001.0353 | 376812.685 | 16360.5401 | 0.0983 | -126331.7539 | 126331.7539
C | Xist Rating 9004 | 17.43 | 2614.17 | 150.304 | 35.7 | 2010.19 | 7922.87 | 10538.1 | 0.3 | 1.25 | 23.892 | 14.94 | 1 | 1 | 2590 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5254978.3923 | 418891.5766 | 6533.3162 | 39152.2021 | 379739.3745 | 16347.2949 | 0.098681 | -126229.4784 | 126229.4784
C | Xist Rating 9005 | 17.47 | 2615.35 | 150.304 | 35.7 | 2010.41 | 7926.29 | 10538.1 | 0.3 | 1.25 | 23.894 | 14.949 | 1 | 1 | 2600 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5257925.7935 | 421980.7547 | 6583.8639 | 39303.3689 | 382677.3858 | 16359.9242 | 0.099062 | -126326.9982 | 126326.9982
C | Xist Rating 9006 | 17.47 | 2617.03 | 150.304 | 35.6 | 2009.58 | 7913.27 | 10538 | 0.3 | 1.25 | 23.894 | 14.96 | 1 | 1 | 2610 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5259131.1474 | 425081.2546 | 6634.6064 | 39454.5357 | 385626.7189 | 16374.5608 | 0.099443 | -126440.0182 | 126440.0182
C | Xist Rating 9007 | 17.48 | 2618.43 | 150.304 | 35.6 | 2009.21 | 7907.57 | 10538 | 0.29 | 1.25 | 23.894 | 14.971 | 1 | 1 | 2620 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5260975.7403 | 428193.0763 | 6685.5437 | 39605.7025 | 388587.3738 | 16361.1362 | 0.099824 | -126336.3566 | 126336.3566
C | Xist Rating 9008 | 17.5 | 2619.86 | 150.304 | 35.6 | 2008.9 | 7902.78 | 10538 | 0.29 | 1.25 | 23.932 | 14.981 | 1 | 1 | 2630 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5263036.754 | 431316.2198 | 6736.6758 | 39756.8693 | 391559.3505 | 16375.9263 | 0.10021 | -126450.5621 | 126450.5621
C | Xist Rating 9009 | 17.55 | 2621.1 | 150.304 | 35.6 | 2009.17 | 7907.05 | 10538 | 0.28 | 1.25 | 23.937 | 14.99 | 1 | 1 | 2640 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5266235.487 | 434450.6852 | 6788.0027 | 39908.0361 | 394542.6491 | 16360.229 | 0.10059 | -126329.3516 | 126329.3516
C | Xist Rating 9010 | 17.56 | 2622.61 | 150.304 | 35.6 | 2008.61 | 7898.38 | 10538 | 0.28 | 1.25 | 23.933 | 15.001 | 1 | 1 | 2650 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5267800.6721 | 437596.4724 | 6839.5243 | 40059.2029 | 397537.2695 | 16374.5237 | 0.10097 | -126439.7319 | 126439.7319
C | Xist Rating 9011 | 17.58 | 2623.95 | 150.304 | 35.6 | 2008.58 | 7897.84 | 10538 | 0.28 | 1.25 | 23.934 | 15.011 | 1 | 1 | 2660 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5270413.491 | 440753.5814 | 6891.2408 | 40210.3697 | 400543.2116 | 16387.9459 | 0.10135 | -126543.3744 | 126543.3744
C | Xist Rating 9012 | 17.61 | 2625.33 | 150.304 | 35.6 | 2008.5 | 7896.65 | 10538 | 0.27 | 1.25 | 23.934 | 15.021 | 1 | 1 | 2670 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5272975.305 | 443922.0122 | 6943.152 | 40361.5365 | 403560.4756 | 16372.6902 | 0.10173 | -126425.5737 | 126425.5737
C | Xist Rating 9013 | 17.67 | 2626.75 | 150.304 | 35.6 | 2008.78 | 7901.02 | 10538 | 0.27 | 1.25 | 23.975 | 15.031 | 1 | 1 | 2680 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5276562.865 | 447101.7648 | 6995.258 | 40512.7033 | 406589.0615 | 16387.3017 | 0.10211 | -126538.3996 | 126538.3996
C | Xist Rating 9014 | 17.72 | 2628.13 | 150.305 | 35.6 | 2009.05 | 7905.2 | 10538 | 0.26 | 1.25 | 23.976 | 15.041 | 1 | 1 | 2690 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5280044.5765 | 450292.8392 | 7047.5588 | 40663.8701 | 409628.9691 | 16371.711 | 0.10249 | -126418.0123 | 126418.0123
C | Xist Rating 9015 | 17.81 | 2629.33 | 150.305 | 35.6 | 2010.32 | 7924.83 | 10538 | 0.26 | 1.25 | 23.982 | 15.05 | 1 | 1 | 2700 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5285794.6856 | 453495.2355 | 7100.0544 | 40815.0369 | 412680.1985 | 16384.0405 | 0.10287 | -126513.2178 | 126513.2178
C | Xist Rating 9016 | 17.87 | 2630.98 | 150.305 | 35.6 | 2010.61 | 7929.48 | 10537.9 | 0.26 | 1.25 | 23.98 | 15.061 | 1 | 1 | 2710 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5289874.6978 | 456708.9535 | 7152.7448 | 40966.2037 | 415742.7498 | 16398.1958 | 0.10325 | -126622.5211 | 126622.5211
C | Xist Rating 9017 | 17.88 | 2632.33 | 150.305 | 35.6 | 2010.47 | 7927.19 | 10537.9 | 0.25 | 1.25 | 23.976 | 15.071 | 1 | 1 | 2720 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5292220.4951 | 459933.9934 | 7205.63 | 41117.3705 | 418816.6229 | 16382.0164 | 0.10363 | -126497.5884 | 126497.5884
C | Xist Rating 9018 | 17.88 | 2633.65 | 150.305 | 35.6 | 2009.93 | 7918.79 | 10538 | 0.25 | 1.25 | 24.012 | 15.08 | 1 | 1 | 2730 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5293452.1445 | 463170.3551 | 7258.71 | 41268.5373 | 421901.8178 | 16395.151 | 0.10402 | -126599.0104 | 126599.0104
C | Xist Rating 9019 | 17.87 | 2634.93 | 150.305 | 35.6 | 2009.24 | 7908.21 | 10538 | 0.25 | 1.25 | 24.007 | 15.089 | 1 | 1 | 2740 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5294206.7532 | 466418.0387 | 7311.9847 | 41419.7041 | 424998.3345 | 16407.0348 | 0.1044 | -126690.7739 | 126690.7739
C | Xist Rating 9020 | 17.84 | 2636.48 | 150.305 | 35.6 | 2008.1 | 7890.49 | 10537.9 | 0.25 | 1.25 | 24.001 | 15.1 | 1 | 1 | 2750 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5294315.488 | 469677.044 | 7365.4543 | 41570.8709 | 428106.173 | 16420.9637 | 0.10478 | -126798.3287 | 126798.3287
C | Xist Rating 9021 | 17.84 | 2637.91 | 150.305 | 35.6 | 2007.42 | 7879.94 | 10538 | 0.24 | 1.25 | 24 | 15.109 | 1 | 1 | 2760 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5295393.2922 | 472947.3711 | 7419.1186 | 41722.0378 | 431225.3334 | 16403.277 | 0.10516 | -126661.7567 | 126661.7567
C | Xist Rating 9022 | 17.81 | 2639.14 | 150.305 | 35.6 | 2006.62 | 7867.65 | 10537.9 | 0.24 | 1.25 | 23.996 | 15.118 | 1 | 1 | 2770 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5295751.1068 | 476229.0201 | 7472.9777 | 41873.2046 | 434355.8156 | 16415.0862 | 0.10554 | -126752.9441 | 126752.9441
C | Xist Rating 9023 | 17.82 | 2640.69 | 150.305 | 35.6 | 2005.97 | 7857.67 | 10538 | 0.24 | 1.25 | 24.041 | 15.129 | 1 | 1 | 2780 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5297144.9193 | 479521.9909 | 7527.0316 | 42024.3714 | 437497.6195 | 16430.4369 | 0.10592 | -126871.4787 | 126871.4787
C | Xist Rating 9024 | 17.81 | 2642.1 | 150.305 | 35.6 | 2005.47 | 7850.13 | 10537.9 | 0.23 | 1.25 | 24.012 | 15.138 | 1 | 1 | 2790 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5298652.287 | 482826.2835 | 7581.2803 | 42175.5382 | 440650.7453 | 16411.4697 | 0.1063 | -126725.0188 | 126725.0188
C | Xist Rating 9025 | 17.84 | 2643.07 | 150.305 | 35.6 | 2005.81 | 7855.35 | 10537.9 | 0.23 | 1.25 | 24.019 | 15.146 | 1 | 1 | 2800 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5301496.2367 | 486141.8979 | 7635.7238 | 42326.705 | 443815.193 | 16422.4553 | 0.10668 | -126809.8469 | 126809.8469
C | Xist Rating 9026 | 17.77 | 2644.82 | 150.305 | 35.6 | 2003.98 | 7827.4 | 10537.8 | 0.23 | 1.25 | 24.005 | 15.157 | 1 | 1 | 2810 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5300166.3836 | 489468.8341 | 7690.3621 | 42477.8718 | 446990.9624 | 16435.9495 | 0.10706 | -126914.0453 | 126914.0453
C | Xist Rating 9027 | 17.78 | 2646.29 | 150.305 | 35.6 | 2003.55 | 7820.8 | 10537.8 | 0.23 | 1.25 | 24.01 | 15.166 | 1 | 1 | 2820 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5301974.3295 | 492807.0922 | 7745.1952 | 42629.0386 | 450178.0536 | 16447.9162 | 0.10744 | -127006.4489 | 127006.4489
C | Xist Rating 9028 | 17.81 | 2647.66 | 150.305 | 35.6 | 2003.37 | 7818.08 | 10537.8 | 0.22 | 1.25 | 24.056 | 15.176 | 1 | 1 | 2830 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5304242.6142 | 496156.6721 | 7800.223 | 42780.2054 | 453376.4667 | 16431.6027 | 0.10783 | -126880.4805 | 126880.4805
C | Xist Rating 9029 | 17.79 | 2648.98 | 150.305 | 35.6 | 2002.55 | 7805.66 | 10537.8 | 0.22 | 1.25 | 24.051 | 15.185 | 1 | 1 | 2840 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5304714.899 | 499517.5737 | 7855.4457 | 42931.3722 | 456586.2016 | 16443.1814 | 0.10821 | -126969.8883 | 126969.8883
C | Xist Rating 9030 | 17.79 | 2650.42 | 150.305 | 35.6 | 2002.11 | 7798.9 | 10537.8 | 0.22 | 1.25 | 24.054 | 15.194 | 1 | 1 | 2850 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5306432.3862 | 502889.7972 | 7910.8631 | 43082.539 | 459807.2583 | 16454.984 | 0.10859 | -127061.0246 | 127061.0246
C | Xist Rating 9031 | 17.86 | 2651.83 | 150.305 | 35.6 | 2002.67 | 7807.45 | 10537.9 | 0.22 | 1.25 | 24.07 | 15.204 | 1 | 1 | 2860 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5310740.3861 | 506273.3426 | 7966.4753 | 43233.7058 | 463039.6368 | 16468.1923 | 0.10897 | -127163.0157 | 127163.0157
C | Xist Rating 9032 | 17.85 | 2653.02 | 150.305 | 35.6 | 2002.12 | 7799 | 10537.9 | 0.21 | 1.25 | 24.068 | 15.212 | 1 | 1 | 2870 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5311664.4024 | 509668.2097 | 8022.2824 | 43384.8726 | 466283.3371 | 16447.8546 | 0.10935 | -127005.9735 | 127005.9735
C | Xist Rating 9033 | 17.94 | 2654.53 | 150.305 | 35.6 | 2003.03 | 7812.82 | 10537.9 | 0.21 | 1.25 | 24.128 | 15.222 | 1 | 1 | 2880 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5317103.2259 | 513074.3986 | 8078.2842 | 43536.0394 | 469538.3592 | 16462.1318 | 0.10973 | -127116.2179 | 127116.2179
C | Xist Rating 9034 | 18.08 | 2655.87 | 150.305 | 35.6 | 2004.89 | 7841.18 | 10538 | 0.21 | 1.25 | 24.154 | 15.232 | 1 | 1 | 2890 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5324727.2043 | 516491.9094 | 8134.4807 | 43687.2062 | 472804.7032 | 16475.4953 | 0.11011 | -127219.4073 | 127219.4073
C | Xist Rating 9035 | 18.26 | 2657.26 | 150.305 | 35.6 | 2007.32 | 7878.35 | 10538.1 | 0.21 | 1.25 | 24.189 | 15.241 | 1 | 1 | 2900 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5333971.1432 | 519920.742 | 8190.8721 | 43838.373 | 476082.369 | 16488.0708 | 0.11049 | -127316.5126 | 127316.5126
C | Xist Rating 9036 | 18.24 | 2658.8 | 150.305 | 35.6 | 2006.46 | 7865.15 | 10538 | 0.2 | 1.25 | 24.187 | 15.251 | 1 | 1 | 2910 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5334775.848 | 523360.8964 | 8247.4583 | 43989.5398 | 479371.3566 | 16469.1285 | 0.11087 | -127170.2451 | 127170.2451
C | Xist Rating 9037 | 18.5 | 2660.19 | 150.305 | 35.6 | 2010.3 | 7924.41 | 10538.2 | 0.2 | 1.25 | 24.238 | 15.261 | 1 | 1 | 2920 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5347779.957 | 526812.3726 | 8304.2393 | 44140.7066 | 482671.666 | 16483.0169 | 0.11125 | -127277.4876 | 127277.4876
C | Xist Rating 9038 | 19.33 | 2661.57 | 150.305 | 35.6 | 2024.14 | 8143.85 | 10538.3 | 0.2 | 1.25 | 24.378 | 15.271 | 1 | 1 | 2930 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5387390.2998 | 530275.1706 | 8361.215 | 44291.8734 | 485983.2972 | 16499.2523 | 0.11164 | -127402.8524 | 127402.8524
C | Xist Rating 9039 | 19.85 | 2662.94 | 150.305 | 35.6 | 2032.54 | 8281.55 | 10538.4 | 0.19 | 1.25 | 24.435 | 15.281 | 1 | 1 | 2940 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5412532.0676 | 533749.2904 | 8418.3855 | 44443.0402 | 489306.2502 | 16481.1235 | 0.11202 | -127262.8671 | 127262.8671
C | Xist Rating 9040 | 20.29 | 2664.35 | 150.305 | 35.6 | 2039.58 | 8399.64 | 10538.4 | 0.19 | 1.25 | 24.485 | 15.291 | 1 | 1 | 2950 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5434154.973 | 537234.7321 | 8475.7509 | 44594.207 | 492640.5251 | 16494.8458 | 0.1124 | -127368.8267 | 127368.8267
C | Xist Rating 9041 | 20.57 | 2665.72 | 150.305 | 35.6 | 2043.77 | 8471.04 | 10538.4 | 0.19 | 1.25 | 24.514 | 15.3 | 1 | 1 | 2960 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5448118.5644 | 540731.4956 | 8533.311 | 44745.3738 | 495986.1218 | 16507.0086 | 0.11278 | -127462.7451 | 127462.7451
C | Xist Rating 9042 | 21.57 | 2667.11 | 150.305 | 35.6 | 2060.3 | 8762.66 | 10538.3 | 0.18 | 1.25 | 24.615 | 15.311 | 1 | 1 | 2970 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5495046.733 | 544239.5809 | 8591.0659 | 44896.5406 | 499343.0402 | 16490.3049 | 0.11316 | -127333.7632 | 127333.7632
C | Xist Rating 9043 | 21.58 | 2668.33 | 150.305 | 35.6 | 2060.1 | 8758.99 | 10538.3 | 0.18 | 1.25 | 24.65 | 15.32 | 1 | 1 | 2980 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5497026.633 | 547758.988 | 8649.0156 | 45047.7074 | 502711.2805 | 16502.479 | 0.11354 | -127427.7682 | 127427.7682
C | Xist Rating 9044 | 21.58 | 2669.89 | 150.305 | 35.6 | 2059.32 | 8744.94 | 10538.2 | 0.18 | 1.25 | 24.644 | 15.329 | 1 | 1 | 2990 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5498157.8748 | 551289.7169 | 8707.16 | 45198.8742 | 506090.8427 | 16513.6696 | 0.11392 | -127514.1791 | 127514.1791
C | Xist Rating 9045 | 21.57 | 2671.32 | 150.305 | 35.6 | 2058.56 | 8731.17 | 10538.3 | 0.18 | 1.25 | 24.636 | 15.339 | 1 | 1 | 3000 | 152.4 | 2 | 5.4 | 19.05 | 1.3333 | 32 | E | Rod | 5499072.4992 | 554831.7676 | 8765.4993 | 45350.041 | 509481.7266 | 16525.8493 | 0.1143 | -127608.2277 | 127608.2277
C | Xist Rating 9046 | -84.84 | 277.815 | 150.312 | 35.9 | 2338.74 | 6853.6 | 58745 | 2.49 | 10.95 | 27.06 | 643.211 | 1 | 1 | 1000 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 649737.0531 | 73054.0159 | 973.9444 | 15396.6189 | 57657.397 | 670993.8645 | 0.038101 | -5181236.7611 | 5181236.7611
C | Xist Rating 9047 | -84.71 | 280.671 | 150.312 | 35.9 | 2335.36 | 6831.88 | 58283.5 | 2.47 | 10.84 | 27.161 | 631.091 | 1 | 1 | 1010 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 655467.8266 | 74366.8958 | 993.5206 | 15550.5851 | 58816.3107 | 658424.2588 | 0.038482 | -5084177.5976 | 5084177.5976
C | Xist Rating 9048 | -83.58 | 302.432 | 150.312 | 35.9 | 2327.58 | 6820.62 | 54967 | 2.48 | 10.07 | 27.209 | 546.907 | 1 | 1 | 1020 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 703934.6746 | 75691.3071 | 1013.2917 | 15704.5512 | 59986.7559 | 571047.2407 | 0.038863 | -4409475.4248 | 4409475.4248
C | Xist Rating 9049 | -83.38 | 308.29 | 150.31 | 35.9 | 2312.22 | 6704.06 | 54177.8 | 2.4 | 9.89 | 26.526 | 528.428 | 1 | 1 | 1030 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 712834.3038 | 77027.25 | 1033.2576 | 15858.5174 | 61168.7325 | 551710.8967 | 0.039244 | -4260165.3015 | 4260165.3015
C | Xist Rating 9050 | -83.27 | 311.222 | 150.31 | 35.9 | 2306.62 | 6663.94 | 53793.7 | 2.35 | 9.8 | 26.379 | 519.592 | 1 | 1 | 1040 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 717870.8896 | 78374.7243 | 1053.4182 | 16012.4836 | 62362.2406 | 542485.328 | 0.039625 | -4188927.9061 | 4188927.9061
C | Xist Rating 9051 | -83.01 | 316.959 | 150.31 | 35.9 | 2300 | 6622.25 | 53042.7 | 2.32 | 9.63 | 26.275 | 502.302 | 1 | 1 | 1050 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 729005.7 | 79733.7301 | 1073.7737 | 16166.4498 | 63567.2802 | 524508.8749 | 0.040006 | -4050118.4998 | 4050118.4998
C | Xist Rating 9052 | -82.89 | 319.87 | 150.31 | 35.9 | 2295.76 | 6593.79 | 52676 | 2.29 | 9.54 | 26.227 | 494.081 | 1 | 1 | 1060 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 734344.7512 | 81104.2673 | 1094.3239 | 16320.416 | 64783.8513 | 515956.0278 | 0.040387 | -3984075.682 | 3984075.682
C | Xist Rating 9053 | -81.76 | 343.214 | 150.309 | 35.9 | 2282.25 | 6535.85 | 49856.5 | 2.27 | 8.9 | 25.952 | 432.258 | 1 | 1 | 1070 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 783300.1515 | 82486.3361 | 1115.0689 | 16474.3822 | 66011.9539 | 451724.763 | 0.040768 | -3488098.8807 | 3488098.8807
C | Xist Rating 9054 | -81.53 | 347.585 | 150.309 | 35.9 | 2282.35 | 6546.24 | 49379.8 | 2.22 | 8.79 | 25.807 | 422.502 | 1 | 1 | 1080 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 793310.6247 | 83879.9363 | 1136.0087 | 16628.3484 | 67251.5879 | 441541.1781 | 0.041149 | -3409463.9374 | 3409463.9374
C | Xist Rating 9055 | -81.2 | 353.402 | 150.308 | 35.9 | 2285.74 | 6586.97 | 48760.6 | 2.16 | 8.65 | 25.603 | 409.982 | 1 | 1 | 1090 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 807785.0875 | 85285.068 | 1157.1433 | 16782.3146 | 68502.7534 | 428467.6754 | 0.04153 | -3308513.815 | 3308513.815
C | Xist Rating 9056 | -80.9 | 357.741 | 150.308 | 35.9 | 2294.96 | 6674.04 | 48306.6 | 2.11 | 8.55 | 25.609 | 400.949 | 1 | 1 | 1100 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 821001.2854 | 86701.7312 | 1178.4727 | 16936.2808 | 69765.4504 | 419049.212 | 0.041911 | -3235786.9376 | 3235786.9376
C | Xist Rating 9057 | -80.73 | 360.84 | 150.307 | 35.9 | 2296.03 | 6689.65 | 48009.4 | 2.03 | 8.48 | 25.193 | 395.357 | 1 | 1 | 1110 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 828499.4652 | 88129.9258 | 1199.9969 | 17090.2469 | 71039.6789 | 413122.1977 | 0.042292 | -3190020.1037 | 3190020.1037
C | Xist Rating 9058 | -79.4 | 386.865 | 150.308 | 35.9 | 2289.57 | 6695.13 | 45447.6 | 2.08 | 7.92 | 25.551 | 345.938 | 1 | 1 | 1120 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 885754.4981 | 89569.652 | 1221.7158 | 17244.2131 | 72325.4389 | 361924.191 | 0.042673 | -2794682.6674 | 2794682.6674
C | Xist Rating 9059 | -79.21 | 389.918 | 150.307 | 35.9 | 2293.23 | 6733.12 | 45188.4 | 2.01 | 7.86 | 25.292 | 341.44 | 1 | 1 | 1130 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 894171.6551 | 91020.9096 | 1243.6296 | 17398.1793 | 73622.7303 | 357159.8844 | 0.043054 | -2757893.9549 | 2757893.9549
C | Xist Rating 9060 | -78.91 | 395.806 | 150.307 | 35.9 | 2292.33 | 6738.46 | 44680.7 | 1.95 | 7.75 | 24.885 | 332.46 | 1 | 1 | 1140 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 907317.968 | 92483.6987 | 1265.7381 | 17552.1455 | 74931.5532 | 347738.8551 | 0.043435 | -2685147.2635 | 2685147.2635
C | Xist Rating 9061 | -78.6 | 401.631 | 150.306 | 35.9 | 2293.02 | 6757.54 | 44185.6 | 1.91 | 7.64 | 24.795 | 323.785 | 1 | 1 | 1150 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 920947.9156 | 93958.0193 | 1288.0414 | 17706.1117 | 76251.9076 | 338691.4604 | 0.043816 | -2615285.68 | 2615285.68
C | Xist Rating 9062 | -78.32 | 407.534 | 150.306 | 35.9 | 2291.15 | 6754.47 | 43702.9 | 1.86 | 7.53 | 24.583 | 315.52 | 1 | 1 | 1160 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 35 | E | Rod | 933721.5241 | 95443.8714 | 1310.5395 | 17860.0779 | 77583.7935 | 330044.5332 | 0.044197 | -2548516.3999 | 2548516.3999
C | Xist Rating 9063 | -77.12 | 430.865 | 150.306 | 35.9 | 2286.94 | 6771.53 | 41831.8 | 1.88 | 7.13 | 24.693 | 283.791 | 1 | 1 | 1170 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 985362.4031 | 96941.2549 | 1333.2324 | 18014.0441 | 78927.2108 | 297151.1432 | 0.044578 | -2294522.362 | 2294522.362
C | Xist Rating 9064 | -77.01 | 432.484 | 150.306 | 35.9 | 2290.72 | 6808.01 | 41724.5 | 1.83 | 7.1 | 24.573 | 282.211 | 1 | 1 | 1180 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 990699.7485 | 98450.1699 | 1356.1201 | 18168.0103 | 80282.1596 | 295454.2048 | 0.044959 | -2281419.0535 | 2281419.0535
C | Xist Rating 9065 | -76.45 | 444.119 | 150.305 | 35.8 | 2285.95 | 6792.07 | 40885.5 | 1.78 | 6.92 | 24.356 | 268.912 | 1 | 1 | 1190 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1015233.8281 | 99970.6164 | 1379.2026 | 18321.9765 | 81648.64 | 281577.2299 | 0.04534 | -2174264.7316 | 2174264.7316
C | Xist Rating 9066 | -76.17 | 447.064 | 150.305 | 35.8 | 2298.34 | 6909.35 | 40681.6 | 1.75 | 6.88 | 24.413 | 265.797 | 1 | 1 | 1200 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1027505.0738 | 101502.5944 | 1402.4799 | 18475.9426 | 83026.6517 | 278327.803 | 0.045721 | -2149173.5184 | 2149173.5184
C | Xist Rating 9067 | -75.86 | 453.036 | 150.305 | 35.8 | 2297.86 | 6918.46 | 40281.3 | 1.69 | 6.8 | 24.233 | 259.74 | 1 | 1 | 1210 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1041013.303 | 103046.1038 | 1425.9519 | 18629.9088 | 84416.195 | 271960.8228 | 0.046102 | -2100009.3848 | 2100009.3848
C | Xist Rating 9068 | -74.6 | 479.416 | 150.305 | 35.8 | 2286.16 | 6874.02 | 38537.5 | 1.7 | 6.43 | 24.223 | 233.512 | 1 | 1 | 1220 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1096021.6826 | 104601.1448 | 1449.6188 | 18783.875 | 85817.2698 | 244753.7661 | 0.046483 | -1889923.7045 | 1889923.7045
C | Xist Rating 9069 | -74.23 | 485.239 | 150.305 | 35.8 | 2292.23 | 6942.52 | 38183.2 | 1.67 | 6.35 | 24.252 | 228.475 | 1 | 1 | 1230 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1112279.393 | 106167.7172 | 1473.4804 | 18937.8412 | 87229.876 | 239503.9125 | 0.046864 | -1849385.7269 | 1849385.7269
C | Xist Rating 9070 | -73.91 | 491.202 | 150.305 | 35.8 | 2292.82 | 6961.26 | 37835.7 | 1.62 | 6.28 | 24.127 | 223.668 | 1 | 1 | 1240 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1126237.7696 | 107745.8211 | 1497.5369 | 19091.8074 | 88654.0137 | 234451.3501 | 0.047245 | -1810371.1791 | 1810371.1791
C | Xist Rating 9071 | -73.71 | 494.291 | 150.304 | 35.8 | 2297.02 | 7006.93 | 37664.6 | 1.58 | 6.24 | 24.044 | 221.393 | 1 | 1 | 1250 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1135396.3128 | 109335.4565 | 1521.7881 | 19245.7736 | 90089.6829 | 232044.8641 | 0.047626 | -1791788.9325 | 1791788.9325
C | Xist Rating 9072 | -73.25 | 503.048 | 150.304 | 35.8 | 2297.3 | 7029.96 | 37161.2 | 1.55 | 6.14 | 23.983 | 214.473 | 1 | 1 | 1260 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1155652.1704 | 110936.6233 | 1546.2341 | 19399.7398 | 91536.8835 | 224829.4042 | 0.048007 | -1736073.0633 | 1736073.0633
C | Xist Rating 9073 | -72.01 | 528.024 | 150.304 | 35.8 | 2290.52 | 7025.41 | 35777.4 | 1.56 | 5.85 | 24.058 | 195.824 | 1 | 1 | 1270 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1209449.5325 | 112549.3217 | 1570.8749 | 19553.706 | 92995.6157 | 205499.4235 | 0.048388 | -1586812.0763 | 1586812.0763
C | Xist Rating 9074 | -71.71 | 534.056 | 150.304 | 35.8 | 2290.04 | 7034.39 | 35477.1 | 1.52 | 5.79 | 23.914 | 192.063 | 1 | 1 | 1280 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1223009.6022 | 114173.5515 | 1595.7105 | 19707.6722 | 94465.8793 | 201542.6818 | 0.048769 | -1556259.1661 | 1556259.1661
C | Xist Rating 9075 | -71.4 | 540.035 | 150.304 | 35.8 | 2290.3 | 7050.29 | 35182.5 | 1.48 | 5.73 | 23.853 | 188.393 | 1 | 1 | 1290 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1236842.1605 | 115809.3128 | 1620.7408 | 19861.6383 | 95947.6744 | 197687.1538 | 0.04915 | -1526487.8006 | 1526487.8006
C | Xist Rating 9076 | -70.94 | 548.771 | 150.304 | 35.8 | 2290.95 | 7076.72 | 34750.8 | 1.46 | 5.64 | 23.89 | 182.992 | 1 | 1 | 1300 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1257206.9224 | 117456.6055 | 1645.966 | 20015.6045 | 97441.001 | 192069.3966 | 0.049531 | -1483108.9689 | 1483108.9689
C | Xist Rating 9077 | -70.69 | 553.334 | 150.304 | 35.8 | 2292.25 | 7099.37 | 34539.4 | 1.43 | 5.59 | 23.843 | 180.465 | 1 | 1 | 1310 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1268379.8615 | 119115.4298 | 1671.3859 | 20169.5707 | 98945.8591 | 189414.7143 | 0.049912 | -1462610.2154 | 1462610.2154
C | Xist Rating 9078 | -69.45 | 578.408 | 150.304 | 35.8 | 2286.06 | 7098.99 | 33362.4 | 1.43 | 5.35 | 23.897 | 166.148 | 1 | 1 | 1320 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1322275.3925 | 120785.7855 | 1697.0007 | 20323.5369 | 100462.2486 | 174566.3846 | 0.050293 | -1347955.3494 | 1347955.3494
C | Xist Rating 9079 | -69.01 | 587.361 | 150.304 | 35.8 | 2284.47 | 7103.85 | 32979.3 | 1.39 | 5.28 | 23.77 | 161.766 | 1 | 1 | 1330 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1341808.5837 | 122467.6727 | 1722.8102 | 20477.5031 | 101990.1696 | 169963.4917 | 0.050674 | -1312413.0304 | 1312413.0304
C | Xist Rating 9080 | -68.52 | 596.212 | 150.303 | 35.8 | 2287.46 | 7153.21 | 32606.2 | 1.36 | 5.2 | 23.662 | 157.537 | 1 | 1 | 1340 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1363811.1015 | 124161.0914 | 1748.8145 | 20631.4693 | 103529.6221 | 165534.8373 | 0.051055 | -1278216.1355 | 1278216.1355
C | Xist Rating 9081 | -68.21 | 600.793 | 150.303 | 35.8 | 2293.15 | 7219.54 | 32423.3 | 1.33 | 5.16 | 23.617 | 155.544 | 1 | 1 | 1350 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1377708.4679 | 125866.0416 | 1775.0136 | 20785.4355 | 105080.6061 | 163432.957 | 0.051436 | -1261985.9729 | 1261985.9729
C | Xist Rating 9082 | -67.86 | 603.684 | 150.304 | 35.8 | 2307.66 | 7372.52 | 32302.7 | 1.32 | 5.14 | 23.724 | 154.203 | 1 | 1 | 1360 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1393097.4194 | 127582.5232 | 1801.4075 | 20939.4017 | 106643.1216 | 162048.6233 | 0.051817 | -1251296.5145 | 1251296.5145
C | Xist Rating 9083 | -66.32 | 639.16 | 150.303 | 35.8 | 2284.9 | 7228.5 | 30901.8 | 1.31 | 4.86 | 23.618 | 138.872 | 1 | 1 | 1370 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1460416.684 | 129310.5364 | 1827.9962 | 21093.3679 | 108217.1685 | 146118.3449 | 0.052198 | -1128287.1279 | 1128287.1279
C | Xist Rating 9084 | -66.21 | 642.313 | 150.303 | 35.8 | 2282.25 | 7208.87 | 30793.1 | 1.29 | 4.84 | 23.547 | 137.807 | 1 | 1 | 1380 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1465918.8443 | 131050.081 | 1854.7797 | 21247.334 | 109802.7469 | 144991.3279 | 0.052579 | -1119584.6007 | 1119584.6007
C | Xist Rating 9085 | -65.8 | 649.808 | 150.303 | 35.8 | 2283.77 | 7241.19 | 30526.1 | 1.26 | 4.78 | 23.501 | 135.083 | 1 | 1 | 1390 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1484012.0162 | 132801.1571 | 1881.7579 | 21401.3002 | 111399.8568 | 142128.4489 | 0.05296 | -1097478.2082 | 1097478.2082
C | Xist Rating 9086 | -65.37 | 657.299 | 150.303 | 35.8 | 2286.51 | 7285.97 | 30264.8 | 1.23 | 4.73 | 23.485 | 132.442 | 1 | 1 | 1400 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1502920.7365 | 134563.7646 | 1908.931 | 21555.2664 | 113008.4982 | 139353.5689 | 0.053341 | -1076051.3204 | 1076051.3204
C | Xist Rating 9087 | -64.92 | 666.211 | 150.303 | 35.8 | 2287.05 | 7312.34 | 29956.8 | 1.21 | 4.67 | 23.441 | 129.358 | 1 | 1 | 1410 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1523657.8676 | 136337.9037 | 1936.2988 | 21709.2326 | 114628.6711 | 136130.7368 | 0.053722 | -1051165.4654 | 1051165.4654
C | Xist Rating 9088 | -63.62 | 692.833 | 150.303 | 35.8 | 2280.51 | 7309.24 | 29051.2 | 1.22 | 4.49 | 23.518 | 120.321 | 1 | 1 | 1420 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1580012.5848 | 138123.5742 | 1963.8614 | 21863.1988 | 116260.3754 | 126779.4403 | 0.054103 | -978957.2324 | 978957.2324
C | Xist Rating 9089 | -63.34 | 697.654 | 150.303 | 35.8 | 2282.96 | 7344.87 | 28910.3 | 1.18 | 4.47 | 23.433 | 119.062 | 1 | 1 | 1430 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1592716.1758 | 139920.7762 | 1991.6188 | 22017.165 | 117903.6112 | 125418.1033 | 0.054484 | -968445.3487 | 968445.3487
C | Xist Rating 9090 | -62.74 | 709.458 | 150.303 | 35.8 | 2282.42 | 7367.1 | 28541.5 | 1.16 | 4.39 | 23.416 | 115.581 | 1 | 1 | 1440 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1619281.1284 | 141729.5097 | 2019.571 | 22171.1312 | 119558.3785 | 121783.961 | 0.054865 | -940383.4654 | 940383.4654
C | Xist Rating 9091 | -62.36 | 716.987 | 150.303 | 35.7 | 2283.01 | 7390.73 | 28316.2 | 1.14 | 4.35 | 23.372 | 113.52 | 1 | 1 | 1450 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1636888.4909 | 143549.7746 | 2047.718 | 22325.0974 | 121224.6773 | 119622.0923 | 0.055246 | -923690.0882 | 923690.0882
C | Xist Rating 9092 | -61.98 | 721.449 | 150.303 | 35.7 | 2292.07 | 7497.24 | 28183.4 | 1.13 | 4.32 | 23.431 | 112.312 | 1 | 1 | 1460 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1653611.6094 | 145381.5711 | 2076.0598 | 22479.0635 | 122902.5075 | 118368.5969 | 0.055627 | -914010.9291 | 914010.9291
C | Xist Rating 9093 | -60.66 | 751.391 | 150.303 | 35.7 | 2277.54 | 7415.13 | 27310 | 1.11 | 4.16 | 23.386 | 104.375 | 1 | 1 | 1470 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1711323.0581 | 147224.899 | 2104.5964 | 22633.0297 | 124591.8693 | 110103.7334 | 0.056008 | -850191.8443 | 850191.8443
C | Xist Rating 9094 | -60.19 | 760.347 | 150.303 | 35.7 | 2278.55 | 7446.83 | 27065.8 | 1.1 | 4.11 | 23.373 | 102.261 | 1 | 1 | 1480 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1732488.6569 | 149079.7584 | 2133.3277 | 22786.9959 | 126292.7625 | 107903.5205 | 0.056389 | -833202.3833 | 833202.3833
C | Xist Rating 9095 | -59.78 | 767.877 | 150.303 | 35.7 | 2279.76 | 7477.47 | 26866 | 1.08 | 4.07 | 23.357 | 100.564 | 1 | 1 | 1490 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1750575.2695 | 150946.1493 | 2162.2539 | 22940.9621 | 128005.1872 | 106120.3381 | 0.05677 | -819433.1212 | 819433.1212
C | Xist Rating 9096 | -59.41 | 775.5 | 150.303 | 35.7 | 2279.28 | 7489.87 | 26669.5 | 1.06 | 4.03 | 23.314 | 98.924 | 1 | 1 | 1500 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1767581.64 | 152824.0717 | 2191.3748 | 23094.9283 | 129729.1433 | 104394.0342 | 0.057151 | -806103.0603 | 806103.0603
C | Xist Rating 9097 | -58.94 | 784.483 | 150.303 | 35.7 | 2280.08 | 7519.84 | 26437.9 | 1.04 | 3.99 | 23.304 | 96.986 | 1 | 1 | 1510 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1788683.9986 | 154713.5255 | 2220.6906 | 23248.8945 | 131464.631 | 102360.2375 | 0.057532 | -790398.6214 | 790398.6214
C | Xist Rating 9098 | -57.53 | 814.108 | 150.303 | 35.7 | 2273.7 | 7522.93 | 25679.6 | 1.05 | 3.84 | 23.319 | 90.632 | 1 | 1 | 1520 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1851037.3596 | 156614.5108 | 2250.2011 | 23402.8607 | 133211.6501 | 95789.4333 | 0.057913 | -739660.6127 | 739660.6127
C | Xist Rating 9099 | -57.12 | 823.435 | 150.302 | 35.7 | 2270.27 | 7506.47 | 25467.1 | 1.02 | 3.8 | 23.239 | 88.987 | 1 | 1 | 1530 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1869419.7774 | 158527.0276 | 2279.9064 | 23556.8269 | 134970.2007 | 94038.5047 | 0.058294 | -726140.4063 | 726140.4063
C | Xist Rating 9100 | -56.78 | 828.172 | 150.302 | 35.7 | 2276.2 | 7582.41 | 25362.3 | 1 | 3.78 | 23.227 | 88.199 | 1 | 1 | 1540 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1885085.1064 | 160451.0759 | 2309.8065 | 23710.7931 | 136740.2828 | 93197.881 | 0.058675 | -719649.3327 | 719649.3327
C | Xist Rating 9101 | -56.02 | 842.993 | 150.302 | 35.7 | 2276.31 | 7619.52 | 25020 | 0.99 | 3.72 | 23.224 | 85.508 | 1 | 1 | 1550 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1918913.3958 | 162386.6556 | 2339.9013 | 23864.7592 | 138521.8964 | 90397.3491 | 0.059056 | -698024.3679 | 698024.3679
C | Xist Rating 9102 | -55.59 | 847.504 | 150.302 | 35.7 | 2287.23 | 7754.43 | 24919.2 | 0.98 | 3.7 | 23.276 | 84.747 | 1 | 1 | 1560 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 1938436.5739 | 164333.7669 | 2370.191 | 24018.7254 | 140315.0414 | 89604.6815 | 0.059437 | -691903.5989 | 691903.5989
C | Xist Rating 9103 | -54.16 | 882.091 | 150.302 | 35.7 | 2268.8 | 7630.02 | 24160.9 | 0.97 | 3.56 | 23.235 | 78.955 | 1 | 1 | 1570 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2001288.0608 | 166292.4096 | 2400.6755 | 24172.6916 | 142119.718 | 83580.7441 | 0.059818 | -645388.3515 | 645388.3515
C | Xist Rating 9104 | -53.69 | 889.742 | 150.302 | 35.7 | 2272.82 | 7693.78 | 24006.3 | 0.95 | 3.53 | 23.231 | 77.845 | 1 | 1 | 1580 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2022223.4124 | 168262.5838 | 2431.3547 | 24326.6578 | 143935.926 | 82404.9329 | 0.0602 | -636309.0488 | 636309.0488
C | Xist Rating 9105 | -53.22 | 897.429 | 150.302 | 35.7 | 2276.12 | 7750 | 23854.3 | 0.93 | 3.5 | 23.23 | 76.765 | 1 | 1 | 1590 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2042656.0955 | 170244.2895 | 2462.2288 | 24480.624 | 145763.6655 | 81260.0669 | 0.060581 | -627468.6967 | 627468.6967
C | Xist Rating 9106 | -52.61 | 907.864 | 150.302 | 35.7 | 2280.11 | 7822.58 | 23644.7 | 0.92 | 3.46 | 23.245 | 75.256 | 1 | 1 | 1600 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2070029.785 | 172237.5266 | 2493.2976 | 24634.5902 | 147602.9364 | 79686.9859 | 0.060962 | -615321.7826 | 615321.7826
C | Xist Rating 9107 | -52.33 | 912.796 | 150.302 | 35.7 | 2282.06 | 7856.83 | 23555.9 | 0.9 | 3.45 | 23.216 | 74.673 | 1 | 1 | 1610 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2083055.2398 | 174242.2953 | 2524.5612 | 24788.5564 | 149453.7389 | 79055.6929 | 0.061343 | -610447.1056 | 610447.1056
C | Xist Rating 9108 | -50.61 | 951.558 | 150.302 | 35.7 | 2268.51 | 7795.08 | 22804.4 | 0.9 | 3.31 | 23.25 | 69.341 | 1 | 1 | 1620 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2158618.8386 | 176258.5954 | 2556.0196 | 24942.5226 | 151316.0728 | 73530.0073 | 0.061724 | -567779.2254 | 567779.2254
C | Xist Rating 9109 | -50.21 | 956.145 | 150.302 | 35.7 | 2276.67 | 7903.68 | 22722.7 | 0.89 | 3.29 | 23.28 | 68.805 | 1 | 1 | 1630 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2176826.6371 | 178286.427 | 2587.6728 | 25096.4888 | 153189.9382 | 72967.7151 | 0.062105 | -563437.3541 | 563437.3541
C | Xist Rating 9110 | -49.79 | 963.979 | 150.302 | 35.7 | 2277.88 | 7937.22 | 22587.9 | 0.87 | 3.27 | 23.253 | 67.93 | 1 | 1 | 1640 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2195828.4845 | 180325.79 | 2619.5208 | 25250.4549 | 155075.3351 | 72032.3621 | 0.062486 | -556214.8062 | 556214.8062
C | Xist Rating 9111 | -49.25 | 974.771 | 150.302 | 35.7 | 2277.68 | 7961.46 | 22402.4 | 0.85 | 3.23 | 23.224 | 66.719 | 1 | 1 | 1650 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2220216.4113 | 182376.6846 | 2651.5635 | 25404.4211 | 156972.2635 | 70747.5893 | 0.062867 | -546294.1312 | 546294.1312
C | Xist Rating 9112 | -48.65 | 985.32 | 150.302 | 35.7 | 2280.69 | 8025.33 | 22220.2 | 0.84 | 3.2 | 23.235 | 65.524 | 1 | 1 | 1660 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2247209.4708 | 184439.1106 | 2683.8011 | 25558.3873 | 158880.7233 | 69498.839 | 0.063248 | -536651.6129 | 536651.6129
C | Xist Rating 9113 | -47.15 | 1019.95 | 150.302 | 35.7 | 2267.78 | 7955.82 | 21632.5 | 0.84 | 3.09 | 23.252 | 61.677 | 1 | 1 | 1670 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2313022.211 | 186513.0681 | 2716.2334 | 25712.3535 | 160800.7146 | 65513.5532 | 0.063629 | -505878.292 | 505878.292
C | Xist Rating 9114 | -46.76 | 1024.65 | 150.302 | 35.7 | 2274.89 | 8055.61 | 21560 | 0.83 | 3.08 | 23.269 | 61.243 | 1 | 1 | 1680 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2330966.0385 | 188598.5571 | 2748.8606 | 25866.3197 | 162732.2374 | 65055.1524 | 0.06401 | -502338.6428 | 502338.6428
C | Xist Rating 9115 | -46.15 | 1038.45 | 150.302 | 35.7 | 2270.78 | 8038.74 | 21345.7 | 0.81 | 3.04 | 23.231 | 59.924 | 1 | 1 | 1690 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2358091.491 | 190695.5776 | 2781.6825 | 26020.2859 | 164675.2917 | 63656.4442 | 0.064391 | -491538.1885 | 491538.1885
C | Xist Rating 9116 | -45.65 | 1047.59 | 150.302 | 35.7 | 2272.78 | 8087.14 | 21205.4 | 0.8 | 3.02 | 23.236 | 59.071 | 1 | 1 | 1700 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2380941.6002 | 192804.1295 | 2814.6992 | 26174.2521 | 166629.8775 | 62761.6421 | 0.064772 | -484628.7638 | 484628.7638
C | Xist Rating 9117 | -45.12 | 1058.33 | 150.302 | 35.7 | 2272.32 | 8108.54 | 21044.4 | 0.79 | 2.99 | 23.224 | 58.103 | 1 | 1 | 1710 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2404864.4256 | 194924.213 | 2847.9107 | 26328.2183 | 168595.9947 | 61746.1709 | 0.065153 | -476787.5646 | 476787.5646
C | Xist Rating 9118 | -43.71 | 1090.16 | 150.302 | 35.7 | 2263.17 | 8075.09 | 20566.8 | 0.79 | 2.9 | 23.25 | 55.202 | 1 | 1 | 1720 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2467217.4072 | 197055.8279 | 2881.317 | 26482.1845 | 170573.6434 | 58743.2945 | 0.065534 | -453600.1494 | 453600.1494
C | Xist Rating 9119 | -43.06 | 1103.83 | 150.302 | 35.7 | 2261.65 | 8090.22 | 20374.1 | 0.78 | 2.87 | 23.239 | 54.083 | 1 | 1 | 1730 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2496477.1195 | 199198.9743 | 2914.9181 | 26636.1506 | 172562.8236 | 57570.753 | 0.065915 | -444546.0946 | 444546.0946
C | Xist Rating 9120 | -42.65 | 1110.1 | 150.302 | 35.7 | 2265.6 | 8156.62 | 20289.7 | 0.76 | 2.85 | 23.244 | 53.615 | 1 | 1 | 1740 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2515042.56 | 201353.6521 | 2948.714 | 26790.1168 | 174563.5353 | 57056.9068 | 0.066296 | -440578.3102 | 440578.3102
C | Xist Rating 9121 | -42.09 | 1122.47 | 150.302 | 35.7 | 2263.18 | 8156.4 | 20123.2 | 0.75 | 2.82 | 23.22 | 52.677 | 1 | 1 | 1750 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2540351.6546 | 203519.8615 | 2982.7046 | 26944.083 | 176575.7784 | 56071.0685 | 0.066677 | -432965.9278 | 432965.9278
C | Xist Rating 9122 | -41.67 | 1131.73 | 150.302 | 35.7 | 2261.6 | 8159.26 | 20000.4 | 0.74 | 2.8 | 23.213 | 51.993 | 1 | 1 | 1760 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2559520.568 | 205697.6023 | 3016.8901 | 27098.0492 | 178599.5531 | 55349.8145 | 0.067058 | -427396.596 | 427396.596
C | Xist Rating 9123 | -40.03 | 1169.46 | 150.303 | 35.7 | 2250.62 | 8114.66 | 19497 | 0.74 | 2.71 | 23.248 | 49.141 | 1 | 1 | 1770 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2632010.0652 | 207886.8746 | 3051.2703 | 27252.0154 | 180634.8592 | 52397.7717 | 0.067439 | -404601.7041 | 404601.7041
C | Xist Rating 9124 | -39.55 | 1178.82 | 150.303 | 35.7 | 2251.66 | 8151.3 | 19382.7 | 0.73 | 2.69 | 23.239 | 48.538 | 1 | 1 | 1780 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2654301.8412 | 210087.6784 | 3085.8453 | 27405.9816 | 182681.6968 | 51760.1953 | 0.06782 | -399678.508 | 399678.508
C | Xist Rating 9125 | -39.19 | 1183.78 | 150.303 | 35.7 | 2255.96 | 8219.73 | 19326 | 0.72 | 2.68 | 23.232 | 48.257 | 1 | 1 | 1790 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2670560.3288 | 212300.0136 | 3120.6151 | 27559.9478 | 184740.0659 | 51456.931 | 0.068201 | -397336.7818 | 397336.7818
C | Xist Rating 9126 | -38.44 | 1200.49 | 150.303 | 35.7 | 2252.92 | 8222.27 | 19121.5 | 0.71 | 2.65 | 23.222 | 47.165 | 1 | 1 | 1800 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2704607.9308 | 214523.8804 | 3155.5797 | 27713.914 | 186809.9664 | 50311.0712 | 0.068582 | -388488.7555 | 388488.7555
C | Xist Rating 9127 | -38.22 | 1209.73 | 150.303 | 35.6 | 2246 | 8153.76 | 19012.3 | 0.7 | 2.63 | 23.509 | 46.585 | 1 | 1 | 1810 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2717053.58 | 216759.2786 | 3190.7391 | 27867.8802 | 188891.3985 | 49713.5915 | 0.068963 | -383875.1761 | 383875.1761
C | Xist Rating 9128 | -36.33 | 1247.72 | 150.303 | 35.7 | 2243.19 | 8214.63 | 18562.4 | 0.7 | 2.55 | 23.253 | 44.225 | 1 | 1 | 1820 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2798873.0268 | 219006.2083 | 3226.0933 | 28021.8463 | 190984.362 | 47255.4924 | 0.069344 | -364894.3866 | 364894.3866
C | Xist Rating 9129 | -36.61 | 1241.7 | 150.304 | 35.6 | 2247.65 | 8259.14 | 18631 | 0.69 | 2.56 | 23.573 | 44.582 | 1 | 1 | 1830 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2790907.005 | 221264.6695 | 3261.6423 | 28175.8125 | 193088.857 | 47632.5703 | 0.069725 | -367806.0821 | 367806.0821
C | Xist Rating 9130 | -36.08 | 1249.31 | 150.304 | 35.6 | 2251.83 | 8335.69 | 18545.2 | 0.69 | 2.55 | 23.608 | 44.151 | 1 | 1 | 1840 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2813233.7373 | 223534.6622 | 3297.386 | 28329.7787 | 195204.8834 | 47194.2602 | 0.070106 | -364421.5677 | 364421.5677
C | Xist Rating 9131 | -35.51 | 1261.81 | 150.304 | 35.6 | 2249.63 | 8337.38 | 18409.2 | 0.67 | 2.52 | 23.593 | 43.479 | 1 | 1 | 1850 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2838605.6303 | 225816.1863 | 3333.3246 | 28483.7449 | 197332.4414 | 46463.7035 | 0.070487 | -358780.402 | 358780.402
C | Xist Rating 9132 | -34.88 | 1275.82 | 150.304 | 35.6 | 2246.99 | 8336.8 | 18259 | 0.66 | 2.5 | 23.576 | 42.74 | 1 | 1 | 1860 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2866754.7818 | 228109.2419 | 3369.4579 | 28637.7111 | 199471.5308 | 45682.7329 | 0.070868 | -352749.9539 | 352749.9539
C | Xist Rating 9133 | -33.31 | 1310.73 | 150.304 | 35.6 | 2240.46 | 8339.59 | 17879.5 | 0.66 | 2.43 | 23.629 | 40.84 | 1 | 1 | 1870 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2936638.1358 | 230413.829 | 3405.7861 | 28791.6773 | 201622.1517 | 43719.4927 | 0.071249 | -337590.3342 | 337590.3342
C | Xist Rating 9134 | -32.68 | 1324.72 | 150.304 | 35.6 | 2237.73 | 8337.28 | 17738.7 | 0.65 | 2.41 | 23.615 | 40.176 | 1 | 1 | 1880 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2964365.6856 | 232729.9476 | 3442.309 | 28945.6435 | 203784.3041 | 43016.2412 | 0.07163 | -332160.0119 | 332160.0119
C | Xist Rating 9135 | -32.15 | 1334.01 | 150.304 | 35.7 | 2239.7 | 8388.36 | 17646.5 | 0.64 | 2.39 | 23.636 | 39.746 | 1 | 1 | 1890 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 2987782.197 | 235057.5976 | 3479.0267 | 29099.6097 | 205957.988 | 42557.6996 | 0.072011 | -328619.2758 | 328619.2758
C | Xist Rating 9136 | -31.73 | 1343.76 | 150.304 | 35.6 | 2237.9 | 8387.12 | 17554.8 | 0.63 | 2.38 | 23.62 | 39.337 | 1 | 1 | 1900 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3007200.504 | 237396.7792 | 3515.9392 | 29253.5759 | 208143.2033 | 42118.7459 | 0.072392 | -325229.7915 | 325229.7915
C | Xist Rating 9137 | -31.2 | 1353.22 | 150.304 | 35.7 | 2239.81 | 8438.01 | 17464.8 | 0.62 | 2.36 | 23.632 | 38.928 | 1 | 1 | 1910 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3030955.6882 | 239747.4922 | 3553.0464 | 29407.542 | 210339.9502 | 41681.0849 | 0.072773 | -321850.2894 | 321850.2894
C | Xist Rating 9138 | -29.38 | 1395.6 | 150.304 | 35.7 | 2229.47 | 8404.75 | 17050.1 | 0.62 | 2.29 | 23.685 | 36.974 | 1 | 1 | 1920 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3111448.332 | 242109.7367 | 3590.3485 | 29561.5082 | 212548.2285 | 39661.2547 | 0.073154 | -306253.6957 | 306253.6957
C | Xist Rating 9139 | -28.78 | 1409.68 | 150.304 | 35.7 | 2226.53 | 8398.52 | 16923.6 | 0.61 | 2.27 | 23.676 | 36.416 | 1 | 1 | 1930 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3138694.8104 | 244483.5127 | 3627.8454 | 29715.4744 | 214768.0382 | 39067.3897 | 0.073535 | -301668.0278 | 301668.0278
C | Xist Rating 9140 | -28.35 | 1414.27 | 150.304 | 35.7 | 2232.73 | 8499.58 | 16881.9 | 0.61 | 2.26 | 23.718 | 36.238 | 1 | 1 | 1940 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3157683.0571 | 246868.8201 | 3665.537 | 29869.4406 | 216999.3795 | 38891.2387 | 0.073916 | -300307.836 | 300307.836
C | Xist Rating 9141 | -27.94 | 1427.34 | 150.304 | 35.7 | 2225.7 | 8430.25 | 16771.8 | 0.59 | 2.24 | 23.676 | 35.773 | 1 | 1 | 1950 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3176830.638 | 249265.6591 | 3703.4235 | 30023.4068 | 219242.2523 | 38371.1932 | 0.074297 | -296292.1832 | 296292.1832
C | Xist Rating 9142 | -27.28 | 1442.81 | 150.304 | 35.7 | 2222.3 | 8420.98 | 16636.8 | 0.58 | 2.22 | 23.711 | 35.184 | 1 | 1 | 1960 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3206356.663 | 251674.0295 | 3741.5047 | 30177.373 | 221496.6565 | 37746.7618 | 0.074678 | -291470.489 | 291470.489
C | Xist Rating 9143 | -25.62 | 1480.92 | 150.304 | 35.7 | 2215.02 | 8416.46 | 16302.9 | 0.58 | 2.16 | 23.785 | 33.713 | 1 | 1 | 1970 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3280267.4184 | 254093.9314 | 3779.7807 | 30331.3392 | 223762.5922 | 36229.0851 | 0.075059 | -279751.3919 | 279751.3919
C | Xist Rating 9144 | -25.08 | 1491.89 | 150.304 | 35.7 | 2214.82 | 8441.13 | 16213.9 | 0.58 | 2.15 | 23.821 | 33.345 | 1 | 1 | 1980 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3304267.8098 | 256525.3647 | 3818.2515 | 30485.3054 | 226040.0594 | 35854.9545 | 0.07544 | -276862.4548 | 276862.4548
C | Xist Rating 9145 | -24.51 | 1506.16 | 150.304 | 35.7 | 2210.69 | 8416.48 | 16101.3 | 0.57 | 2.13 | 23.842 | 32.884 | 1 | 1 | 1990 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3329652.8504 | 258968.3296 | 3856.9171 | 30639.2716 | 228329.058 | 35362.219 | 0.075821 | -273057.6814 | 273057.6814
C | Xist Rating 9146 | -23.96 | 1517.25 | 150.304 | 35.7 | 2210.6 | 8442.48 | 16014.8 | 0.56 | 2.12 | 23.842 | 32.535 | 1 | 1 | 2000 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3354032.85 | 261422.8259 | 3895.7775 | 30793.2377 | 230629.5882 | 34984.5005 | 0.076202 | -270141.0394 | 270141.0394
C | Xist Rating 9147 | -23.55 | 1525.34 | 150.304 | 35.7 | 2211.36 | 8473.33 | 15953.6 | 0.55 | 2.11 | 23.849 | 32.295 | 1 | 1 | 2010 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3373075.8624 | 263888.8537 | 3934.8326 | 30947.2039 | 232941.6498 | 34720.1115 | 0.076583 | -268099.4973 | 268099.4973
C | Xist Rating 9148 | -21.76 | 1568.17 | 150.304 | 35.7 | 2201.62 | 8442.17 | 15614.7 | 0.55 | 2.05 | 23.887 | 30.887 | 1 | 1 | 2020 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3452514.4354 | 266366.413 | 3974.0826 | 31101.1701 | 235265.2429 | 33265.6777 | 0.076964 | -256868.7455 | 256868.7455
C | Xist Rating 9149 | -21.03 | 1583.58 | 150.304 | 35.7 | 2200.82 | 8469.39 | 15499.7 | 0.54 | 2.03 | 23.896 | 30.432 | 1 | 1 | 2030 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3485174.5356 | 268855.5038 | 4013.5273 | 31255.1363 | 237600.3675 | 32777.7564 | 0.077345 | -253101.1466 | 253101.1466
C | Xist Rating 9150 | -20.58 | 1593.53 | 150.304 | 35.7 | 2199.93 | 8479.77 | 15431.6 | 0.53 | 2.02 | 23.887 | 30.181 | 1 | 1 | 2040 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3505654.4529 | 271356.126 | 4053.1669 | 31409.1025 | 239947.0235 | 32500.5902 | 0.077726 | -250960.9424 | 250960.9424
C | Xist Rating 9151 | -19.97 | 1602.66 | 150.304 | 35.7 | 2204.78 | 8576.25 | 15364.2 | 0.53 | 2.01 | 23.919 | 29.918 | 1 | 1 | 2050 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3533512.7148 | 273868.2798 | 4093.0012 | 31563.0687 | 242305.2111 | 32234.6984 | 0.078107 | -248907.7966 | 248907.7966
C | Xist Rating 9152 | -19.45 | 1617.32 | 150.304 | 35.7 | 2199.17 | 8527.5 | 15264.3 | 0.52 | 1.99 | 23.897 | 29.545 | 1 | 1 | 2060 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3556761.6244 | 276391.965 | 4133.0303 | 31717.0349 | 244674.9301 | 31829.8781 | 0.078488 | -245781.8814 | 245781.8814
C | Xist Rating 9153 | -17.56 | 1663.26 | 150.304 | 35.7 | 2189.06 | 8495.31 | 14936.2 | 0.52 | 1.94 | 23.935 | 28.261 | 1 | 1 | 2070 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3640975.9356 | 278927.1817 | 4173.2542 | 31871.0011 | 247056.1806 | 30503.8497 | 0.078869 | -235542.6417 | 235542.6417
C | Xist Rating 9154 | -17.12 | 1673 | 150.304 | 35.7 | 2188.38 | 8508.43 | 14873.5 | 0.51 | 1.93 | 23.936 | 28.038 | 1 | 1 | 2080 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3661159.74 | 281473.9298 | 4213.6729 | 32024.9672 | 249448.9626 | 30255.5752 | 0.07925 | -233625.5318 | 233625.5318
C | Xist Rating 9155 | -16.54 | 1685.69 | 150.304 | 35.7 | 2187.53 | 8526.93 | 14790.9 | 0.5 | 1.91 | 23.948 | 27.738 | 1 | 1 | 2090 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3687497.4457 | 284032.2095 | 4254.2864 | 32178.9334 | 251853.276 | 29927.6356 | 0.079631 | -231093.2691 | 231093.2691
C | Xist Rating 9156 | -16 | 1698.4 | 150.304 | 35.7 | 2185.73 | 8531.02 | 14709.2 | 0.5 | 1.9 | 23.948 | 27.444 | 1 | 1 | 2100 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3712243.832 | 286602.0206 | 4295.0947 | 32332.8996 | 254269.121 | 29627.6844 | 0.080012 | -228777.1252 | 228777.1252
C | Xist Rating 9157 | -15.5 | 1709.58 | 150.304 | 35.7 | 2184.72 | 8543.05 | 14638.6 | 0.49 | 1.89 | 23.949 | 27.193 | 1 | 1 | 2110 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3734953.6176 | 289183.3632 | 4336.0977 | 32486.8658 | 256696.4974 | 29349.7849 | 0.080393 | -226631.2591 | 226631.2591
C | Xist Rating 9158 | -13.78 | 1752.85 | 150.304 | 35.7 | 2174.65 | 8500.26 | 14358.9 | 0.49 | 1.84 | 23.98 | 26.162 | 1 | 1 | 2120 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3811835.2525 | 291776.2373 | 4377.2956 | 32640.832 | 259135.4053 | 28285.7967 | 0.080774 | -218415.4242 | 218415.4242
C | Xist Rating 9159 | -13.13 | 1768.61 | 150.304 | 35.7 | 2172.05 | 8499.13 | 14263.7 | 0.48 | 1.83 | 23.977 | 25.829 | 1 | 1 | 2130 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3841509.3505 | 294380.6428 | 4418.6882 | 32794.7982 | 261585.8446 | 27922.2109 | 0.081155 | -215607.9115 | 215607.9115
C | Xist Rating 9160 | -12.58 | 1784.4 | 150.304 | 35.7 | 2166.97 | 8459.99 | 14169.7 | 0.48 | 1.81 | 23.973 | 25.504 | 1 | 1 | 2140 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3866741.268 | 296996.5799 | 4460.2756 | 32948.7644 | 264047.8155 | 27589.6736 | 0.081536 | -213040.1465 | 213040.1465
C | Xist Rating 9161 | -12.17 | 1792.63 | 150.304 | 35.7 | 2167.35 | 8484.92 | 14123.5 | 0.47 | 1.8 | 23.977 | 25.353 | 1 | 1 | 2150 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3885256.6305 | 299624.0484 | 4502.0578 | 33102.7306 | 266521.3178 | 27415.096 | 0.081917 | -211692.1046 | 211692.1046
C | Xist Rating 9162 | -11.66 | 1803.77 | 150.304 | 35.7 | 2167.17 | 8509.14 | 14059 | 0.47 | 1.79 | 23.982 | 25.136 | 1 | 1 | 2160 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3909076.2309 | 302263.0484 | 4544.0348 | 33256.6968 | 269006.3516 | 27195.0208 | 0.082298 | -209992.7419 | 209992.7419
C | Xist Rating 9163 | -9.89 | 1850.36 | 150.304 | 35.7 | 2155.61 | 8447.77 | 13785.9 | 0.46 | 1.75 | 24.012 | 24.185 | 1 | 1 | 2170 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 3988654.5196 | 304913.5799 | 4586.2066 | 33410.6629 | 271502.9169 | 26190.4764 | 0.082679 | -202235.9162 | 202235.9162
C | Xist Rating 9164 | -9.2 | 1865.89 | 150.304 | 35.7 | 2154.49 | 8468.34 | 13699 | 0.46 | 1.74 | 24.025 | 23.895 | 1 | 1 | 2180 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 4020041.3461 | 307575.6428 | 4628.5732 | 33564.6291 | 274011.0137 | 25894.8473 | 0.08306 | -199953.1468 | 199953.1468
C | Xist Rating 9165 | -8.72 | 1877.26 | 150.304 | 35.7 | 2153.19 | 8474.75 | 13638.9 | 0.45 | 1.73 | 24.025 | 23.703 | 1 | 1 | 2190 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 4042097.4594 | 310249.2373 | 4671.1346 | 33718.5953 | 276530.642 | 25676.825 | 0.083441 | -198269.6366 | 198269.6366
C | Xist Rating 9166 | -8.28 | 1889.03 | 150.304 | 35.7 | 2150.68 | 8462.42 | 13579.4 | 0.45 | 1.72 | 24.011 | 23.519 | 1 | 1 | 2200 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 4062699.0404 | 312934.3632 | 4713.8907 | 33872.5615 | 279061.8017 | 25489.9661 | 0.083822 | -196826.7619 | 196826.7619
C | Xist Rating 9167 | -7.63 | 1904.82 | 150.304 | 35.7 | 2148.45 | 8465.61 | 13495.3 | 0.44 | 1.7 | 24.014 | 23.247 | 1 | 1 | 2210 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 4092410.529 | 315631.0206 | 4756.8417 | 34026.5277 | 281604.4929 | 25188.6827 | 0.084203 | -194500.3312 | 194500.3312
C | Xist Rating 9168 | -5.82 | 1951.28 | 150.304 | 35.7 | 2138.83 | 8430.71 | 13246 | 0.44 | 1.66 | 24.055 | 22.423 | 1 | 1 | 2220 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 34 | E | Rod | 4173456.2024 | 318339.2095 | 4799.9874 | 34180.4939 | 284158.7156 | 24339.4914 | 0.084584 | -187943.1012 | 187943.1012
C | Xist Rating 9169 | -5.24 | 1963.94 | 150.304 | 35.7 | 2138.54 | 8456.09 | 13182.4 | 0.44 | 1.65 | 24.055 | 22.225 | 1 | 1 | 2230 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4199964.2476 | 321058.9298 | 4843.3279 | 34334.4601 | 286724.4698 | 24138.6131 | 0.084965 | -186391.9718 | 186391.9718
C | Xist Rating 9170 | -4.66 | 1978.57 | 150.304 | 35.7 | 2136.3 | 8454.73 | 13111.7 | 0.43 | 1.64 | 24.046 | 22.01 | 1 | 1 | 2240 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4226819.091 | 323790.1817 | 4886.8633 | 34488.4263 | 289301.7554 | 23895.5387 | 0.085346 | -184515.016 | 184515.016
C | Xist Rating 9171 | -4.04 | 1994.68 | 150.304 | 35.7 | 2133.29 | 8444.88 | 13034 | 0.42 | 1.63 | 24.042 | 21.773 | 1 | 1 | 2250 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4255230.8972 | 326532.965 | 4930.5934 | 34642.3925 | 291890.5725 | 23629.6282 | 0.085727 | -182461.7257 | 182461.7257
C | Xist Rating 9172 | -3.64 | 2002.87 | 150.304 | 35.7 | 2133.99 | 8474.55 | 12995.5 | 0.42 | 1.62 | 24.05 | 21.661 | 1 | 1 | 2260 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4274104.5513 | 329287.2798 | 4974.5182 | 34796.3586 | 294490.9211 | 23518.183 | 0.086108 | -181601.1753 | 181601.1753
C | Xist Rating 9173 | -1.74 | 2052.74 | 150.304 | 35.7 | 2123.62 | 8431.93 | 12751.8 | 0.42 | 1.59 | 24.077 | 20.897 | 1 | 1 | 2270 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4359239.7188 | 332053.1261 | 5018.6379 | 34950.3248 | 297102.8012 | 22730.4518 | 0.086489 | -175518.5239 | 175518.5239
C | Xist Rating 9174 | -1.17 | 2067.32 | 150.304 | 35.7 | 2121.36 | 8429.44 | 12686.2 | 0.41 | 1.58 | 24.074 | 20.705 | 1 | 1 | 2280 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4385529.9552 | 334830.5038 | 5062.9524 | 35104.291 | 299726.2128 | 22510.8605 | 0.08687 | -173822.8979 | 173822.8979
C | Xist Rating 9175 | -0.46 | 2084.69 | 150.304 | 35.7 | 2119.2 | 8435.87 | 12606.9 | 0.41 | 1.56 | 24.075 | 20.471 | 1 | 1 | 2290 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4417875.048 | 337619.413 | 5107.4617 | 35258.2572 | 302361.1558 | 22272.3183 | 0.087251 | -171980.9382 | 171980.9382
C | Xist Rating 9176 | -0.00803 | 2096.22 | 150.304 | 35.7 | 2117.66 | 8437.24 | 12557.1 | 0.4 | 1.56 | 24.082 | 20.33 | 1 | 1 | 2300 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4439081.2452 | 340419.8538 | 5152.1657 | 35412.2234 | 305007.6304 | 22105.7827 | 0.087632 | -170694.9944 | 170694.9944
| Xist Rating 9177 | 0.42 | 2108.01 | 150.304 | 35.7 | 2115.29 | 8425.17 | 12507.8 | 0.4 | 1.55 | 24.08 | 20.194 | 1 | 1 | 2310 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4459052.4729 | 343231.826 | 5197.0645 | 35566.1896 | 307665.6364 | 21968.7819 | 0.088013 | -169637.1109 | 169637.1109
| Xist Rating 9178 | 2.31 | 2159.24 | 150.304 | 35.7 | 2104.55 | 8376.85 | 12277.3 | 0.4 | 1.51 | 24.106 | 19.505 | 1 | 1 | 2320 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4544228.542 | 346055.3296 | 5242.1582 | 35720.1558 | 310335.1738 | 21258.6556 | 0.088394 | -164153.7033 | 164153.7033
| Xist Rating 9179 | 2.87 | 2173.84 | 150.304 | 35.7 | 2102.33 | 8374.14 | 12217 | 0.39 | 1.5 | 24.105 | 19.338 | 1 | 1 | 2330 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4570129.0472 | 348890.3648 | 5287.4466 | 35874.122 | 313016.2428 | 21064.3311 | 0.088775 | -162653.1814 | 162653.1814
| Xist Rating 9180 | 3.46 | 2188.43 | 150.304 | 35.7 | 2100.61 | 8379.15 | 12157.3 | 0.39 | 1.49 | 24.108 | 19.174 | 1 | 1 | 2340 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4597037.9423 | 351736.9314 | 5332.9298 | 36028.0882 | 315708.8433 | 20898.3541 | 0.089156 | -161371.5504 | 161371.5504
| Xist Rating 9181 | 3.99 | 2201.59 | 150.304 | 35.7 | 2099.37 | 8388.2 | 12104.9 | 0.38 | 1.49 | 24.112 | 19.032 | 1 | 1 | 2350 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4621951.9983 | 354595.0295 | 5378.6078 | 36182.0543 | 318412.9752 | 20729.867 | 0.089537 | -160070.538 | 160070.538
| Xist Rating 9182 | 4.55 | 2217.75 | 150.304 | 35.7 | 2095.81 | 8367.44 | 12040 | 0.38 | 1.48 | 24.106 | 18.855 | 1 | 1 | 2360 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4647982.6275 | 357464.6591 | 5424.4805 | 36336.0205 | 321128.6386 | 20549.9187 | 0.089918 | -158681.0247 | 158681.0247
| Xist Rating 9183 | 6.26 | 2264.63 | 150.304 | 35.7 | 2086.35 | 8325.03 | 11847 | 0.38 | 1.45 | 24.129 | 18.307 | 1 | 1 | 2370 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4724810.8005 | 360345.8202 | 5470.5481 | 36489.9867 | 323855.8335 | 19985.8561 | 0.090299 | -154325.483 | 154325.483
| Xist Rating 9184 | 6.75 | 2279.46 | 150.304 | 35.7 | 2082.81 | 8300.38 | 11791.4 | 0.38 | 1.44 | 24.12 | 18.162 | 1 | 1 | 2380 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4747682.0826 | 363238.5127 | 5516.8105 | 36643.9529 | 326594.5598 | 19839.0189 | 0.09068 | -153191.6455 | 153191.6455
| Xist Rating 9185 | 7.35 | 2295.16 | 150.304 | 35.7 | 2080.64 | 8301 | 11730.2 | 0.37 | 1.43 | 24.118 | 17.997 | 1 | 1 | 2390 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 4775401.7024 | 366142.7368 | 5563.2676 | 36797.9191 | 329344.8177 | 19645.8559 | 0.091061 | -151700.0917 | 151700.0917
C | Xist Rating 9186 | 18.86 | 2629.7 | 150.304 | 35.7 | 2010.56 | 7928.26 | 10538.5 | 0.41 | 1.25 | 24.093 | 14.867 | 1 | 1 | 2400 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5287169.632 | 369058.4923 | 5609.9196 | 36951.8853 | 332106.607 | 16502.0369 | 0.091442 | -127424.3549 | 127424.3549
C | Xist Rating 9187 | 18.89 | 2631.15 | 150.304 | 35.7 | 2010.85 | 7932.96 | 10538.3 | 0.41 | 1.25 | 24.081 | 14.879 | 1 | 1 | 2410 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5290847.9775 | 371985.7792 | 5656.7663 | 37105.8515 | 334879.9278 | 16518.3952 | 0.091823 | -127550.6695 | 127550.6695
C | Xist Rating 9188 | 18.99 | 2632.55 | 150.304 | 35.7 | 2011.9 | 7949.25 | 10538.4 | 0.4 | 1.25 | 24.12 | 14.89 | 1 | 1 | 2420 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5296427.345 | 374924.5977 | 5703.8078 | 37259.8177 | 337664.78 | 16509.8146 | 0.092204 | -127484.4117 | 127484.4117
C | Xist Rating 9189 | 19.11 | 2633.91 | 150.304 | 35.7 | 2013.24 | 7970.14 | 10538.4 | 0.39 | 1.25 | 24.122 | 14.901 | 1 | 1 | 2430 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5302692.9684 | 377874.9477 | 5751.0441 | 37413.7839 | 340461.1638 | 16499.3752 | 0.092585 | -127403.8021 | 127403.8021
C | Xist Rating 9190 | 19.22 | 2635.28 | 150.304 | 35.7 | 2014.61 | 7991.73 | 10538.3 | 0.38 | 1.25 | 24.123 | 14.912 | 1 | 1 | 2440 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5309061.4408 | 380836.8291 | 5798.4752 | 37567.75 | 343269.079 | 16488.6744 | 0.092966 | -127321.1734 | 127321.1734
C | Xist Rating 9191 | 19.26 | 2636.6 | 150.304 | 35.7 | 2014.82 | 7994.98 | 10538.3 | 0.38 | 1.25 | 24.113 | 14.922 | 1 | 1 | 2450 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5312274.412 | 383810.242 | 5846.1011 | 37721.7162 | 346088.5258 | 16502.7511 | 0.093347 | -127429.8694 | 127429.8694
C | Xist Rating 9192 | 19.25 | 2638.07 | 150.304 | 35.7 | 2014.01 | 7982.35 | 10538.3 | 0.37 | 1.25 | 24.105 | 14.933 | 1 | 1 | 2460 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5313099.3607 | 386795.1864 | 5893.9217 | 37875.6824 | 348919.5039 | 16491.3663 | 0.093728 | -127341.9595 | 127341.9595
C | Xist Rating 9193 | 19.25 | 2639.43 | 150.304 | 35.7 | 2013.53 | 7974.81 | 10538.3 | 0.37 | 1.25 | 24.146 | 14.944 | 1 | 1 | 2470 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5314571.4879 | 389791.6622 | 5941.9372 | 38029.6486 | 351762.0136 | 16508.4672 | 0.094109 | -127474.0081 | 127474.0081
C | Xist Rating 9194 | 19.26 | 2640.78 | 150.304 | 35.7 | 2013.07 | 7967.63 | 10538.3 | 0.36 | 1.25 | 24.139 | 14.955 | 1 | 1 | 2480 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5316074.9946 | 392799.6696 | 5990.1474 | 38183.6148 | 354616.0548 | 16496.7733 | 0.09449 | -127383.7106 | 127383.7106
C | Xist Rating 9195 | 19.26 | 2642.17 | 150.304 | 35.7 | 2012.54 | 7959.31 | 10538.3 | 0.35 | 1.25 | 24.132 | 14.965 | 1 | 1 | 2490 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5317472.8118 | 395819.2084 | 6038.5525 | 38337.581 | 357481.6274 | 16483.8378 | 0.094871 | -127283.8258 | 127283.8258
C | Xist Rating 9196 | 19.29 | 2643.16 | 150.304 | 35.7 | 2012.81 | 7963.48 | 10538.3 | 0.35 | 1.25 | 24.129 | 14.974 | 1 | 1 | 2500 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5320178.8796 | 398850.2787 | 6087.1523 | 38491.5472 | 360358.7315 | 16496.8526 | 0.095252 | -127384.3226 | 127384.3226
C | Xist Rating 9197 | 19.23 | 2645.01 | 150.304 | 35.7 | 2010.68 | 7930.23 | 10538.3 | 0.34 | 1.25 | 24.126 | 14.987 | 1 | 1 | 2510 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5318268.7068 | 401892.8805 | 6135.9469 | 38645.5134 | 363247.3671 | 16486.8763 | 0.095633 | -127307.2884 | 127307.2884
C | Xist Rating 9198 | 19.24 | 2646.46 | 150.304 | 35.7 | 2010.13 | 7921.75 | 10538.3 | 0.34 | 1.25 | 24.162 | 14.998 | 1 | 1 | 2520 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5319728.6398 | 404947.0137 | 6184.9363 | 38799.4796 | 366147.5342 | 16503.3593 | 0.096014 | -127434.5657 | 127434.5657
C | Xist Rating 9199 | 19.32 | 2647.8 | 150.304 | 35.7 | 2010.64 | 7929.65 | 10538.4 | 0.33 | 1.25 | 24.152 | 15.008 | 1 | 1 | 2530 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5323772.592 | 408012.6785 | 6234.1205 | 38953.4457 | 369059.2327 | 16489.6511 | 0.096395 | -127328.7152 | 127328.7152
C | Xist Rating 9200 | 19.33 | 2648.95 | 150.304 | 35.7 | 2011.02 | 7935.6 | 10538.2 | 0.33 | 1.25 | 24.142 | 15.017 | 1 | 1 | 2540 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5327091.429 | 411089.8747 | 6283.4995 | 39107.4119 | 371982.4628 | 16502.1945 | 0.096776 | -127425.5717 | 127425.5717
C | Xist Rating 9201 | 19.33 | 2650.5 | 150.304 | 35.7 | 2010.42 | 7926.3 | 10538.2 | 0.32 | 1.25 | 24.133 | 15.028 | 1 | 1 | 2550 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5328618.21 | 414178.6024 | 6333.0732 | 39261.3781 | 374917.2243 | 16489.2649 | 0.097157 | -127325.7329 | 127325.7329
C | Xist Rating 9202 | 19.28 | 2651.95 | 150.304 | 35.7 | 2009 | 7904.37 | 10538.1 | 0.32 | 1.25 | 24.133 | 15.039 | 1 | 1 | 2560 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5327767.55 | 417278.8616 | 6382.8418 | 39415.3443 | 377863.5173 | 16504.15 | 0.097538 | -127440.6716 | 127440.6716
C | Xist Rating 9203 | 19.3 | 2653.34 | 150.305 | 35.7 | 2008.75 | 7900.49 | 10538.2 | 0.31 | 1.25 | 24.15 | 15.049 | 1 | 1 | 2570 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5329896.725 | 420390.6522 | 6432.8051 | 39569.3105 | 380821.3417 | 16490.8026 | 0.097919 | -127337.6068 | 127337.6068
C | Xist Rating 9204 | 19.32 | 2654.7 | 150.305 | 35.7 | 2008.52 | 7896.94 | 10538.1 | 0.31 | 1.25 | 24.188 | 15.06 | 1 | 1 | 2580 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5332018.044 | 423513.9744 | 6482.9633 | 39723.2767 | 383790.6977 | 16506.9443 | 0.0983 | -127462.248 | 127462.248
C | Xist Rating 9205 | 19.31 | 2656.06 | 150.305 | 35.7 | 2007.91 | 7887.46 | 10538.1 | 0.3 | 1.25 | 24.183 | 15.07 | 1 | 1 | 2590 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5333129.4346 | 426648.828 | 6533.3162 | 39877.2429 | 386771.5851 | 16492.4349 | 0.098681 | -127350.2107 | 127350.2107
C | Xist Rating 9206 | 19.34 | 2657.24 | 150.305 | 35.7 | 2008.09 | 7890.31 | 10538.1 | 0.3 | 1.25 | 24.184 | 15.079 | 1 | 1 | 2600 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5335977.0716 | 429795.2131 | 6583.8639 | 40031.2091 | 389764.004 | 16505.0683 | 0.099062 | -127447.7627 | 127447.7627
C | Xist Rating 9207 | 19.34 | 2658.93 | 150.305 | 35.7 | 2007.25 | 7877.26 | 10538.1 | 0.3 | 1.25 | 24.183 | 15.091 | 1 | 1 | 2610 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5337137.2425 | 432953.1296 | 6634.6064 | 40185.1752 | 392767.9544 | 16520.7473 | 0.099443 | -127568.8318 | 127568.8318
C | Xist Rating 9208 | 19.35 | 2660.32 | 150.305 | 35.6 | 2006.93 | 7872.38 | 10538.1 | 0.29 | 1.25 | 24.184 | 15.101 | 1 | 1 | 2620 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5339076.0176 | 436122.5777 | 6685.5437 | 40339.1414 | 395783.4363 | 16506.0177 | 0.099824 | -127455.0935 | 127455.0935
C | Xist Rating 9209 | 19.36 | 2661.75 | 150.305 | 35.6 | 2006.39 | 7864.13 | 10538.1 | 0.29 | 1.25 | 24.217 | 15.111 | 1 | 1 | 2630 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5340508.5825 | 439303.5572 | 6736.6758 | 40493.1076 | 398810.4496 | 16520.6746 | 0.10021 | -127568.2702 | 127568.2702
C | Xist Rating 9210 | 19.42 | 2662.99 | 150.305 | 35.6 | 2006.88 | 7871.67 | 10538.1 | 0.28 | 1.25 | 24.227 | 15.121 | 1 | 1 | 2640 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5344301.3712 | 442496.0683 | 6788.0027 | 40647.0738 | 401848.9944 | 16505.8812 | 0.10059 | -127454.0398 | 127454.0398
C | Xist Rating 9211 | 19.43 | 2664.5 | 150.305 | 35.6 | 2006.31 | 7862.81 | 10538.1 | 0.28 | 1.25 | 24.222 | 15.131 | 1 | 1 | 2650 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5345812.995 | 445700.1107 | 6839.5243 | 40801.04 | 404899.0707 | 16519.1406 | 0.10097 | -127556.4253 | 127556.4253
C | Xist Rating 9212 | 19.45 | 2665.84 | 150.305 | 35.6 | 2006.23 | 7861.73 | 10538 | 0.28 | 1.25 | 24.224 | 15.141 | 1 | 1 | 2660 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5348288.1832 | 448915.6847 | 6891.2408 | 40955.0062 | 407960.6785 | 16532.6325 | 0.10135 | -127660.6056 | 127660.6056
C | Xist Rating 9213 | 19.48 | 2667.23 | 150.305 | 35.6 | 2006.17 | 7860.69 | 10538 | 0.27 | 1.25 | 24.224 | 15.151 | 1 | 1 | 2670 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5350916.8091 | 452142.7902 | 6943.152 | 41108.9724 | 411033.8178 | 16517.0661 | 0.10173 | -127540.406 | 127540.406
C | Xist Rating 9214 | 19.54 | 2668.64 | 150.305 | 35.6 | 2006.48 | 7865.59 | 10538 | 0.27 | 1.25 | 24.265 | 15.161 | 1 | 1 | 2680 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5354572.7872 | 455381.4271 | 6995.258 | 41262.9386 | 414118.4885 | 16531.7126 | 0.10211 | -127653.5029 | 127653.5029
C | Xist Rating 9215 | 19.58 | 2670.02 | 150.305 | 35.6 | 2006.71 | 7868.93 | 10538.1 | 0.26 | 1.25 | 24.265 | 15.171 | 1 | 1 | 2690 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5357955.8342 | 458631.5955 | 7047.5588 | 41416.9048 | 417214.6907 | 16515.776 | 0.10249 | -127530.4445 | 127530.4445
C | Xist Rating 9216 | 19.68 | 2671.22 | 150.305 | 35.6 | 2007.9 | 7887.36 | 10538 | 0.26 | 1.25 | 24.271 | 15.18 | 1 | 1 | 2700 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5363542.638 | 461893.2954 | 7100.0544 | 41570.8709 | 420322.4244 | 16528.1392 | 0.10287 | -127625.91 | 127625.91
C | Xist Rating 9217 | 19.73 | 2672.88 | 150.305 | 35.6 | 2008.05 | 7889.64 | 10538 | 0.26 | 1.25 | 24.269 | 15.191 | 1 | 1 | 2710 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5367276.684 | 465166.5268 | 7152.7448 | 41724.8371 | 423441.6896 | 16542.3282 | 0.10325 | -127735.4734 | 127735.4734
C | Xist Rating 9218 | 19.77 | 2674.22 | 150.305 | 35.6 | 2008.42 | 7895.37 | 10538 | 0.25 | 1.25 | 24.267 | 15.201 | 1 | 1 | 2720 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5370956.9324 | 468451.2896 | 7205.63 | 41878.8033 | 426572.4863 | 16525.8911 | 0.10363 | -127608.5507 | 127608.5507
C | Xist Rating 9219 | 19.75 | 2675.54 | 150.305 | 35.6 | 2007.59 | 7882.64 | 10538 | 0.25 | 1.25 | 24.302 | 15.21 | 1 | 1 | 2730 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5371387.3486 | 471747.5839 | 7258.71 | 42032.7695 | 429714.8144 | 16539.0278 | 0.10402 | -127709.9883 | 127709.9883
C | Xist Rating 9220 | 19.74 | 2676.83 | 150.305 | 35.6 | 2006.87 | 7871.57 | 10538 | 0.25 | 1.25 | 24.297 | 15.219 | 1 | 1 | 2740 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5372049.8221 | 475055.4097 | 7311.9847 | 42186.7357 | 432868.674 | 16550.944 | 0.1044 | -127802.0027 | 127802.0027
C | Xist Rating 9221 | 19.7 | 2678.37 | 150.305 | 35.6 | 2005.67 | 7853.15 | 10538 | 0.25 | 1.25 | 24.292 | 15.23 | 1 | 1 | 2750 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5371926.3579 | 478374.767 | 7365.4543 | 42340.7019 | 436034.0651 | 16564.9362 | 0.10478 | -127910.0464 | 127910.0464
C | Xist Rating 9222 | 19.7 | 2679.8 | 150.305 | 35.6 | 2005.09 | 7844.25 | 10538 | 0.24 | 1.25 | 24.289 | 15.24 | 1 | 1 | 2760 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5373240.182 | 481705.6558 | 7419.1186 | 42494.6681 | 439210.9877 | 16547.9012 | 0.10516 | -127778.5067 | 127778.5067
C | Xist Rating 9223 | 19.68 | 2681.03 | 150.305 | 35.6 | 2004.3 | 7832.07 | 10538 | 0.24 | 1.25 | 24.283 | 15.248 | 1 | 1 | 2770 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5373588.429 | 485048.076 | 7472.9777 | 42648.6343 | 442399.4418 | 16558.6434 | 0.10554 | -127861.455 | 127861.455
C | Xist Rating 9224 | 19.72 | 2682.58 | 150.305 | 35.6 | 2004.34 | 7832.79 | 10538 | 0.24 | 1.25 | 24.313 | 15.259 | 1 | 1 | 2780 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5376802.3972 | 488402.0278 | 7527.0316 | 42802.6005 | 445599.4273 | 16573.5764 | 0.10592 | -127976.764 | 127976.764
C | Xist Rating 9225 | 19.67 | 2683.99 | 150.305 | 35.6 | 2003.17 | 7814.92 | 10537.9 | 0.23 | 1.25 | 24.297 | 15.268 | 1 | 1 | 2790 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5376488.2483 | 491767.511 | 7581.2803 | 42956.5666 | 448810.9443 | 16554.6722 | 0.1063 | -127830.7908 | 127830.7908
C | Xist Rating 9226 | 19.7 | 2684.96 | 150.305 | 35.6 | 2003.39 | 7818.35 | 10537.9 | 0.23 | 1.25 | 24.302 | 15.276 | 1 | 1 | 2800 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5379022.0144 | 495144.5257 | 7635.7238 | 43110.5328 | 452033.9928 | 16565.6295 | 0.10668 | -127915.3999 | 127915.3999
C | Xist Rating 9227 | 19.7 | 2686.71 | 150.305 | 35.6 | 2002.63 | 7806.84 | 10537.9 | 0.23 | 1.25 | 24.308 | 15.287 | 1 | 1 | 2810 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5380486.0473 | 498533.0718 | 7690.3621 | 43264.499 | 455268.5728 | 16579.7323 | 0.10706 | -128024.2977 | 128024.2977
C | Xist Rating 9228 | 19.64 | 2688.18 | 150.305 | 35.6 | 2001.11 | 7783.7 | 10537.9 | 0.23 | 1.25 | 24.296 | 15.297 | 1 | 1 | 2820 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5379343.8798 | 501933.1495 | 7745.1952 | 43418.4652 | 458514.6842 | 16592.2744 | 0.10744 | -128121.145 | 128121.145
C | Xist Rating 9229 | 19.66 | 2689.56 | 150.305 | 35.6 | 2000.89 | 7780.33 | 10537.9 | 0.22 | 1.25 | 24.342 | 15.306 | 1 | 1 | 2830 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5381513.7084 | 505344.7586 | 7800.223 | 43572.4314 | 461772.3272 | 16574.5891 | 0.10783 | -127984.5838 | 127984.5838
C | Xist Rating 9230 | 19.69 | 2690.87 | 150.305 | 35.6 | 2001.01 | 7782.19 | 10537.9 | 0.22 | 1.25 | 24.351 | 15.315 | 1 | 1 | 2840 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5384457.7787 | 508767.8992 | 7855.4457 | 43726.3976 | 465041.5016 | 16586.5881 | 0.10821 | -128077.237 | 128077.237
C | Xist Rating 9231 | 19.65 | 2692.32 | 150.305 | 35.6 | 1999.75 | 7763.23 | 10537.9 | 0.22 | 1.25 | 24.342 | 15.325 | 1 | 1 | 2850 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5383966.92 | 512202.5713 | 7910.8631 | 43880.3638 | 468322.2075 | 16599.1215 | 0.10859 | -128174.0165 | 128174.0165
C | Xist Rating 9232 | 19.7 | 2693.72 | 150.305 | 35.6 | 1999.98 | 7766.62 | 10537.9 | 0.22 | 1.25 | 24.354 | 15.334 | 1 | 1 | 2860 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5387386.1256 | 515648.7748 | 7966.4753 | 44034.33 | 471614.4449 | 16611.2069 | 0.10897 | -128267.3368 | 128267.3368
C | Xist Rating 9233 | 19.82 | 2694.91 | 150.305 | 35.6 | 2001.59 | 7790.97 | 10538 | 0.21 | 1.25 | 24.378 | 15.343 | 1 | 1 | 2870 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5394104.9069 | 519106.5099 | 8022.2824 | 44188.2962 | 474918.2137 | 16592.2728 | 0.10935 | -128121.1326 | 128121.1326
C | Xist Rating 9234 | 19.78 | 2696.42 | 150.305 | 35.6 | 2000.3 | 7771.4 | 10538 | 0.21 | 1.25 | 24.412 | 15.353 | 1 | 1 | 2880 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5393648.926 | 522575.7764 | 8078.2842 | 44342.2623 | 478233.514 | 16605.8743 | 0.10973 | -128226.1595 | 128226.1595
C | Xist Rating 9235 | 19.92 | 2697.76 | 150.305 | 35.6 | 2002.09 | 7798.46 | 10538 | 0.21 | 1.25 | 24.437 | 15.362 | 1 | 1 | 2890 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5401158.3184 | 526056.5744 | 8134.4807 | 44496.2285 | 481560.3458 | 16618.1988 | 0.11011 | -128321.3263 | 128321.3263
C | Xist Rating 9236 | 20.08 | 2699.15 | 150.305 | 35.6 | 2004.35 | 7832.86 | 10538.1 | 0.21 | 1.25 | 24.469 | 15.371 | 1 | 1 | 2900 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5410041.3025 | 529548.9039 | 8190.8721 | 44650.1947 | 484898.7091 | 16630.7191 | 0.11049 | -128418.0049 | 128418.0049
C | Xist Rating 9237 | 20.06 | 2700.69 | 150.305 | 35.6 | 2003.41 | 7818.5 | 10538.1 | 0.2 | 1.25 | 24.467 | 15.381 | 1 | 1 | 2910 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5410589.3529 | 533052.7648 | 8247.4583 | 44804.1609 | 488248.6039 | 16611.438 | 0.11087 | -128269.1207 | 128269.1207
C | Xist Rating 9238 | 20.3 | 2702.08 | 150.305 | 35.6 | 2006.85 | 7871.14 | 10538.2 | 0.2 | 1.25 | 24.519 | 15.391 | 1 | 1 | 2920 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5422669.248 | 536568.1573 | 8304.2393 | 44958.1271 | 491610.0302 | 16625.3776 | 0.11125 | -128376.7592 | 128376.7592
C | Xist Rating 9239 | 21.03 | 2703.47 | 150.306 | 35.6 | 2018.61 | 8055.08 | 10538.4 | 0.2 | 1.25 | 24.65 | 15.401 | 1 | 1 | 2930 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5457251.5767 | 540095.0812 | 8361.215 | 45112.0933 | 494982.9879 | 16641.4017 | 0.11164 | -128500.4931 | 128500.4931
C | Xist Rating 9240 | 21.65 | 2704.83 | 150.306 | 35.6 | 2028.66 | 8217.36 | 10538.4 | 0.19 | 1.25 | 24.719 | 15.411 | 1 | 1 | 2940 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5487180.4278 | 543633.5366 | 8418.3855 | 45266.0595 | 498367.4771 | 16623.2394 | 0.11202 | -128360.2483 | 128360.2483
C | Xist Rating 9241 | 22.04 | 2706.24 | 150.306 | 35.6 | 2034.09 | 8307.11 | 10538.6 | 0.19 | 1.25 | 24.766 | 15.421 | 1 | 1 | 2950 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5504735.7216 | 547183.5234 | 8475.7509 | 45420.0257 | 501763.4978 | 16636.9105 | 0.1124 | -128465.8126 | 128465.8126
C | Xist Rating 9242 | 22.39 | 2707.61 | 150.306 | 35.6 | 2039.95 | 8405.75 | 10538.5 | 0.19 | 1.25 | 24.815 | 15.431 | 1 | 1 | 2960 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5523389.0195 | 550745.0418 | 8533.311 | 45573.9919 | 505171.0499 | 16650.6399 | 0.11278 | -128571.8281 | 128571.8281
C | Xist Rating 9243 | 23.41 | 2709 | 150.305 | 35.6 | 2056.61 | 8696.19 | 10538.4 | 0.18 | 1.25 | 24.911 | 15.442 | 1 | 1 | 2970 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5571356.49 | 554318.0916 | 8591.0659 | 45727.958 | 508590.1336 | 16633.4413 | 0.11316 | -128439.0247 | 128439.0247
C | Xist Rating 9244 | 23.44 | 2710.22 | 150.306 | 35.6 | 2056.93 | 8701.85 | 10538.4 | 0.18 | 1.25 | 24.946 | 15.45 | 1 | 1 | 2980 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5574732.8246 | 557902.6729 | 8649.0156 | 45881.9242 | 512020.7487 | 16644.6008 | 0.11354 | -128525.195 | 128525.195
C | Xist Rating 9245 | 23.44 | 2711.78 | 150.306 | 35.6 | 2056.12 | 8687.43 | 10538.4 | 0.18 | 1.25 | 24.94 | 15.46 | 1 | 1 | 2990 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5575745.0936 | 561498.7857 | 8707.16 | 46035.8904 | 515462.8953 | 16656.8537 | 0.11392 | -128619.8094 | 128619.8094
C | Xist Rating 9246 | 23.43 | 2713.21 | 150.306 | 35.6 | 2055.39 | 8674.45 | 10538.4 | 0.18 | 1.25 | 24.935 | 15.469 | 1 | 1 | 3000 | 152.4 | 2 | 5.5 | 19.05 | 1.3333 | 33 | E | Rod | 5576704.7019 | 565106.43 | 8765.4993 | 46189.8566 | 518916.5734 | 16668.0915 | 0.1143 | -128706.5841 | 128706.5841
C | Xist Rating 9247 | -84.58 | 282.59 | 150.312 | 35.9 | 2336.73 | 6836.32 | 58745 | 2.49 | 10.95 | 27.323 | 651.278 | 1 | 1 | 1000 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 660336.5307 | 74382.2707 | 973.9444 | 15676.5574 | 58705.7134 | 679400.7856 | 0.038101 | -5246152.7772 | 5246152.7772
C | Xist Rating 9248 | -84.45 | 285.495 | 150.312 | 35.9 | 2333.19 | 6813.37 | 58283.4 | 2.47 | 10.84 | 27.423 | 639.004 | 1 | 1 | 1010 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 666114.0791 | 75719.0212 | 993.5206 | 15833.323 | 59885.6982 | 666671.1947 | 0.038482 | -5147858.2506 | 5147858.2506
C | Xist Rating 9249 | -83.31 | 307.627 | 150.312 | 35.9 | 2325.39 | 6801.87 | 54966.9 | 2.49 | 10.07 | 27.472 | 553.765 | 1 | 1 | 1020 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 715352.7495 | 77067.5127 | 1013.2917 | 15990.0885 | 61077.4242 | 578211.6445 | 0.038863 | -4464797.0521 | 4464797.0521
C | Xist Rating 9250 | -83.1 | 313.581 | 150.311 | 35.9 | 2309.95 | 6685.06 | 54178.5 | 2.4 | 9.89 | 26.793 | 535.06 | 1 | 1 | 1030 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 724356.4309 | 78427.7454 | 1033.2576 | 16146.8541 | 62280.8913 | 558627.8035 | 0.039244 | -4313575.8228 | 4313575.8228
C | Xist Rating 9251 | -82.99 | 316.56 | 150.31 | 35.9 | 2304.63 | 6647.33 | 53793.7 | 2.36 | 9.8 | 26.64 | 526.098 | 1 | 1 | 1040 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 729553.6728 | 79799.7193 | 1053.4182 | 16303.6197 | 63496.0996 | 549282.8106 | 0.039625 | -4241416.2647 | 4241416.2647
C | Xist Rating 9252 | -82.73 | 322.393 | 150.31 | 35.9 | 2298.01 | 6605.8 | 53042.7 | 2.32 | 9.63 | 26.536 | 508.588 | 1 | 1 | 1050 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 740862.3379 | 81183.4342 | 1073.7737 | 16460.3853 | 64723.049 | 531065.3753 | 0.040006 | -4100746.0579 | 4100746.0579
C | Xist Rating 9253 | -82.61 | 325.352 | 150.31 | 35.9 | 2293.76 | 6577.34 | 52675.9 | 2.29 | 9.54 | 26.487 | 500.262 | 1 | 1 | 1060 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 746279.4035 | 82578.8904 | 1094.3239 | 16617.1508 | 65961.7395 | 522403.2765 | 0.040387 | -4033859.627 | 4033859.627
C | Xist Rating 9254 | -81.45 | 349.091 | 150.31 | 35.9 | 2280.33 | 6520.19 | 49856.5 | 2.27 | 8.9 | 26.212 | 437.664 | 1 | 1 | 1070 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 796042.68 | 83986.0876 | 1115.0689 | 16773.9164 | 67212.1712 | 457367.1928 | 0.040768 | -3531668.2283 | 3531668.2283
C | Xist Rating 9255 | -81.22 | 353.534 | 150.309 | 35.9 | 2280.6 | 6531.79 | 49380.6 | 2.22 | 8.79 | 26.065 | 427.782 | 1 | 1 | 1080 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 806269.6404 | 85405.026 | 1136.0087 | 16930.682 | 68474.3441 | 447052.1774 | 0.041149 | -3452018.4133 | 3452018.4133
C | Xist Rating 9256 | -80.89 | 359.447 | 150.309 | 35.9 | 2282.87 | 6563.27 | 48760.5 | 2.16 | 8.65 | 25.86 | 415.101 | 1 | 1 | 1090 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 820570.7729 | 86835.7056 | 1157.1433 | 17087.4476 | 69748.258 | 433810.8713 | 0.04153 | -3349772.5577 | 3349772.5577
C | Xist Rating 9257 | -80.59 | 363.857 | 150.309 | 35.9 | 2292.01 | 6649.15 | 48306.6 | 2.12 | 8.55 | 25.866 | 405.952 | 1 | 1 | 1100 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 833963.8826 | 88278.1263 | 1178.4727 | 17244.2131 | 71033.9132 | 424284.3112 | 0.041911 | -3276210.9854 | 3276210.9854
C | Xist Rating 9258 | -80.42 | 367.004 | 150.308 | 35.9 | 2292.88 | 6662.99 | 48010.2 | 2.03 | 8.49 | 25.457 | 400.295 | 1 | 1 | 1110 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 841496.1315 | 89732.2881 | 1199.9969 | 17400.9787 | 72331.3094 | 418276.9677 | 0.042292 | -3229823.8719 | 3229823.8719
C | Xist Rating 9259 | -79.06 | 393.472 | 150.309 | 35.9 | 2286.77 | 6671.24 | 45447.6 | 2.08 | 7.92 | 25.809 | 350.251 | 1 | 1 | 1120 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 899779.9654 | 91198.1911 | 1221.7158 | 17557.7443 | 73640.4468 | 366430.176 | 0.042673 | -2829476.6888 | 2829476.6888
C | Xist Rating 9260 | -78.87 | 396.573 | 150.308 | 35.9 | 2290.48 | 6709.45 | 45188.4 | 2.01 | 7.86 | 25.55 | 345.693 | 1 | 1 | 1130 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 908342.525 | 92675.8352 | 1243.6296 | 17714.5099 | 74961.3254 | 361602.8852 | 0.043054 | -2792201.6295 | 2792201.6295
C | Xist Rating 9261 | -78.57 | 402.557 | 150.307 | 35.9 | 2289.68 | 6715.59 | 44680.7 | 1.95 | 7.75 | 25.143 | 336.598 | 1 | 1 | 1140 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 921726.7118 | 94165.2205 | 1265.7381 | 17871.2754 | 76293.9451 | 352061.87 | 0.043435 | -2718528.4388 | 2718528.4388
C | Xist Rating 9262 | -78.25 | 408.477 | 150.307 | 35.9 | 2290.96 | 6739.67 | 44185.6 | 1.91 | 7.64 | 25.054 | 327.815 | 1 | 1 | 1150 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 935804.4679 | 95666.3469 | 1288.0414 | 18028.041 | 77638.3059 | 342902.1095 | 0.043816 | -2647799.1961 | 2647799.1961
C | Xist Rating 9263 | -77.96 | 414.476 | 150.306 | 35.9 | 2288.75 | 6733.64 | 43703 | 1.86 | 7.53 | 24.843 | 319.442 | 1 | 1 | 1160 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 948631.945 | 97179.2145 | 1310.5395 | 18184.8066 | 78994.4079 | 334142.6695 | 0.044197 | -2580161.1225 | 2580161.1225
C | Xist Rating 9264 | -76.75 | 438.202 | 150.307 | 35.9 | 2284.03 | 6746.08 | 41831.8 | 1.88 | 7.13 | 25.026 | 287.317 | 1 | 1 | 1170 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1000866.5141 | 98703.8232 | 1333.2324 | 18341.5722 | 80362.251 | 300845.7212 | 0.044578 | -2323050.9139 | 2323050.9139
C | Xist Rating 9265 | -76.63 | 439.845 | 150.306 | 35.9 | 2287.79 | 6782.25 | 41724.3 | 1.83 | 7.1 | 24.901 | 285.713 | 1 | 1 | 1180 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1006272.9926 | 100240.173 | 1356.1201 | 18498.3377 | 81741.8353 | 299122.7749 | 0.044959 | -2309746.7787 | 2309746.7787
C | Xist Rating 9266 | -76.07 | 451.671 | 150.306 | 35.8 | 2281.89 | 6756.42 | 40885.3 | 1.78 | 6.92 | 24.677 | 272.243 | 1 | 1 | 1190 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1030663.5382 | 101788.264 | 1379.2026 | 18655.1033 | 83133.1607 | 285066.9463 | 0.04534 | -2201211.3967 | 2201211.3967
C | Xist Rating 9267 | -75.78 | 454.664 | 150.306 | 35.8 | 2295.53 | 6884.07 | 40681.6 | 1.75 | 6.88 | 24.738 | 269.092 | 1 | 1 | 1200 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1043694.8519 | 103348.0961 | 1402.4799 | 18811.8689 | 84536.2272 | 281780.2481 | 0.045721 | -2175832.3845 | 2175832.3845
C | Xist Rating 9268 | -75.47 | 460.733 | 150.306 | 35.8 | 2295.2 | 6894.44 | 40281.3 | 1.7 | 6.8 | 24.553 | 262.958 | 1 | 1 | 1210 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1057474.3816 | 104919.6694 | 1425.9519 | 18968.6344 | 85951.0349 | 275345.3595 | 0.046102 | -2126143.8804 | 2126143.8804
C | Xist Rating 9269 | -74.18 | 487.555 | 150.306 | 35.8 | 2283.52 | 6850.21 | 38537.5 | 1.7 | 6.43 | 24.542 | 236.402 | 1 | 1 | 1220 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1113341.5936 | 106502.9838 | 1449.6188 | 19125.4 | 87377.5838 | 247784.6828 | 0.046483 | -1913327.6397 | 1913327.6397
C | Xist Rating 9270 | -73.81 | 493.474 | 150.306 | 35.8 | 2289.42 | 6916.78 | 38183.2 | 1.67 | 6.35 | 24.571 | 231.301 | 1 | 1 | 1230 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1129769.2451 | 108098.0393 | 1473.4804 | 19282.1656 | 88815.8737 | 242468.0808 | 0.046864 | -1872274.2484 | 1872274.2484
C | Xist Rating 9271 | -73.48 | 499.532 | 150.305 | 35.8 | 2290.37 | 6938.78 | 37835.7 | 1.62 | 6.28 | 24.445 | 226.432 | 1 | 1 | 1240 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1144113.1068 | 109704.836 | 1497.5369 | 19438.9312 | 90265.9049 | 237350.3936 | 0.047245 | -1832756.8249 | 1832756.8249
C | Xist Rating 9272 | -73.28 | 502.669 | 150.305 | 35.8 | 2294.66 | 6985.03 | 37664.6 | 1.58 | 6.24 | 24.359 | 224.127 | 1 | 1 | 1250 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1153454.4475 | 111323.3739 | 1521.7881 | 19595.6967 | 91727.6771 | 234912.0053 | 0.047626 | -1813928.2369 | 1813928.2369
C | Xist Rating 9273 | -72.81 | 511.57 | 150.305 | 35.8 | 2294.95 | 7008 | 37161.2 | 1.55 | 6.14 | 24.297 | 217.119 | 1 | 1 | 1260 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1174027.5715 | 112953.6528 | 1546.2341 | 19752.4623 | 93201.1905 | 227604.7593 | 0.048007 | -1757503.6203 | 1757503.6203
C | Xist Rating 9274 | -71.56 | 536.965 | 150.305 | 35.8 | 2287.91 | 7000.92 | 35777.3 | 1.56 | 5.85 | 24.371 | 198.237 | 1 | 1 | 1270 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1228527.5932 | 114595.673 | 1570.8749 | 19909.2279 | 94686.4451 | 208033.1166 | 0.048388 | -1606376.5832 | 1606376.5832
C | Xist Rating 9275 | -71.24 | 543.092 | 150.305 | 35.8 | 2287.85 | 7013.76 | 35477.1 | 1.52 | 5.79 | 24.226 | 194.427 | 1 | 1 | 1280 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1242513.0322 | 116249.4342 | 1595.7105 | 20065.9935 | 96183.4408 | 204024.9019 | 0.048769 | -1575426.2113 | 1575426.2113
C | Xist Rating 9276 | -70.93 | 549.168 | 150.305 | 35.8 | 2288.06 | 7029.05 | 35182.4 | 1.48 | 5.73 | 24.161 | 190.711 | 1 | 1 | 1290 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1256529.3341 | 117914.9366 | 1620.7408 | 20222.759 | 97692.1776 | 200120.7515 | 0.04915 | -1545279.3973 | 1545279.3973
C | Xist Rating 9277 | -70.45 | 558.047 | 150.305 | 35.8 | 2289.05 | 7058.6 | 34750.9 | 1.46 | 5.64 | 24.205 | 185.242 | 1 | 1 | 1300 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1277397.4854 | 119592.1802 | 1645.966 | 20379.5246 | 99212.6556 | 194432.8174 | 0.049531 | -1501358.6775 | 1501358.6775
C | Xist Rating 9278 | -70.21 | 562.682 | 150.304 | 35.8 | 2289.94 | 7077.27 | 34539.4 | 1.43 | 5.59 | 24.152 | 182.682 | 1 | 1 | 1310 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1288508.0191 | 121281.1649 | 1671.3859 | 20536.2902 | 100744.8747 | 191743.012 | 0.049912 | -1480588.7133 | 1480588.7133
C | Xist Rating 9279 | -68.95 | 588.175 | 150.304 | 35.8 | 2283.72 | 7076.49 | 33362.4 | 1.43 | 5.35 | 24.207 | 168.185 | 1 | 1 | 1320 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1343227.011 | 122981.8907 | 1697.0007 | 20693.0558 | 102288.8349 | 176708.0353 | 0.050293 | -1364492.6084 | 1364492.6084
C | Xist Rating 9280 | -68.51 | 597.272 | 150.304 | 35.8 | 2281.96 | 7079.67 | 32979.3 | 1.39 | 5.28 | 24.074 | 163.748 | 1 | 1 | 1330 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1362950.8131 | 124694.3577 | 1722.8102 | 20849.8213 | 103844.5364 | 172046.9872 | 0.050674 | -1328501.2306 | 1328501.2306
C | Xist Rating 9281 | -68.01 | 606.267 | 150.304 | 35.8 | 2284.51 | 7124.44 | 32606.1 | 1.37 | 5.2 | 23.962 | 159.464 | 1 | 1 | 1340 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1385023.0242 | 126418.5658 | 1748.8145 | 21006.5869 | 105411.9789 | 167574.9231 | 0.051055 | -1293969.137 | 1293969.137
C | Xist Rating 9282 | -67.69 | 610.919 | 150.304 | 35.8 | 2290.66 | 7194.87 | 32423.3 | 1.33 | 5.16 | 23.918 | 157.446 | 1 | 1 | 1350 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1399407.7165 | 128154.5151 | 1775.0136 | 21163.3525 | 106991.1626 | 165432.4063 | 0.051436 | -1277425.1902 | 1277425.1902
C | Xist Rating 9283 | -67.33 | 613.858 | 150.304 | 35.8 | 2305.66 | 7352.1 | 32302.7 | 1.32 | 5.14 | 24.028 | 156.088 | 1 | 1 | 1360 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1415347.8363 | 129902.2055 | 1801.4075 | 21320.1181 | 108582.0874 | 164030.6554 | 0.051817 | -1266601.2415 | 1266601.2415
C | Xist Rating 9284 | -65.81 | 649.921 | 150.304 | 35.8 | 2279.86 | 7178.34 | 30901.5 | 1.32 | 4.86 | 23.895 | 140.564 | 1 | 1 | 1370 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1481728.8911 | 131661.637 | 1827.9962 | 21476.8836 | 110184.7534 | 147912.4419 | 0.052198 | -1142140.669 | 1142140.669
C | Xist Rating 9285 | -65.66 | 653.122 | 150.303 | 35.8 | 2279.84 | 7184.86 | 30793 | 1.29 | 4.84 | 23.845 | 139.486 | 1 | 1 | 1380 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1489013.6605 | 133432.8097 | 1854.7797 | 21633.6492 | 111799.1605 | 146758.7462 | 0.052579 | -1133232.1364 | 1133232.1364
C | Xist Rating 9286 | -65.22 | 660.736 | 150.304 | 35.8 | 2282.84 | 7231.74 | 30526.5 | 1.26 | 4.78 | 23.817 | 136.727 | 1 | 1 | 1390 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1508354.5702 | 135215.7235 | 1881.7579 | 21790.4148 | 113425.3088 | 143860.5482 | 0.05296 | -1110853.0196 | 1110853.0196
C | Xist Rating 9287 | -64.81 | 668.346 | 150.304 | 35.8 | 2284.06 | 7261.24 | 30264.5 | 1.23 | 4.73 | 23.778 | 134.051 | 1 | 1 | 1400 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1526542.3648 | 137010.3785 | 1908.931 | 21947.1804 | 115063.1982 | 141047.1289 | 0.053341 | -1089128.5422 | 1089128.5422
C | Xist Rating 9288 | -64.31 | 677.402 | 150.304 | 35.8 | 2286.53 | 7306.98 | 29957 | 1.21 | 4.67 | 23.755 | 130.929 | 1 | 1 | 1410 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1548899.9951 | 138816.7746 | 1936.2988 | 22103.9459 | 116712.8287 | 137786.2311 | 0.053722 | -1063948.7533 | 1063948.7533
C | Xist Rating 9289 | -63.03 | 704.467 | 150.304 | 35.8 | 2278.05 | 7284.05 | 29051.2 | 1.22 | 4.49 | 23.814 | 121.78 | 1 | 1 | 1420 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1604811.0493 | 140634.9119 | 1963.8614 | 22260.7115 | 118374.2004 | 128317.5951 | 0.054103 | -990834.4564 | 990834.4564
C | Xist Rating 9290 | -62.79 | 709.36 | 150.303 | 35.8 | 2277.82 | 7292.04 | 28910 | 1.18 | 4.47 | 23.705 | 120.502 | 1 | 1 | 1430 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1615794.3952 | 142464.7903 | 1991.6188 | 22417.4771 | 120047.3132 | 126934.1143 | 0.054484 | -980151.5839 | 980151.5839
C | Xist Rating 9291 | -62.13 | 721.355 | 150.304 | 35.8 | 2280.2 | 7344.06 | 28541.6 | 1.16 | 4.39 | 23.709 | 116.979 | 1 | 1 | 1440 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1644833.671 | 144306.4099 | 2019.571 | 22574.2426 | 121732.1672 | 123257.7202 | 0.054865 | -951763.4432 | 951763.4432
C | Xist Rating 9292 | -61.74 | 729.004 | 150.303 | 35.7 | 2280.61 | 7365.68 | 28316.2 | 1.14 | 4.35 | 23.665 | 114.892 | 1 | 1 | 1450 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1662573.8124 | 146159.7705 | 2047.718 | 22731.0082 | 123428.7623 | 121068.622 | 0.055246 | -934859.8072 | 934859.8072
C | Xist Rating 9293 | -61.35 | 733.538 | 150.304 | 35.7 | 2290.13 | 7476.54 | 28183.2 | 1.13 | 4.32 | 23.727 | 113.669 | 1 | 1 | 1460 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1679897.3799 | 148024.8724 | 2076.0598 | 22887.7738 | 125137.0986 | 119799.7289 | 0.055627 | -925061.7515 | 925061.7515
C | Xist Rating 9294 | -60.01 | 763.97 | 150.303 | 35.7 | 2275.4 | 7392.44 | 27310 | 1.12 | 4.16 | 23.679 | 105.632 | 1 | 1 | 1470 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1738337.338 | 149901.7154 | 2104.5964 | 23044.5394 | 126857.176 | 111446.1587 | 0.056008 | -860557.6964 | 860557.6964
C | Xist Rating 9295 | -59.53 | 773.07 | 150.303 | 35.7 | 2276.46 | 7424.62 | 27065.8 | 1.1 | 4.11 | 23.665 | 103.492 | 1 | 1 | 1480 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1759862.9322 | 151790.2995 | 2133.3277 | 23201.3049 | 128588.9945 | 109203.2206 | 0.056389 | -843238.3231 | 843238.3231
C | Xist Rating 9296 | -59.12 | 780.72 | 150.303 | 35.7 | 2277.89 | 7457.29 | 26866 | 1.08 | 4.07 | 23.649 | 101.773 | 1 | 1 | 1490 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1778394.2808 | 153690.6247 | 2162.2539 | 23358.0705 | 130332.5542 | 107396.9452 | 0.05677 | -829290.7427 | 829290.7427
C | Xist Rating 9297 | -58.74 | 788.463 | 150.303 | 35.7 | 2277.42 | 7469.81 | 26669.5 | 1.06 | 4.03 | 23.605 | 100.111 | 1 | 1 | 1500 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1795661.4055 | 155602.6911 | 2191.3748 | 23514.8361 | 132087.855 | 105647.4717 | 0.057151 | -815781.7727 | 815781.7727
C | Xist Rating 9298 | -58.26 | 797.589 | 150.303 | 35.7 | 2278.21 | 7499.6 | 26437.9 | 1.04 | 3.99 | 23.594 | 98.149 | 1 | 1 | 1510 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1817075.2357 | 157526.4987 | 2220.6906 | 23671.6017 | 133854.897 | 103588.425 | 0.057532 | -799882.3599 | 799882.3599
C | Xist Rating 9299 | -56.81 | 827.705 | 150.303 | 35.7 | 2272.14 | 7505.87 | 25680.1 | 1.05 | 3.84 | 23.623 | 91.719 | 1 | 1 | 1520 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1880661.6387 | 159462.0474 | 2250.2011 | 23828.3672 | 135633.6801 | 96940.0292 | 0.057913 | -748545.2099 | 748545.2099
C | Xist Rating 9300 | -56.43 | 837.176 | 150.303 | 35.7 | 2267.83 | 7479.91 | 25466.9 | 1.02 | 3.8 | 23.526 | 90.05 | 1 | 1 | 1530 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1898572.8481 | 161409.3372 | 2279.9064 | 23985.1328 | 137424.2044 | 95162.5051 | 0.058294 | -734819.6396 | 734819.6396
C | Xist Rating 9301 | -56.08 | 841.984 | 150.303 | 35.7 | 2273.9 | 7556.98 | 25362.3 | 1 | 3.78 | 23.518 | 89.252 | 1 | 1 | 1540 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1914587.4176 | 163368.3682 | 2309.8065 | 24141.8984 | 139226.4698 | 94311.5075 | 0.058675 | -728248.4617 | 728248.4617
C | Xist Rating 9302 | -55.31 | 857.045 | 150.303 | 35.7 | 2273.81 | 7591.58 | 25019.8 | 0.99 | 3.72 | 23.514 | 86.527 | 1 | 1 | 1550 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1948757.4914 | 165339.1403 | 2339.9013 | 24298.664 | 141040.4763 | 91475.5262 | 0.059056 | -706349.7655 | 706349.7655
C | Xist Rating 9303 | -54.86 | 861.628 | 150.303 | 35.7 | 2285.08 | 7729.83 | 24919.1 | 0.98 | 3.7 | 23.564 | 85.756 | 1 | 1 | 1560 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 1968888.9102 | 167321.6536 | 2370.191 | 24455.4295 | 142866.224 | 90672.2624 | 0.059437 | -700147.176 | 700147.176
C | Xist Rating 9304 | -53.4 | 896.777 | 150.303 | 35.7 | 2266.87 | 7608.28 | 24160.9 | 0.97 | 3.56 | 23.521 | 79.891 | 1 | 1 | 1570 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2032876.878 | 169315.908 | 2400.6755 | 24612.1951 | 144703.7128 | 84572.302 | 0.059818 | -653044.8985 | 653044.8985
C | Xist Rating 9305 | -52.93 | 904.548 | 150.303 | 35.7 | 2270.78 | 7670.49 | 24006.3 | 0.95 | 3.53 | 23.516 | 78.767 | 1 | 1 | 1580 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2054029.5074 | 171321.9035 | 2431.3547 | 24768.9607 | 146552.9428 | 83381.6038 | 0.0602 | -643850.6422 | 643850.6422
C | Xist Rating 9306 | -52.45 | 912.354 | 150.303 | 35.7 | 2274.1 | 7726.61 | 23854.3 | 0.93 | 3.5 | 23.516 | 77.673 | 1 | 1 | 1590 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2074784.2314 | 173339.6402 | 2462.2288 | 24925.7263 | 148413.9139 | 82221.9801 | 0.060581 | -634896.336 | 634896.336
C | Xist Rating 9307 | -51.84 | 922.957 | 150.303 | 35.7 | 2277.88 | 7796.32 | 23644.6 | 0.92 | 3.46 | 23.536 | 76.145 | 1 | 1 | 1600 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2102385.2912 | 175369.118 | 2493.2976 | 25082.4918 | 150286.6262 | 80629.4117 | 0.060962 | -622598.945 | 622598.945
C | Xist Rating 9308 | -51.55 | 927.961 | 150.303 | 35.7 | 2280.03 | 7832.83 | 23555.9 | 0.9 | 3.45 | 23.501 | 75.554 | 1 | 1 | 1610 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2115778.9188 | 177410.337 | 2524.5612 | 25239.2574 | 152171.0796 | 79989.1211 | 0.061343 | -617654.7901 | 617654.7901
C | Xist Rating 9309 | -49.8 | 967.357 | 150.303 | 35.7 | 2266.51 | 7771.49 | 22804.4 | 0.9 | 3.31 | 23.535 | 70.156 | 1 | 1 | 1620 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2192524.3141 | 179463.2971 | 2556.0196 | 25396.023 | 154067.2741 | 74395.0095 | 0.061724 | -574458.5431 | 574458.5431
C | Xist Rating 9310 | -49.38 | 972.016 | 150.303 | 35.7 | 2275.3 | 7887.17 | 22722.7 | 0.89 | 3.29 | 23.568 | 69.613 | 1 | 1 | 1630 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2211628.0048 | 181527.9984 | 2587.6728 | 25552.7886 | 155975.2098 | 73825.5496 | 0.062105 | -570061.325 | 570061.325
C | Xist Rating 9311 | -48.97 | 979.97 | 150.303 | 35.7 | 2275.68 | 7910.56 | 22587.9 | 0.87 | 3.27 | 23.537 | 68.727 | 1 | 1 | 1640 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2230098.1296 | 183604.4408 | 2619.5208 | 25709.5541 | 157894.8866 | 72878.2088 | 0.062486 | -562746.2101 | 562746.2101
C | Xist Rating 9312 | -48.44 | 990.929 | 150.303 | 35.7 | 2274.5 | 7922.77 | 22402.3 | 0.85 | 3.23 | 23.505 | 67.499 | 1 | 1 | 1650 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2253868.0105 | 185692.6243 | 2651.5635 | 25866.3197 | 159826.3046 | 71575.2835 | 0.062867 | -552685.367 | 552685.367
C | Xist Rating 9313 | -47.8 | 1001.65 | 150.303 | 35.7 | 2278.93 | 8003.56 | 22220.2 | 0.84 | 3.2 | 23.52 | 66.29 | 1 | 1 | 1660 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2282690.2345 | 187792.549 | 2683.8011 | 26023.0853 | 161769.4637 | 70312.1423 | 0.063248 | -542931.7253 | 542931.7253
C | Xist Rating 9314 | -46.28 | 1036.84 | 150.303 | 35.7 | 2265.87 | 7932.38 | 21632.4 | 0.84 | 3.09 | 23.536 | 62.395 | 1 | 1 | 1670 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2349344.6508 | 189904.2148 | 2716.2334 | 26179.8508 | 163724.364 | 66277.053 | 0.063629 | -511773.835 | 511773.835
C | Xist Rating 9315 | -45.88 | 1041.61 | 150.303 | 35.7 | 2273.1 | 8033.1 | 21560 | 0.83 | 3.08 | 23.554 | 61.956 | 1 | 1 | 1680 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2367683.691 | 192027.6218 | 2748.8606 | 26336.6164 | 165691.0054 | 65813.4153 | 0.06401 | -508193.7477 | 508193.7477
C | Xist Rating 9316 | -45.27 | 1055.62 | 150.303 | 35.7 | 2269.08 | 8017.49 | 21345.7 | 0.81 | 3.04 | 23.515 | 60.619 | 1 | 1 | 1690 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2395286.2296 | 194162.7699 | 2781.6825 | 26493.382 | 167669.3879 | 64395.627 | 0.064391 | -497245.9619 | 497245.9619
C | Xist Rating 9317 | -44.75 | 1064.91 | 150.303 | 35.7 | 2271.25 | 8067.79 | 21205.4 | 0.8 | 3.02 | 23.521 | 59.755 | 1 | 1 | 1700 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2418676.8375 | 196309.6592 | 2814.6992 | 26650.1476 | 169659.5116 | 63489.349 | 0.064772 | -490247.924 | 490247.924
C | Xist Rating 9318 | -44.21 | 1075.82 | 150.303 | 35.7 | 2270.78 | 8088.87 | 21044.4 | 0.79 | 2.99 | 23.509 | 58.775 | 1 | 1 | 1710 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2442950.5396 | 198468.2896 | 2847.9107 | 26806.9131 | 171661.3764 | 62461.2996 | 0.065153 | -482309.599 | 482309.599
C | Xist Rating 9319 | -42.78 | 1108.16 | 150.303 | 35.7 | 2261.65 | 8055.71 | 20566.8 | 0.79 | 2.9 | 23.534 | 55.838 | 1 | 1 | 1720 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2506270.064 | 200638.6611 | 2881.317 | 26963.6787 | 173674.9824 | 59421.0773 | 0.065534 | -458833.8084 | 458833.8084
C | Xist Rating 9320 | -42.12 | 1122.04 | 150.303 | 35.7 | 2260.13 | 8070.82 | 20374 | 0.78 | 2.87 | 23.523 | 54.705 | 1 | 1 | 1730 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2535956.2652 | 202820.7738 | 2914.9181 | 27120.4443 | 175700.3295 | 58233.8772 | 0.065915 | -449666.5635 | 449666.5635
C | Xist Rating 9321 | -41.72 | 1128.41 | 150.303 | 35.7 | 2263.41 | 8128.38 | 20289.7 | 0.77 | 2.85 | 23.526 | 54.23 | 1 | 1 | 1740 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2554054.4781 | 205014.6276 | 2948.714 | 27277.2099 | 177737.4177 | 57730.6483 | 0.066296 | -445780.7632 | 445780.7632
C | Xist Rating 9322 | -41.13 | 1140.98 | 150.303 | 35.7 | 2261.59 | 8135.84 | 20123.2 | 0.75 | 2.82 | 23.503 | 53.281 | 1 | 1 | 1750 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2580428.9582 | 207220.2226 | 2982.7046 | 27433.9754 | 179786.2471 | 56714.9711 | 0.066677 | -437937.973 | 437937.973
C | Xist Rating 9323 | -40.72 | 1150.38 | 150.303 | 35.7 | 2259.77 | 8135.44 | 20000.4 | 0.74 | 2.8 | 23.496 | 52.588 | 1 | 1 | 1760 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2599594.2126 | 209437.5587 | 3016.8901 | 27590.741 | 181846.8177 | 55984.2425 | 0.067058 | -432295.4808 | 432295.4808
C | Xist Rating 9324 | -39.04 | 1188.71 | 150.303 | 35.7 | 2249.04 | 8094.22 | 19497 | 0.74 | 2.71 | 23.531 | 49.701 | 1 | 1 | 1770 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2673456.3384 | 211666.636 | 3051.2703 | 27747.5066 | 183919.1294 | 52995.9461 | 0.067439 | -409220.6484 | 409220.6484
C | Xist Rating 9325 | -38.55 | 1198.22 | 150.303 | 35.7 | 2250.08 | 8130.71 | 19382.6 | 0.73 | 2.69 | 23.522 | 49.09 | 1 | 1 | 1780 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2696090.8576 | 213907.4544 | 3085.8453 | 27904.2722 | 186003.1822 | 52349.9298 | 0.06782 | -404232.2815 | 404232.2815
C | Xist Rating 9326 | -38.2 | 1203.25 | 150.304 | 35.7 | 2254.41 | 8199.21 | 19325.8 | 0.72 | 2.68 | 23.516 | 48.805 | 1 | 1 | 1790 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2712618.8325 | 216160.0139 | 3120.6151 | 28061.0377 | 188098.9762 | 52042.4349 | 0.068201 | -401857.8871 | 401857.8871
C | Xist Rating 9327 | -37.66 | 1220.23 | 150.304 | 35.7 | 2242.59 | 8086.17 | 19122.3 | 0.71 | 2.65 | 23.808 | 47.69 | 1 | 1 | 1800 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2736475.5957 | 218424.3146 | 3155.5797 | 28217.8033 | 190206.5113 | 50889.8524 | 0.068582 | -392957.9506 | 392957.9506
C | Xist Rating 9328 | -37.19 | 1229.61 | 150.304 | 35.6 | 2244.79 | 8137.82 | 19012.2 | 0.7 | 2.63 | 23.796 | 47.112 | 1 | 1 | 1810 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2760216.2319 | 220700.3564 | 3190.7391 | 28374.5689 | 192325.7875 | 50277.1797 | 0.068963 | -388227.0549 | 388227.0549
C | Xist Rating 9329 | -35.27 | 1268.21 | 150.304 | 35.7 | 2241.84 | 8196.61 | 18562.4 | 0.7 | 2.55 | 23.537 | 44.723 | 1 | 1 | 1820 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2843123.9064 | 222988.1394 | 3226.0933 | 28531.3345 | 194456.8049 | 47788.8829 | 0.069344 | -369013.0865 | 369013.0865
C | Xist Rating 9330 | -35.56 | 1262.1 | 150.304 | 35.6 | 2246.2 | 8239.63 | 18631 | 0.7 | 2.56 | 23.861 | 45.084 | 1 | 1 | 1830 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2834929.02 | 225287.6635 | 3261.6423 | 28688.1 | 196599.5634 | 48189.7703 | 0.069725 | -372108.6328 | 372108.6328
C | Xist Rating 9331 | -35.02 | 1269.83 | 150.304 | 35.6 | 2250.32 | 8314.98 | 18545.2 | 0.69 | 2.55 | 23.895 | 44.648 | 1 | 1 | 1840 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2857523.8456 | 227598.9287 | 3297.386 | 28844.8656 | 198754.0631 | 47726.7269 | 0.070106 | -368533.1345 | 368533.1345
C | Xist Rating 9332 | -34.45 | 1282.51 | 150.304 | 35.6 | 2248.11 | 8316.49 | 18409.2 | 0.68 | 2.52 | 23.881 | 43.967 | 1 | 1 | 1850 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 35 | E | Rod | 2883223.5561 | 229921.9351 | 3333.3246 | 29001.6312 | 200920.304 | 47006.2955 | 0.070487 | -362970.1537 | 362970.1537
C | Xist Rating 9333 | -33.81 | 1296.74 | 150.304 | 35.6 | 2245.5 | 8316.27 | 18259 | 0.66 | 2.5 | 23.852 | 43.219 | 1 | 1 | 1860 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 2911829.67 | 232256.6827 | 3369.4579 | 29158.3968 | 203098.2859 | 46195.361 | 0.070868 | -356708.3324 | 356708.3324
C | Xist Rating 9334 | -32.2 | 1332.21 | 150.304 | 35.6 | 2238.95 | 8318.68 | 17879.6 | 0.66 | 2.43 | 23.905 | 41.296 | 1 | 1 | 1870 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 2982751.5795 | 234603.1714 | 3405.7861 | 29315.1623 | 205288.009 | 44208.3171 | 0.071249 | -341364.906 | 341364.906
C | Xist Rating 9335 | -31.57 | 1346.43 | 150.304 | 35.6 | 2236.47 | 8319.77 | 17738.7 | 0.65 | 2.41 | 23.892 | 40.623 | 1 | 1 | 1880 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3011250.3021 | 236961.4012 | 3442.309 | 29471.9279 | 207489.4733 | 43495.6228 | 0.07163 | -335861.6701 | 335861.6701
C | Xist Rating 9336 | -31.04 | 1355.86 | 150.304 | 35.6 | 2238.78 | 8375.67 | 17646.1 | 0.64 | 2.39 | 23.91 | 40.187 | 1 | 1 | 1890 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3035472.2508 | 239331.3721 | 3479.0267 | 29628.6935 | 209702.6787 | 43030.5337 | 0.072011 | -332270.375 | 332270.375
C | Xist Rating 9337 | -30.62 | 1365.74 | 150.304 | 35.6 | 2236.01 | 8360.62 | 17554.9 | 0.63 | 2.38 | 23.895 | 39.772 | 1 | 1 | 1900 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3053808.2974 | 241713.0843 | 3515.9392 | 29785.459 | 211927.6252 | 42585.2479 | 0.072392 | -328831.996 | 328831.996
C | Xist Rating 9338 | -30.07 | 1375.35 | 150.304 | 35.7 | 2238.23 | 8415.6 | 17464.8 | 0.62 | 2.36 | 23.91 | 39.358 | 1 | 1 | 1910 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3078349.6305 | 244106.5375 | 3553.0464 | 29942.2246 | 214164.3129 | 42142.3959 | 0.072773 | -325412.4101 | 325412.4101
C | Xist Rating 9339 | -28.22 | 1418.42 | 150.304 | 35.7 | 2228.1 | 8385.27 | 17050 | 0.62 | 2.29 | 23.963 | 37.38 | 1 | 1 | 1920 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3160381.602 | 246511.7319 | 3590.3485 | 30098.9902 | 216412.7417 | 40097.7189 | 0.073154 | -309623.9568 | 309623.9568
C | Xist Rating 9340 | -27.61 | 1432.71 | 150.304 | 35.7 | 2225.26 | 8380.52 | 16923.5 | 0.61 | 2.27 | 23.954 | 36.815 | 1 | 1 | 1930 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3188152.2546 | 248928.6674 | 3627.8454 | 30255.7558 | 218672.9117 | 39496.4212 | 0.073535 | -304980.8954 | 304980.8954
C | Xist Rating 9341 | -27.19 | 1437.37 | 150.304 | 35.7 | 2230.85 | 8472.35 | 16881.8 | 0.61 | 2.26 | 23.997 | 36.635 | 1 | 1 | 1940 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3206556.8645 | 251357.3441 | 3665.537 | 30412.5213 | 220944.8228 | 39318.3222 | 0.073916 | -303605.662 | 303605.662
C | Xist Rating 9342 | -26.78 | 1450.63 | 150.304 | 35.7 | 2223.04 | 8392.13 | 16772 | 0.59 | 2.24 | 23.974 | 36.165 | 1 | 1 | 1950 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3224808.5152 | 253797.7619 | 3703.4235 | 30569.2869 | 223228.475 | 38793.6527 | 0.074297 | -299554.3032 | 299554.3032
C | Xist Rating 9343 | -26.09 | 1466.34 | 150.304 | 35.7 | 2220.57 | 8396.16 | 16636.8 | 0.58 | 2.22 | 23.995 | 35.568 | 1 | 1 | 1960 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3256110.6138 | 256249.9209 | 3741.5047 | 30726.0525 | 225523.8684 | 38160.0169 | 0.074678 | -294661.5352 | 294661.5352
C | Xist Rating 9344 | -24.4 | 1505.07 | 150.304 | 35.7 | 2213.1 | 8388.86 | 16303 | 0.58 | 2.16 | 24.07 | 34.078 | 1 | 1 | 1970 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3330870.417 | 258713.821 | 3779.7807 | 30882.8181 | 227831.003 | 36622.7338 | 0.075059 | -282791.0425 | 282791.0425
C | Xist Rating 9345 | -23.85 | 1516.2 | 150.304 | 35.7 | 2213.27 | 8418.59 | 16214 | 0.58 | 2.15 | 24.106 | 33.706 | 1 | 1 | 1980 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3355759.974 | 261189.4623 | 3818.2515 | 31039.5836 | 230149.8786 | 36244.5233 | 0.07544 | -279870.6016 | 279870.6016
C | Xist Rating 9346 | -23.25 | 1530.68 | 150.304 | 35.7 | 2209.61 | 8400.76 | 16101.4 | 0.57 | 2.13 | 24.123 | 33.239 | 1 | 1 | 1990 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3382205.8348 | 263676.8447 | 3856.9171 | 31196.3492 | 232480.4955 | 35745.1732 | 0.075821 | -276014.7528 | 276014.7528
C | Xist Rating 9347 | -22.72 | 1541.94 | 150.305 | 35.7 | 2208.84 | 8416.91 | 16014.8 | 0.56 | 2.12 | 24.126 | 32.886 | 1 | 1 | 2000 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3405898.7496 | 266175.9682 | 3895.7775 | 31353.1148 | 234822.8534 | 35363.2713 | 0.076202 | -273065.8068 | 273065.8068
C | Xist Rating 9348 | -22.29 | 1550.15 | 150.305 | 35.7 | 2209.57 | 8447.16 | 15953.6 | 0.55 | 2.11 | 24.134 | 32.643 | 1 | 1 | 2010 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3425164.9355 | 268686.8329 | 3934.8326 | 31509.8804 | 237176.9525 | 35095.6317 | 0.076583 | -270999.1651 | 270999.1651
C | Xist Rating 9349 | -20.48 | 1593.66 | 150.305 | 35.7 | 2199.85 | 8416.26 | 15614.7 | 0.55 | 2.05 | 24.171 | 31.218 | 1 | 1 | 2020 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3505812.951 | 271209.4387 | 3974.0826 | 31666.6459 | 239542.7928 | 33623.5639 | 0.076964 | -259632.2481 | 259632.2481
C | Xist Rating 9350 | -19.7 | 1609.32 | 150.305 | 35.7 | 2200.32 | 8462.05 | 15499.7 | 0.54 | 2.03 | 24.188 | 30.757 | 1 | 1 | 2030 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3541018.9824 | 273743.7857 | 4013.5273 | 31823.4115 | 241920.3742 | 33129.6163 | 0.077345 | -255818.1157 | 255818.1157
C | Xist Rating 9351 | -19.28 | 1619.41 | 150.305 | 35.7 | 2198.5 | 8458.59 | 15431.6 | 0.53 | 2.02 | 24.17 | 30.501 | 1 | 1 | 2040 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3560272.885 | 276289.8738 | 4053.1669 | 31980.1771 | 244309.6967 | 32846.6251 | 0.077726 | -253632.9324 | 253632.9324
C | Xist Rating 9352 | -18.65 | 1628.68 | 150.305 | 35.7 | 2203.12 | 8551.2 | 15364.2 | 0.53 | 2.01 | 24.205 | 30.236 | 1 | 1 | 2050 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3588177.4816 | 278847.703 | 4093.0012 | 32136.9427 | 246710.7604 | 32578.8697 | 0.078107 | -251565.3959 | 251565.3959
C | Xist Rating 9353 | -18.15 | 1643.56 | 150.305 | 35.7 | 2197.22 | 8498.3 | 15264.3 | 0.52 | 1.99 | 24.181 | 29.858 | 1 | 1 | 2060 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3611262.9032 | 281417.2734 | 4133.0303 | 32293.7082 | 249123.5652 | 32168.5647 | 0.078488 | -248397.1295 | 248397.1295
C | Xist Rating 9354 | -16.21 | 1690.22 | 150.305 | 35.7 | 2187.66 | 8474.21 | 14936.2 | 0.52 | 1.94 | 24.22 | 28.558 | 1 | 1 | 2070 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3697626.6852 | 283998.585 | 4173.2542 | 32450.4738 | 251548.1111 | 30826.0348 | 0.078869 | -238030.4693 | 238030.4693
C | Xist Rating 9355 | -15.76 | 1700.11 | 150.305 | 35.7 | 2186.94 | 8486.77 | 14873.5 | 0.51 | 1.93 | 24.222 | 28.332 | 1 | 1 | 2080 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3718038.5634 | 286591.6376 | 4213.6729 | 32607.2394 | 253984.3983 | 30574.493 | 0.07925 | -236088.1308 | 236088.1308
C | Xist Rating 9356 | -15.16 | 1713 | 150.305 | 35.7 | 2186.36 | 8509.26 | 14790.8 | 0.5 | 1.91 | 24.232 | 28.028 | 1 | 1 | 2090 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3745234.68 | 289196.4315 | 4254.2864 | 32764.005 | 256432.4265 | 30242.1032 | 0.079631 | -233521.5046 | 233521.5046
C | Xist Rating 9357 | -14.63 | 1725.89 | 150.305 | 35.7 | 2184.1 | 8506.2 | 14709.2 | 0.5 | 1.9 | 24.231 | 27.73 | 1 | 1 | 2100 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3769516.349 | 291812.9664 | 4295.0947 | 32920.7705 | 258892.1959 | 29938.0146 | 0.080012 | -231173.4127 | 231173.4127
C | Xist Rating 9358 | -14.13 | 1737.24 | 150.305 | 35.7 | 2183.07 | 8517.84 | 14638.6 | 0.49 | 1.89 | 24.233 | 27.476 | 1 | 1 | 2110 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3792516.5268 | 294441.2425 | 4336.0977 | 33077.5361 | 261363.7064 | 29656.8417 | 0.080393 | -229002.2704 | 229002.2704
C | Xist Rating 9359 | -12.36 | 1781.19 | 150.305 | 35.7 | 2173.58 | 8483.9 | 14358.9 | 0.49 | 1.84 | 24.266 | 26.432 | 1 | 1 | 2120 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3871558.9602 | 297081.2598 | 4377.2956 | 33234.3017 | 263846.9581 | 28579.5085 | 0.080774 | -220683.3891 | 220683.3891
C | Xist Rating 9360 | -11.7 | 1797.19 | 150.305 | 35.7 | 2170.9 | 8481.61 | 14263.7 | 0.48 | 1.83 | 24.264 | 26.095 | 1 | 1 | 2130 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3901519.771 | 299733.0182 | 4418.6882 | 33391.0673 | 266341.9509 | 28211.6044 | 0.081155 | -217842.5308 | 217842.5308
C | Xist Rating 9361 | -11.14 | 1813.22 | 150.305 | 35.7 | 2165.8 | 8442.18 | 14169.8 | 0.48 | 1.81 | 24.26 | 25.766 | 1 | 1 | 2140 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3927071.876 | 302396.5177 | 4460.2756 | 33547.8328 | 268848.6849 | 27874.9748 | 0.081536 | -215243.1666 | 215243.1666
C | Xist Rating 9362 | -10.73 | 1821.58 | 150.305 | 35.7 | 2166.17 | 8466.91 | 14123.5 | 0.47 | 1.8 | 24.264 | 25.613 | 1 | 1 | 2150 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3945851.9486 | 305071.7584 | 4502.0578 | 33704.5984 | 271367.16 | 27698.1054 | 0.081917 | -213877.4278 | 213877.4278
C | Xist Rating 9363 | -10.21 | 1832.87 | 150.305 | 35.7 | 2165.93 | 8490.01 | 14059 | 0.47 | 1.79 | 24.269 | 25.393 | 1 | 1 | 2160 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 3969868.1191 | 307758.7402 | 4544.0348 | 33861.364 | 273897.3762 | 27474.9751 | 0.082298 | -212154.4749 | 212154.4749
C | Xist Rating 9364 | -8.4 | 1880.19 | 150.305 | 35.7 | 2154.53 | 8431.24 | 13785.9 | 0.46 | 1.75 | 24.3 | 24.43 | 1 | 1 | 2170 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4050925.7607 | 310457.4632 | 4586.2066 | 34018.1295 | 276439.3336 | 26457.7947 | 0.082679 | -204300.0778 | 204300.0778
C | Xist Rating 9365 | -7.71 | 1895.97 | 150.305 | 35.7 | 2153.1 | 8446.97 | 13699 | 0.46 | 1.74 | 24.314 | 24.137 | 1 | 1 | 2180 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4082213.007 | 313167.9273 | 4628.5732 | 34174.8951 | 278993.0321 | 26159.1545 | 0.08306 | -201994.0571 | 201994.0571
C | Xist Rating 9366 | -7.22 | 1907.5 | 150.305 | 35.7 | 2151.89 | 8454.74 | 13638.8 | 0.45 | 1.73 | 24.314 | 23.943 | 1 | 1 | 2190 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4104730.175 | 315890.1325 | 4671.1346 | 34331.6607 | 281558.4718 | 25938.8311 | 0.083441 | -200292.7783 | 200292.7783
C | Xist Rating 9367 | -6.77 | 1919.44 | 150.305 | 35.7 | 2149.41 | 8442.77 | 13579.3 | 0.45 | 1.72 | 24.299 | 23.756 | 1 | 1 | 2200 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4125663.5304 | 318624.0789 | 4713.8907 | 34488.4263 | 284135.6526 | 25748.8707 | 0.083822 | -198825.954 | 198825.954
C | Xist Rating 9368 | -6.1 | 1935.47 | 150.305 | 35.7 | 2147.37 | 8448.99 | 13495.3 | 0.44 | 1.7 | 24.302 | 23.481 | 1 | 1 | 2210 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4156170.2139 | 321369.7664 | 4756.8417 | 34645.1918 | 286724.5746 | 25444.2445 | 0.084203 | -196473.7119 | 196473.7119
C | Xist Rating 9369 | -4.23 | 1982.66 | 150.305 | 35.7 | 2138.5 | 8425.52 | 13246.1 | 0.44 | 1.66 | 24.34 | 22.646 | 1 | 1 | 2220 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4239918.41 | 324127.1951 | 4799.9874 | 34801.9574 | 289325.2377 | 24583.5552 | 0.084584 | -189827.6971 | 189827.6971
C | Xist Rating 9370 | -3.65 | 1995.52 | 150.305 | 35.7 | 2138.1 | 8449.2 | 13182.5 | 0.44 | 1.65 | 24.345 | 22.446 | 1 | 1 | 2230 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4266621.312 | 326896.3649 | 4843.3279 | 34958.723 | 291937.6419 | 24380.876 | 0.084965 | -188262.6618 | 188262.6618
C | Xist Rating 9371 | -3.08 | 2010.36 | 150.305 | 35.7 | 2135.32 | 8439.37 | 13111.7 | 0.43 | 1.64 | 24.34 | 22.228 | 1 | 1 | 2240 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4292761.9152 | 329677.2759 | 4886.8633 | 35115.4886 | 294561.7873 | 24134.6249 | 0.085346 | -186361.1758 | 186361.1758
C | Xist Rating 9372 | -2.45 | 2026.7 | 150.305 | 35.7 | 2132.36 | 8430.31 | 13034 | 0.43 | 1.63 | 24.336 | 21.988 | 1 | 1 | 2250 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4321654.012 | 332469.928 | 4930.5934 | 35272.2541 | 297197.6739 | 23889.9032 | 0.085727 | -184471.5 | 184471.5
C | Xist Rating 9373 | -2.04 | 2035.02 | 150.305 | 35.7 | 2133.04 | 8459.67 | 12995.6 | 0.42 | 1.62 | 24.344 | 21.875 | 1 | 1 | 2260 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4340779.0608 | 335274.3212 | 4974.5182 | 35429.0197 | 299845.3015 | 23752.9307 | 0.086108 | -183413.8344 | 183413.8344
C | Xist Rating 9374 | -0.15 | 2085.67 | 150.305 | 35.7 | 2122 | 8406.54 | 12751.8 | 0.42 | 1.59 | 24.368 | 21.101 | 1 | 1 | 2270 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4425791.74 | 338090.4556 | 5018.6379 | 35585.7853 | 302504.6703 | 22954.7416 | 0.086489 | -177250.4302 | 177250.4302
C | Xist Rating 9375 | 0.42 | 2100.47 | 150.305 | 35.7 | 2119.51 | 8400.32 | 12686.2 | 0.41 | 1.58 | 24.364 | 20.907 | 1 | 1 | 2280 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4451967.1697 | 340918.3312 | 5062.9524 | 35742.5509 | 305175.7803 | 22732.7888 | 0.08687 | -175536.5692 | 175536.5692
C | Xist Rating 9376 | 1.12 | 2118.09 | 150.305 | 35.7 | 2116.94 | 8400.11 | 12606.9 | 0.41 | 1.56 | 24.365 | 20.669 | 1 | 1 | 2290 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4483869.4446 | 343757.9478 | 5107.4617 | 35899.3164 | 307858.6314 | 22490.1459 | 0.087251 | -173662.9451 | 173662.9451
C | Xist Rating 9377 | 1.58 | 2129.79 | 150.305 | 35.7 | 2115.39 | 8401.23 | 12557.1 | 0.41 | 1.56 | 24.366 | 20.527 | 1 | 1 | 2300 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4505336.4681 | 346609.3056 | 5152.1657 | 36056.082 | 310553.2236 | 22347.1992 | 0.087632 | -172559.1487 | 172559.1487
| Xist Rating 9378 | 2 | 2141.75 | 150.305 | 35.7 | 2112.7 | 8384.32 | 12507.7 | 0.4 | 1.55 | 24.37 | 20.389 | 1 | 1 | 2310 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4524875.225 | 349472.4046 | 5197.0645 | 36212.8476 | 313259.557 | 22183.3004 | 0.088013 | -171293.5652 | 171293.5652
| Xist Rating 9379 | 3.93 | 2193.78 | 150.305 | 35.7 | 2102.08 | 8337.79 | 12277.2 | 0.4 | 1.51 | 24.389 | 19.691 | 1 | 1 | 2320 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4611501.0624 | 352347.2447 | 5242.1582 | 36369.6132 | 315977.6316 | 21463.5883 | 0.088394 | -165736.1396 | 165736.1396
| Xist Rating 9380 | 4.49 | 2208.6 | 150.305 | 35.7 | 2099.82 | 8334.39 | 12217 | 0.39 | 1.5 | 24.395 | 19.522 | 1 | 1 | 2330 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4637662.452 | 355233.826 | 5287.4466 | 36526.3787 | 318707.4472 | 21267.2272 | 0.088775 | -164219.8908 | 164219.8908
| Xist Rating 9381 | 5.08 | 2223.41 | 150.305 | 35.7 | 2098.05 | 8338.52 | 12157.4 | 0.39 | 1.49 | 24.398 | 19.356 | 1 | 1 | 2340 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4664825.3505 | 358132.1483 | 5332.9298 | 36683.1443 | 321449.004 | 21099.2238 | 0.089156 | -162922.6133 | 162922.6133
| Xist Rating 9382 | 5.63 | 2236.76 | 150.305 | 35.7 | 2096.96 | 8349.84 | 12104.9 | 0.38 | 1.49 | 24.403 | 19.213 | 1 | 1 | 2350 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4690396.2496 | 361042.2119 | 5378.6078 | 36839.9099 | 324202.302 | 20929.4835 | 0.089537 | -161611.9236 | 161611.9236
| Xist Rating 9383 | 6.2 | 2253.15 | 150.305 | 35.7 | 2093.41 | 8329.17 | 12040.1 | 0.38 | 1.48 | 24.397 | 19.033 | 1 | 1 | 2360 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4716766.7415 | 363964.0165 | 5424.4805 | 36996.6755 | 326967.3411 | 20746.4692 | 0.089918 | -160198.736 | 160198.736
| Xist Rating 9384 | 7.93 | 2300.77 | 150.305 | 35.7 | 2083.96 | 8287.2 | 11847 | 0.38 | 1.45 | 24.42 | 18.478 | 1 | 1 | 2370 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4794712.6492 | 366897.5624 | 5470.5481 | 37153.441 | 329744.1213 | 20175.1867 | 0.090299 | -155787.4439 | 155787.4439
| Xist Rating 9385 | 8.43 | 2315.81 | 150.305 | 35.7 | 2080.43 | 8262.69 | 11791.4 | 0.38 | 1.44 | 24.41 | 18.331 | 1 | 1 | 2380 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4817880.5983 | 369842.8493 | 5516.8105 | 37310.2066 | 332532.6427 | 20026.2816 | 0.09068 | -154637.6381 | 154637.6381
| Xist Rating 9386 | 9.04 | 2331.75 | 150.305 | 35.7 | 2078.26 | 8263.22 | 11730.3 | 0.37 | 1.43 | 24.409 | 18.165 | 1 | 1 | 2390 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 4845982.755 | 372799.8774 | 5563.2676 | 37466.9722 | 335332.9052 | 19831.8584 | 0.091061 | -153136.3538 | 153136.3538
C | Xist Rating 9387 | 20.73 | 2671.59 | 150.305 | 35.7 | 2008.5 | 7896.38 | 10538.4 | 0.41 | 1.25 | 24.365 | 14.997 | 1 | 1 | 2400 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5365888.515 | 375768.6467 | 5609.9196 | 37623.7377 | 338144.9089 | 16649.0389 | 0.091442 | -128559.4656 | 128559.4656
C | Xist Rating 9388 | 20.76 | 2673.04 | 150.305 | 35.7 | 2008.55 | 7897.24 | 10538.3 | 0.41 | 1.25 | 24.371 | 15.009 | 1 | 1 | 2410 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5368934.492 | 378749.157 | 5656.7663 | 37780.5033 | 340968.6537 | 16666.2445 | 0.091823 | -128692.3223 | 128692.3223
C | Xist Rating 9389 | 20.86 | 2674.44 | 150.305 | 35.7 | 2009.57 | 7912.97 | 10538.4 | 0.4 | 1.25 | 24.41 | 15.02 | 1 | 1 | 2420 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5374474.3908 | 381741.4086 | 5703.8078 | 37937.2689 | 343804.1397 | 16657.4025 | 0.092204 | -128624.0469 | 128624.0469
C | Xist Rating 9390 | 20.97 | 2675.8 | 150.305 | 35.7 | 2010.81 | 7932.22 | 10538.4 | 0.39 | 1.25 | 24.411 | 15.031 | 1 | 1 | 2430 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5380525.398 | 384745.4012 | 5751.0441 | 38094.0345 | 346651.3668 | 16646.6568 | 0.092585 | -128541.0716 | 128541.0716
C | Xist Rating 9391 | 21.1 | 2677.17 | 150.305 | 35.7 | 2012.36 | 7956.48 | 10538.3 | 0.38 | 1.25 | 24.414 | 15.042 | 1 | 1 | 2440 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5387429.8212 | 387761.1351 | 5798.4752 | 38250.8 | 349510.335 | 16635.7736 | 0.092966 | -128457.0342 | 128457.0342
C | Xist Rating 9392 | 21.14 | 2678.49 | 150.305 | 35.7 | 2012.55 | 7959.33 | 10538.4 | 0.38 | 1.25 | 24.403 | 15.052 | 1 | 1 | 2450 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5390595.0495 | 390788.61 | 5846.1011 | 38407.5656 | 352381.0444 | 16649.8581 | 0.093347 | -128565.7907 | 128565.7907
C | Xist Rating 9393 | 21.12 | 2679.97 | 150.305 | 35.7 | 2011.66 | 7945.6 | 10538.3 | 0.37 | 1.25 | 24.396 | 15.064 | 1 | 1 | 2460 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5391188.4502 | 393827.8261 | 5893.9217 | 38564.3312 | 355263.4949 | 16639.2823 | 0.093728 | -128484.127 | 128484.127
C | Xist Rating 9394 | 21.13 | 2681.32 | 150.305 | 35.7 | 2011.21 | 7938.49 | 10538.3 | 0.37 | 1.25 | 24.437 | 15.074 | 1 | 1 | 2470 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5392697.5972 | 396878.7834 | 5941.9372 | 38721.0968 | 358157.6866 | 16655.3929 | 0.094109 | -128608.5293 | 128608.5293
C | Xist Rating 9395 | 21.13 | 2682.67 | 150.305 | 35.7 | 2010.75 | 7931.31 | 10538.3 | 0.36 | 1.25 | 24.429 | 15.085 | 1 | 1 | 2480 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5394178.7025 | 399941.4817 | 5990.1474 | 38877.8623 | 361063.6194 | 16643.3837 | 0.09449 | -128515.7975 | 128515.7975
C | Xist Rating 9396 | 21.1 | 2684.07 | 150.305 | 35.7 | 2009.41 | 7910.53 | 10538.4 | 0.35 | 1.25 | 24.428 | 15.096 | 1 | 1 | 2490 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5393397.0987 | 403015.9213 | 6038.5525 | 39034.6279 | 363981.2934 | 16631.4442 | 0.094871 | -128423.6036 | 128423.6036
C | Xist Rating 9397 | 21.13 | 2685.05 | 150.305 | 35.7 | 2009.72 | 7915.3 | 10538.4 | 0.35 | 1.25 | 24.426 | 15.104 | 1 | 1 | 2500 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5396198.686 | 406102.1019 | 6087.1523 | 39191.3935 | 366910.7085 | 16643.5062 | 0.095252 | -128516.7428 | 128516.7428
C | Xist Rating 9398 | 21.1 | 2686.9 | 150.305 | 35.7 | 2008.34 | 7893.91 | 10538.3 | 0.34 | 1.25 | 24.417 | 15.117 | 1 | 1 | 2510 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5396208.746 | 409200.0238 | 6135.9469 | 39348.1591 | 369851.8647 | 16633.0128 | 0.095633 | -128435.7159 | 128435.7159
C | Xist Rating 9399 | 21.19 | 2688.36 | 150.305 | 35.7 | 2008.42 | 7895.09 | 10538.5 | 0.34 | 1.25 | 24.452 | 15.128 | 1 | 1 | 2520 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5399355.9912 | 412309.6867 | 6184.9363 | 39504.9246 | 372804.7621 | 16649.5017 | 0.096014 | -128563.039 | 128563.039
C | Xist Rating 9400 | 21.18 | 2689.69 | 150.305 | 35.7 | 2008.83 | 7901.57 | 10538.3 | 0.33 | 1.25 | 24.435 | 15.138 | 1 | 1 | 2530 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5403129.9627 | 415431.0908 | 6234.1205 | 39661.6902 | 375769.4006 | 16635.247 | 0.096395 | -128452.9675 | 128452.9675
C | Xist Rating 9401 | 21.21 | 2690.84 | 150.305 | 35.7 | 2008.92 | 7902.9 | 10538.3 | 0.33 | 1.25 | 24.429 | 15.147 | 1 | 1 | 2540 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5405682.2928 | 418564.2361 | 6283.4995 | 39818.4558 | 378745.7803 | 16647.9825 | 0.096776 | -128551.3077 | 128551.3077
C | Xist Rating 9402 | 21.11 | 2692.39 | 150.305 | 35.7 | 2006.62 | 7867.51 | 10538.2 | 0.32 | 1.25 | 24.431 | 15.159 | 1 | 1 | 2550 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5402603.6218 | 421709.1224 | 6333.0732 | 39975.2214 | 381733.9011 | 16636.2081 | 0.097157 | -128460.3894 | 128460.3894
C | Xist Rating 9403 | 21.15 | 2693.84 | 150.305 | 35.7 | 2006.61 | 7867.41 | 10538.2 | 0.32 | 1.25 | 24.425 | 15.169 | 1 | 1 | 2560 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5405486.2824 | 424865.75 | 6382.8418 | 40131.9869 | 384733.763 | 16649.8771 | 0.097538 | -128565.9379 | 128565.9379
C | Xist Rating 9404 | 21.16 | 2695.23 | 150.305 | 35.7 | 2006.41 | 7864.37 | 10538.2 | 0.31 | 1.25 | 24.441 | 15.18 | 1 | 1 | 2570 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5407736.4243 | 428034.1186 | 6432.8051 | 40288.7525 | 387745.3661 | 16637.2381 | 0.097919 | -128468.3423 | 128468.3423
C | Xist Rating 9405 | 21.18 | 2696.59 | 150.305 | 35.7 | 2006.16 | 7860.43 | 10538.2 | 0.31 | 1.25 | 24.478 | 15.19 | 1 | 1 | 2580 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5409790.9944 | 431214.2284 | 6482.9633 | 40445.5181 | 390768.7104 | 16652.3458 | 0.0983 | -128585 | 128585
C | Xist Rating 9406 | 21.17 | 2697.95 | 150.305 | 35.7 | 2005.56 | 7851.27 | 10538.2 | 0.3 | 1.25 | 24.473 | 15.2 | 1 | 1 | 2590 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5410900.602 | 434406.0794 | 6533.3162 | 40602.2837 | 393803.7957 | 16637.54 | 0.098681 | -128470.6741 | 128470.6741
C | Xist Rating 9407 | 21.22 | 2699.13 | 150.305 | 35.7 | 2005.87 | 7856.06 | 10538.2 | 0.3 | 1.25 | 24.476 | 15.209 | 1 | 1 | 2600 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5414103.8931 | 437609.6715 | 6583.8639 | 40759.0492 | 396850.6223 | 16650.2824 | 0.099062 | -128569.0672 | 128569.0672
C | Xist Rating 9408 | 21.2 | 2700.82 | 150.306 | 35.7 | 2004.9 | 7841.27 | 10538.1 | 0.3 | 1.25 | 24.473 | 15.221 | 1 | 1 | 2610 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5414874.018 | 440825.0047 | 6634.6064 | 40915.8148 | 399909.1899 | 16665.9305 | 0.099443 | -128689.8974 | 128689.8974
C | Xist Rating 9409 | 21.2 | 2702.22 | 150.306 | 35.7 | 2004.3 | 7832.11 | 10538.1 | 0.29 | 1.25 | 24.468 | 15.231 | 1 | 1 | 2620 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5416059.546 | 444052.0791 | 6685.5437 | 41072.5804 | 402979.4987 | 16650.6949 | 0.099824 | -128572.2525 | 128572.2525
C | Xist Rating 9410 | 21.22 | 2703.64 | 150.306 | 35.6 | 2004.05 | 7828.32 | 10538.1 | 0.29 | 1.25 | 24.506 | 15.241 | 1 | 1 | 2630 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5418229.742 | 447290.8946 | 6736.6758 | 41229.3459 | 406061.5487 | 16665.5597 | 0.10021 | -128687.0342 | 128687.0342
C | Xist Rating 9411 | 21.29 | 2704.89 | 150.306 | 35.7 | 2004.53 | 7835.51 | 10538.1 | 0.28 | 1.25 | 24.516 | 15.251 | 1 | 1 | 2640 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5422033.1517 | 450541.4513 | 6788.0027 | 41386.1115 | 409155.3398 | 16650.4619 | 0.10059 | -128570.4531 | 128570.4531
C | Xist Rating 9412 | 21.26 | 2706.39 | 150.306 | 35.6 | 2003.61 | 7821.58 | 10538.1 | 0.28 | 1.25 | 24.506 | 15.261 | 1 | 1 | 2650 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5422550.0679 | 453803.7491 | 6839.5243 | 41542.8771 | 412260.872 | 16663.5912 | 0.10097 | -128671.8345 | 128671.8345
C | Xist Rating 9413 | 21.31 | 2707.73 | 150.306 | 35.6 | 2003.85 | 7825.15 | 10538.1 | 0.28 | 1.25 | 24.513 | 15.271 | 1 | 1 | 2660 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5425884.7605 | 457077.7881 | 6891.2408 | 41699.6427 | 415378.1454 | 16677.2856 | 0.10135 | -128777.5791 | 128777.5791
C | Xist Rating 9414 | 21.34 | 2709.12 | 150.306 | 35.6 | 2003.74 | 7823.59 | 10538.1 | 0.27 | 1.25 | 24.513 | 15.281 | 1 | 1 | 2670 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5428372.1088 | 460363.5682 | 6943.152 | 41856.4082 | 418507.1599 | 16661.4096 | 0.10173 | -128654.9887 | 128654.9887
C | Xist Rating 9415 | 21.4 | 2710.53 | 150.306 | 35.6 | 2004.05 | 7828.21 | 10538.1 | 0.27 | 1.25 | 24.554 | 15.291 | 1 | 1 | 2680 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5432037.6465 | 463661.0894 | 6995.258 | 42013.1738 | 421647.9156 | 16676.0912 | 0.10211 | -128768.3558 | 128768.3558
C | Xist Rating 9416 | 21.47 | 2711.91 | 150.306 | 35.6 | 2004.71 | 7838.23 | 10538.1 | 0.26 | 1.25 | 24.558 | 15.301 | 1 | 1 | 2690 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5436593.0961 | 466970.3518 | 7047.5588 | 42169.9394 | 424800.4124 | 16659.9665 | 0.10249 | -128643.8449 | 128643.8449
C | Xist Rating 9417 | 21.53 | 2713.11 | 150.306 | 35.6 | 2005.4 | 7848.87 | 10538.1 | 0.26 | 1.25 | 24.559 | 15.31 | 1 | 1 | 2700 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5440870.794 | 470291.3553 | 7100.0544 | 42326.705 | 427964.6503 | 16672.2065 | 0.10287 | -128738.3593 | 128738.3593
C | Xist Rating 9418 | 21.58 | 2714.77 | 150.306 | 35.6 | 2005.44 | 7849.62 | 10538 | 0.26 | 1.25 | 24.558 | 15.321 | 1 | 1 | 2710 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5444308.3488 | 473624.1 | 7152.7448 | 42483.4705 | 431140.6294 | 16686.4606 | 0.10325 | -128848.4257 | 128848.4257
C | Xist Rating 9419 | 21.63 | 2716.11 | 150.306 | 35.6 | 2006.04 | 7858.82 | 10538 | 0.25 | 1.25 | 24.556 | 15.331 | 1 | 1 | 2720 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5448625.3044 | 476968.5858 | 7205.63 | 42640.2361 | 434328.3497 | 16669.7049 | 0.10363 | -128719.0422 | 128719.0422
C | Xist Rating 9420 | 21.62 | 2717.43 | 150.306 | 35.6 | 2005.29 | 7847.3 | 10538 | 0.25 | 1.25 | 24.592 | 15.34 | 1 | 1 | 2730 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5449235.2047 | 480324.8127 | 7258.71 | 42797.0017 | 437527.8111 | 16682.9045 | 0.10402 | -128820.9661 | 128820.9661
C | Xist Rating 9421 | 21.6 | 2718.72 | 150.306 | 35.6 | 2004.49 | 7834.98 | 10538 | 0.25 | 1.25 | 24.586 | 15.35 | 1 | 1 | 2740 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5449647.0528 | 483692.7808 | 7311.9847 | 42953.7673 | 440739.0136 | 16695.861 | 0.1044 | -128921.0134 | 128921.0134
C | Xist Rating 9422 | 21.58 | 2720.27 | 150.306 | 35.6 | 2003.55 | 7820.63 | 10538 | 0.25 | 1.25 | 24.583 | 15.36 | 1 | 1 | 2750 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5450196.9585 | 487072.4901 | 7365.4543 | 43110.5328 | 443961.9572 | 16708.9087 | 0.10478 | -129021.7641 | 129021.7641
C | Xist Rating 9423 | 21.55 | 2721.69 | 150.306 | 35.6 | 2002.61 | 7806.3 | 10538 | 0.24 | 1.25 | 24.578 | 15.37 | 1 | 1 | 2760 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5450483.6109 | 490463.9404 | 7419.1186 | 43267.2984 | 447196.642 | 16691.4869 | 0.10516 | -128887.2377 | 128887.2377
C | Xist Rating 9424 | 21.53 | 2722.93 | 150.306 | 35.6 | 2001.81 | 7794.27 | 10538 | 0.24 | 1.25 | 24.572 | 15.379 | 1 | 1 | 2770 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5450788.5033 | 493867.132 | 7472.9777 | 43424.064 | 450443.068 | 16703.2987 | 0.10554 | -128978.4451 | 128978.4451
C | Xist Rating 9425 | 21.58 | 2724.47 | 150.306 | 35.6 | 2001.88 | 7795.31 | 10538 | 0.24 | 1.25 | 24.602 | 15.389 | 1 | 1 | 2780 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5454062.0036 | 497282.0646 | 7527.0316 | 43580.8296 | 453701.2351 | 16717.2243 | 0.10592 | -129085.9751 | 129085.9751
C | Xist Rating 9426 | 21.52 | 2725.88 | 150.306 | 35.6 | 2000.71 | 7777.65 | 10537.9 | 0.23 | 1.25 | 24.585 | 15.398 | 1 | 1 | 2790 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5453695.3748 | 500708.7384 | 7581.2803 | 43737.5951 | 456971.1433 | 16697.9611 | 0.1063 | -128937.2291 | 128937.2291
C | Xist Rating 9427 | 21.55 | 2726.86 | 150.306 | 35.6 | 2000.9 | 7780.48 | 10537.9 | 0.23 | 1.25 | 24.588 | 15.406 | 1 | 1 | 2800 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5456174.174 | 504147.1534 | 7635.7238 | 43894.3607 | 460252.7927 | 16708.8903 | 0.10668 | -129021.6216 | 129021.6216
C | Xist Rating 9428 | 21.54 | 2728.6 | 150.306 | 35.6 | 2000.09 | 7768.34 | 10537.9 | 0.23 | 1.25 | 24.593 | 15.417 | 1 | 1 | 2810 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5457445.574 | 507597.3095 | 7690.3621 | 44051.1263 | 463546.1832 | 16722.9935 | 0.10706 | -129130.5234 | 129130.5234
C | Xist Rating 9429 | 21.48 | 2730.08 | 150.306 | 35.6 | 1998.6 | 7745.89 | 10537.9 | 0.23 | 1.25 | 24.58 | 15.427 | 1 | 1 | 2820 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5456337.888 | 511059.2067 | 7745.1952 | 44207.8919 | 466851.3149 | 16735.536 | 0.10744 | -129227.3732 | 129227.3732
C | Xist Rating 9430 | 21.52 | 2731.45 | 150.306 | 35.6 | 1998.66 | 7746.8 | 10537.9 | 0.22 | 1.25 | 24.631 | 15.436 | 1 | 1 | 2830 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5459239.857 | 514532.8451 | 7800.223 | 44364.6574 | 470168.1877 | 16717.6593 | 0.10783 | -129089.3336 | 129089.3336
C | Xist Rating 9431 | 21.54 | 2732.77 | 150.306 | 35.6 | 1998.43 | 7743.3 | 10537.9 | 0.22 | 1.25 | 24.635 | 15.445 | 1 | 1 | 2840 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5461249.5511 | 518018.2246 | 7855.4457 | 44521.423 | 473496.8016 | 16729.5468 | 0.10821 | -129181.1256 | 129181.1256
C | Xist Rating 9432 | 21.49 | 2734.21 | 150.306 | 35.6 | 1997.13 | 7723.8 | 10537.9 | 0.22 | 1.25 | 24.625 | 15.455 | 1 | 1 | 2850 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5460572.8173 | 521515.3453 | 7910.8631 | 44678.1886 | 476837.1567 | 16742.0801 | 0.10859 | -129277.9044 | 129277.9044
C | Xist Rating 9433 | 21.53 | 2735.61 | 150.306 | 35.6 | 1997.31 | 7726.43 | 10537.9 | 0.22 | 1.25 | 24.637 | 15.464 | 1 | 1 | 2860 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5463861.2091 | 525024.2071 | 7966.4753 | 44834.9541 | 480189.2529 | 16754.1934 | 0.10897 | -129371.4401 | 129371.4401
C | Xist Rating 9434 | 21.64 | 2736.81 | 150.306 | 35.6 | 1998.71 | 7747.52 | 10538 | 0.21 | 1.25 | 24.66 | 15.473 | 1 | 1 | 2870 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5470089.5151 | 528544.81 | 8022.2824 | 44991.7197 | 483553.0903 | 16734.8961 | 0.10935 | -129222.4315 | 129222.4315
C | Xist Rating 9435 | 21.61 | 2738.31 | 150.306 | 35.6 | 1997.53 | 7729.7 | 10538 | 0.21 | 1.25 | 24.694 | 15.483 | 1 | 1 | 2880 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5469856.3743 | 532077.1541 | 8078.2842 | 45148.4853 | 486928.6688 | 16748.5241 | 0.10973 | -129327.6634 | 129327.6634
C | Xist Rating 9436 | 21.74 | 2739.66 | 150.306 | 35.6 | 1999.19 | 7754.7 | 10538 | 0.21 | 1.25 | 24.719 | 15.492 | 1 | 1 | 2890 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5477100.8754 | 535621.2394 | 8134.4807 | 45305.2509 | 490315.9885 | 16760.8752 | 0.11011 | -129423.0352 | 129423.0352
C | Xist Rating 9437 | 21.9 | 2741.04 | 150.306 | 35.6 | 2001.25 | 7785.7 | 10538.1 | 0.21 | 1.25 | 24.749 | 15.501 | 1 | 1 | 2900 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5485506.3 | 539177.0657 | 8190.8721 | 45462.0164 | 493715.0493 | 16773.3674 | 0.11049 | -129519.4972 | 129519.4972
C | Xist Rating 9438 | 22.06 | 2742.58 | 150.306 | 35.6 | 2003.26 | 7816.16 | 10538.2 | 0.2 | 1.25 | 24.784 | 15.512 | 1 | 1 | 2910 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 34 | E | Rod | 5494100.8108 | 542744.6333 | 8247.4583 | 45618.782 | 497125.8512 | 16755.7511 | 0.11087 | -129383.4688 | 129383.4688
C | Xist Rating 9439 | 22.11 | 2743.97 | 150.306 | 35.6 | 2003.61 | 7821.55 | 10538.2 | 0.2 | 1.25 | 24.795 | 15.521 | 1 | 1 | 2920 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 33 | E | Rod | 5497845.7317 | 546323.9419 | 8304.2393 | 45775.5476 | 500548.3943 | 16767.6074 | 0.11125 | -129475.0201 | 129475.0201
C | Xist Rating 9440 | 22.73 | 2745.36 | 150.306 | 35.6 | 2013.38 | 7972.29 | 10538.4 | 0.2 | 1.25 | 24.923 | 15.531 | 1 | 1 | 2930 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 33 | E | Rod | 5527452.9168 | 549914.9917 | 8361.215 | 45932.3132 | 503982.6786 | 16783.5775 | 0.11164 | -129598.3365 | 129598.3365
C | Xist Rating 9441 | 23.45 | 2746.73 | 150.306 | 35.6 | 2024.66 | 8152.13 | 10538.5 | 0.19 | 1.25 | 25.018 | 15.542 | 1 | 1 | 2940 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 33 | E | Rod | 5561194.3618 | 553517.7827 | 8418.3855 | 46089.0787 | 507428.7039 | 16766.7694 | 0.11202 | -129468.5487 | 129468.5487
C | Xist Rating 9442 | 23.83 | 2748.14 | 150.306 | 35.6 | 2030.58 | 8248.87 | 10538.6 | 0.19 | 1.25 | 25.06 | 15.551 | 1 | 1 | 2950 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 33 | E | Rod | 5580318.1212 | 557132.3148 | 8475.7509 | 46245.8443 | 510886.4705 | 16779.3018 | 0.1124 | -129565.3206 | 129565.3206
C | Xist Rating 9443 | 24.24 | 2749.51 | 150.306 | 35.6 | 2036.9 | 8354.22 | 10538.6 | 0.19 | 1.25 | 25.106 | 15.561 | 1 | 1 | 2960 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 33 | E | Rod | 5600476.919 | 560758.588 | 8533.311 | 46402.6099 | 514355.9781 | 16792.9807 | 0.11278 | -129670.9454 | 129670.9454
C | Xist Rating 9444 | 25.25 | 2750.89 | 150.306 | 35.6 | 2053.12 | 8633.98 | 10538.5 | 0.18 | 1.25 | 25.205 | 15.572 | 1 | 1 | 2970 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 33 | E | Rod | 5647907.2768 | 564396.6024 | 8591.0659 | 46559.3755 | 517837.2269 | 16775.4913 | 0.11316 | -129535.8971 | 129535.8971
C | Xist Rating 9445 | 25.34 | 2752.11 | 150.306 | 35.6 | 2054.39 | 8656.65 | 10538.4 | 0.18 | 1.25 | 25.241 | 15.58 | 1 | 1 | 2980 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 33 | E | Rod | 5653907.2629 | 568046.3579 | 8649.0156 | 46716.141 | 521330.2169 | 16786.6985 | 0.11354 | -129622.4363 | 129622.4363
C | Xist Rating 9446 | 25.33 | 2753.67 | 150.306 | 35.6 | 2053.57 | 8642.12 | 10538.4 | 0.18 | 1.25 | 25.236 | 15.59 | 1 | 1 | 2990 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 33 | E | Rod | 5654854.1019 | 571707.8546 | 8707.16 | 46872.9066 | 524834.948 | 16798.9994 | 0.11392 | -129717.4207 | 129717.4207
C | Xist Rating 9447 | 25.32 | 2755.1 | 150.306 | 35.6 | 2052.84 | 8629.09 | 10538.4 | 0.18 | 1.25 | 25.23 | 15.599 | 1 | 1 | 3000 | 152.4 | 2 | 5.6 | 19.05 | 1.3333 | 33 | E | Rod | 5655779.484 | 575381.0924 | 8765.4993 | 47029.6722 | 528351.4202 | 16810.2368 | 0.1143 | -129804.1929 | 129804.1929
C | Xist Rating 9448 | -84.33 | 287.366 | 150.313 | 35.9 | 2334.72 | 6819.2 | 58744.9 | 2.5 | 10.95 | 27.72 | 659.345 | 1 | 1 | 1000 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 670919.1475 | 75710.5256 | 973.9444 | 15956.4959 | 59754.0297 | 687835.0883 | 0.038101 | -5311280.2265 | 5311280.2265
C | Xist Rating 9449 | -84.2 | 290.318 | 150.313 | 35.9 | 2331.04 | 6795.01 | 58283.4 | 2.48 | 10.84 | 27.823 | 646.916 | 1 | 1 | 1010 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 676742.8707 | 77071.1465 | 993.5206 | 16116.0609 | 60955.0857 | 674945.1201 | 0.038482 | -5211747.3092 | 5211747.3092
C | Xist Rating 9450 | -83.03 | 312.821 | 150.313 | 35.9 | 2323.18 | 6783.01 | 54966.9 | 2.49 | 10.07 | 27.871 | 560.622 | 1 | 1 | 1020 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 726739.4908 | 78443.7183 | 1013.2917 | 16275.6258 | 62168.0925 | 585378.0526 | 0.038863 | -4520134.1556 | 4520134.1556
C | Xist Rating 9451 | -82.82 | 318.871 | 150.312 | 35.9 | 2307.89 | 6667.81 | 54178.5 | 2.4 | 9.89 | 27.175 | 541.68 | 1 | 1 | 1030 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 735919.1922 | 79828.2409 | 1033.2576 | 16435.1908 | 63393.0501 | 565544.9911 | 0.039244 | -4366988.5121 | 4366988.5121
C | Xist Rating 9452 | -82.71 | 321.898 | 150.311 | 35.9 | 2302.64 | 6630.87 | 53793.7 | 2.36 | 9.8 | 27.019 | 532.604 | 1 | 1 | 1040 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 741215.2107 | 81224.7142 | 1053.4182 | 16594.7558 | 64629.9585 | 556080.978 | 0.039625 | -4293909.9113 | 4293909.9113
C | Xist Rating 9453 | -82.44 | 327.827 | 150.311 | 35.9 | 2295.99 | 6589.13 | 53042.7 | 2.32 | 9.63 | 26.913 | 514.875 | 1 | 1 | 1050 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 752687.5137 | 82633.1384 | 1073.7737 | 16754.3207 | 65878.8177 | 537635.5805 | 0.040006 | -4151479.4414 | 4151479.4414
C | Xist Rating 9454 | -82.32 | 330.834 | 150.311 | 35.9 | 2291.76 | 6560.9 | 52675.9 | 2.29 | 9.54 | 26.864 | 506.443 | 1 | 1 | 1060 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 758192.1278 | 84053.5134 | 1094.3239 | 16913.8857 | 67139.6277 | 528863.2556 | 0.040387 | -4083741.8733 | 4083741.8733
C | Xist Rating 9455 | -81.15 | 354.968 | 150.31 | 35.9 | 2278.35 | 6503.96 | 49856.5 | 2.27 | 8.9 | 26.58 | 443.069 | 1 | 1 | 1070 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 808741.3428 | 85485.8392 | 1115.0689 | 17073.4506 | 68412.3886 | 463020.3426 | 0.040768 | -3575320.3526 | 3575320.3526
C | Xist Rating 9456 | -80.91 | 359.482 | 150.31 | 35.9 | 2278.23 | 6512.43 | 49380.5 | 2.22 | 8.79 | 26.428 | 433.061 | 1 | 1 | 1080 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 818982.6769 | 86930.1158 | 1136.0087 | 17233.0156 | 69697.1002 | 452573.4227 | 0.041149 | -3494652.0063 | 3494652.0063
C | Xist Rating 9457 | -80.58 | 365.491 | 150.31 | 35.9 | 2280.01 | 6539.63 | 48760.4 | 2.16 | 8.65 | 26.216 | 420.219 | 1 | 1 | 1090 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 833323.1349 | 88386.3432 | 1157.1433 | 17392.5806 | 70993.7626 | 439163.4767 | 0.04153 | -3391103.958 | 3391103.958
C | Xist Rating 9458 | -80.28 | 369.974 | 150.31 | 35.9 | 2288.61 | 6620.56 | 48306.6 | 2.12 | 8.55 | 26.222 | 410.953 | 1 | 1 | 1100 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 846726.1961 | 89854.5214 | 1178.4727 | 17552.1455 | 72302.3759 | 429515.0548 | 0.041911 | -3316601.4015 | 3316601.4015
C | Xist Rating 9459 | -80.1 | 373.168 | 150.309 | 35.9 | 2290.01 | 6638.76 | 48010.1 | 2.04 | 8.49 | 25.803 | 405.224 | 1 | 1 | 1110 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 854558.4517 | 91334.6504 | 1199.9969 | 17711.7105 | 73622.9399 | 423443.512 | 0.042292 | -3269718.5571 | 3269718.5571
C | Xist Rating 9460 | -78.73 | 400.079 | 150.309 | 35.9 | 2283.95 | 6647.34 | 45447.6 | 2.08 | 7.92 | 26.163 | 354.564 | 1 | 1 | 1120 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 913760.432 | 92826.7302 | 1221.7158 | 17871.2754 | 74955.4548 | 370946.1856 | 0.042673 | -2864348.1178 | 2864348.1178
C | Xist Rating 9461 | -78.54 | 403.228 | 150.309 | 35.9 | 2287.25 | 6681.79 | 45188.4 | 2.02 | 7.86 | 25.896 | 349.945 | 1 | 1 | 1130 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 922283.243 | 94330.7609 | 1243.6296 | 18030.8404 | 76299.9205 | 366066.9237 | 0.043054 | -2826671.7509 | 2826671.7509
C | Xist Rating 9462 | -78.23 | 409.307 | 150.308 | 35.9 | 2286.53 | 6688.53 | 44680.4 | 1.96 | 7.75 | 25.479 | 340.737 | 1 | 1 | 1140 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 935892.7347 | 95846.7423 | 1265.7381 | 18190.4053 | 77656.337 | 356406.7155 | 0.043435 | -2752078.1843 | 2752078.1843
C | Xist Rating 9463 | -77.9 | 415.324 | 150.308 | 35.9 | 2288.33 | 6716.99 | 44185.6 | 1.91 | 7.64 | 25.389 | 331.843 | 1 | 1 | 1150 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 950398.3689 | 97374.6745 | 1288.0414 | 18349.9703 | 79024.7042 | 347118.1643 | 0.043816 | -2680354.454 | 2680354.454
C | Xist Rating 9464 | -77.6 | 421.419 | 150.307 | 35.9 | 2286.42 | 6713.53 | 43702.7 | 1.86 | 7.53 | 25.173 | 323.365 | 1 | 1 | 1160 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 963540.83 | 98914.5576 | 1310.5395 | 18509.5353 | 80405.0223 | 338248.6143 | 0.044197 | -2611866.1399 | 2611866.1399
C | Xist Rating 9465 | -76.37 | 445.539 | 150.308 | 35.9 | 2281.58 | 6724.75 | 41831.8 | 1.88 | 7.13 | 25.36 | 290.843 | 1 | 1 | 1170 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1016532.8716 | 100466.3914 | 1333.2324 | 18669.1002 | 81797.2912 | 304540.3978 | 0.044578 | -2351580.2272 | 2351580.2272
C | Xist Rating 9466 | -76.26 | 447.206 | 150.307 | 35.9 | 2284.83 | 6756.3 | 41724.3 | 1.84 | 7.1 | 25.23 | 289.216 | 1 | 1 | 1180 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1021789.685 | 102030.1761 | 1356.1201 | 18828.6652 | 83201.5109 | 302805.8251 | 0.044959 | -2338186.3163 | 2338186.3163
C | Xist Rating 9467 | -75.69 | 459.224 | 150.307 | 35.8 | 2278.95 | 6730.64 | 40885.3 | 1.78 | 6.92 | 24.999 | 275.578 | 1 | 1 | 1190 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1046548.5348 | 103605.9116 | 1379.2026 | 18988.2301 | 84617.6814 | 288560.9117 | 0.04534 | -2228190.8709 | 2228190.8709
C | Xist Rating 9468 | -75.39 | 462.265 | 150.307 | 35.8 | 2292.75 | 6859.09 | 40681.6 | 1.75 | 6.88 | 25.062 | 272.388 | 1 | 1 | 1200 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1059858.0787 | 105193.5978 | 1402.4799 | 19147.7951 | 86045.8027 | 285233.6376 | 0.045721 | -2202498.5426 | 2202498.5426
C | Xist Rating 9469 | -75.08 | 468.429 | 150.306 | 35.8 | 2292.31 | 6868.43 | 40281.2 | 1.7 | 6.8 | 24.873 | 266.175 | 1 | 1 | 1210 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1073784.481 | 106793.2349 | 1425.9519 | 19307.3601 | 87485.8748 | 278715.7143 | 0.046102 | -2152168.8667 | 2152168.8667
C | Xist Rating 9470 | -73.78 | 495.694 | 150.306 | 35.8 | 2279.57 | 6814.81 | 38537.3 | 1.7 | 6.43 | 24.858 | 239.288 | 1 | 1 | 1220 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1129969.1716 | 108404.8228 | 1449.6188 | 19466.925 | 88937.8978 | 250811.1665 | 0.046483 | -1936697.3454 | 1936697.3454
C | Xist Rating 9471 | -73.38 | 501.708 | 150.306 | 35.8 | 2286.8 | 6892.95 | 38183.2 | 1.67 | 6.35 | 24.891 | 234.127 | 1 | 1 | 1230 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1147305.8544 | 110028.3615 | 1473.4804 | 19626.49 | 90401.8715 | 245432.3411 | 0.046864 | -1895163.4807 | 1895163.4807
C | Xist Rating 9472 | -73.06 | 507.863 | 150.306 | 35.8 | 2287.56 | 6913.08 | 37835.7 | 1.63 | 6.28 | 24.761 | 229.196 | 1 | 1 | 1240 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1161767.0843 | 111663.851 | 1497.5369 | 19786.0549 | 91877.796 | 240263.0199 | 0.047245 | -1855247.3528 | 1855247.3528
C | Xist Rating 9473 | -72.84 | 511.048 | 150.306 | 35.8 | 2292.34 | 6963.53 | 37664.6 | 1.58 | 6.24 | 24.675 | 226.86 | 1 | 1 | 1250 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1171495.7723 | 113311.2912 | 1521.7881 | 19945.6199 | 93365.6713 | 237778.1966 | 0.047626 | -1836060.206 | 1836060.206
C | Xist Rating 9474 | -72.37 | 520.092 | 150.306 | 35.8 | 2292.63 | 6986.43 | 37161.2 | 1.56 | 6.14 | 24.611 | 219.765 | 1 | 1 | 1260 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1192378.522 | 114970.6824 | 1546.2341 | 20105.1849 | 94865.4975 | 230394.0146 | 0.048007 | -1779041.5099 | 1779041.5099
C | Xist Rating 9475 | -71.1 | 545.907 | 150.306 | 35.8 | 2285.52 | 6978.63 | 35777.3 | 1.56 | 5.85 | 24.685 | 200.651 | 1 | 1 | 1270 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1247681.3666 | 116642.0243 | 1570.8749 | 20264.7498 | 96377.2744 | 210567.9371 | 0.048388 | -1625949.7948 | 1625949.7948
C | Xist Rating 9476 | -70.78 | 552.129 | 150.305 | 35.8 | 2285.37 | 6990.49 | 35477.1 | 1.52 | 5.79 | 24.536 | 196.792 | 1 | 1 | 1280 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1261819.0527 | 118325.317 | 1595.7105 | 20424.3148 | 97901.0022 | 206507.986 | 0.048769 | -1594599.9287 | 1594599.9287
C | Xist Rating 9477 | -70.46 | 558.3 | 150.305 | 35.8 | 2285.91 | 7008.82 | 35182.4 | 1.48 | 5.73 | 24.47 | 193.028 | 1 | 1 | 1290 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1276223.553 | 120020.5605 | 1620.7408 | 20583.8797 | 99436.6808 | 202553.3964 | 0.04915 | -1564063.6357 | 1564063.6357
C | Xist Rating 9478 | -69.98 | 567.323 | 150.305 | 35.8 | 2286.77 | 7036.98 | 34750.8 | 1.46 | 5.64 | 24.511 | 187.491 | 1 | 1 | 1300 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1297337.2167 | 121727.7548 | 1645.966 | 20743.4447 | 100984.3101 | 196794.434 | 0.049531 | -1519594.4546 | 1519594.4546
C | Xist Rating 9479 | -69.72 | 572.03 | 150.305 | 35.8 | 2287.8 | 7056.81 | 34539.4 | 1.43 | 5.59 | 24.461 | 184.898 | 1 | 1 | 1310 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1308690.234 | 123446.9 | 1671.3859 | 20903.0097 | 102543.8903 | 194070.2712 | 0.049912 | -1498559.1922 | 1498559.1922
C | Xist Rating 9480 | -68.45 | 597.942 | 150.305 | 35.8 | 2281.19 | 7052.29 | 33362.4 | 1.43 | 5.35 | 24.515 | 170.223 | 1 | 1 | 1320 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1364019.311 | 125177.9959 | 1697.0007 | 21062.5746 | 104115.4213 | 178850.5553 | 0.050293 | -1381036.5796 | 1381036.5796
C | Xist Rating 9481 | -68 | 607.182 | 150.305 | 35.8 | 2279.71 | 7057.99 | 32979.3 | 1.4 | 5.28 | 24.381 | 165.73 | 1 | 1 | 1330 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1384198.8772 | 126921.0426 | 1722.8102 | 21222.1396 | 105698.9031 | 174145.2665 | 0.050674 | -1344703.5872 | 1344703.5872
C | Xist Rating 9482 | -67.49 | 616.321 | 150.305 | 35.8 | 2281.99 | 7099.98 | 32606.1 | 1.37 | 5.2 | 24.264 | 161.392 | 1 | 1 | 1340 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1406438.3588 | 128676.0402 | 1748.8145 | 21381.7045 | 107294.3357 | 169601.9994 | 0.051055 | -1309621.6826 | 1309621.6826
C | Xist Rating 9483 | -67.17 | 621.045 | 150.304 | 35.8 | 2288.09 | 7169.65 | 32423 | 1.33 | 5.16 | 24.218 | 159.348 | 1 | 1 | 1350 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1421006.854 | 130442.9886 | 1775.0136 | 21541.2695 | 108901.7191 | 167431.7751 | 0.051436 | -1292863.786 | 1292863.786
C | Xist Rating 9484 | -66.8 | 624.032 | 150.305 | 35.8 | 2303.11 | 7326.24 | 32302.7 | 1.32 | 5.14 | 24.331 | 157.974 | 1 | 1 | 1360 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1437214.3395 | 132221.8877 | 1801.4075 | 21700.8345 | 110521.0533 | 166013.6456 | 0.051817 | -1281913.3661 | 1281913.3661
C | Xist Rating 9485 | -65.26 | 660.681 | 150.304 | 35.8 | 2277.34 | 7153.45 | 30901.5 | 1.32 | 4.86 | 24.195 | 142.257 | 1 | 1 | 1370 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1504595.2685 | 134012.7377 | 1827.9962 | 21860.3994 | 112152.3383 | 149694.938 | 0.052198 | -1155904.6314 | 1155904.6314
C | Xist Rating 9486 | -65.1 | 663.93 | 150.304 | 35.8 | 2277.47 | 7161.38 | 30793 | 1.29 | 4.84 | 24.14 | 141.165 | 1 | 1 | 1380 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1512080.6571 | 135815.5385 | 1854.7797 | 22019.9644 | 113795.5741 | 148525.9251 | 0.052579 | -1146877.8235 | 1146877.8235
C | Xist Rating 9487 | -64.66 | 671.664 | 150.304 | 35.8 | 2280.41 | 7207.44 | 30526.3 | 1.26 | 4.78 | 24.114 | 138.371 | 1 | 1 | 1390 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1531669.3022 | 137630.29 | 1881.7579 | 22179.5293 | 115450.7607 | 145591.1558 | 0.05296 | -1124216.3132 | 1124216.3132
C | Xist Rating 9488 | -64.23 | 679.394 | 150.304 | 35.8 | 2282.28 | 7243.24 | 30264.5 | 1.23 | 4.73 | 24.076 | 135.662 | 1 | 1 | 1400 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1550567.3383 | 139456.9924 | 1908.931 | 22339.0943 | 117117.8981 | 142743.1519 | 0.053341 | -1102224.7822 | 1102224.7822
C | Xist Rating 9489 | -63.75 | 688.593 | 150.304 | 35.8 | 2282.95 | 7270.57 | 29956.9 | 1.21 | 4.67 | 24.046 | 132.498 | 1 | 1 | 1410 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1572023.3893 | 141295.6456 | 1936.2988 | 22498.6592 | 118796.9864 | 139437.8894 | 0.053722 | -1076702.4212 | 1076702.4212
C | Xist Rating 9490 | -62.43 | 716.101 | 150.304 | 35.8 | 2276.29 | 7266.16 | 29051 | 1.22 | 4.49 | 24.111 | 123.239 | 1 | 1 | 1420 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1630053.5453 | 143146.2496 | 1963.8614 | 22658.2242 | 120488.0254 | 129855.8276 | 0.054103 | -1002712.28 | 1002712.28
C | Xist Rating 9491 | -62.19 | 721.066 | 150.304 | 35.8 | 2275.45 | 7267.75 | 28910 | 1.18 | 4.47 | 23.999 | 121.943 | 1 | 1 | 1430 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1640749.6297 | 145008.8044 | 1991.6188 | 22817.7892 | 122191.0153 | 128452.8278 | 0.054484 | -991878.6872 | 991878.6872
C | Xist Rating 9492 | -61.52 | 733.253 | 150.304 | 35.8 | 2277.94 | 7320.61 | 28541.5 | 1.16 | 4.39 | 24.002 | 118.377 | 1 | 1 | 1440 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1670306.3388 | 146883.31 | 2019.571 | 22977.3541 | 123905.9559 | 124731.4794 | 0.054865 | -963143.4211 | 963143.4211
C | Xist Rating 9493 | -61.09 | 741.021 | 150.304 | 35.8 | 2280.29 | 7362.33 | 28316.3 | 1.14 | 4.35 | 23.976 | 116.264 | 1 | 1 | 1450 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1689742.7761 | 148769.7665 | 2047.718 | 23136.9191 | 125632.8474 | 122516.4854 | 0.055246 | -946039.8248 | 946039.8248
C | Xist Rating 9494 | -60.72 | 745.627 | 150.304 | 35.8 | 2288.01 | 7454.06 | 28183.2 | 1.13 | 4.32 | 24.02 | 115.025 | 1 | 1 | 1460 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1706002.0323 | 150668.1737 | 2076.0598 | 23296.484 | 127371.6896 | 121229.6007 | 0.055627 | -936102.8418 | 936102.8418
C | Xist Rating 9495 | -59.37 | 776.55 | 150.304 | 35.8 | 2273.29 | 7370.24 | 27310 | 1.12 | 4.16 | 23.971 | 106.89 | 1 | 1 | 1470 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1765323.3495 | 152578.5317 | 2104.5964 | 23456.049 | 129122.4827 | 112774.1391 | 0.056008 | -870812.0091 | 870812.0091
C | Xist Rating 9496 | -58.88 | 785.793 | 150.304 | 35.7 | 2274.34 | 7402.07 | 27065.8 | 1.1 | 4.11 | 23.957 | 104.722 | 1 | 1 | 1480 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1787160.4516 | 154500.8405 | 2133.3277 | 23615.614 | 130885.2266 | 110501.8822 | 0.056389 | -853266.2439 | 853266.2439
C | Xist Rating 9497 | -58.46 | 793.563 | 150.304 | 35.7 | 2275.98 | 7436.89 | 26866 | 1.08 | 4.07 | 23.942 | 102.981 | 1 | 1 | 1490 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 36 | E | Rod | 1806133.5167 | 156435.1002 | 2162.2539 | 23775.1789 | 132659.9213 | 108672.5859 | 0.05677 | -839140.9022 | 839140.9022
C | Xist Rating 9498 | -58.06 | 801.425 | 150.304 | 35.7 | 2275.86 | 7453.07 | 26669.5 | 1.06 | 4.03 | 23.874 | 101.299 | 1 | 1 | 1500 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 1823931.1005 | 158381.3106 | 2191.3748 | 23934.7439 | 134446.5667 | 106900.3798 | 0.057151 | -825456.3967 | 825456.3967
C | Xist Rating 9499 | -57.58 | 810.696 | 150.304 | 35.7 | 2276.35 | 7479.47 | 26437.9 | 1.04 | 3.99 | 23.86 | 99.312 | 1 | 1 | 1510 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 1845427.8396 | 160339.4719 | 2220.6906 | 24094.3088 | 136245.163 | 104814.9231 | 0.057532 | -809353.0531 | 809353.0531
C | Xist Rating 9500 | -56.12 | 841.302 | 150.304 | 35.7 | 2269.86 | 7481.04 | 25680.1 | 1.05 | 3.84 | 23.894 | 92.804 | 1 | 1 | 1520 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 1909637.7577 | 162309.5839 | 2250.2011 | 24253.8738 | 138055.7101 | 98086.1874 | 0.057913 | -757395.5394 | 757395.5394
C | Xist Rating 9501 | -55.7 | 850.917 | 150.304 | 35.7 | 2266.44 | 7464.72 | 25467.5 | 1.02 | 3.8 | 23.804 | 91.115 | 1 | 1 | 1530 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 1928552.3255 | 164291.6468 | 2279.9064 | 24413.4388 | 139878.208 | 96287.953 | 0.058294 | -743510.0496 | 743510.0496
C | Xist Rating 9502 | -55.37 | 855.797 | 150.304 | 35.7 | 2271.81 | 7533.99 | 25362.3 | 1 | 3.78 | 23.781 | 90.304 | 1 | 1 | 1540 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 1944208.1826 | 166285.6605 | 2309.8065 | 24573.0037 | 141712.6567 | 95422.1627 | 0.058675 | -736824.6469 | 736824.6469
C | Xist Rating 9503 | -54.59 | 871.096 | 150.304 | 35.7 | 2271.63 | 7567.41 | 25019.8 | 0.99 | 3.72 | 23.778 | 87.546 | 1 | 1 | 1550 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 1978807.8065 | 168291.6249 | 2339.9013 | 24732.5687 | 143559.0563 | 92551.9149 | 0.059056 | -714661.3538 | 714661.3538
C | Xist Rating 9504 | -54.13 | 875.752 | 150.304 | 35.7 | 2282.82 | 7703.94 | 24919.2 | 0.98 | 3.7 | 23.835 | 86.765 | 1 | 1 | 1560 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 1999184.1806 | 170309.5402 | 2370.191 | 24892.1336 | 145417.4066 | 91738.6784 | 0.059437 | -708381.7574 | 708381.7574
C | Xist Rating 9505 | -52.65 | 911.463 | 150.304 | 35.7 | 2264.94 | 7586.53 | 24160.9 | 0.97 | 3.56 | 23.786 | 80.827 | 1 | 1 | 1570 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2064409.0072 | 172339.4063 | 2400.6755 | 25051.6986 | 147287.7077 | 85562.4264 | 0.059818 | -660690.3762 | 660690.3762
C | Xist Rating 9506 | -52.18 | 919.354 | 150.304 | 35.7 | 2268.22 | 7641.29 | 24006.2 | 0.95 | 3.53 | 23.78 | 79.688 | 1 | 1 | 1580 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2085297.1299 | 174381.2232 | 2431.3547 | 25211.2636 | 149169.9597 | 84355.8232 | 0.0602 | -651373.3065 | 651373.3065
C | Xist Rating 9507 | -51.71 | 927.28 | 150.304 | 35.7 | 2271.64 | 7698.37 | 23853.8 | 0.93 | 3.5 | 23.772 | 78.579 | 1 | 1 | 1590 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2106446.3392 | 176434.9909 | 2462.2288 | 25370.8285 | 151064.1624 | 83179.828 | 0.060581 | -642292.5829 | 642292.5829
C | Xist Rating 9508 | -51.06 | 938.05 | 150.304 | 35.7 | 2275.95 | 7773.84 | 23644.5 | 0.92 | 3.46 | 23.803 | 77.034 | 1 | 1 | 1600 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2134954.8975 | 178500.7094 | 2493.2976 | 25530.3935 | 152970.3159 | 81570.254 | 0.060962 | -629863.8795 | 629863.8795
C | Xist Rating 9509 | -50.76 | 943.126 | 150.303 | 35.7 | 2278.02 | 7809.18 | 23555.9 | 0.9 | 3.45 | 23.768 | 76.435 | 1 | 1 | 1610 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2148459.8905 | 180578.3787 | 2524.5612 | 25689.9584 | 154888.4203 | 80921.3801 | 0.061343 | -624853.447 | 624853.447
C | Xist Rating 9510 | -48.99 | 983.156 | 150.304 | 35.7 | 2264.58 | 7748.93 | 22804.3 | 0.9 | 3.31 | 23.801 | 70.971 | 1 | 1 | 1620 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2226435.4145 | 182667.9988 | 2556.0196 | 25849.5234 | 156818.4754 | 75258.7699 | 0.061724 | -581128.2725 | 581128.2725
C | Xist Rating 9511 | -48.56 | 987.887 | 150.304 | 35.7 | 2273.19 | 7861.82 | 22722.7 | 0.89 | 3.29 | 23.835 | 70.421 | 1 | 1 | 1630 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2245654.8495 | 184769.5698 | 2587.6728 | 26009.0883 | 158760.4814 | 74682.0186 | 0.062105 | -576674.7513 | 576674.7513
C | Xist Rating 9512 | -48.13 | 995.961 | 150.304 | 35.7 | 2274.25 | 7893.29 | 22587.9 | 0.87 | 3.27 | 23.806 | 69.524 | 1 | 1 | 1640 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2265064.3043 | 186883.0915 | 2619.5208 | 26168.6533 | 160714.4382 | 73723.0961 | 0.062486 | -569270.2063 | 569270.2063
C | Xist Rating 9513 | -47.61 | 1007.09 | 150.304 | 35.7 | 2272.36 | 7896.85 | 22402.3 | 0.85 | 3.23 | 23.772 | 68.279 | 1 | 1 | 1650 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2288471.0324 | 189008.564 | 2651.5635 | 26328.2183 | 162680.3458 | 72402.0977 | 0.062867 | -559069.8066 | 559069.8066
C | Xist Rating 9514 | -46.98 | 1017.97 | 150.304 | 35.7 | 2275.79 | 7965.01 | 22220.1 | 0.84 | 3.2 | 23.784 | 67.055 | 1 | 1 | 1660 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2316685.9463 | 191145.9874 | 2683.8011 | 26487.7832 | 164658.2041 | 71123.0945 | 0.063248 | -549193.6833 | 549193.6833
C | Xist Rating 9515 | -45.42 | 1053.73 | 150.304 | 35.7 | 2263.96 | 7908.98 | 21632.4 | 0.84 | 3.09 | 23.804 | 63.113 | 1 | 1 | 1670 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2385602.5708 | 193295.3615 | 2716.2334 | 26647.3482 | 166648.0133 | 67039.5467 | 0.063629 | -517661.6093 | 517661.6093
C | Xist Rating 9516 | -45 | 1058.57 | 150.304 | 35.7 | 2271.3 | 8010.65 | 21560 | 0.83 | 3.08 | 23.822 | 62.668 | 1 | 1 | 1680 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2404330.041 | 195456.6865 | 2748.8606 | 26806.9131 | 168649.7733 | 66569.5771 | 0.06401 | -514032.6287 | 514032.6287
C | Xist Rating 9517 | -44.38 | 1072.8 | 150.304 | 35.7 | 2267.31 | 7995.41 | 21345.7 | 0.81 | 3.04 | 23.784 | 61.315 | 1 | 1 | 1690 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2432370.168 | 197629.9622 | 2781.6825 | 26966.4781 | 170663.4841 | 65134.9278 | 0.064391 | -502954.6472 | 502954.6472
C | Xist Rating 9518 | -43.85 | 1082.23 | 150.304 | 35.7 | 2269.82 | 8049.75 | 21205.4 | 0.8 | 3.02 | 23.79 | 60.44 | 1 | 1 | 1700 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2456467.2986 | 199815.1888 | 2814.6992 | 27126.0431 | 172689.1457 | 64217.1191 | 0.064772 | -495867.5716 | 495867.5716
C | Xist Rating 9519 | -43.3 | 1093.3 | 150.304 | 35.7 | 2269.24 | 8069.38 | 21044.4 | 0.79 | 2.99 | 23.778 | 59.448 | 1 | 1 | 1710 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2480960.092 | 202012.3662 | 2847.9107 | 27285.608 | 174726.7581 | 63176.498 | 0.065153 | -487832.1711 | 487832.1711
C | Xist Rating 9520 | -41.84 | 1126.16 | 150.304 | 35.7 | 2260.34 | 8039.19 | 20566.8 | 0.79 | 2.9 | 23.804 | 56.475 | 1 | 1 | 1720 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2545504.4944 | 204221.4943 | 2881.317 | 27445.173 | 176776.3214 | 60099.0459 | 0.065534 | -464068.9021 | 464068.9021
C | Xist Rating 9521 | -41.17 | 1140.26 | 150.304 | 35.7 | 2258.63 | 8051.77 | 20374 | 0.78 | 2.87 | 23.793 | 55.327 | 1 | 1 | 1730 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2575425.4438 | 206442.5733 | 2914.9181 | 27604.7379 | 178837.8354 | 58896.1545 | 0.065915 | -454780.4936 | 454780.4936
C | Xist Rating 9522 | -40.77 | 1146.72 | 150.304 | 35.7 | 2261.9 | 8108.92 | 20289.6 | 0.77 | 2.85 | 23.796 | 54.846 | 1 | 1 | 1740 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2593765.968 | 208675.6031 | 2948.714 | 27764.3029 | 180911.3002 | 58386.5784 | 0.066296 | -450845.6821 | 450845.6821
C | Xist Rating 9523 | -40.2 | 1159.48 | 150.304 | 35.7 | 2259.4 | 8107.54 | 20123.2 | 0.75 | 2.82 | 23.771 | 53.885 | 1 | 1 | 1750 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2619729.112 | 210920.5837 | 2982.7046 | 27923.8679 | 182996.7158 | 57357.9912 | 0.066677 | -442903.2039 | 442903.2039
C | Xist Rating 9524 | -39.76 | 1169.03 | 150.304 | 35.7 | 2258.19 | 8114.98 | 20000.4 | 0.74 | 2.8 | 23.766 | 53.183 | 1 | 1 | 1760 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2639891.8557 | 213177.5151 | 3016.8901 | 28083.4328 | 185094.0823 | 56617.9116 | 0.067058 | -437188.5053 | 437188.5053
C | Xist Rating 9525 | -38.06 | 1207.97 | 150.304 | 35.7 | 2247.37 | 8072.65 | 19497 | 0.74 | 2.71 | 23.801 | 50.261 | 1 | 1 | 1770 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2714755.5389 | 215446.3973 | 3051.2703 | 28242.9978 | 187203.3995 | 53593.3573 | 0.067439 | -413833.6992 | 413833.6992
C | Xist Rating 9526 | -37.56 | 1217.63 | 150.304 | 35.7 | 2248.27 | 8107.08 | 19382.6 | 0.73 | 2.69 | 23.791 | 49.642 | 1 | 1 | 1780 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2737561.0001 | 217727.2303 | 3085.8453 | 28402.5627 | 189324.6676 | 52938.8489 | 0.06782 | -408779.7585 | 408779.7585
C | Xist Rating 9527 | -37.19 | 1222.73 | 150.304 | 35.7 | 2252.66 | 8176.05 | 19326.1 | 0.72 | 2.68 | 23.786 | 49.354 | 1 | 1 | 1790 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2754394.9618 | 220020.0141 | 3120.6151 | 28562.1277 | 191457.8864 | 52628.1684 | 0.068201 | -406380.7662 | 406380.7662
C | Xist Rating 9528 | -36.65 | 1239.97 | 150.305 | 35.6 | 2242.78 | 8088.72 | 19121.9 | 0.71 | 2.65 | 24.07 | 48.222 | 1 | 1 | 1800 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2780979.9166 | 222324.7488 | 3155.5797 | 28721.6927 | 193603.0561 | 51457.3424 | 0.068582 | -397339.9584 | 397339.9584
C | Xist Rating 9529 | -35.89 | 1249.49 | 150.305 | 35.7 | 2251.81 | 8230.97 | 19011.9 | 0.7 | 2.63 | 23.782 | 47.651 | 1 | 1 | 1810 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2813614.0769 | 224641.4342 | 3190.7391 | 28881.2576 | 195760.1766 | 50836.1353 | 0.068963 | -392543.1615 | 392543.1615
C | Xist Rating 9530 | -34.54 | 1288.7 | 150.305 | 35.6 | 2231.72 | 8062.81 | 18562.6 | 0.7 | 2.55 | 24.096 | 45.21 | 1 | 1 | 1820 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2876017.564 | 226970.0704 | 3226.0933 | 29040.8226 | 197929.2479 | 48326.5543 | 0.069344 | -373164.842 | 373164.842
C | Xist Rating 9531 | -34.51 | 1282.49 | 150.305 | 35.6 | 2244.86 | 8221.6 | 18631 | 0.7 | 2.56 | 24.136 | 45.587 | 1 | 1 | 1830 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2879010.5014 | 229310.6575 | 3261.6423 | 29200.3875 | 200110.2699 | 48727.9256 | 0.069725 | -376264.1254 | 376264.1254
C | Xist Rating 9532 | -34 | 1290.34 | 150.305 | 35.6 | 2247.53 | 8277.15 | 18545.2 | 0.69 | 2.55 | 24.17 | 45.145 | 1 | 1 | 1840 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2900077.8602 | 231663.1953 | 3297.386 | 29359.9525 | 202303.2428 | 48258.5107 | 0.070106 | -372639.4279 | 372639.4279
C | Xist Rating 9533 | -33.39 | 1303.22 | 150.305 | 35.6 | 2246.56 | 8295.43 | 18409.1 | 0.68 | 2.52 | 24.155 | 44.455 | 1 | 1 | 1850 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2927761.9232 | 234027.684 | 3333.3246 | 29519.5175 | 204508.1665 | 47528.5334 | 0.070487 | -367002.7365 | 367002.7365
C | Xist Rating 9534 | -32.73 | 1317.66 | 150.305 | 35.6 | 2244.01 | 8295.87 | 18259 | 0.66 | 2.5 | 24.138 | 43.698 | 1 | 1 | 1860 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 2956842.2166 | 236404.1234 | 3369.4579 | 29679.0824 | 206725.041 | 46708.5394 | 0.070868 | -360670.9599 | 360670.9599
C | Xist Rating 9535 | -31.11 | 1353.7 | 150.305 | 35.6 | 2237.42 | 8297.66 | 17879.5 | 0.66 | 2.43 | 24.192 | 41.751 | 1 | 1 | 1870 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3028795.454 | 238792.5137 | 3405.7861 | 29838.6474 | 208953.8663 | 44696.7114 | 0.071249 | -345136.1578 | 345136.1578
C | Xist Rating 9536 | -30.46 | 1368.13 | 150.305 | 35.6 | 2235.04 | 8300.02 | 17738.6 | 0.65 | 2.41 | 24.179 | 41.07 | 1 | 1 | 1880 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3057825.2752 | 241192.8548 | 3442.309 | 29998.2123 | 211194.6424 | 43975.5523 | 0.07163 | -339567.5579 | 339567.5579
C | Xist Rating 9537 | -29.91 | 1377.7 | 150.305 | 35.6 | 2237.29 | 8354.79 | 17646.2 | 0.64 | 2.39 | 24.204 | 40.628 | 1 | 1 | 1890 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3082314.433 | 243605.1466 | 3479.0267 | 30157.7773 | 213447.3694 | 43504.4521 | 0.072011 | -335929.8477 | 335929.8477
C | Xist Rating 9538 | -29.49 | 1387.73 | 150.305 | 35.6 | 2234.8 | 8343.71 | 17554.8 | 0.63 | 2.38 | 24.182 | 40.208 | 1 | 1 | 1900 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3101299.004 | 246029.3893 | 3515.9392 | 30317.3422 | 215712.0471 | 43053.4322 | 0.072392 | -332447.1913 | 332447.1913
C | Xist Rating 9539 | -29 | 1397.48 | 150.305 | 35.7 | 2234.81 | 8367.42 | 17464.8 | 0.62 | 2.36 | 24.199 | 39.789 | 1 | 1 | 1910 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3123102.2788 | 248465.5828 | 3553.0464 | 30476.9072 | 217988.6756 | 42605.3292 | 0.072773 | -328987.0586 | 328987.0586
C | Xist Rating 9540 | -27.12 | 1441.23 | 150.305 | 35.7 | 2224.98 | 8341.23 | 17050 | 0.62 | 2.29 | 24.255 | 37.787 | 1 | 1 | 1920 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3206707.9254 | 250913.7271 | 3590.3485 | 30636.4722 | 220277.255 | 40535.9687 | 0.073154 | -313008.0053 | 313008.0053
C | Xist Rating 9541 | -26.47 | 1455.73 | 150.305 | 35.7 | 2222.67 | 8343.81 | 16923.5 | 0.61 | 2.27 | 24.246 | 37.215 | 1 | 1 | 1930 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3235607.3991 | 253373.8222 | 3627.8454 | 30796.0371 | 222577.7851 | 39927.23 | 0.073535 | -308307.4868 | 308307.4868
C | Xist Rating 9542 | -26.01 | 1460.47 | 150.305 | 35.7 | 2229.47 | 8452.59 | 16881.8 | 0.61 | 2.26 | 24.285 | 37.032 | 1 | 1 | 1940 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3256074.0509 | 255845.8681 | 3665.537 | 30955.6021 | 224890.266 | 39745.8832 | 0.073916 | -306907.1746 | 306907.1746
C | Xist Rating 9543 | -25.6 | 1473.92 | 150.305 | 35.7 | 2221.48 | 8369.98 | 16772 | 0.59 | 2.24 | 24.263 | 36.556 | 1 | 1 | 1950 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3274283.8016 | 258329.8648 | 3703.4235 | 31115.167 | 227214.6978 | 39214.6095 | 0.074297 | -302804.8203 | 302804.8203
C | Xist Rating 9544 | -24.88 | 1489.87 | 150.305 | 35.7 | 2219.26 | 8377.47 | 16637 | 0.58 | 2.22 | 24.282 | 35.952 | 1 | 1 | 1960 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3306408.8962 | 260825.8124 | 3741.5047 | 31274.732 | 229551.0804 | 38573.4248 | 0.074678 | -297853.7618 | 297853.7618
C | Xist Rating 9545 | -23.18 | 1529.21 | 150.305 | 35.7 | 2211.41 | 8364.54 | 16303 | 0.58 | 2.16 | 24.366 | 34.444 | 1 | 1 | 1970 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3381710.2861 | 263333.7107 | 3779.7807 | 31434.297 | 231899.4137 | 37017.9843 | 0.075059 | -285843.0625 | 285843.0625
C | Xist Rating 9546 | -22.62 | 1540.51 | 150.305 | 35.7 | 2211.52 | 8393.28 | 16214 | 0.58 | 2.15 | 24.401 | 34.067 | 1 | 1 | 1980 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3406868.6752 | 265853.5598 | 3818.2515 | 31593.8619 | 234259.6979 | 36634.6068 | 0.07544 | -282882.7232 | 282882.7232
C | Xist Rating 9547 | -22.01 | 1555.21 | 150.305 | 35.7 | 2207.9 | 8376.13 | 16101.4 | 0.57 | 2.13 | 24.415 | 33.594 | 1 | 1 | 1990 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3433748.159 | 268385.3597 | 3856.9171 | 31753.4269 | 236631.9329 | 36128.6868 | 0.075821 | -278976.1429 | 278976.1429
C | Xist Rating 9548 | -21.48 | 1566.64 | 150.305 | 35.7 | 2207.21 | 8393.31 | 16014.8 | 0.56 | 2.12 | 24.417 | 33.236 | 1 | 1 | 2000 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3457903.4744 | 270929.1105 | 3895.7775 | 31912.9918 | 239016.1187 | 35741.3549 | 0.076202 | -275985.2689 | 275985.2689
C | Xist Rating 9549 | -21.04 | 1574.96 | 150.305 | 35.7 | 2208.01 | 8424.41 | 15953.6 | 0.55 | 2.11 | 24.425 | 32.99 | 1 | 1 | 2010 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3477527.4296 | 273484.812 | 3934.8326 | 32072.5568 | 241412.2552 | 35470.4108 | 0.076583 | -273893.1097 | 273893.1097
C | Xist Rating 9550 | -19.2 | 1619.15 | 150.305 | 35.7 | 2198.28 | 8393.27 | 15614.7 | 0.55 | 2.05 | 24.461 | 31.547 | 1 | 1 | 2020 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3559345.062 | 276052.4644 | 3974.0826 | 32232.1218 | 243820.3426 | 33979.672 | 0.076964 | -262382.02 | 262382.02
C | Xist Rating 9551 | -18.4 | 1635.05 | 150.305 | 35.7 | 2199.02 | 8442.91 | 15499.6 | 0.54 | 2.03 | 24.477 | 31.081 | 1 | 1 | 2030 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3595507.651 | 278632.0676 | 4013.5273 | 32391.6867 | 246240.3808 | 33480.2904 | 0.077345 | -258525.9275 | 258525.9275
C | Xist Rating 9552 | -17.97 | 1645.28 | 150.305 | 35.7 | 2197.06 | 8437.27 | 15431.6 | 0.53 | 2.02 | 24.46 | 30.822 | 1 | 1 | 2040 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3614778.8768 | 281223.6215 | 4053.1669 | 32551.2517 | 248672.3698 | 33194.0378 | 0.077726 | -256315.5609 | 256315.5609
C | Xist Rating 9553 | -17.34 | 1654.7 | 150.305 | 35.7 | 2201.74 | 8530.46 | 15364.3 | 0.53 | 2.01 | 24.497 | 30.553 | 1 | 1 | 2050 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3643219.178 | 283827.1263 | 4093.0012 | 32710.8166 | 251116.3097 | 32922.2947 | 0.078107 | -254217.2326 | 254217.2326
C | Xist Rating 9554 | -16.82 | 1669.79 | 150.305 | 35.7 | 2195.78 | 8476.72 | 15264.4 | 0.52 | 1.99 | 24.472 | 30.17 | 1 | 1 | 2060 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3666491.4862 | 286442.5819 | 4133.0303 | 32870.3816 | 253572.2003 | 32506.5489 | 0.078488 | -251006.954 | 251006.954
C | Xist Rating 9555 | -14.87 | 1717.19 | 150.305 | 35.7 | 2185.73 | 8445.3 | 14936.3 | 0.52 | 1.94 | 24.51 | 28.855 | 1 | 1 | 2070 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3753313.6987 | 289069.9883 | 4173.2542 | 33029.9466 | 256040.0417 | 31148.4611 | 0.078869 | -240520.1599 | 240520.1599
C | Xist Rating 9556 | -14.41 | 1727.22 | 150.305 | 35.7 | 2185.46 | 8464.58 | 14873.5 | 0.51 | 1.93 | 24.513 | 28.626 | 1 | 1 | 2080 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3774770.2212 | 291709.3454 | 4213.6729 | 33189.5115 | 258519.8339 | 30893.6486 | 0.07925 | -238552.5656 | 238552.5656
C | Xist Rating 9557 | -13.82 | 1740.3 | 150.305 | 35.7 | 2184.36 | 8478.98 | 14790.9 | 0.5 | 1.91 | 24.522 | 28.318 | 1 | 1 | 2090 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3801441.708 | 294360.6534 | 4254.2864 | 33349.0765 | 261011.577 | 30556.8518 | 0.079631 | -235951.9102 | 235951.9102
C | Xist Rating 9558 | -13.24 | 1753.38 | 150.305 | 35.7 | 2182.99 | 8489.34 | 14709.2 | 0.5 | 1.9 | 24.523 | 28.016 | 1 | 1 | 2100 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3827611.0062 | 297023.9122 | 4295.0947 | 33508.6414 | 263515.2708 | 30248.7683 | 0.080012 | -233572.9711 | 233572.9711
C | Xist Rating 9559 | -12.73 | 1764.9 | 150.305 | 35.7 | 2181.93 | 8500.47 | 14638.6 | 0.49 | 1.89 | 24.525 | 27.759 | 1 | 1 | 2110 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3850888.257 | 299699.1219 | 4336.0977 | 33668.2064 | 266030.9155 | 29964.2693 | 0.080393 | -231376.1445 | 231376.1445
C | Xist Rating 9560 | -10.94 | 1809.54 | 150.306 | 35.7 | 2172.34 | 8465.01 | 14359 | 0.49 | 1.84 | 24.559 | 26.703 | 1 | 1 | 2120 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3930936.1236 | 302386.2823 | 4377.2956 | 33827.7713 | 268558.5109 | 28874.5848 | 0.080774 | -222961.8899 | 222961.8899
C | Xist Rating 9561 | -10.27 | 1825.78 | 150.306 | 35.7 | 2169.73 | 8463.74 | 14263.7 | 0.48 | 1.83 | 24.557 | 26.361 | 1 | 1 | 2130 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3961449.6394 | 305085.3935 | 4418.6882 | 33987.3363 | 271098.0572 | 28501.2728 | 0.081155 | -220079.2733 | 220079.2733
C | Xist Rating 9562 | -9.7 | 1842.04 | 150.305 | 35.7 | 2164.62 | 8424.32 | 14169.8 | 0.48 | 1.81 | 24.552 | 26.029 | 1 | 1 | 2140 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 3987316.6248 | 307796.4555 | 4460.2756 | 34146.9013 | 273649.5542 | 28161.5447 | 0.081536 | -217455.9834 | 217455.9834
C | Xist Rating 9563 | -9.31 | 1850.52 | 150.305 | 35.7 | 2164.57 | 8442.55 | 14123.3 | 0.47 | 1.8 | 24.556 | 25.873 | 1 | 1 | 2150 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4005580.0764 | 310519.4683 | 4502.0578 | 34306.4662 | 276213.0021 | 27981.3412 | 0.081917 | -216064.4997 | 216064.4997
C | Xist Rating 9564 | -8.75 | 1861.98 | 150.306 | 35.7 | 2164.77 | 8472.14 | 14059 | 0.47 | 1.79 | 24.562 | 25.65 | 1 | 1 | 2160 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4030758.4446 | 313254.432 | 4544.0348 | 34466.0312 | 278788.4008 | 27755.2024 | 0.082298 | -214318.3162 | 214318.3162
C | Xist Rating 9565 | -6.92 | 1910.03 | 150.306 | 35.7 | 2153.24 | 8411.46 | 13785.9 | 0.46 | 1.75 | 24.593 | 24.676 | 1 | 1 | 2170 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4112752.9972 | 316001.3464 | 4586.2066 | 34625.5961 | 281375.7503 | 26726.3753 | 0.082679 | -206373.9859 | 206373.9859
C | Xist Rating 9566 | -6.21 | 1926.05 | 150.306 | 35.7 | 2152.15 | 8432.3 | 13699 | 0.46 | 1.74 | 24.607 | 24.379 | 1 | 1 | 2180 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4145148.5075 | 318760.2117 | 4628.5732 | 34785.1611 | 283975.0506 | 26423.6415 | 0.08306 | -204036.3557 | 204036.3557
C | Xist Rating 9567 | -5.69 | 1937.75 | 150.306 | 35.7 | 2151.24 | 8444.61 | 13639 | 0.45 | 1.73 | 24.606 | 24.182 | 1 | 1 | 2190 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4168565.31 | 321531.0277 | 4671.1346 | 34944.7261 | 286586.3017 | 26199.9313 | 0.083441 | -202308.9243 | 202308.9243
C | Xist Rating 9568 | -5.26 | 1949.85 | 150.306 | 35.7 | 2148.42 | 8427.53 | 13579.3 | 0.45 | 1.72 | 24.591 | 23.993 | 1 | 1 | 2200 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4189096.737 | 324313.7946 | 4713.8907 | 35104.291 | 289209.5036 | 26007.9527 | 0.083822 | -200826.5168 | 200826.5168
C | Xist Rating 9569 | -4.58 | 1966.13 | 150.306 | 35.7 | 2146.31 | 8432.51 | 13495.3 | 0.44 | 1.7 | 24.594 | 23.714 | 1 | 1 | 2210 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4219924.4803 | 327108.5123 | 4756.8417 | 35263.856 | 291844.6563 | 25698.9422 | 0.084203 | -198440.4198 | 198440.4198
C | Xist Rating 9570 | -2.67 | 2014.04 | 150.306 | 35.7 | 2137.62 | 8411.95 | 13246.2 | 0.44 | 1.66 | 24.632 | 22.869 | 1 | 1 | 2220 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4305252.1848 | 329915.1807 | 4799.9874 | 35423.4209 | 294491.7598 | 24827.9255 | 0.084584 | -191714.6597 | 191714.6597
C | Xist Rating 9571 | -2.08 | 2027.09 | 150.306 | 35.7 | 2137.29 | 8436.51 | 13182.5 | 0.44 | 1.65 | 24.638 | 22.667 | 1 | 1 | 2230 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4332479.1861 | 332733.8 | 4843.3279 | 35582.9859 | 297150.8141 | 24623.2709 | 0.084965 | -190134.3707 | 190134.3707
C | Xist Rating 9572 | -1.51 | 2042.15 | 150.306 | 35.7 | 2134.37 | 8424.6 | 13111.7 | 0.43 | 1.64 | 24.632 | 22.446 | 1 | 1 | 2240 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4358703.6955 | 335564.3701 | 4886.8633 | 35742.5509 | 299821.8192 | 24373.6246 | 0.085346 | -188206.6688 | 188206.6688
C | Xist Rating 9573 | -0.88 | 2058.73 | 150.306 | 35.7 | 2131.2 | 8412.2 | 13034 | 0.43 | 1.63 | 24.628 | 22.203 | 1 | 1 | 2250 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4387565.376 | 338406.891 | 4930.5934 | 35902.1158 | 302504.7752 | 24125.8438 | 0.085727 | -186293.3706 | 186293.3706
C | Xist Rating 9574 | -0.47 | 2067.17 | 150.306 | 35.7 | 2131.63 | 8437.44 | 12995.6 | 0.42 | 1.62 | 24.636 | 22.088 | 1 | 1 | 2260 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4406441.5871 | 341261.3627 | 4974.5182 | 36061.6808 | 305199.6819 | 23986.5547 | 0.086108 | -185217.8173 | 185217.8173
C | Xist Rating 9575 | 1.41 | 2118.6 | 150.306 | 35.7 | 2119.8 | 8372.07 | 12751.9 | 0.42 | 1.59 | 24.658 | 21.305 | 1 | 1 | 2270 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4491008.28 | 344127.7852 | 5018.6379 | 36221.2457 | 307906.5395 | 23178.9887 | 0.086489 | -178982.0066 | 178982.0066
C | Xist Rating 9576 | 1.98 | 2133.61 | 150.306 | 35.7 | 2117.06 | 8362 | 12686.2 | 0.41 | 1.58 | 24.654 | 21.109 | 1 | 1 | 2280 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4516980.3866 | 347006.1585 | 5062.9524 | 36380.8107 | 310625.3478 | 22954.7171 | 0.08687 | -177250.2406 | 177250.2406
C | Xist Rating 9577 | 2.69 | 2151.5 | 150.306 | 35.7 | 2114.53 | 8362.37 | 12606.9 | 0.41 | 1.56 | 24.655 | 20.868 | 1 | 1 | 2290 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4549411.295 | 349896.4826 | 5107.4617 | 36540.3757 | 313356.107 | 22709.012 | 0.087251 | -175352.971 | 175352.971
C | Xist Rating 9578 | 3.15 | 2163.36 | 150.306 | 35.7 | 2112.96 | 8363.03 | 12557.1 | 0.41 | 1.56 | 24.656 | 20.724 | 1 | 1 | 2300 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4571093.1456 | 352798.7575 | 5152.1657 | 36699.9406 | 316098.8169 | 22564.0416 | 0.087632 | -174233.5482 | 174233.5482
| Xist Rating 9579 | 3.58 | 2175.49 | 150.306 | 35.7 | 2110.29 | 8346.52 | 12507.8 | 0.4 | 1.55 | 24.66 | 20.584 | 1 | 1 | 2310 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4590914.7921 | 355712.9833 | 5197.0645 | 36859.5056 | 318853.4777 | 22397.8188 | 0.088013 | -172950.0194 | 172950.0194
| Xist Rating 9580 | 5.54 | 2228.32 | 150.306 | 35.7 | 2099.68 | 8300.26 | 12277.3 | 0.4 | 1.51 | 24.679 | 19.878 | 1 | 1 | 2320 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4678758.9376 | 358639.1598 | 5242.1582 | 37019.0705 | 321620.0893 | 21669.8507 | 0.088394 | -167328.8433 | 167328.8433
| Xist Rating 9581 | 6.11 | 2243.36 | 150.306 | 35.7 | 2097.41 | 8296.58 | 12217.1 | 0.39 | 1.5 | 24.685 | 19.707 | 1 | 1 | 2330 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4705245.6976 | 361577.2871 | 5287.4466 | 37178.6355 | 324398.6516 | 21471.1617 | 0.088775 | -165794.6193 | 165794.6193
| Xist Rating 9582 | 6.71 | 2258.38 | 150.306 | 35.7 | 2095.61 | 8300.1 | 12157.4 | 0.39 | 1.49 | 24.688 | 19.538 | 1 | 1 | 2340 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4732683.7118 | 364527.3653 | 5332.9298 | 37338.2005 | 327189.1648 | 21300.0935 | 0.089156 | -164473.6761 | 164473.6761
| Xist Rating 9583 | 7.28 | 2271.93 | 150.306 | 35.7 | 2094.69 | 8313.94 | 12104.9 | 0.38 | 1.49 | 24.694 | 19.393 | 1 | 1 | 2350 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4758989.0517 | 367489.3942 | 5378.6078 | 37497.7654 | 329991.6288 | 21128.0615 | 0.089537 | -163145.2901 | 163145.2901
| Xist Rating 9584 | 7.85 | 2288.56 | 150.306 | 35.7 | 2091.14 | 8293.38 | 12040.1 | 0.38 | 1.48 | 24.688 | 19.211 | 1 | 1 | 2360 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4785699.3584 | 370463.374 | 5424.4805 | 37657.3304 | 332806.0436 | 20943.0198 | 0.089918 | -161716.4473 | 161716.4473
| Xist Rating 9585 | 9.61 | 2336.9 | 150.306 | 35.7 | 2081.71 | 8251.57 | 11847.1 | 0.38 | 1.45 | 24.711 | 18.65 | 1 | 1 | 2370 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4864748.099 | 373449.3045 | 5470.5481 | 37816.8953 | 335632.4092 | 20365.5558 | 0.090299 | -157257.4239 | 157257.4239
| Xist Rating 9586 | 10.14 | 2352.16 | 150.306 | 35.7 | 2078.6 | 8234.04 | 11791.4 | 0.38 | 1.44 | 24.698 | 18.501 | 1 | 1 | 2380 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4889199.776 | 376447.1859 | 5516.8105 | 37976.4603 | 338470.7256 | 20214.5017 | 0.09068 | -156091.0237 | 156091.0237
| Xist Rating 9587 | 10.75 | 2368.34 | 150.306 | 35.7 | 2076.44 | 8234.49 | 11730.3 | 0.37 | 1.43 | 24.696 | 18.332 | 1 | 1 | 2390 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 4917715.9096 | 379457.0181 | 5563.2676 | 38136.0252 | 341320.9928 | 20016.6639 | 0.091061 | -154563.3727 | 154563.3727
C | Xist Rating 9588 | 22.57 | 2713.49 | 150.306 | 35.7 | 2005.96 | 7857.38 | 10538.3 | 0.41 | 1.25 | 24.658 | 15.127 | 1 | 1 | 2400 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5443152.4004 | 382478.8011 | 5609.9196 | 38295.5902 | 344183.2109 | 16796.9672 | 0.091442 | -129701.7285 | 129701.7285
C | Xist Rating 9589 | 22.63 | 2714.93 | 150.306 | 35.7 | 2006.35 | 7863.29 | 10538.4 | 0.41 | 1.25 | 24.661 | 15.139 | 1 | 1 | 2410 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5447099.8055 | 385512.5349 | 5656.7663 | 38455.1552 | 347057.3797 | 16814.0938 | 0.091823 | -129833.975 | 129833.975
C | Xist Rating 9590 | 22.74 | 2716.33 | 150.306 | 35.7 | 2007.36 | 7878.71 | 10538.5 | 0.4 | 1.25 | 24.7 | 15.15 | 1 | 1 | 2420 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5452652.1888 | 388558.2194 | 5703.8078 | 38614.7201 | 349943.4993 | 16804.9905 | 0.092204 | -129763.6821 | 129763.6821
C | Xist Rating 9591 | 22.85 | 2717.69 | 150.306 | 35.7 | 2008.58 | 7897.56 | 10538.5 | 0.39 | 1.25 | 24.702 | 15.161 | 1 | 1 | 2430 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5458697.7802 | 391615.8548 | 5751.0441 | 38774.2851 | 352841.5698 | 16794.0234 | 0.092585 | -129678.9972 | 129678.9972
C | Xist Rating 9592 | 22.98 | 2719.06 | 150.306 | 35.7 | 2010.23 | 7923.24 | 10538.4 | 0.38 | 1.25 | 24.705 | 15.172 | 1 | 1 | 2440 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5465935.9838 | 394685.441 | 5798.4752 | 38933.85 | 355751.591 | 16782.8728 | 0.092966 | -129592.895 | 129592.895
C | Xist Rating 9593 | 23 | 2720.39 | 150.306 | 35.7 | 2010.17 | 7922.37 | 10538.3 | 0.38 | 1.25 | 24.695 | 15.183 | 1 | 1 | 2450 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5468446.3663 | 397766.9781 | 5846.1011 | 39093.415 | 358673.5631 | 16798.087 | 0.093347 | -129710.3754 | 129710.3754
C | Xist Rating 9594 | 23 | 2721.86 | 150.306 | 35.7 | 2009.45 | 7911.13 | 10538.3 | 0.37 | 1.25 | 24.687 | 15.194 | 1 | 1 | 2460 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5469441.577 | 400860.4659 | 5893.9217 | 39252.98 | 361607.4859 | 16786.1597 | 0.093728 | -129618.2755 | 129618.2755
C | Xist Rating 9595 | 23.01 | 2723.21 | 150.306 | 35.7 | 2009.11 | 7905.91 | 10538.3 | 0.37 | 1.25 | 24.721 | 15.204 | 1 | 1 | 2470 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5471228.4431 | 403965.9045 | 5941.9372 | 39412.5449 | 364553.3596 | 16802.0318 | 0.094109 | -129740.8362 | 129740.8362
C | Xist Rating 9596 | 22.97 | 2724.56 | 150.306 | 35.7 | 2007.77 | 7885.04 | 10538.4 | 0.36 | 1.25 | 24.726 | 15.215 | 1 | 1 | 2480 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5470289.8312 | 407083.2939 | 5990.1474 | 39572.1099 | 367511.184 | 16790.2743 | 0.09449 | -129650.0476 | 129650.0476
C | Xist Rating 9597 | 22.97 | 2725.96 | 150.306 | 35.7 | 2007.25 | 7877.16 | 10538.4 | 0.35 | 1.25 | 24.719 | 15.226 | 1 | 1 | 2490 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5471683.21 | 410212.6342 | 6038.5525 | 39731.6748 | 370480.9593 | 16777.8168 | 0.094871 | -129553.8541 | 129553.8541
C | Xist Rating 9598 | 23.01 | 2726.94 | 150.306 | 35.7 | 2007.53 | 7881.42 | 10538.4 | 0.35 | 1.25 | 24.716 | 15.235 | 1 | 1 | 2500 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5474413.8582 | 413353.9252 | 6087.1523 | 39891.2398 | 373462.6854 | 16790.9237 | 0.095252 | -129655.0621 | 129655.0621
C | Xist Rating 9599 | 22.97 | 2728.79 | 150.306 | 35.7 | 2006.07 | 7858.92 | 10538.4 | 0.34 | 1.25 | 24.708 | 15.247 | 1 | 1 | 2510 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5474143.7553 | 416507.167 | 6135.9469 | 40050.8048 | 376456.3623 | 16779.1493 | 0.095633 | -129564.1434 | 129564.1434
C | Xist Rating 9600 | 23.02 | 2730.25 | 150.306 | 35.7 | 2006.44 | 7864.64 | 10538.3 | 0.34 | 1.25 | 24.736 | 15.258 | 1 | 1 | 2520 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5478082.81 | 419672.3597 | 6184.9363 | 40210.3697 | 379461.99 | 16795.4138 | 0.096014 | -129689.7331 | 129689.7331
C | Xist Rating 9601 | 23.03 | 2731.59 | 150.306 | 35.7 | 2006.12 | 7859.78 | 10538.3 | 0.33 | 1.25 | 24.728 | 15.268 | 1 | 1 | 2530 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5479897.3308 | 422849.5031 | 6234.1205 | 40369.9347 | 382479.5685 | 16781.217 | 0.096395 | -129580.1096 | 129580.1096
C | Xist Rating 9602 | 23 | 2732.74 | 150.306 | 35.7 | 2005.58 | 7851.5 | 10538.2 | 0.33 | 1.25 | 24.725 | 15.278 | 1 | 1 | 2540 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5480728.6892 | 426038.5974 | 6283.4995 | 40529.4996 | 385509.0978 | 16795.1471 | 0.096776 | -129687.6738 | 129687.6738
C | Xist Rating 9603 | 23.02 | 2734.28 | 150.306 | 35.7 | 2004.92 | 7841.47 | 10538.3 | 0.32 | 1.25 | 24.721 | 15.289 | 1 | 1 | 2550 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 35 | E | Rod | 5482012.6576 | 429239.6425 | 6333.0732 | 40689.0646 | 388550.5779 | 16781.8202 | 0.097157 | -129584.7674 | 129584.7674
C | Xist Rating 9604 | 23.02 | 2735.73 | 150.306 | 35.7 | 2004.38 | 7833.15 | 10538.3 | 0.32 | 1.25 | 24.712 | 15.3 | 1 | 1 | 2560 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5483442.4974 | 432452.6384 | 6382.8418 | 40848.6296 | 391604.0088 | 16796.4592 | 0.097538 | -129697.8055 | 129697.8055
C | Xist Rating 9605 | 23.03 | 2737.12 | 150.306 | 35.7 | 2004.19 | 7830.35 | 10538.3 | 0.31 | 1.25 | 24.73 | 15.31 | 1 | 1 | 2570 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5485708.5328 | 435677.585 | 6432.8051 | 41008.1945 | 394669.3905 | 16782.5636 | 0.097919 | -129590.5074 | 129590.5074
C | Xist Rating 9606 | 23.05 | 2738.49 | 150.306 | 35.7 | 2003.93 | 7826.29 | 10538.2 | 0.31 | 1.25 | 24.767 | 15.32 | 1 | 1 | 2580 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5487742.2657 | 438914.4825 | 6482.9633 | 41167.7595 | 397746.7231 | 16797.7114 | 0.0983 | -129707.4751 | 129707.4751
C | Xist Rating 9607 | 23.04 | 2739.85 | 150.306 | 35.7 | 2003.36 | 7817.73 | 10538.2 | 0.3 | 1.25 | 24.761 | 15.33 | 1 | 1 | 2590 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5488905.896 | 442163.3308 | 6533.3162 | 41327.3244 | 400836.0064 | 16782.5755 | 0.098681 | -129590.5996 | 129590.5996
C | Xist Rating 9608 | 23.09 | 2741.02 | 150.306 | 35.7 | 2003.62 | 7821.66 | 10538.2 | 0.3 | 1.25 | 24.762 | 15.339 | 1 | 1 | 2600 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5491962.4924 | 445424.1299 | 6583.8639 | 41486.8894 | 403937.2405 | 16795.2867 | 0.099062 | -129688.7518 | 129688.7518
C | Xist Rating 9609 | 23.06 | 2742.71 | 150.306 | 35.7 | 2002.56 | 7805.46 | 10538.2 | 0.3 | 1.25 | 24.758 | 15.351 | 1 | 1 | 2610 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5492441.3376 | 448696.8798 | 6634.6064 | 41646.4543 | 407050.4255 | 16810.9381 | 0.099443 | -129809.608 | 129809.608
C | Xist Rating 9610 | 23.08 | 2744.11 | 150.306 | 35.7 | 2002.27 | 7801.08 | 10538.2 | 0.29 | 1.25 | 24.758 | 15.361 | 1 | 1 | 2620 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5494449.1297 | 451981.5805 | 6685.5437 | 41806.0193 | 410175.5612 | 16795.5765 | 0.099824 | -129690.9894 | 129690.9894
C | Xist Rating 9611 | 23.09 | 2745.53 | 150.306 | 35.7 | 2001.86 | 7794.9 | 10538.2 | 0.29 | 1.25 | 24.794 | 15.371 | 1 | 1 | 2630 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5496166.6858 | 455278.232 | 6736.6758 | 41965.5843 | 413312.6478 | 16810.4105 | 0.10021 | -129805.5342 | 129805.5342
C | Xist Rating 9612 | 23.11 | 2746.78 | 150.306 | 35.7 | 2001.82 | 7794.26 | 10538.1 | 0.28 | 1.25 | 24.793 | 15.381 | 1 | 1 | 2640 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5498559.1396 | 458586.8344 | 6788.0027 | 42125.1492 | 416461.6851 | 16794.6449 | 0.10059 | -129683.7961 | 129683.7961
C | Xist Rating 9613 | 23.13 | 2748.28 | 150.306 | 35.7 | 2001.39 | 7787.8 | 10538.1 | 0.28 | 1.25 | 24.794 | 15.391 | 1 | 1 | 2650 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5500380.1092 | 461907.3875 | 6839.5243 | 42284.7142 | 419622.6733 | 16808.1749 | 0.10097 | -129788.2711 | 129788.2711
C | Xist Rating 9614 | 23.18 | 2749.62 | 150.306 | 35.7 | 2001.59 | 7790.86 | 10538.1 | 0.28 | 1.25 | 24.801 | 15.401 | 1 | 1 | 2660 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5503611.8958 | 465239.8914 | 6891.2408 | 42444.2791 | 422795.6123 | 16821.9054 | 0.10135 | -129894.2948 | 129894.2948
C | Xist Rating 9615 | 23.21 | 2751.01 | 150.307 | 35.7 | 2001.5 | 7789.57 | 10538.1 | 0.27 | 1.25 | 24.8 | 15.411 | 1 | 1 | 2670 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5506146.515 | 468584.3462 | 6943.152 | 42603.8441 | 425980.5021 | 16805.6886 | 0.10173 | -129769.0724 | 129769.0724
C | Xist Rating 9616 | 23.26 | 2752.43 | 150.307 | 35.6 | 2001.75 | 7793.35 | 10538.1 | 0.27 | 1.25 | 24.841 | 15.421 | 1 | 1 | 2680 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5509676.7525 | 471940.7517 | 6995.258 | 42763.4091 | 429177.3427 | 16820.4049 | 0.10211 | -129882.7077 | 129882.7077
C | Xist Rating 9617 | 23.33 | 2753.8 | 150.307 | 35.6 | 2002.38 | 7802.8 | 10538.2 | 0.26 | 1.25 | 24.845 | 15.431 | 1 | 1 | 2690 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5514154.044 | 475309.1081 | 7047.5588 | 42922.974 | 432386.134 | 16803.9688 | 0.10249 | -129755.7928 | 129755.7928
C | Xist Rating 9618 | 23.41 | 2755.01 | 150.307 | 35.6 | 2003.37 | 7817.79 | 10538.1 | 0.26 | 1.25 | 24.849 | 15.44 | 1 | 1 | 2700 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5519304.3837 | 478689.4152 | 7100.0544 | 43082.539 | 435606.8762 | 16816.3367 | 0.10287 | -129851.2944 | 129851.2944
C | Xist Rating 9619 | 23.43 | 2756.66 | 150.307 | 35.6 | 2003 | 7812.24 | 10538.1 | 0.26 | 1.25 | 24.845 | 15.451 | 1 | 1 | 2710 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5521589.98 | 482081.6732 | 7152.7448 | 43242.1039 | 438839.5692 | 16830.5298 | 0.10325 | -129960.8902 | 129960.8902
C | Xist Rating 9620 | 23.5 | 2758.01 | 150.307 | 35.6 | 2003.82 | 7824.82 | 10538.1 | 0.25 | 1.25 | 24.844 | 15.461 | 1 | 1 | 2720 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5526555.5982 | 485485.882 | 7205.63 | 43401.6689 | 442084.2131 | 16813.4881 | 0.10363 | -129829.2984 | 129829.2984
C | Xist Rating 9621 | 23.48 | 2759.33 | 150.307 | 35.6 | 2003.08 | 7813.44 | 10538.1 | 0.25 | 1.25 | 24.88 | 15.47 | 1 | 1 | 2730 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5527158.7364 | 488902.0415 | 7258.71 | 43561.2339 | 445340.8077 | 16826.72 | 0.10402 | -129931.4715 | 129931.4715
C | Xist Rating 9622 | 23.46 | 2760.61 | 150.307 | 35.6 | 2002.24 | 7800.72 | 10538.1 | 0.25 | 1.25 | 24.873 | 15.48 | 1 | 1 | 2740 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5527403.7664 | 492330.1519 | 7311.9847 | 43720.7988 | 448609.3531 | 16839.6781 | 0.1044 | -130031.5309 | 130031.5309
C | Xist Rating 9623 | 23.44 | 2762.16 | 150.307 | 35.6 | 2001.31 | 7786.61 | 10538.1 | 0.25 | 1.25 | 24.87 | 15.49 | 1 | 1 | 2750 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5527938.4296 | 495770.2131 | 7365.4543 | 43880.3638 | 451889.8493 | 16852.758 | 0.10478 | -130132.5299 | 130132.5299
C | Xist Rating 9624 | 23.42 | 2763.58 | 150.307 | 35.6 | 2000.36 | 7772.23 | 10538.1 | 0.24 | 1.25 | 24.865 | 15.5 | 1 | 1 | 2760 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5528154.8888 | 499222.2251 | 7419.1186 | 44039.9287 | 455182.2964 | 16835.0133 | 0.10516 | -129995.5102 | 129995.5102
C | Xist Rating 9625 | 23.42 | 2764.82 | 150.307 | 35.6 | 1999.98 | 7766.58 | 10538.1 | 0.24 | 1.25 | 24.865 | 15.509 | 1 | 1 | 2770 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5529584.7036 | 502686.1879 | 7472.9777 | 44199.4937 | 458486.6942 | 16847.0347 | 0.10554 | -130088.3366 | 130088.3366
C | Xist Rating 9626 | 23.39 | 2766.37 | 150.307 | 35.6 | 1998.8 | 7748.81 | 10538.1 | 0.24 | 1.25 | 24.898 | 15.519 | 1 | 1 | 2780 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5529420.356 | 506162.1015 | 7527.0316 | 44359.0587 | 461803.0428 | 16861.0816 | 0.10592 | -130196.8028 | 130196.8028
C | Xist Rating 9627 | 23.44 | 2767.78 | 150.307 | 35.6 | 1998.98 | 7751.5 | 10538.1 | 0.23 | 1.25 | 24.884 | 15.529 | 1 | 1 | 2790 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5532736.8644 | 509649.9659 | 7581.2803 | 44518.6236 | 465131.3423 | 16842.6048 | 0.1063 | -130054.1296 | 130054.1296
C | Xist Rating 9628 | 23.41 | 2768.75 | 150.307 | 35.6 | 1998.62 | 7746.1 | 10538 | 0.23 | 1.25 | 24.874 | 15.536 | 1 | 1 | 2800 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5533679.125 | 513149.7811 | 7635.7238 | 44678.1886 | 468471.5926 | 16852.1511 | 0.10668 | -130127.8434 | 130127.8434
C | Xist Rating 9629 | 23.41 | 2770.49 | 150.307 | 35.6 | 1997.84 | 7734.33 | 10538 | 0.23 | 1.25 | 24.877 | 15.547 | 1 | 1 | 2810 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5534995.7416 | 516661.5472 | 7690.3621 | 44837.7535 | 471823.7936 | 16866.2259 | 0.10706 | -130236.5254 | 130236.5254
C | Xist Rating 9630 | 23.34 | 2771.97 | 150.307 | 35.6 | 1996.3 | 7711.35 | 10537.9 | 0.23 | 1.25 | 24.864 | 15.557 | 1 | 1 | 2820 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5533683.711 | 520185.264 | 7745.1952 | 44997.3185 | 475187.9455 | 16878.7976 | 0.10744 | -130333.6013 | 130333.6013
C | Xist Rating 9631 | 23.37 | 2773.34 | 150.307 | 35.6 | 1996.26 | 7710.8 | 10538 | 0.22 | 1.25 | 24.914 | 15.566 | 1 | 1 | 2830 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5536307.7084 | 523720.9316 | 7800.223 | 45156.8835 | 478564.0482 | 16860.562 | 0.10783 | -130192.7905 | 130192.7905
C | Xist Rating 9632 | 23.39 | 2774.66 | 150.307 | 35.6 | 1996.04 | 7707.47 | 10538 | 0.22 | 1.25 | 24.918 | 15.575 | 1 | 1 | 2840 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5538332.3464 | 527268.5501 | 7855.4457 | 45316.4484 | 481952.1017 | 16872.4774 | 0.10821 | -130284.7979 | 130284.7979
C | Xist Rating 9633 | 23.34 | 2776.1 | 150.307 | 35.6 | 1994.73 | 7688.02 | 10537.9 | 0.22 | 1.25 | 24.908 | 15.585 | 1 | 1 | 2850 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5537569.953 | 530828.1193 | 7910.8631 | 45476.0134 | 485352.1059 | 16885.0386 | 0.10859 | -130381.7922 | 130381.7922
C | Xist Rating 9634 | 23.38 | 2777.51 | 150.307 | 35.6 | 1994.85 | 7689.73 | 10538 | 0.22 | 1.25 | 24.92 | 15.594 | 1 | 1 | 2860 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5540715.8235 | 534399.6394 | 7966.4753 | 45635.5783 | 488764.061 | 16897.1798 | 0.10897 | -130475.5434 | 130475.5434
C | Xist Rating 9635 | 23.49 | 2778.7 | 150.307 | 35.6 | 1996.21 | 7709.96 | 10538 | 0.21 | 1.25 | 24.943 | 15.603 | 1 | 1 | 2870 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5546868.727 | 537983.1102 | 8022.2824 | 45795.1433 | 492187.9669 | 16877.5463 | 0.10935 | -130323.9391 | 130323.9391
C | Xist Rating 9636 | 23.44 | 2780.21 | 150.307 | 35.6 | 1994.85 | 7689.82 | 10538 | 0.21 | 1.25 | 24.975 | 15.613 | 1 | 1 | 2880 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5546101.9185 | 541578.5319 | 8078.2842 | 45954.7082 | 495623.8236 | 16891.1468 | 0.10973 | -130428.958 | 130428.958
C | Xist Rating 9637 | 23.57 | 2781.55 | 150.307 | 35.6 | 1996.52 | 7714.68 | 10538.1 | 0.21 | 1.25 | 25 | 15.622 | 1 | 1 | 2890 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5553420.206 | 545185.9044 | 8134.4807 | 46114.2732 | 499071.6312 | 16903.5243 | 0.11011 | -130524.534 | 130524.534
C | Xist Rating 9638 | 23.73 | 2782.93 | 150.307 | 35.6 | 1998.5 | 7744.2 | 10538.2 | 0.21 | 1.25 | 25.032 | 15.632 | 1 | 1 | 2900 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5561685.605 | 548805.2276 | 8190.8721 | 46273.8382 | 502531.3895 | 16917.1361 | 0.11049 | -130629.6409 | 130629.6409
C | Xist Rating 9639 | 23.93 | 2784.47 | 150.307 | 35.6 | 2000.31 | 7771.33 | 10538.4 | 0.2 | 1.25 | 25.088 | 15.642 | 1 | 1 | 2910 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5569803.1857 | 552436.5017 | 8247.4583 | 46433.4031 | 506003.0986 | 16898.6867 | 0.11087 | -130487.1791 | 130487.1791
C | Xist Rating 9640 | 23.91 | 2785.87 | 150.307 | 35.6 | 2000.01 | 7766.89 | 10538.3 | 0.2 | 1.25 | 25.097 | 15.651 | 1 | 1 | 2920 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5571767.8587 | 556079.7266 | 8304.2393 | 46592.9681 | 509486.7585 | 16910.5179 | 0.11125 | -130578.5365 | 130578.5365
C | Xist Rating 9641 | 24.39 | 2787.25 | 150.307 | 35.6 | 2007.46 | 7880.25 | 10538.5 | 0.2 | 1.25 | 25.203 | 15.661 | 1 | 1 | 2930 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5595292.885 | 559734.9023 | 8361.215 | 46752.533 | 512982.3693 | 16925.9371 | 0.11164 | -130697.5998 | 130697.5998
C | Xist Rating 9642 | 25.16 | 2788.62 | 150.307 | 35.6 | 2019.57 | 8070.2 | 10538.6 | 0.19 | 1.25 | 25.291 | 15.672 | 1 | 1 | 2940 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5631813.2934 | 563402.0288 | 8418.3855 | 46912.098 | 516489.9308 | 16908.6098 | 0.11202 | -130563.8031 | 130563.8031
C | Xist Rating 9643 | 25.67 | 2790.03 | 150.307 | 35.6 | 2027.41 | 8196.74 | 10538.6 | 0.19 | 1.25 | 25.349 | 15.682 | 1 | 1 | 2950 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5656534.7223 | 567081.1061 | 8475.7509 | 47071.663 | 520009.4431 | 16922.606 | 0.1124 | -130671.8776 | 130671.8776
C | Xist Rating 9644 | 26.08 | 2791.4 | 150.307 | 35.6 | 2033.72 | 8300.89 | 10538.6 | 0.19 | 1.25 | 25.396 | 15.691 | 1 | 1 | 2960 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5676926.008 | 570772.1342 | 8533.311 | 47231.2279 | 523540.9063 | 16935.2962 | 0.11278 | -130769.8681 | 130769.8681
C | Xist Rating 9645 | 26.48 | 2792.78 | 150.307 | 35.6 | 2039.7 | 8401.51 | 10538.6 | 0.19 | 1.25 | 25.441 | 15.701 | 1 | 1 | 2970 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5696433.366 | 574475.1131 | 8591.0659 | 47390.7929 | 527084.3203 | 16948.9823 | 0.11316 | -130875.5488 | 130875.5488
C | Xist Rating 9646 | 27.24 | 2794.01 | 150.307 | 35.6 | 2051.89 | 8612.39 | 10538.5 | 0.18 | 1.25 | 25.538 | 15.71 | 1 | 1 | 2980 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5733001.1789 | 578190.0429 | 8649.0156 | 47550.3578 | 530639.685 | 16928.8444 | 0.11354 | -130720.0488 | 130720.0488
C | Xist Rating 9647 | 27.23 | 2795.56 | 150.307 | 35.6 | 2051.07 | 8597.92 | 10538.5 | 0.18 | 1.25 | 25.533 | 15.72 | 1 | 1 | 2990 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5733889.2492 | 581916.9234 | 8707.16 | 47709.9228 | 534207.0006 | 16941.1692 | 0.11392 | -130815.2182 | 130815.2182
C | Xist Rating 9648 | 27.22 | 2796.99 | 150.307 | 35.6 | 2050.34 | 8585.08 | 10538.5 | 0.18 | 1.25 | 25.527 | 15.729 | 1 | 1 | 3000 | 152.4 | 2 | 5.7 | 19.05 | 1.3333 | 34 | E | Rod | 5734780.4766 | 585655.7547 | 8765.4993 | 47869.4878 | 537786.267 | 16952.4306 | 0.1143 | -130902.1755 | 130902.1755
C | Xist Rating 9649 | -84.07 | 292.142 | 150.314 | 35.9 | 2332.79 | 6802.72 | 58745 | 2.5 | 10.95 | 28.117 | 667.413 | 1 | 1 | 1000 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 37 | E | Rod | 681505.9362 | 77038.7804 | 973.9444 | 16236.4344 | 60802.346 | 696258.182 | 0.038101 | -5376321.1235 | 5376321.1235
C | Xist Rating 9650 | -83.94 | 295.142 | 150.314 | 35.9 | 2328.86 | 6776.51 | 58283.4 | 2.48 | 10.84 | 28.223 | 654.829 | 1 | 1 | 1010 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 37 | E | Rod | 687344.3981 | 78423.2719 | 993.5206 | 16398.7988 | 62024.4731 | 683207.6688 | 0.038482 | -5275548.5202 | 5275548.5202
C | Xist Rating 9651 | -82.76 | 318.016 | 150.314 | 35.9 | 2321.04 | 6764.78 | 54966.9 | 2.49 | 10.07 | 28.271 | 567.48 | 1 | 1 | 1020 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 37 | E | Rod | 738127.8566 | 79819.9239 | 1013.2917 | 16561.1631 | 63258.7608 | 592545.613 | 0.038863 | -4575480.1572 | 4575480.1572
C | Xist Rating 9652 | -82.55 | 324.162 | 150.313 | 35.9 | 2305.83 | 6650.67 | 54178.4 | 2.4 | 9.89 | 27.557 | 548.3 | 1 | 1 | 1030 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 37 | E | Rod | 747462.4645 | 81228.7363 | 1033.2576 | 16723.5275 | 64505.2088 | 572462.1788 | 0.039244 | -4420401.2014 | 4420401.2014
C | Xist Rating 9653 | -82.43 | 327.237 | 150.312 | 35.9 | 2300.65 | 6614.38 | 53793.7 | 2.36 | 9.8 | 27.398 | 539.111 | 1 | 1 | 1040 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 37 | E | Rod | 752857.8041 | 82649.7092 | 1053.4182 | 16885.8918 | 65763.8174 | 562880.1839 | 0.039625 | -4346411.5769 | 4346411.5769
C | Xist Rating 9654 | -82.16 | 333.261 | 150.312 | 35.9 | 2294.02 | 6572.92 | 53042.6 | 2.32 | 9.63 | 27.29 | 521.162 | 1 | 1 | 1050 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 37 | E | Rod | 764507.3992 | 84082.8426 | 1073.7737 | 17048.2562 | 67034.5864 | 544205.7858 | 0.040006 | -4202212.8249 | 4202212.8249
C | Xist Rating 9655 | -82.03 | 336.316 | 150.312 | 35.9 | 2289.75 | 6544.49 | 52675.9 | 2.29 | 9.54 | 27.24 | 512.624 | 1 | 1 | 1060 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 37 | E | Rod | 770079.561 | 85528.1364 | 1094.3239 | 17210.6205 | 68317.5159 | 535323.1259 | 0.040387 | -4133623.2793 | 4133623.2793
C | Xist Rating 9656 | -80.84 | 360.845 | 150.311 | 35.9 | 2276.48 | 6488.81 | 49856.6 | 2.27 | 8.9 | 26.95 | 448.474 | 1 | 1 | 1070 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 37 | E | Rod | 821456.4256 | 86985.5908 | 1115.0689 | 17372.9849 | 69612.6059 | 468673.7102 | 0.040768 | -3618974.1583 | 3618974.1583
C | Xist Rating 9657 | -80.61 | 365.431 | 150.311 | 35.9 | 2275.87 | 6493.19 | 49380.4 | 2.22 | 8.79 | 26.792 | 438.338 | 1 | 1 | 1080 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 37 | E | Rod | 831673.45 | 88455.2055 | 1136.0087 | 17535.3492 | 70919.8563 | 458092.6985 | 0.041149 | -3537270.3911 | 3537270.3911
C | Xist Rating 9658 | -80.28 | 371.536 | 150.31 | 35.9 | 2277.17 | 6516.33 | 48760.4 | 2.16 | 8.65 | 26.572 | 425.338 | 1 | 1 | 1090 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 37 | E | Rod | 846050.6331 | 89936.9808 | 1157.1433 | 17697.7135 | 72239.2673 | 444517.1207 | 0.04153 | -3432443.3773 | 3432443.3773
C | Xist Rating 9659 | -79.97 | 376.09 | 150.31 | 35.9 | 2285.75 | 6596.73 | 48306.6 | 2.12 | 8.55 | 26.578 | 415.956 | 1 | 1 | 1100 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 37 | E | Rod | 859647.7175 | 91430.9165 | 1178.4727 | 17860.0779 | 73570.8386 | 434747.8755 | 0.041911 | -3357007.8555 | 3357007.8555
C | Xist Rating 9660 | -79.79 | 379.332 | 150.309 | 35.9 | 2287.16 | 6614.92 | 48010.1 | 2.04 | 8.49 | 26.149 | 410.153 | 1 | 1 | 1110 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 37 | E | Rod | 867592.9771 | 92937.0127 | 1199.9969 | 18022.4422 | 74914.5705 | 428597.39 | 0.042292 | -3309515.4371 | 3309515.4371
C | Xist Rating 9661 | -78.39 | 406.687 | 150.31 | 35.9 | 2281.18 | 6623.88 | 45447.5 | 2.08 | 7.92 | 26.517 | 358.877 | 1 | 1 | 1120 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 37 | E | Rod | 927726.2507 | 94455.2694 | 1221.7158 | 18184.8066 | 76270.4628 | 375462.1952 | 0.042673 | -2899219.5469 | 2899219.5469
C | Xist Rating 9662 | -78.2 | 409.883 | 150.309 | 35.9 | 2284.63 | 6659.48 | 45188.4 | 2.02 | 7.86 | 26.154 | 354.198 | 1 | 1 | 1130 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 936430.9983 | 95985.6865 | 1243.6296 | 18347.1709 | 77638.5156 | 370510.0552 | 0.043054 | -2860980.4345 | 2860980.4345
C | Xist Rating 9663 | -77.89 | 416.058 | 150.309 | 35.9 | 2283.73 | 6664.64 | 44680.4 | 1.96 | 7.75 | 25.737 | 344.876 | 1 | 1 | 1140 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 950164.1363 | 97528.2641 | 1265.7381 | 18509.5353 | 79018.7288 | 360730.9008 | 0.043435 | -2785468.3966 | 2785468.3966
C | Xist Rating 9664 | -77.55 | 422.17 | 150.308 | 35.9 | 2285.72 | 6694.57 | 44185.6 | 1.92 | 7.64 | 25.647 | 335.871 | 1 | 1 | 1150 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 964962.4124 | 99083.0022 | 1288.0414 | 18671.8996 | 80411.1025 | 351339.8586 | 0.043816 | -2712953.2578 | 2712953.2578
C | Xist Rating 9665 | -77.24 | 428.361 | 150.308 | 35.9 | 2283.9 | 6691.84 | 43702.7 | 1.86 | 7.53 | 25.43 | 327.286 | 1 | 1 | 1160 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 978333.6879 | 100649.9007 | 1310.5395 | 18834.264 | 81815.6367 | 342345.422 | 0.044197 | -2643500.6031 | 2643500.6031
C | Xist Rating 9666 | -75.99 | 452.876 | 150.308 | 35.9 | 2279.33 | 6705.26 | 41832 | 1.88 | 7.13 | 25.618 | 294.368 | 1 | 1 | 1170 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1032253.8531 | 102228.9597 | 1333.2324 | 18996.6283 | 83232.3314 | 308226.5426 | 0.044578 | -2380043.6601 | 2380043.6601
C | Xist Rating 9667 | -75.88 | 454.567 | 150.308 | 35.9 | 2282.88 | 6739.29 | 41724 | 1.84 | 7.1 | 25.489 | 292.722 | 1 | 1 | 1180 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1037721.913 | 103820.1792 | 1356.1201 | 19158.9926 | 84661.1865 | 306472.0073 | 0.044959 | -2366495.6033 | 2366495.6033
C | Xist Rating 9668 | -75.31 | 466.777 | 150.307 | 35.8 | 2276.66 | 6710.75 | 40885 | 1.79 | 6.92 | 25.257 | 278.915 | 1 | 1 | 1190 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1062692.5248 | 105423.5591 | 1379.2026 | 19321.357 | 86102.2021 | 292064.3498 | 0.04534 | -2255243.4914 | 2255243.4914
C | Xist Rating 9669 | -75.02 | 469.865 | 150.307 | 35.8 | 2288.71 | 6823.05 | 40681.3 | 1.76 | 6.88 | 25.317 | 275.679 | 1 | 1 | 1200 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1075384.7242 | 107039.0995 | 1402.4799 | 19483.7213 | 87555.3782 | 288688.9574 | 0.045721 | -2229179.6063 | 2229179.6063
C | Xist Rating 9670 | -74.68 | 476.125 | 150.307 | 35.8 | 2289.66 | 6844.64 | 40281.2 | 1.7 | 6.8 | 25.131 | 269.392 | 1 | 1 | 1210 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1090164.3675 | 108666.8004 | 1425.9519 | 19646.0857 | 89020.7147 | 282080.3525 | 0.046102 | -2178149.7104 | 2178149.7104
C | Xist Rating 9671 | -73.37 | 503.833 | 150.307 | 35.8 | 2276.84 | 6790.44 | 38537.2 | 1.7 | 6.43 | 25.115 | 242.177 | 1 | 1 | 1220 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1147147.1277 | 110306.6618 | 1449.6188 | 19808.45 | 90498.2117 | 253835.2808 | 0.046483 | -1960048.7542 | 1960048.7542
C | Xist Rating 9672 | -72.96 | 509.943 | 150.307 | 35.8 | 2284.18 | 6869.19 | 38183.2 | 1.67 | 6.35 | 25.15 | 236.952 | 1 | 1 | 1230 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1164801.6017 | 111958.6836 | 1473.4804 | 19970.8144 | 91987.8692 | 248389.9463 | 0.046864 | -1918001.3247 | 1918001.3247
C | Xist Rating 9673 | -72.63 | 516.193 | 150.307 | 35.8 | 2284.95 | 6889.24 | 37835.7 | 1.63 | 6.28 | 25.02 | 231.96 | 1 | 1 | 1240 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1179475.1953 | 113622.8659 | 1497.5369 | 20133.1787 | 93489.6872 | 243156.8948 | 0.047245 | -1877593.0879 | 1877593.0879
C | Xist Rating 9674 | -72.41 | 519.426 | 150.306 | 35.8 | 2289.79 | 6940.1 | 37664.5 | 1.59 | 6.24 | 24.934 | 229.594 | 1 | 1 | 1250 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1189376.4605 | 115299.2086 | 1521.7881 | 20295.5431 | 95003.6656 | 240654.3509 | 0.047626 | -1858269.1073 | 1858269.1073
C | Xist Rating 9675 | -71.93 | 528.615 | 150.306 | 35.8 | 2290.33 | 6965.1 | 37161.2 | 1.56 | 6.14 | 24.871 | 222.411 | 1 | 1 | 1260 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1210702.7929 | 116987.7119 | 1546.2341 | 20457.9074 | 96529.8045 | 233164.7893 | 0.048007 | -1800436.6978 | 1800436.6978
C | Xist Rating 9676 | -70.64 | 554.848 | 150.306 | 35.8 | 2282.99 | 6955.04 | 35777.3 | 1.56 | 5.85 | 24.944 | 203.064 | 1 | 1 | 1270 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1266712.4355 | 118688.3756 | 1570.8749 | 20620.2717 | 98068.1038 | 213096.8347 | 0.048388 | -1645477.2717 | 1645477.2717
C | Xist Rating 9677 | -70.31 | 561.166 | 150.306 | 35.8 | 2283.13 | 6969.61 | 35477.1 | 1.52 | 5.79 | 24.798 | 199.157 | 1 | 1 | 1280 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1281214.9296 | 120401.1997 | 1595.7105 | 20782.6361 | 99618.5636 | 208986.884 | 0.048769 | -1613741.3219 | 1613741.3219
C | Xist Rating 9678 | -69.98 | 567.433 | 150.306 | 35.8 | 2283.8 | 6989.02 | 35182.4 | 1.49 | 5.73 | 24.73 | 195.346 | 1 | 1 | 1290 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1295903.4854 | 122126.1844 | 1620.7408 | 20945.0004 | 101181.1839 | 204997.1861 | 0.04915 | -1582933.9325 | 1582933.9325
C | Xist Rating 9679 | -69.5 | 576.599 | 150.306 | 35.8 | 2284.64 | 7016.88 | 34750.8 | 1.47 | 5.64 | 24.772 | 189.741 | 1 | 1 | 1300 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1317321.1394 | 123863.3295 | 1645.966 | 21107.3648 | 102755.9647 | 199167.6957 | 0.049531 | -1537920.1526 | 1537920.1526
C | Xist Rating 9680 | -69.24 | 581.378 | 150.306 | 35.8 | 2285.69 | 7036.75 | 34539.4 | 1.43 | 5.59 | 24.723 | 187.115 | 1 | 1 | 1310 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1328849.8808 | 125612.635 | 1671.3859 | 21269.7291 | 104342.9059 | 196394.6224 | 0.049912 | -1516507.2155 | 1516507.2155
C | Xist Rating 9681 | -67.95 | 607.709 | 150.306 | 35.8 | 2278.81 | 7029.61 | 33362.4 | 1.44 | 5.35 | 24.776 | 172.261 | 1 | 1 | 1320 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1384853.3463 | 127374.1011 | 1697.0007 | 21432.0935 | 105942.0076 | 181003.7581 | 0.050293 | -1397663.0413 | 1397663.0413
C | Xist Rating 9682 | -67.49 | 617.093 | 150.305 | 35.8 | 2277.33 | 7035.23 | 32979.3 | 1.4 | 5.28 | 24.642 | 167.712 | 1 | 1 | 1330 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1405324.4017 | 129147.7276 | 1722.8102 | 21594.4578 | 107553.2698 | 176225.3544 | 0.050674 | -1360765.4742 | 1360765.4742
C | Xist Rating 9683 | -66.98 | 626.375 | 150.305 | 35.8 | 2279.46 | 7075.59 | 32606.1 | 1.37 | 5.2 | 24.524 | 163.32 | 1 | 1 | 1340 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1427796.7575 | 130933.5146 | 1748.8145 | 21756.8222 | 109176.6924 | 171625.6195 | 0.051055 | -1325247.5407 | 1325247.5407
C | Xist Rating 9684 | -66.66 | 631.171 | 150.305 | 35.8 | 2284.9 | 7138.35 | 32422.9 | 1.34 | 5.16 | 24.476 | 161.248 | 1 | 1 | 1350 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1442162.6179 | 132731.462 | 1775.0136 | 21919.1865 | 110812.2755 | 169440.4978 | 0.051436 | -1308374.6106 | 1308374.6106
C | Xist Rating 9685 | -66.31 | 634.206 | 150.305 | 35.8 | 2298.76 | 7282.49 | 32302.3 | 1.33 | 5.14 | 24.574 | 159.858 | 1 | 1 | 1360 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1457887.3846 | 134541.57 | 1801.4075 | 22081.5508 | 112460.0191 | 168004.7113 | 0.051817 | -1297287.8479 | 1297287.8479
C | Xist Rating 9686 | -64.71 | 671.442 | 150.305 | 35.8 | 2274.89 | 7129.3 | 30901.5 | 1.32 | 4.86 | 24.456 | 143.951 | 1 | 1 | 1370 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1527456.6914 | 136363.8383 | 1827.9962 | 22243.9152 | 114119.9232 | 151475.3112 | 0.052198 | -1169652.2014 | 1169652.2014
C | Xist Rating 9687 | -64.56 | 674.738 | 150.305 | 35.8 | 2274.57 | 7132.82 | 30793 | 1.29 | 4.84 | 24.402 | 142.843 | 1 | 1 | 1380 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1534738.8127 | 138198.2672 | 1854.7797 | 22406.2795 | 115791.9877 | 150289.4322 | 0.052579 | -1160495.158 | 1160495.158
C | Xist Rating 9688 | -64.13 | 682.592 | 150.305 | 35.8 | 2276.72 | 7170.78 | 30525.9 | 1.26 | 4.78 | 24.356 | 140.015 | 1 | 1 | 1390 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1554070.8582 | 140044.8565 | 1881.7579 | 22568.6439 | 117476.2127 | 147317.4456 | 0.05296 | -1137546.2656 | 1137546.2656
C | Xist Rating 9689 | -63.67 | 690.441 | 150.305 | 35.8 | 2279.88 | 7219.09 | 30264.5 | 1.23 | 4.73 | 24.337 | 137.272 | 1 | 1 | 1400 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1574122.6271 | 141903.6063 | 1908.931 | 22731.0082 | 119172.5981 | 144435.2805 | 0.053341 | -1115290.9502 | 1115290.9502
C | Xist Rating 9690 | -63.17 | 699.785 | 150.305 | 35.8 | 2281.1 | 7251.82 | 29956.8 | 1.21 | 4.67 | 24.309 | 134.07 | 1 | 1 | 1410 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1596279.5635 | 143774.5166 | 1936.2988 | 22893.3726 | 120881.144 | 141090.522 | 0.053722 | -1089463.6115 | 1089463.6115
C | Xist Rating 9691 | -61.83 | 727.735 | 150.305 | 35.8 | 2273.95 | 7242.32 | 29051 | 1.22 | 4.49 | 24.374 | 124.698 | 1 | 1 | 1420 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1654833.0032 | 145657.5873 | 1963.8614 | 23055.7369 | 122601.8504 | 131391.4199 | 0.054103 | -1014569.7164 | 1014569.7164
C | Xist Rating 9692 | -61.59 | 732.772 | 150.305 | 35.8 | 2273.67 | 7249.58 | 28909.8 | 1.18 | 4.47 | 24.263 | 123.386 | 1 | 1 | 1430 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1666081.7132 | 147552.8185 | 1991.6188 | 23218.1013 | 124334.7173 | 129971.3492 | 0.054484 | -1003604.3071 | 1003604.3071
C | Xist Rating 9693 | -60.93 | 745.15 | 150.305 | 35.8 | 2274.36 | 7283.84 | 28541.5 | 1.16 | 4.39 | 24.262 | 119.773 | 1 | 1 | 1440 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1694739.354 | 149460.2102 | 2019.571 | 23380.4656 | 126079.7446 | 126200.6907 | 0.054865 | -974488.2814 | 974488.2814
C | Xist Rating 9694 | -60.47 | 753.038 | 150.305 | 35.8 | 2277.92 | 7337.64 | 28316.3 | 1.14 | 4.35 | 24.24 | 117.636 | 1 | 1 | 1450 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1715360.321 | 151379.7624 | 2047.718 | 23542.8299 | 127836.9324 | 123960.8664 | 0.055246 | -957192.9516 | 957192.9516
C | Xist Rating 9695 | -60.1 | 757.716 | 150.305 | 35.8 | 2285.77 | 7430.37 | 28183.2 | 1.13 | 4.32 | 24.284 | 116.381 | 1 | 1 | 1460 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1731964.5013 | 153311.475 | 2076.0598 | 23705.1943 | 129606.2807 | 122657.3278 | 0.055627 | -947127.3721 | 947127.3721
C | Xist Rating 9696 | -58.72 | 789.13 | 150.305 | 35.8 | 2271.19 | 7348.26 | 27309.8 | 1.12 | 4.16 | 24.235 | 108.147 | 1 | 1 | 1470 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1792264.1647 | 155255.348 | 2104.5964 | 23867.5586 | 131387.7894 | 114099.0146 | 0.056008 | -881042.3467 | 881042.3467
C | Xist Rating 9697 | -58.23 | 798.517 | 150.305 | 35.7 | 2272.2 | 7379.46 | 27065.8 | 1.1 | 4.11 | 24.222 | 105.952 | 1 | 1 | 1480 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1814390.3274 | 157211.3816 | 2133.3277 | 24029.923 | 133181.4586 | 111798.5736 | 0.056389 | -863278.9504 | 863278.9504
C | Xist Rating 9698 | -57.8 | 806.406 | 150.305 | 35.7 | 2273.74 | 7413.09 | 26865.9 | 1.08 | 4.07 | 24.211 | 104.191 | 1 | 1 | 1490 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1833557.5784 | 159179.5756 | 2162.2539 | 24192.2873 | 134987.2883 | 109948.5724 | 0.05677 | -848993.7321 | 848993.7321
C | Xist Rating 9699 | -57.39 | 814.388 | 150.305 | 35.7 | 2273.85 | 7431.59 | 26669.5 | 1.06 | 4.03 | 24.171 | 102.488 | 1 | 1 | 1500 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1851796.1538 | 161159.9301 | 2191.3748 | 24354.6517 | 136805.2784 | 108156.322 | 0.057151 | -835154.4492 | 835154.4492
C | Xist Rating 9700 | -56.9 | 823.802 | 150.305 | 35.7 | 2274.67 | 7461.33 | 26438 | 1.04 | 3.99 | 24.16 | 100.476 | 1 | 1 | 1510 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1873877.6953 | 163152.4451 | 2220.6906 | 24517.016 | 138635.4291 | 106044.8531 | 0.057532 | -818850.2462 | 818850.2462
C | Xist Rating 9701 | -55.42 | 854.899 | 150.304 | 35.7 | 2267.76 | 7458.18 | 25680.1 | 1.06 | 3.84 | 24.182 | 93.888 | 1 | 1 | 1520 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1938705.7562 | 165157.1205 | 2250.2011 | 24679.3804 | 140477.7401 | 99248.9993 | 0.057913 | -766374.4645 | 766374.4645
C | Xist Rating 9702 | -54.99 | 864.657 | 150.304 | 35.7 | 2264.42 | 7442.86 | 25467.5 | 1.02 | 3.8 | 24.09 | 92.177 | 1 | 1 | 1530 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1957946.6039 | 167173.9564 | 2279.9064 | 24841.7447 | 142332.2117 | 97410.8449 | 0.058294 | -752180.7238 | 752180.7238
C | Xist Rating 9703 | -54.66 | 869.609 | 150.304 | 35.7 | 2269.76 | 7511.52 | 25362.1 | 1 | 3.78 | 24.067 | 91.356 | 1 | 1 | 1540 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 1973803.7238 | 169202.9528 | 2309.8065 | 25004.109 | 144198.8437 | 96534.4056 | 0.058675 | -745413.0918 | 745413.0918
C | Xist Rating 9704 | -53.87 | 885.148 | 150.304 | 35.7 | 2269.52 | 7543.95 | 25019.8 | 0.99 | 3.72 | 24.064 | 88.564 | 1 | 1 | 1550 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2008861.089 | 171244.1096 | 2339.9013 | 25166.4734 | 146077.6362 | 93628.7783 | 0.059056 | -722976.608 | 722976.608
C | Xist Rating 9705 | -53.42 | 889.876 | 150.304 | 35.7 | 2280.16 | 7673.73 | 24919.2 | 0.98 | 3.7 | 24.12 | 87.773 | 1 | 1 | 1560 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2029059.6602 | 173297.4269 | 2370.191 | 25328.8377 | 147968.5892 | 92805.0153 | 0.059437 | -716615.728 | 716615.728
C | Xist Rating 9706 | -51.89 | 926.15 | 150.304 | 35.7 | 2263.04 | 7565.31 | 24160.9 | 0.97 | 3.56 | 24.072 | 81.763 | 1 | 1 | 1570 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2095914.496 | 175362.9047 | 2400.6755 | 25491.2021 | 149871.7026 | 86553.9842 | 0.059818 | -668346.9232 | 668346.9232
C | Xist Rating 9707 | -51.42 | 934.16 | 150.304 | 35.7 | 2266.35 | 7620.17 | 24006.3 | 0.95 | 3.53 | 24.067 | 80.61 | 1 | 1 | 1580 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2117133.516 | 177440.5429 | 2431.3547 | 25653.5664 | 151786.9765 | 85332.6286 | 0.0602 | -658915.939 | 658915.939
C | Xist Rating 9708 | -50.94 | 942.206 | 150.304 | 35.7 | 2269.67 | 7675.78 | 23853.9 | 0.93 | 3.5 | 24.057 | 79.487 | 1 | 1 | 1590 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2138496.692 | 179530.3416 | 2462.2288 | 25815.9308 | 153714.4109 | 84141.6749 | 0.060581 | -649719.7105 | 649719.7105
C | Xist Rating 9709 | -50.3 | 953.143 | 150.304 | 35.7 | 2273.56 | 7746 | 23644.1 | 0.92 | 3.46 | 24.08 | 77.921 | 1 | 1 | 1600 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2167027.7991 | 181632.3008 | 2493.2976 | 25978.2951 | 155654.0057 | 82509.6791 | 0.060962 | -637117.871 | 637117.871
C | Xist Rating 9710 | -49.98 | 958.291 | 150.304 | 35.7 | 2276.09 | 7786.57 | 23555.9 | 0.9 | 3.45 | 24.053 | 77.316 | 1 | 1 | 1610 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2181156.5622 | 183746.4205 | 2524.5612 | 26140.6595 | 157605.761 | 81854.8082 | 0.061343 | -632061.1315 | 632061.1315
C | Xist Rating 9711 | -48.2 | 998.956 | 150.304 | 35.7 | 2262.28 | 7722.15 | 22803.9 | 0.9 | 3.31 | 24.079 | 71.784 | 1 | 1 | 1620 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2259918.1797 | 185872.7006 | 2556.0196 | 26303.0238 | 159569.6768 | 76121.2376 | 0.061724 | -587788.0196 | 587788.0196
C | Xist Rating 9712 | -47.75 | 1003.76 | 150.304 | 35.7 | 2271.17 | 7837.76 | 22722.7 | 0.89 | 3.29 | 24.12 | 71.229 | 1 | 1 | 1630 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2279709.5992 | 188011.1412 | 2587.6728 | 26465.3881 | 161545.753 | 75539.658 | 0.062105 | -583297.2158 | 583297.2158
C | Xist Rating 9713 | -47.31 | 1011.95 | 150.304 | 35.7 | 2272.23 | 7869.09 | 22587.9 | 0.87 | 3.27 | 24.091 | 70.32 | 1 | 1 | 1640 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2299383.1485 | 190161.7422 | 2619.5208 | 26627.7525 | 163533.9897 | 74567.9683 | 0.062486 | -575794.0851 | 575794.0851
C | Xist Rating 9714 | -46.77 | 1023.25 | 150.304 | 35.7 | 2270.96 | 7879.99 | 22402.3 | 0.86 | 3.23 | 24.057 | 69.061 | 1 | 1 | 1650 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2323759.82 | 192324.5037 | 2651.5635 | 26790.1168 | 165534.3869 | 73249.9131 | 0.062867 | -565616.4129 | 565616.4129
C | Xist Rating 9715 | -46.14 | 1034.3 | 150.304 | 35.7 | 2273.78 | 7940.45 | 22220.1 | 0.84 | 3.2 | 24.068 | 67.821 | 1 | 1 | 1660 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2351770.654 | 194499.4257 | 2683.8011 | 26952.4812 | 167546.9446 | 71936.3353 | 0.063248 | -555473.3131 | 555473.3131
C | Xist Rating 9716 | -44.54 | 1070.62 | 150.304 | 35.7 | 2262.69 | 7893.57 | 21632.4 | 0.84 | 3.09 | 24.089 | 63.832 | 1 | 1 | 1670 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2422481.1678 | 196686.5082 | 2716.2334 | 27114.8455 | 169571.6627 | 67804.1479 | 0.063629 | -523565.6568 | 523565.6568
C | Xist Rating 9717 | -44.13 | 1075.53 | 150.304 | 35.7 | 2269.49 | 7988.21 | 21560 | 0.83 | 3.08 | 24.107 | 63.381 | 1 | 1 | 1680 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2440904.5797 | 198885.7511 | 2748.8606 | 27277.2099 | 171608.5413 | 67327.84 | 0.06401 | -519887.7336 | 519887.7336
C | Xist Rating 9718 | -43.5 | 1089.98 | 150.304 | 35.7 | 2265.55 | 7973.62 | 21345.7 | 0.81 | 3.04 | 24.068 | 62.01 | 1 | 1 | 1690 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2469404.189 | 201097.1545 | 2781.6825 | 27439.5742 | 173657.5803 | 65874.1106 | 0.064391 | -508662.4207 | 508662.4207
C | Xist Rating 9719 | -42.95 | 1099.55 | 150.304 | 35.7 | 2268.16 | 8028.87 | 21205.4 | 0.8 | 3.02 | 24.075 | 61.125 | 1 | 1 | 1700 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2493955.328 | 203320.7184 | 2814.6992 | 27601.9386 | 175718.7799 | 64945.8645 | 0.064772 | -501494.7508 | 501494.7508
C | Xist Rating 9720 | -42.4 | 1110.79 | 150.304 | 35.7 | 2267.74 | 8050.45 | 21044.3 | 0.79 | 2.99 | 24.062 | 60.12 | 1 | 1 | 1710 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2518982.9146 | 205556.4428 | 2847.9107 | 27764.3029 | 177792.1399 | 63891.5661 | 0.065153 | -493353.738 | 493353.738
C | Xist Rating 9721 | -40.91 | 1144.16 | 150.304 | 35.7 | 2258.76 | 8019.21 | 20566.8 | 0.79 | 2.9 | 24.088 | 57.111 | 1 | 1 | 1720 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2584382.8416 | 207804.3276 | 2881.317 | 27926.6672 | 179877.6603 | 60776.8287 | 0.065534 | -469302.5611 | 469302.5611
C | Xist Rating 9722 | -40.23 | 1158.48 | 150.304 | 35.7 | 2257.15 | 8032.97 | 20374 | 0.78 | 2.87 | 24.077 | 55.949 | 1 | 1 | 1730 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2614863.132 | 210064.3729 | 2914.9181 | 28089.0316 | 181975.3413 | 59559.2787 | 0.065915 | -459900.9625 | 459900.9625
C | Xist Rating 9723 | -39.82 | 1165.04 | 150.304 | 35.7 | 2260.42 | 8089.92 | 20289.6 | 0.77 | 2.85 | 24.08 | 55.462 | 1 | 1 | 1740 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2633479.7168 | 212336.5786 | 2948.714 | 28251.3959 | 184085.1827 | 59043.3494 | 0.066296 | -455917.0933 | 455917.0933
C | Xist Rating 9724 | -39.24 | 1177.99 | 150.304 | 35.7 | 2257.98 | 8089.26 | 20123.2 | 0.75 | 2.82 | 24.055 | 54.489 | 1 | 1 | 1750 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2659877.8602 | 214620.9448 | 2982.7046 | 28413.7603 | 186207.1845 | 58001.9526 | 0.066677 | -447875.7034 | 447875.7034
C | Xist Rating 9725 | -38.8 | 1187.67 | 150.304 | 35.7 | 2256.6 | 8094.5 | 20000.3 | 0.74 | 2.8 | 24.049 | 53.779 | 1 | 1 | 1760 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2680096.122 | 216917.4715 | 3016.8901 | 28576.1246 | 188341.3469 | 57253.3781 | 0.067058 | -442095.4091 | 442095.4091
C | Xist Rating 9726 | -37.09 | 1227.23 | 150.304 | 35.7 | 2245.33 | 8046.41 | 19497 | 0.74 | 2.71 | 24.082 | 50.821 | 1 | 1 | 1770 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2755536.3359 | 219226.1587 | 3051.2703 | 28738.489 | 190487.6697 | 54191.4143 | 0.067439 | -418451.7368 | 418451.7368
C | Xist Rating 9727 | -36.56 | 1237.03 | 150.305 | 35.7 | 2246.73 | 8087.07 | 19382.6 | 0.73 | 2.69 | 24.074 | 50.194 | 1 | 1 | 1780 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2779272.4119 | 221547.0063 | 3085.8453 | 28900.8533 | 192646.153 | 53528.5834 | 0.06782 | -413333.532 | 413333.532
C | Xist Rating 9728 | -36.21 | 1242.2 | 150.305 | 35.7 | 2250.41 | 8146.59 | 19325.9 | 0.72 | 2.68 | 24.069 | 49.903 | 1 | 1 | 1790 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2795459.302 | 223880.0144 | 3120.6151 | 29063.2177 | 194816.7967 | 53214.6529 | 0.068201 | -410909.4444 | 410909.4444
C | Xist Rating 9729 | -35.37 | 1259.71 | 150.305 | 35.7 | 2248.84 | 8168.23 | 19121.7 | 0.71 | 2.65 | 24.061 | 48.769 | 1 | 1 | 1800 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2832886.2364 | 226225.183 | 3155.5797 | 29225.582 | 196999.601 | 52024.8855 | 0.068582 | -401722.3755 | 401722.3755
C | Xist Rating 9730 | -34.86 | 1269.38 | 150.305 | 35.7 | 2250.31 | 8210.91 | 19012.1 | 0.7 | 2.63 | 24.065 | 48.178 | 1 | 1 | 1810 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2856498.5078 | 228582.512 | 3190.7391 | 29387.9463 | 199194.5656 | 51399.4963 | 0.068963 | -396893.2861 | 396893.2861
C | Xist Rating 9731 | -33.16 | 1309.19 | 150.305 | 35.7 | 2239.15 | 8160.77 | 18562.5 | 0.7 | 2.55 | 24.092 | 45.719 | 1 | 1 | 1820 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2931472.7885 | 230952.0015 | 3226.0933 | 29550.3107 | 201401.6908 | 48854.9215 | 0.069344 | -377244.754 | 377244.754
C | Xist Rating 9732 | -33.46 | 1302.89 | 150.305 | 35.6 | 2243.5 | 8203.39 | 18631 | 0.7 | 2.56 | 24.423 | 46.089 | 1 | 1 | 1830 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2923033.715 | 233333.6515 | 3261.6423 | 29712.675 | 203620.9764 | 49265.7315 | 0.069725 | -380416.9196 | 380416.9196
C | Xist Rating 9733 | -32.94 | 1310.86 | 150.306 | 35.6 | 2246.69 | 8265.71 | 18545.1 | 0.69 | 2.55 | 24.455 | 45.641 | 1 | 1 | 1840 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2945096.0534 | 235727.4619 | 3297.386 | 29875.0394 | 205852.4225 | 48789.8251 | 0.070106 | -376742.0968 | 376742.0968
C | Xist Rating 9734 | -32.33 | 1323.93 | 150.305 | 35.6 | 2245.01 | 8274.27 | 18409.1 | 0.68 | 2.52 | 24.442 | 44.943 | 1 | 1 | 1850 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 2972236.0893 | 238133.4328 | 3333.3246 | 30037.4037 | 208096.0291 | 48051.5044 | 0.070487 | -371040.9799 | 371040.9799
C | Xist Rating 9735 | -31.67 | 1338.59 | 150.305 | 35.6 | 2242.27 | 8272.2 | 18259 | 0.66 | 2.5 | 24.425 | 44.176 | 1 | 1 | 1860 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3001480.1993 | 240551.5642 | 3369.4579 | 30199.7681 | 210351.7961 | 47220.7343 | 0.070868 | -364625.9933 | 364625.9933
C | Xist Rating 9736 | -30.01 | 1375.18 | 150.306 | 35.6 | 2235.96 | 8277.59 | 17879.5 | 0.66 | 2.43 | 24.478 | 42.206 | 1 | 1 | 1870 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3074847.4728 | 242981.856 | 3405.7861 | 30362.1324 | 212619.7236 | 45185.0505 | 0.071249 | -348906.9824 | 348906.9824
C | Xist Rating 9737 | -29.4 | 1389.83 | 150.306 | 35.6 | 2232.91 | 8270.76 | 17738.4 | 0.65 | 2.41 | 24.469 | 41.516 | 1 | 1 | 1880 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3103365.3053 | 245424.3084 | 3442.309 | 30524.4968 | 214899.8116 | 44454.6075 | 0.07163 | -343266.6956 | 343266.6956
C | Xist Rating 9738 | -28.79 | 1399.54 | 150.306 | 35.6 | 2236.02 | 8337.16 | 17646.2 | 0.64 | 2.39 | 24.491 | 41.07 | 1 | 1 | 1890 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3129399.4308 | 247878.9212 | 3479.0267 | 30686.8611 | 217192.0601 | 43979.0296 | 0.072011 | -339594.4087 | 339594.4087
C | Xist Rating 9739 | -28.4 | 1409.72 | 150.306 | 35.6 | 2232.58 | 8312.91 | 17554.8 | 0.63 | 2.38 | 24.471 | 40.644 | 1 | 1 | 1900 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3147312.6776 | 250345.6944 | 3515.9392 | 30849.2254 | 219496.469 | 43521.7238 | 0.072392 | -336063.2151 | 336063.2151
C | Xist Rating 9740 | -27.9 | 1419.61 | 150.306 | 35.7 | 2232.14 | 8330.21 | 17464.7 | 0.62 | 2.36 | 24.491 | 40.219 | 1 | 1 | 1910 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3168768.2654 | 252824.6281 | 3553.0464 | 31011.5898 | 221813.0383 | 43067.3833 | 0.072773 | -332554.9177 | 332554.9177
C | Xist Rating 9741 | -25.96 | 1464.04 | 150.306 | 35.7 | 2223.21 | 8316.51 | 17050.1 | 0.62 | 2.29 | 24.543 | 38.194 | 1 | 1 | 1920 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3254868.3684 | 255315.7223 | 3590.3485 | 31173.9541 | 224141.7682 | 40974.005 | 0.073154 | -316390.4057 | 316390.4057
C | Xist Rating 9742 | -25.3 | 1478.76 | 150.306 | 35.7 | 2220.94 | 8319.54 | 16923.5 | 0.61 | 2.27 | 24.537 | 37.615 | 1 | 1 | 1930 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3284237.2344 | 257818.977 | 3627.8454 | 31336.3185 | 226482.6585 | 40357.9861 | 0.073535 | -311633.6707 | 311633.6707
C | Xist Rating 9743 | -24.88 | 1483.58 | 150.306 | 35.7 | 2226.76 | 8413.64 | 16881.8 | 0.61 | 2.26 | 24.577 | 37.43 | 1 | 1 | 1940 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3303576.6008 | 260334.3921 | 3665.537 | 31498.6828 | 228835.7093 | 40174.6948 | 0.073916 | -310218.3445 | 310218.3445
C | Xist Rating 9744 | -24.41 | 1497.21 | 150.306 | 35.7 | 2219.96 | 8348.33 | 16772.2 | 0.59 | 2.24 | 24.553 | 36.947 | 1 | 1 | 1950 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3323746.3116 | 262861.9677 | 3703.4235 | 31661.0472 | 231200.9206 | 39635.618 | 0.074297 | -306055.7356 | 306055.7356
C | Xist Rating 9745 | -23.69 | 1513.41 | 150.306 | 35.7 | 2217.4 | 8350.95 | 16637 | 0.58 | 2.22 | 24.577 | 36.336 | 1 | 1 | 1960 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3355835.334 | 265401.7038 | 3741.5047 | 31823.4115 | 233578.2923 | 38987.2404 | 0.074678 | -301049.1363 | 301049.1363
C | Xist Rating 9746 | -21.94 | 1553.35 | 150.306 | 35.7 | 2210.15 | 8346.46 | 16303.1 | 0.59 | 2.16 | 24.656 | 34.81 | 1 | 1 | 1970 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3433136.5025 | 267953.6003 | 3779.7807 | 31985.7759 | 235967.8245 | 37434.6999 | 0.075059 | -289060.8301 | 289060.8301
C | Xist Rating 9747 | -21.38 | 1564.82 | 150.306 | 35.7 | 2210.25 | 8375.1 | 16214 | 0.58 | 2.15 | 24.689 | 34.428 | 1 | 1 | 1980 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3458643.405 | 270517.6574 | 3818.2515 | 32148.1402 | 238369.5172 | 37024.33 | 0.07544 | -285892.0625 | 285892.0625
C | Xist Rating 9748 | -20.77 | 1579.73 | 150.306 | 35.7 | 2206.41 | 8354.66 | 16101.4 | 0.57 | 2.13 | 24.706 | 33.949 | 1 | 1 | 1990 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3485532.0693 | 273093.8748 | 3856.9171 | 32310.5045 | 240783.3703 | 36512.1495 | 0.075821 | -281937.1403 | 281937.1403
C | Xist Rating 9749 | -20.23 | 1591.33 | 150.306 | 35.7 | 2205.71 | 8371.68 | 16014.8 | 0.56 | 2.12 | 24.708 | 33.586 | 1 | 1 | 2000 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3510012.4943 | 275682.2528 | 3895.7775 | 32472.8689 | 243209.3839 | 36119.4386 | 0.076202 | -278904.731 | 278904.731
C | Xist Rating 9750 | -19.79 | 1599.77 | 150.306 | 35.7 | 2206.47 | 8401.98 | 15953.6 | 0.55 | 2.11 | 24.715 | 33.337 | 1 | 1 | 2010 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3529844.5119 | 278282.7912 | 3934.8326 | 32635.2332 | 245647.558 | 35845.1403 | 0.076583 | -276786.6716 | 276786.6716
C | Xist Rating 9751 | -17.92 | 1644.65 | 150.306 | 35.7 | 2196.97 | 8374.28 | 15614.6 | 0.55 | 2.05 | 24.75 | 31.877 | 1 | 1 | 2020 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3613246.7105 | 280895.4901 | 3974.0826 | 32797.5976 | 248097.8925 | 34336.7687 | 0.076964 | -265139.4263 | 265139.4263
C | Xist Rating 9752 | -17.11 | 1660.79 | 150.306 | 35.7 | 2197.28 | 8417.37 | 15499.6 | 0.54 | 2.03 | 24.765 | 31.405 | 1 | 1 | 2030 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3649220.6512 | 283520.3494 | 4013.5273 | 32959.9619 | 250560.3875 | 33830.9152 | 0.077345 | -261233.3599 | 261233.3599
C | Xist Rating 9753 | -16.71 | 1671.16 | 150.306 | 35.7 | 2194.52 | 8399.92 | 15431.7 | 0.53 | 2.02 | 24.749 | 31.143 | 1 | 1 | 2040 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3667394.0432 | 286157.3693 | 4053.1669 | 33122.3263 | 253035.043 | 33541.402 | 0.077726 | -258997.8153 | 258997.8153
C | Xist Rating 9754 | -16.03 | 1680.72 | 150.306 | 35.7 | 2200.31 | 8509.06 | 15364.3 | 0.53 | 2.01 | 24.789 | 30.871 | 1 | 1 | 2050 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3698105.0232 | 288806.5496 | 4093.0012 | 33284.6906 | 255521.859 | 33266.7581 | 0.078107 | -256877.0882 | 256877.0882
C | Xist Rating 9755 | -15.51 | 1696.03 | 150.306 | 35.7 | 2194.28 | 8454.5 | 15264.3 | 0.52 | 1.99 | 24.764 | 30.483 | 1 | 1 | 2060 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3721564.7084 | 291467.8903 | 4133.0303 | 33447.055 | 258020.8354 | 32845.6196 | 0.078488 | -253625.1683 | 253625.1683
C | Xist Rating 9756 | -13.52 | 1744.16 | 150.306 | 35.7 | 2184.39 | 8425.31 | 14936.3 | 0.52 | 1.94 | 24.8 | 29.152 | 1 | 1 | 2070 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3809925.6624 | 294141.3916 | 4173.2542 | 33609.4193 | 260531.9723 | 31470.8874 | 0.078869 | -243009.8504 | 243009.8504
C | Xist Rating 9757 | -13.05 | 1754.34 | 150.306 | 35.7 | 2184.13 | 8444.63 | 14873.5 | 0.51 | 1.93 | 24.804 | 28.92 | 1 | 1 | 2080 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3831706.6242 | 296827.0533 | 4213.6729 | 33771.7836 | 263055.2696 | 31212.8042 | 0.07925 | -241017.0004 | 241017.0004
C | Xist Rating 9758 | -12.44 | 1767.6 | 150.306 | 35.7 | 2183.2 | 8461.5 | 14790.9 | 0.5 | 1.91 | 24.814 | 28.608 | 1 | 1 | 2090 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3859024.32 | 299524.8754 | 4254.2864 | 33934.148 | 265590.7274 | 30871.6942 | 0.079631 | -238383.0393 | 238383.0393
C | Xist Rating 9759 | -11.85 | 1780.88 | 150.306 | 35.7 | 2181.87 | 8472.52 | 14709.2 | 0.5 | 1.9 | 24.816 | 28.303 | 1 | 1 | 2100 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3885648.6456 | 302234.8581 | 4295.0947 | 34096.5123 | 268138.3457 | 30560.6077 | 0.080012 | -235980.9119 | 235980.9119
C | Xist Rating 9760 | -11.34 | 1792.56 | 150.306 | 35.7 | 2180.77 | 8483.02 | 14638.6 | 0.49 | 1.89 | 24.818 | 28.042 | 1 | 1 | 2110 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3909161.0712 | 304957.0012 | 4336.0977 | 34258.8767 | 270698.1245 | 30271.7432 | 0.080393 | -233750.3765 | 233750.3765
C | Xist Rating 9761 | -9.52 | 1837.88 | 150.306 | 35.7 | 2171.21 | 8447.98 | 14359 | 0.49 | 1.84 | 24.852 | 26.973 | 1 | 1 | 2120 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 3990423.4348 | 307691.3048 | 4377.2956 | 34421.241 | 273270.0637 | 29168.6226 | 0.080774 | -225232.3717 | 225232.3717
C | Xist Rating 9762 | -8.83 | 1854.36 | 150.306 | 35.7 | 2168.6 | 8446.58 | 14263.7 | 0.48 | 1.83 | 24.85 | 26.628 | 1 | 1 | 2130 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 4021365.096 | 310437.7688 | 4418.6882 | 34583.6054 | 275854.1634 | 28791.9796 | 0.081155 | -222324.0349 | 222324.0349
C | Xist Rating 9763 | -8.25 | 1870.87 | 150.306 | 35.7 | 2163.6 | 8408.9 | 14169.8 | 0.48 | 1.81 | 24.847 | 26.291 | 1 | 1 | 2140 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 4047814.332 | 313196.3933 | 4460.2756 | 34745.9697 | 278450.4236 | 28447.2142 | 0.081536 | -219661.8478 | 219661.8478
C | Xist Rating 9764 | -7.87 | 1879.46 | 150.306 | 35.7 | 2163.29 | 8423.01 | 14123.3 | 0.47 | 1.8 | 24.85 | 26.133 | 1 | 1 | 2150 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 4065817.0234 | 315967.1783 | 4502.0578 | 34908.3341 | 281058.8443 | 28264.6676 | 0.081917 | -218252.2711 | 218252.2711
C | Xist Rating 9765 | -7.33 | 1891.09 | 150.306 | 35.7 | 2163.02 | 8445.47 | 14058.9 | 0.47 | 1.79 | 24.858 | 25.908 | 1 | 1 | 2160 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 4090465.4918 | 318750.1238 | 4544.0348 | 35070.6984 | 283679.4254 | 28036.6048 | 0.082298 | -216491.2306 | 216491.2306
C | Xist Rating 9766 | -5.43 | 1939.87 | 150.306 | 35.7 | 2152.23 | 8396.02 | 13785.9 | 0.46 | 1.75 | 24.886 | 24.921 | 1 | 1 | 2170 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 4175046.4101 | 321545.2297 | 4586.2066 | 35233.0627 | 286312.167 | 26993.9174 | 0.082679 | -208439.8751 | 208439.8751
C | Xist Rating 9767 | -4.71 | 1956.13 | 150.306 | 35.7 | 2151.13 | 8416.63 | 13699 | 0.46 | 1.74 | 24.9 | 24.621 | 1 | 1 | 2180 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 36 | E | Rod | 4207889.9269 | 324352.4961 | 4628.5732 | 35395.4271 | 288957.069 | 26688.1285 | 0.08306 | -206078.6543 | 206078.6543
C | Xist Rating 9768 | -4.2 | 1967.99 | 150.306 | 35.7 | 2149.89 | 8423.97 | 13638.9 | 0.45 | 1.73 | 24.894 | 24.422 | 1 | 1 | 2190 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4230962.0211 | 327171.923 | 4671.1346 | 35557.7914 | 291614.1315 | 26461.8932 | 0.083441 | -204331.7249 | 204331.7249
C | Xist Rating 9769 | -3.75 | 1980.27 | 150.306 | 35.7 | 2147.36 | 8411.26 | 13579.3 | 0.45 | 1.72 | 24.879 | 24.23 | 1 | 1 | 2200 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4252352.5872 | 330003.5103 | 4713.8907 | 35720.1558 | 294283.3545 | 26266.8572 | 0.083822 | -202825.709 | 202825.709
C | Xist Rating 9770 | -3.05 | 1996.78 | 150.306 | 35.7 | 2145.43 | 8419.02 | 13495.3 | 0.44 | 1.7 | 24.882 | 23.948 | 1 | 1 | 2210 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4283951.7154 | 332847.2581 | 4756.8417 | 35882.5201 | 296964.738 | 25954.5041 | 0.084203 | -200413.8005 | 200413.8005
C | Xist Rating 9771 | -1.12 | 2045.43 | 150.306 | 35.7 | 2136.6 | 8396.16 | 13246.2 | 0.44 | 1.66 | 24.919 | 23.093 | 1 | 1 | 2220 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4370265.738 | 335703.1664 | 4799.9874 | 36044.8845 | 299658.2819 | 25073.1154 | 0.084584 | -193607.9508 | 193607.9508
C | Xist Rating 9772 | -0.53 | 2058.67 | 150.306 | 35.7 | 2135.94 | 8415.48 | 13182.5 | 0.44 | 1.65 | 24.925 | 22.888 | 1 | 1 | 2230 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4397195.5998 | 338571.2351 | 4843.3279 | 36207.2488 | 302363.9863 | 24865.4018 | 0.084965 | -192004.0418 | 192004.0418
C | Xist Rating 9773 | 0.0323 | 2073.94 | 150.306 | 35.7 | 2132.7 | 8398.49 | 13111.7 | 0.43 | 1.64 | 24.918 | 22.664 | 1 | 1 | 2240 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4423091.838 | 341451.4643 | 4886.8633 | 36369.6132 | 305081.8512 | 24612.3654 | 0.085346 | -190050.1614 | 190050.1614
C | Xist Rating 9774 | 0.66 | 2090.76 | 150.306 | 35.7 | 2129.22 | 8381.51 | 13034.1 | 0.43 | 1.63 | 24.914 | 22.418 | 1 | 1 | 2250 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4451688.0072 | 344343.854 | 4930.5934 | 36531.9775 | 307811.8765 | 24361.5241 | 0.085727 | -188113.2319 | 188113.2319
C | Xist Rating 9775 | 1.06 | 2099.32 | 150.306 | 35.7 | 2129.51 | 8404.27 | 12995.6 | 0.42 | 1.62 | 24.922 | 22.302 | 1 | 1 | 2260 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4470522.9332 | 347248.4041 | 4974.5182 | 36694.3418 | 310554.0623 | 24220.962 | 0.086108 | -187027.8481 | 187027.8481
C | Xist Rating 9776 | 2.96 | 2151.53 | 150.306 | 35.7 | 2117.43 | 8335.18 | 12751.9 | 0.42 | 1.59 | 24.944 | 21.509 | 1 | 1 | 2270 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4555714.1679 | 350165.1148 | 5018.6379 | 36856.7062 | 313308.4086 | 23403.0648 | 0.086489 | -180712.2631 | 180712.2631
C | Xist Rating 9777 | 3.54 | 2166.75 | 150.306 | 35.7 | 2114.7 | 8325.31 | 12686.2 | 0.41 | 1.58 | 24.939 | 21.31 | 1 | 1 | 2280 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4582026.225 | 353093.9858 | 5062.9524 | 37019.0705 | 316074.9153 | 23175.3974 | 0.08687 | -178954.2752 | 178954.2752
C | Xist Rating 9778 | 4.26 | 2184.91 | 150.306 | 35.7 | 2112.18 | 8325.62 | 12607 | 0.41 | 1.56 | 24.94 | 21.067 | 1 | 1 | 2290 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4614923.2038 | 356035.0174 | 5107.4617 | 37181.4349 | 318853.5825 | 22927.6676 | 0.087251 | -177041.372 | 177041.372
C | Xist Rating 9779 | 4.73 | 2196.94 | 150.306 | 35.7 | 2110.58 | 8325.88 | 12557.2 | 0.41 | 1.56 | 24.942 | 20.921 | 1 | 1 | 2300 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4636817.6252 | 358988.2094 | 5152.1657 | 37343.7992 | 321644.4102 | 22780.7149 | 0.087632 | -175906.642 | 175906.642
| Xist Rating 9780 | 5.16 | 2209.23 | 150.306 | 35.7 | 2107.93 | 8309.67 | 12507.8 | 0.4 | 1.55 | 24.946 | 20.779 | 1 | 1 | 2310 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4656902.1939 | 361953.5619 | 5197.0645 | 37506.1636 | 324447.3983 | 22612.1715 | 0.088013 | -174605.1944 | 174605.1944
| Xist Rating 9781 | 7.15 | 2262.86 | 150.306 | 35.7 | 2097.34 | 8263.74 | 12277.3 | 0.4 | 1.51 | 24.964 | 20.064 | 1 | 1 | 2320 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4745986.7924 | 364931.0749 | 5242.1582 | 37668.5279 | 327262.547 | 21874.8667 | 0.088394 | -168911.9219 | 168911.9219
| Xist Rating 9782 | 7.73 | 2278.12 | 150.306 | 35.7 | 2095.04 | 8259.58 | 12217.1 | 0.39 | 1.5 | 24.971 | 19.891 | 1 | 1 | 2330 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4772752.5248 | 367920.7483 | 5287.4466 | 37830.8923 | 330089.8561 | 21673.8948 | 0.088775 | -167360.0706 | 167360.0706
| Xist Rating 9783 | 8.33 | 2293.35 | 150.306 | 35.7 | 2093.2 | 8262.46 | 12157.5 | 0.39 | 1.49 | 24.974 | 19.721 | 1 | 1 | 2340 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4800440.22 | 370922.5822 | 5332.9298 | 37993.2566 | 332929.3256 | 21501.8381 | 0.089156 | -166031.4945 | 166031.4945
| Xist Rating 9784 | 8.92 | 2307.09 | 150.306 | 35.7 | 2092.47 | 8279.07 | 12104.9 | 0.38 | 1.49 | 24.982 | 19.574 | 1 | 1 | 2350 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4827516.6123 | 373936.5766 | 5378.6078 | 38155.6209 | 335780.9556 | 21327.5579 | 0.089537 | -164685.7484 | 164685.7484
| Xist Rating 9785 | 9.52 | 2323.96 | 150.306 | 35.7 | 2089.35 | 8265.26 | 12040.1 | 0.38 | 1.48 | 24.972 | 19.389 | 1 | 1 | 2360 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4855565.826 | 376962.7314 | 5424.4805 | 38317.9853 | 338644.7461 | 21139.2889 | 0.089918 | -163231.9857 | 163231.9857
| Xist Rating 9786 | 11.3 | 2373.04 | 150.306 | 35.7 | 2079.83 | 8222.25 | 11847 | 0.38 | 1.45 | 24.994 | 18.821 | 1 | 1 | 2370 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4935519.7832 | 380001.0467 | 5470.5481 | 38480.3496 | 341520.6971 | 20554.5635 | 0.090299 | -158716.8911 | 158716.8911
| Xist Rating 9787 | 11.82 | 2388.51 | 150.306 | 35.7 | 2076.39 | 8199.33 | 11791.4 | 0.38 | 1.44 | 24.984 | 18.67 | 1 | 1 | 2380 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4959478.2789 | 383051.5225 | 5516.8105 | 38642.714 | 344408.8085 | 20401.6022 | 0.09068 | -157535.7642 | 157535.7642
| Xist Rating 9788 | 12.44 | 2404.93 | 150.306 | 35.7 | 2074.21 | 8199.49 | 11730.3 | 0.37 | 1.43 | 24.983 | 18.5 | 1 | 1 | 2390 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 4988329.8553 | 386114.1588 | 5563.2676 | 38805.0783 | 347309.0804 | 20202.5078 | 0.091061 | -155998.4105 | 155998.4105
C | Xist Rating 9789 | 24.44 | 2755.38 | 150.306 | 35.7 | 2003.81 | 7824.39 | 10538.4 | 0.41 | 1.25 | 24.943 | 15.258 | 1 | 1 | 2400 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5521257.9978 | 389188.9555 | 5609.9196 | 38967.4427 | 350221.5128 | 16945.5811 | 0.091442 | -130849.2858 | 130849.2858
C | Xist Rating 9790 | 24.5 | 2756.82 | 150.306 | 35.7 | 2004.16 | 7829.76 | 10538.4 | 0.41 | 1.25 | 24.946 | 15.269 | 1 | 1 | 2410 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5525108.3712 | 392275.9127 | 5656.7663 | 39129.807 | 353146.1056 | 16961.7215 | 0.091823 | -130973.9177 | 130973.9177
C | Xist Rating 9791 | 24.6 | 2758.23 | 150.307 | 35.7 | 2005.17 | 7845.14 | 10538.5 | 0.4 | 1.25 | 24.986 | 15.28 | 1 | 1 | 2420 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5530720.0491 | 395375.0303 | 5703.8078 | 39292.1714 | 356082.859 | 16952.4049 | 0.092204 | -130901.9771 | 130901.9771
C | Xist Rating 9792 | 24.73 | 2759.58 | 150.307 | 35.7 | 2006.56 | 7866.47 | 10538.5 | 0.39 | 1.25 | 24.986 | 15.291 | 1 | 1 | 2430 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5537262.8448 | 398486.3084 | 5751.0441 | 39454.5357 | 359031.7727 | 16941.0926 | 0.092585 | -130814.6266 | 130814.6266
C | Xist Rating 9793 | 24.88 | 2760.95 | 150.307 | 35.7 | 2008.47 | 7895.95 | 10538.4 | 0.38 | 1.25 | 24.988 | 15.302 | 1 | 1 | 2440 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5545285.2465 | 401609.747 | 5798.4752 | 39616.9 | 361992.847 | 16929.6395 | 0.092966 | -130726.1883 | 130726.1883
C | Xist Rating 9794 | 24.88 | 2762.28 | 150.306 | 35.7 | 2008.03 | 7889.2 | 10538.4 | 0.38 | 1.25 | 24.981 | 15.313 | 1 | 1 | 2450 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5546741.1084 | 404745.3461 | 5846.1011 | 39779.2644 | 364966.0817 | 16945.0271 | 0.093347 | -130845.0077 | 130845.0077
C | Xist Rating 9795 | 24.81 | 2763.75 | 150.306 | 35.7 | 2006.57 | 7866.61 | 10538.4 | 0.37 | 1.25 | 24.983 | 15.324 | 1 | 1 | 2460 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5545657.8375 | 407893.1056 | 5893.9217 | 39941.6287 | 367951.4769 | 16933.2411 | 0.093728 | -130753.9992 | 130753.9992
C | Xist Rating 9796 | 24.84 | 2765.11 | 150.307 | 35.7 | 2006.09 | 7859.24 | 10538.4 | 0.37 | 1.25 | 25.021 | 15.335 | 1 | 1 | 2470 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5547059.5199 | 411053.0256 | 5941.9372 | 40103.9931 | 370949.0325 | 16950.3647 | 0.094109 | -130886.2233 | 130886.2233
C | Xist Rating 9797 | 24.84 | 2766.45 | 150.307 | 35.7 | 2005.64 | 7852.31 | 10538.4 | 0.36 | 1.25 | 25.013 | 15.345 | 1 | 1 | 2480 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5548502.778 | 414225.1061 | 5990.1474 | 40266.3574 | 373958.7487 | 16936.7647 | 0.09449 | -130781.2074 | 130781.2074
C | Xist Rating 9798 | 24.85 | 2767.85 | 150.306 | 35.7 | 2005.11 | 7844.22 | 10538.4 | 0.35 | 1.25 | 25.006 | 15.356 | 1 | 1 | 2490 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5549843.7135 | 417409.347 | 6038.5525 | 40428.7218 | 376980.6253 | 16924.0332 | 0.094871 | -130682.8981 | 130682.8981
C | Xist Rating 9799 | 24.88 | 2768.84 | 150.306 | 35.7 | 2005.37 | 7848.15 | 10538.4 | 0.35 | 1.25 | 25.004 | 15.365 | 1 | 1 | 2500 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5552548.6708 | 420605.7484 | 6087.1523 | 40591.0861 | 380014.6623 | 16937.2243 | 0.095252 | -130784.7566 | 130784.7566
C | Xist Rating 9800 | 24.88 | 2770.69 | 150.306 | 35.7 | 2004.77 | 7839.1 | 10538.4 | 0.34 | 1.25 | 24.989 | 15.377 | 1 | 1 | 2510 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5554596.1913 | 423814.3103 | 6135.9469 | 40753.4505 | 383060.8599 | 16924.9033 | 0.095633 | -130689.6171 | 130689.6171
C | Xist Rating 9801 | 24.89 | 2772.14 | 150.307 | 35.7 | 2004.36 | 7832.81 | 10538.3 | 0.34 | 1.25 | 25.021 | 15.388 | 1 | 1 | 2520 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5556366.5304 | 427035.0327 | 6184.9363 | 40915.8148 | 386119.2179 | 16941.3642 | 0.096014 | -130816.7237 | 130816.7237
C | Xist Rating 9802 | 24.86 | 2773.48 | 150.307 | 35.7 | 2003.5 | 7819.7 | 10538.3 | 0.33 | 1.25 | 25.017 | 15.398 | 1 | 1 | 2530 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5556667.18 | 430267.9155 | 6234.1205 | 41078.1791 | 389189.7363 | 16927.0374 | 0.096395 | -130706.0957 | 130706.0957
C | Xist Rating 9803 | 24.86 | 2774.63 | 150.306 | 35.7 | 2003.03 | 7812.63 | 10538.3 | 0.33 | 1.25 | 25.016 | 15.408 | 1 | 1 | 2540 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5557667.1289 | 433512.9588 | 6283.4995 | 41240.5435 | 392272.4153 | 16941.0853 | 0.096776 | -130814.5703 | 130814.5703
C | Xist Rating 9804 | 24.89 | 2776.18 | 150.306 | 35.7 | 2002.78 | 7808.87 | 10538.3 | 0.32 | 1.25 | 25.007 | 15.419 | 1 | 1 | 2550 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5560077.7804 | 436770.1625 | 6333.0732 | 41402.9078 | 395367.2547 | 16927.286 | 0.097157 | -130708.0157 | 130708.0157
C | Xist Rating 9805 | 24.89 | 2777.62 | 150.306 | 35.7 | 2002.19 | 7799.86 | 10538.3 | 0.32 | 1.25 | 25.002 | 15.43 | 1 | 1 | 2560 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5561322.9878 | 440039.5267 | 6382.8418 | 41565.2722 | 398474.2546 | 16942.1129 | 0.097538 | -130822.5048 | 130822.5048
C | Xist Rating 9806 | 24.9 | 2779.01 | 150.307 | 35.7 | 2002.03 | 7797.45 | 10538.3 | 0.31 | 1.25 | 25.021 | 15.44 | 1 | 1 | 2570 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5563661.3903 | 443321.0514 | 6432.8051 | 41727.6365 | 401593.4149 | 16927.9605 | 0.097919 | -130713.2239 | 130713.2239
C | Xist Rating 9807 | 24.92 | 2780.38 | 150.307 | 35.7 | 2001.79 | 7793.84 | 10538.3 | 0.31 | 1.25 | 25.058 | 15.45 | 1 | 1 | 2580 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5565736.8802 | 446614.7366 | 6482.9633 | 41890.0009 | 404724.7357 | 16943.1488 | 0.0983 | -130830.5038 | 130830.5038
C | Xist Rating 9808 | 24.94 | 2781.74 | 150.307 | 35.7 | 2001.53 | 7789.82 | 10538.3 | 0.3 | 1.25 | 25.055 | 15.46 | 1 | 1 | 2590 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5567736.0622 | 449920.5822 | 6533.3162 | 42052.3652 | 407868.217 | 16927.82 | 0.098681 | -130712.1387 | 130712.1387
C | Xist Rating 9809 | 24.96 | 2782.92 | 150.307 | 35.7 | 2001.49 | 7789.26 | 10538.2 | 0.3 | 1.25 | 25.053 | 15.47 | 1 | 1 | 2600 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5569986.5508 | 453238.5883 | 6583.8639 | 42214.7296 | 411023.8588 | 16941.5043 | 0.099062 | -130817.8053 | 130817.8053
C | Xist Rating 9810 | 24.93 | 2784.6 | 150.307 | 35.7 | 2000.38 | 7772.45 | 10538.2 | 0.3 | 1.25 | 25.047 | 15.481 | 1 | 1 | 2610 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5570258.148 | 456568.7549 | 6634.6064 | 42377.0939 | 414191.661 | 16956.0861 | 0.099443 | -130930.4026 | 130930.4026
C | Xist Rating 9811 | 24.94 | 2786 | 150.307 | 35.7 | 2000.1 | 7768.28 | 10538.2 | 0.29 | 1.25 | 25.048 | 15.491 | 1 | 1 | 2620 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5572278.6 | 459911.0819 | 6685.5437 | 42539.4582 | 417371.6237 | 16940.458 | 0.099824 | -130809.7263 | 130809.7263
C | Xist Rating 9812 | 24.95 | 2787.43 | 150.307 | 35.7 | 1999.7 | 7762.17 | 10538.2 | 0.29 | 1.25 | 25.083 | 15.502 | 1 | 1 | 2630 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5574023.771 | 463265.5695 | 6736.6758 | 42701.8226 | 420563.7469 | 16956.3341 | 0.10021 | -130932.3172 | 130932.3172
C | Xist Rating 9813 | 24.98 | 2788.67 | 150.307 | 35.7 | 1999.65 | 7761.48 | 10538.2 | 0.28 | 1.25 | 25.082 | 15.511 | 1 | 1 | 2640 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5576363.9655 | 466632.2174 | 6788.0027 | 42864.1869 | 423768.0305 | 16939.2255 | 0.10059 | -130800.2094 | 130800.2094
C | Xist Rating 9814 | 25 | 2790.18 | 150.307 | 35.7 | 1999.33 | 7756.72 | 10538.2 | 0.28 | 1.25 | 25.086 | 15.522 | 1 | 1 | 2650 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5578490.5794 | 470011.0259 | 6839.5243 | 43026.5513 | 426984.4746 | 16953.9301 | 0.10097 | -130913.754 | 130913.754
C | Xist Rating 9815 | 25.04 | 2791.52 | 150.307 | 35.7 | 1999.32 | 7756.45 | 10538.2 | 0.28 | 1.25 | 25.09 | 15.531 | 1 | 1 | 2660 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5581141.7664 | 473401.9948 | 6891.2408 | 43188.9156 | 430213.0792 | 16966.5586 | 0.10135 | -131011.2683 | 131011.2683
C | Xist Rating 9816 | 25.09 | 2792.9 | 150.307 | 35.7 | 1999.67 | 7761.76 | 10538.2 | 0.27 | 1.25 | 25.094 | 15.541 | 1 | 1 | 2670 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5584878.343 | 476805.1242 | 6943.152 | 43351.28 | 433453.8442 | 16950.1937 | 0.10173 | -130884.9028 | 130884.9028
C | Xist Rating 9817 | 25.14 | 2794.32 | 150.307 | 35.7 | 1999.77 | 7763.33 | 10538.1 | 0.27 | 1.25 | 25.133 | 15.552 | 1 | 1 | 2680 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5587997.3064 | 480220.414 | 6995.258 | 43513.6443 | 436706.7697 | 16965.9192 | 0.10211 | -131006.3309 | 131006.3309
C | Xist Rating 9818 | 25.2 | 2795.7 | 150.307 | 35.7 | 2000.22 | 7770.07 | 10538.2 | 0.26 | 1.25 | 25.134 | 15.562 | 1 | 1 | 2690 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5592015.054 | 483647.8644 | 7047.5588 | 43676.0087 | 439971.8557 | 16949.0723 | 0.10249 | -130876.244 | 130876.244
C | Xist Rating 9819 | 25.27 | 2796.9 | 150.307 | 35.6 | 2001.05 | 7782.61 | 10538.2 | 0.26 | 1.25 | 25.138 | 15.571 | 1 | 1 | 2700 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5596736.745 | 487087.4751 | 7100.0544 | 43838.373 | 443249.1021 | 16961.4739 | 0.10287 | -130972.0056 | 130972.0056
C | Xist Rating 9820 | 25.34 | 2798.55 | 150.307 | 35.6 | 2001.59 | 7790.89 | 10538.1 | 0.26 | 1.25 | 25.138 | 15.582 | 1 | 1 | 2710 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5601549.6945 | 490539.2464 | 7152.7448 | 44000.7373 | 446538.5091 | 16975.8271 | 0.10325 | -131082.837 | 131082.837
C | Xist Rating 9821 | 25.37 | 2799.9 | 150.307 | 35.6 | 2001.68 | 7792.15 | 10538.1 | 0.25 | 1.25 | 25.134 | 15.591 | 1 | 1 | 2720 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5604503.832 | 494003.1781 | 7205.63 | 44163.1017 | 449840.0764 | 16957.3323 | 0.10363 | -130940.0253 | 130940.0253
C | Xist Rating 9822 | 25.35 | 2801.22 | 150.307 | 35.6 | 2000.9 | 7780.34 | 10538.1 | 0.25 | 1.25 | 25.169 | 15.601 | 1 | 1 | 2730 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5604961.098 | 497479.2703 | 7258.71 | 44325.466 | 453153.8043 | 16971.6046 | 0.10402 | -131050.2321 | 131050.2321
C | Xist Rating 9823 | 25.32 | 2802.5 | 150.307 | 35.6 | 2000.07 | 7767.82 | 10538.1 | 0.25 | 1.25 | 25.162 | 15.61 | 1 | 1 | 2740 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5605196.175 | 500967.523 | 7311.9847 | 44487.8304 | 456479.6926 | 16983.5566 | 0.1044 | -131142.5225 | 131142.5225
C | Xist Rating 9824 | 25.31 | 2804.05 | 150.307 | 35.6 | 1999.23 | 7755.12 | 10538.1 | 0.25 | 1.25 | 25.16 | 15.62 | 1 | 1 | 2750 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5605940.8815 | 504467.9361 | 7365.4543 | 44650.1947 | 459817.7414 | 16996.6997 | 0.10478 | -131244.0097 | 131244.0097
C | Xist Rating 9825 | 25.28 | 2805.48 | 150.307 | 35.6 | 1998.26 | 7740.66 | 10538.1 | 0.24 | 1.25 | 25.154 | 15.63 | 1 | 1 | 2760 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5606078.4648 | 507980.5098 | 7419.1186 | 44812.5591 | 463167.9507 | 16978.599 | 0.10516 | -131104.2412 | 131104.2412
C | Xist Rating 9826 | 25.28 | 2806.71 | 150.307 | 35.6 | 1997.81 | 7733.9 | 10538.1 | 0.24 | 1.25 | 25.153 | 15.639 | 1 | 1 | 2770 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5607273.3051 | 511505.2438 | 7472.9777 | 44974.9234 | 466530.3204 | 16990.6218 | 0.10554 | -131197.0776 | 131197.0776
C | Xist Rating 9827 | 25.24 | 2808.26 | 150.307 | 35.6 | 1996.6 | 7715.77 | 10538.1 | 0.24 | 1.25 | 25.185 | 15.649 | 1 | 1 | 2780 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5606971.916 | 515042.1384 | 7527.0316 | 45137.2878 | 469904.8506 | 17004.6697 | 0.10592 | -131305.5521 | 131305.5521
C | Xist Rating 9828 | 25.25 | 2809.67 | 150.307 | 35.6 | 1996.21 | 7709.93 | 10538.1 | 0.23 | 1.25 | 25.19 | 15.659 | 1 | 1 | 2790 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5608691.3507 | 518591.1934 | 7581.2803 | 45299.6521 | 473291.5413 | 16986.4113 | 0.1063 | -131164.5658 | 131164.5658
C | Xist Rating 9829 | 25.24 | 2810.64 | 150.307 | 35.6 | 1995.71 | 7702.52 | 10538.1 | 0.23 | 1.25 | 25.176 | 15.666 | 1 | 1 | 2800 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5609222.3544 | 522152.4089 | 7635.7238 | 45462.0164 | 476690.3924 | 16995.8737 | 0.10668 | -131237.6316 | 131237.6316
C | Xist Rating 9830 | 25.29 | 2812.39 | 150.307 | 35.6 | 1995.3 | 7696.44 | 10538.2 | 0.23 | 1.25 | 25.177 | 15.678 | 1 | 1 | 2810 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5611561.767 | 525725.7848 | 7690.3621 | 45624.3808 | 480101.404 | 17010.9602 | 0.10706 | -131354.1257 | 131354.1257
C | Xist Rating 9831 | 25.27 | 2813.86 | 150.307 | 35.6 | 1994.83 | 7689.47 | 10538.1 | 0.23 | 1.25 | 25.174 | 15.687 | 1 | 1 | 2820 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5613172.3438 | 529311.3212 | 7745.1952 | 45786.7451 | 483524.5761 | 17022.8151 | 0.10744 | -131445.6663 | 131445.6663
C | Xist Rating 9832 | 25.23 | 2815.23 | 150.308 | 35.6 | 1993.93 | 7676.13 | 10538 | 0.22 | 1.25 | 25.203 | 15.697 | 1 | 1 | 2830 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5613371.5539 | 532909.0181 | 7800.223 | 45949.1095 | 486959.9087 | 17004.6706 | 0.10783 | -131305.5593 | 131305.5593
C | Xist Rating 9833 | 25.25 | 2816.55 | 150.308 | 35.6 | 1993.64 | 7671.79 | 10538.1 | 0.22 | 1.25 | 25.207 | 15.706 | 1 | 1 | 2840 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5615186.742 | 536518.8755 | 7855.4457 | 46111.4738 | 490407.4017 | 17016.6145 | 0.10821 | -131397.7868 | 131397.7868
C | Xist Rating 9834 | 25.19 | 2817.99 | 150.307 | 35.6 | 1992.31 | 7652.14 | 10538 | 0.22 | 1.25 | 25.196 | 15.715 | 1 | 1 | 2850 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5614309.6569 | 540140.8933 | 7910.8631 | 46273.8382 | 493867.0552 | 17028.1376 | 0.10859 | -131486.7651 | 131486.7651
C | Xist Rating 9835 | 25.24 | 2819.4 | 150.307 | 35.6 | 1992.24 | 7651 | 10538.1 | 0.22 | 1.25 | 25.215 | 15.725 | 1 | 1 | 2860 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5616921.456 | 543775.0716 | 7966.4753 | 46436.2025 | 497338.8691 | 17041.5432 | 0.10897 | -131590.2792 | 131590.2792
C | Xist Rating 9836 | 25.29 | 2820.59 | 150.307 | 35.6 | 1992.95 | 7661.57 | 10538.2 | 0.21 | 1.25 | 25.246 | 15.734 | 1 | 1 | 2870 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5621294.8405 | 547421.4104 | 8022.2824 | 46598.5669 | 500822.8435 | 17021.7754 | 0.10935 | -131437.6379 | 131437.6379
C | Xist Rating 9837 | 25.4 | 2822.1 | 150.308 | 35.6 | 1993.99 | 7676.9 | 10538.2 | 0.21 | 1.25 | 25.308 | 15.744 | 1 | 1 | 2880 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5627239.179 | 551079.9096 | 8078.2842 | 46760.9312 | 504318.9784 | 17036.2177 | 0.10973 | -131549.1571 | 131549.1571
C | Xist Rating 9838 | 25.38 | 2823.44 | 150.308 | 35.6 | 1993.22 | 7665.51 | 10538.2 | 0.21 | 1.25 | 25.304 | 15.753 | 1 | 1 | 2890 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5627737.0768 | 554750.5693 | 8134.4807 | 46923.2955 | 507827.2738 | 17047.8376 | 0.11011 | -131638.8833 | 131638.8833
C | Xist Rating 9839 | 25.53 | 2824.83 | 150.308 | 35.6 | 1995.13 | 7693.8 | 10538.3 | 0.21 | 1.25 | 25.333 | 15.762 | 1 | 1 | 2900 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5635903.0779 | 558433.3895 | 8190.8721 | 47085.6599 | 511347.7296 | 17060.3577 | 0.11049 | -131735.5598 | 131735.5598
C | Xist Rating 9840 | 25.74 | 2826.37 | 150.308 | 35.6 | 1997.87 | 7734.55 | 10538.4 | 0.2 | 1.25 | 25.377 | 15.772 | 1 | 1 | 2910 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5646719.8319 | 562128.3702 | 8247.4583 | 47248.0242 | 514880.3459 | 17041.2309 | 0.11087 | -131587.8677 | 131587.8677
C | Xist Rating 9841 | 25.76 | 2827.76 | 150.308 | 35.6 | 1997.78 | 7733.34 | 10538.3 | 0.2 | 1.25 | 25.384 | 15.782 | 1 | 1 | 2920 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5649242.3728 | 565835.5113 | 8304.2393 | 47410.3886 | 518425.1227 | 17054.0741 | 0.11125 | -131687.0399 | 131687.0399
C | Xist Rating 9842 | 25.99 | 2829.15 | 150.308 | 35.6 | 2000.91 | 7780.38 | 10538.4 | 0.2 | 1.25 | 25.462 | 15.791 | 1 | 1 | 2930 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5660874.5265 | 569554.8129 | 8361.215 | 47572.7529 | 521982.0599 | 17067.7451 | 0.11164 | -131792.6037 | 131792.6037
C | Xist Rating 9843 | 26.83 | 2830.51 | 150.308 | 35.6 | 2014.1 | 7983.48 | 10538.6 | 0.19 | 1.25 | 25.562 | 15.801 | 1 | 1 | 2940 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5700930.191 | 573286.2749 | 8418.3855 | 47735.1173 | 525551.1577 | 17049.3617 | 0.11202 | -131650.6518 | 131650.6518
C | Xist Rating 9844 | 27.4 | 2831.92 | 150.308 | 35.6 | 2022.79 | 8121.74 | 10538.6 | 0.19 | 1.25 | 25.627 | 15.812 | 1 | 1 | 2950 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5728379.4568 | 577029.8974 | 8475.7509 | 47897.4816 | 529132.4158 | 17064.5953 | 0.1124 | -131768.2815 | 131768.2815
C | Xist Rating 9845 | 27.82 | 2833.29 | 150.308 | 35.6 | 2029.03 | 8223.31 | 10538.7 | 0.19 | 1.25 | 25.674 | 15.821 | 1 | 1 | 2960 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5748830.4087 | 580785.6804 | 8533.311 | 48059.846 | 532725.8345 | 17077.3092 | 0.11278 | -131866.4549 | 131866.4549
C | Xist Rating 9846 | 28.28 | 2834.68 | 150.308 | 35.6 | 2036.06 | 8340.07 | 10538.7 | 0.19 | 1.25 | 25.728 | 15.831 | 1 | 1 | 2970 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5771578.5608 | 584553.6239 | 8591.0659 | 48222.2103 | 536331.4136 | 17091.2467 | 0.11316 | -131974.0763 | 131974.0763
C | Xist Rating 9847 | 29.12 | 2835.9 | 150.308 | 35.6 | 2049.26 | 8566.18 | 10538.5 | 0.18 | 1.25 | 25.834 | 15.84 | 1 | 1 | 2980 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5811496.434 | 588333.7278 | 8649.0156 | 48384.5746 | 539949.1532 | 17070.9662 | 0.11354 | -131817.4757 | 131817.4757
C | Xist Rating 9848 | 29.11 | 2837.46 | 150.308 | 35.6 | 2048.42 | 8551.54 | 10538.5 | 0.18 | 1.25 | 25.828 | 15.85 | 1 | 1 | 2990 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5812309.8132 | 592125.9922 | 8707.16 | 48546.939 | 543579.0532 | 17083.2908 | 0.11392 | -131912.6433 | 131912.6433
C | Xist Rating 9849 | 29.09 | 2838.89 | 150.308 | 35.6 | 2047.66 | 8538.27 | 10538.5 | 0.18 | 1.25 | 25.823 | 15.859 | 1 | 1 | 3000 | 152.4 | 2 | 5.8 | 19.05 | 1.3333 | 35 | E | Rod | 5813081.4974 | 595930.4171 | 8765.4993 | 48709.3033 | 547221.1138 | 17094.6002 | 0.1143 | -131999.9712 | 131999.9712
C | Xist Rating 9850 | -83.82 | 296.918 | 150.315 | 35.9 | 2330.3 | 6781.64 | 58744.9 | 2.5 | 10.95 | 28.379 | 675.475 | 1 | 1 | 1000 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 691908.0154 | 78367.0353 | 973.9444 | 16516.373 | 61850.6623 | 704659.9164 | 0.038101 | -5441197.0894 | 5441197.0894
C | Xist Rating 9851 | -83.69 | 299.966 | 150.315 | 35.9 | 2326.35 | 6755.31 | 58283.4 | 2.48 | 10.84 | 28.486 | 662.738 | 1 | 1 | 1010 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 697825.9041 | 79775.3973 | 993.5206 | 16681.5367 | 63093.8606 | 691450.6816 | 0.038482 | -5339198.8799 | 5339198.8799
C | Xist Rating 9852 | -82.49 | 323.211 | 150.315 | 35.9 | 2318.96 | 6747.16 | 54966.9 | 2.49 | 10.07 | 28.534 | 574.338 | 1 | 1 | 1020 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 749513.3806 | 81196.1295 | 1013.2917 | 16846.7004 | 64349.429 | 599697.5766 | 0.038863 | -4630705.7241 | 4630705.7241
C | Xist Rating 9853 | -82.27 | 329.452 | 150.313 | 35.9 | 2303.8 | 6633.82 | 54178.4 | 2.4 | 9.89 | 27.819 | 554.92 | 1 | 1 | 1030 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 758991.5176 | 82629.2318 | 1033.2576 | 17011.8642 | 65617.3676 | 579366.0696 | 0.039244 | -4473711.2165 | 4473711.2165
C | Xist Rating 9854 | -82.15 | 332.575 | 150.313 | 35.9 | 2298.7 | 6598.27 | 53793.6 | 2.36 | 9.8 | 27.658 | 545.617 | 1 | 1 | 1040 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 764490.1525 | 84074.7042 | 1053.4182 | 17177.0279 | 66897.6763 | 569665.2592 | 0.039625 | -4398804.1298 | 4398804.1298
C | Xist Rating 9855 | -81.88 | 338.695 | 150.313 | 35.9 | 2292.07 | 6556.92 | 53042.6 | 2.33 | 9.63 | 27.55 | 527.448 | 1 | 1 | 1050 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 776312.6486 | 85532.5468 | 1073.7737 | 17342.1916 | 68190.3552 | 550775.1437 | 0.040006 | -4252939.6649 | 4252939.6649
C | Xist Rating 9856 | -81.75 | 341.798 | 150.313 | 35.9 | 2287.8 | 6528.57 | 52675.8 | 2.29 | 9.54 | 27.5 | 518.805 | 1 | 1 | 1060 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 781965.4644 | 87002.7595 | 1094.3239 | 17507.3553 | 69495.4041 | 541770.3745 | 0.040387 | -4183407.2244 | 4183407.2244
C | Xist Rating 9857 | -80.54 | 366.722 | 150.312 | 35.9 | 2274.27 | 6470.84 | 49856.6 | 2.27 | 8.9 | 27.209 | 453.879 | 1 | 1 | 1070 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 834024.8429 | 88485.3423 | 1115.0689 | 17672.5191 | 70812.8232 | 474314.9927 | 0.040768 | -3662534.6463 | 3662534.6463
C | Xist Rating 9858 | -80.3 | 371.38 | 150.312 | 35.9 | 2273.54 | 6474.27 | 49380.2 | 2.23 | 8.79 | 27.05 | 443.616 | 1 | 1 | 1080 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 844347.2852 | 89980.2953 | 1136.0087 | 17837.6828 | 72142.6125 | 463614.7159 | 0.041149 | -3579909.9457 | 3579909.9457
C | Xist Rating 9859 | -79.97 | 377.58 | 150.311 | 35.9 | 2274.37 | 6493.45 | 48760.4 | 2.17 | 8.65 | 26.829 | 430.457 | 1 | 1 | 1090 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 858756.6246 | 91487.6184 | 1157.1433 | 18002.8465 | 73484.7719 | 449873.425 | 0.04153 | -3473803.3392 | 3473803.3392
C | Xist Rating 9860 | -79.66 | 382.206 | 150.311 | 35.9 | 2282.94 | 6573.35 | 48306.6 | 2.12 | 8.55 | 26.835 | 420.96 | 1 | 1 | 1100 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 872553.3656 | 93007.3116 | 1178.4727 | 18168.0103 | 74839.3014 | 439971.3861 | 0.041911 | -3397342.4196 | 3397342.4196
C | Xist Rating 9861 | -79.48 | 385.497 | 150.31 | 35.9 | 2283.89 | 6587.6 | 48010.1 | 2.04 | 8.48 | 26.404 | 415.079 | 1 | 1 | 1110 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 880432.7433 | 94539.375 | 1199.9969 | 18333.174 | 76206.201 | 433738.916 | 0.042292 | -3349216.9376 | 3349216.9376
C | Xist Rating 9862 | -78.06 | 413.294 | 150.311 | 35.9 | 2278.43 | 6600.79 | 45447.5 | 2.08 | 7.92 | 26.775 | 363.19 | 1 | 1 | 1120 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 941661.4484 | 96083.8085 | 1221.7158 | 18498.3377 | 77585.4708 | 379968.1801 | 0.042673 | -2934013.5683 | 2934013.5683
C | Xist Rating 9863 | -77.86 | 416.538 | 150.31 | 35.9 | 2282.04 | 6637.51 | 45188.3 | 2.02 | 7.86 | 26.502 | 358.452 | 1 | 1 | 1130 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 950556.3775 | 97640.6121 | 1243.6296 | 18663.5015 | 78977.1107 | 374963.4337 | 0.043054 | -2895368.2429 | 2895368.2429
C | Xist Rating 9864 | -77.55 | 422.809 | 150.31 | 35.9 | 2280.65 | 6638.52 | 44680.4 | 1.96 | 7.75 | 26.072 | 349.012 | 1 | 1 | 1140 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 964279.3459 | 99209.7859 | 1265.7381 | 18828.6652 | 80381.1207 | 365059.6826 | 0.043435 | -2818894.1022 | 2818894.1022
C | Xist Rating 9865 | -77.2 | 429.017 | 150.309 | 35.9 | 2282.85 | 6669.99 | 44185.5 | 1.92 | 7.64 | 25.981 | 339.898 | 1 | 1 | 1150 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 979381.4584 | 100791.3298 | 1288.0414 | 18993.8289 | 81797.5009 | 355554.9486 | 0.043816 | -2745501.066 | 2745501.066
C | Xist Rating 9866 | -76.89 | 435.303 | 150.308 | 35.9 | 2281.39 | 6670.37 | 43702.7 | 1.86 | 7.53 | 25.76 | 331.208 | 1 | 1 | 1160 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 993095.9112 | 102385.2438 | 1310.5395 | 19158.9926 | 83226.2512 | 346450.3283 | 0.044197 | -2675197.6016 | 2675197.6016
C | Xist Rating 9867 | -75.63 | 460.213 | 150.309 | 35.9 | 2275.97 | 6676.22 | 41831.8 | 1.89 | 7.13 | 25.948 | 297.891 | 1 | 1 | 1170 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1047430.9816 | 103991.528 | 1333.2324 | 19324.1564 | 84667.3716 | 311931.3177 | 0.044578 | -2408650.9513 | 2408650.9513
C | Xist Rating 9868 | -75.5 | 461.928 | 150.309 | 35.9 | 2280.34 | 6717.21 | 41724 | 1.84 | 7.1 | 25.818 | 296.225 | 1 | 1 | 1180 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1053352.8955 | 105610.1823 | 1356.1201 | 19489.3201 | 86120.8622 | 310141.8866 | 0.044959 | -2394833.4387 | 2394833.4387
C | Xist Rating 9869 | -74.93 | 474.329 | 150.308 | 35.9 | 2273.52 | 6683.52 | 40885 | 1.79 | 6.92 | 25.579 | 282.249 | 1 | 1 | 1190 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1078396.4681 | 107241.2067 | 1379.2026 | 19654.4838 | 87586.7229 | 295557.4484 | 0.04534 | -2282216.2729 | 2282216.2729
C | Xist Rating 9870 | -74.64 | 477.466 | 150.308 | 35.8 | 2285.51 | 6794.69 | 40681.3 | 1.76 | 6.88 | 25.64 | 278.973 | 1 | 1 | 1200 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1091253.3177 | 108884.6013 | 1402.4799 | 19819.6476 | 89064.9537 | 292140.3495 | 0.045721 | -2255830.3411 | 2255830.3411
C | Xist Rating 9871 | -74.29 | 483.821 | 150.308 | 35.8 | 2287.02 | 6821.16 | 40281.2 | 1.7 | 6.8 | 25.451 | 272.609 | 1 | 1 | 1210 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1106508.3034 | 110540.3659 | 1425.9519 | 19984.8113 | 90555.5546 | 285450.7072 | 0.046102 | -2204174.6967 | 2204174.6967
C | Xist Rating 9872 | -72.95 | 511.972 | 150.308 | 35.8 | 2274.22 | 6767.22 | 38537.3 | 1.7 | 6.43 | 25.435 | 245.066 | 1 | 1 | 1220 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1164336.9618 | 112208.5008 | 1449.6188 | 20149.975 | 92058.5257 | 256865.252 | 0.046483 | -1983445.3883 | 1983445.3883
C | Xist Rating 9873 | -72.56 | 518.178 | 150.308 | 35.8 | 2280.48 | 6835.87 | 38182.9 | 1.68 | 6.35 | 25.466 | 239.774 | 1 | 1 | 1230 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1181694.5654 | 113889.0057 | 1473.4804 | 20315.1388 | 93573.867 | 251363.7249 | 0.046864 | -1940964.0543 | 1940964.0543
C | Xist Rating 9874 | -72.21 | 524.524 | 150.307 | 35.8 | 2282.38 | 6865.99 | 37835.7 | 1.63 | 6.28 | 25.336 | 234.723 | 1 | 1 | 1240 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1197163.0871 | 115581.8808 | 1497.5369 | 20480.3025 | 95101.5783 | 246054.8954 | 0.047245 | -1899970.6804 | 1899970.6804
C | Xist Rating 9875 | -71.99 | 527.805 | 150.307 | 35.8 | 2287.21 | 6916.47 | 37664.6 | 1.59 | 6.24 | 25.248 | 232.328 | 1 | 1 | 1250 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1207200.874 | 117287.126 | 1521.7881 | 20645.4662 | 96641.6598 | 243521.5795 | 0.047626 | -1880409.0867 | 1880409.0867
C | Xist Rating 9876 | -71.5 | 537.137 | 150.307 | 35.8 | 2287.78 | 6941.58 | 37161.1 | 1.56 | 6.14 | 25.184 | 225.057 | 1 | 1 | 1260 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1228851.2859 | 119004.7414 | 1546.2341 | 20810.6299 | 98194.1114 | 235940.2337 | 0.048007 | -1821867.9439 | 1821867.9439
C | Xist Rating 9877 | -70.18 | 563.789 | 150.307 | 35.8 | 2280.44 | 6931.42 | 35777.4 | 1.57 | 5.85 | 25.259 | 205.478 | 1 | 1 | 1270 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1285686.9872 | 120734.7269 | 1570.8749 | 20975.7937 | 99758.9332 | 215646.1232 | 0.048388 | -1665162.202 | 1665162.202
C | Xist Rating 9878 | -69.86 | 570.203 | 150.307 | 35.8 | 2280.41 | 6944.31 | 35477.1 | 1.52 | 5.79 | 25.107 | 201.522 | 1 | 1 | 1280 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1300296.6232 | 122477.0825 | 1595.7105 | 21140.9574 | 101336.1251 | 211469.8809 | 0.048769 | -1632914.3659 | 1632914.3659
C | Xist Rating 9879 | -69.51 | 576.565 | 150.307 | 35.8 | 2281.63 | 6968.78 | 35182.1 | 1.49 | 5.73 | 25.038 | 197.663 | 1 | 1 | 1290 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1315508.001 | 124231.8082 | 1620.7408 | 21306.1211 | 102925.6871 | 207429.9235 | 0.04915 | -1601718.8853 | 1601718.8853
C | Xist Rating 9880 | -69.02 | 585.875 | 150.307 | 35.8 | 2282.52 | 6996.92 | 34750.8 | 1.47 | 5.64 | 25.08 | 191.99 | 1 | 1 | 1300 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1337271.405 | 125998.9041 | 1645.966 | 21471.2849 | 104527.6193 | 201529.6619 | 0.049531 | -1556158.6295 | 1556158.6295
C | Xist Rating 9881 | -68.76 | 590.726 | 150.306 | 35.8 | 2283.57 | 7016.76 | 34539.4 | 1.43 | 5.59 | 25.031 | 189.331 | 1 | 1 | 1310 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1348964.1718 | 127778.3701 | 1671.3859 | 21636.4486 | 106141.9215 | 198721.7976 | 0.049912 | -1534477.0461 | 1534477.0461
C | Xist Rating 9882 | -67.45 | 617.476 | 150.307 | 35.8 | 2276.64 | 7008.95 | 33362.4 | 1.44 | 5.35 | 25.085 | 174.299 | 1 | 1 | 1320 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1405770.5606 | 129570.2063 | 1697.0007 | 21801.6123 | 107768.594 | 183146.5455 | 0.050293 | -1414209.0777 | 1414209.0777
C | Xist Rating 9883 | -66.98 | 627.003 | 150.306 | 35.8 | 2274.94 | 7012.48 | 32979.3 | 1.4 | 5.28 | 24.947 | 169.694 | 1 | 1 | 1330 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1426394.2048 | 131374.4126 | 1722.8102 | 21966.776 | 109407.6365 | 178309.1146 | 0.050674 | -1376855.7183 | 1376855.7183
C | Xist Rating 9884 | -66.47 | 636.429 | 150.306 | 35.8 | 2277.09 | 7052.79 | 32606.1 | 1.37 | 5.2 | 24.825 | 165.248 | 1 | 1 | 1340 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1449206.1116 | 133190.989 | 1748.8145 | 22131.9398 | 111059.0492 | 173652.6134 | 0.051055 | -1340899.4508 | 1340899.4508
C | Xist Rating 9885 | -66.17 | 641.297 | 150.305 | 35.8 | 2281.03 | 7100.75 | 32422.7 | 1.34 | 5.16 | 24.759 | 163.15 | 1 | 1 | 1350 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1462817.6959 | 135019.9355 | 1775.0136 | 22297.1035 | 112722.832 | 171438.6697 | 0.051436 | -1323803.9639 | 1323803.9639
C | Xist Rating 9886 | -65.79 | 644.38 | 150.306 | 35.8 | 2296.42 | 7259 | 32302.2 | 1.33 | 5.14 | 24.875 | 161.742 | 1 | 1 | 1360 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1479767.1196 | 136861.2522 | 1801.4075 | 22462.2672 | 114398.985 | 169985.6471 | 0.051817 | -1312584.1086 | 1312584.1086
C | Xist Rating 9887 | -64.16 | 682.202 | 150.305 | 35.8 | 2272.61 | 7106.96 | 30901.5 | 1.32 | 4.86 | 24.755 | 145.644 | 1 | 1 | 1370 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1550379.0872 | 138714.939 | 1827.9962 | 22627.431 | 116087.508 | 153257.7262 | 0.052198 | -1183415.5378 | 1183415.5378
C | Xist Rating 9888 | -64.01 | 685.546 | 150.305 | 35.8 | 2272.36 | 7111.15 | 30793 | 1.29 | 4.84 | 24.7 | 144.522 | 1 | 1 | 1380 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1557807.3086 | 140580.9959 | 1854.7797 | 22792.5947 | 117788.4013 | 152056.8505 | 0.052579 | -1174142.6937 | 1174142.6937
C | Xist Rating 9889 | -63.58 | 693.52 | 150.305 | 35.8 | 2273.83 | 7142.16 | 30525.9 | 1.26 | 4.78 | 24.652 | 141.658 | 1 | 1 | 1390 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1576946.5816 | 142459.423 | 1881.7579 | 22957.7584 | 119501.6646 | 149046.9363 | 0.05296 | -1150900.9339 | 1150900.9339
C | Xist Rating 9890 | -63.1 | 701.489 | 150.306 | 35.8 | 2277.6 | 7196.28 | 30264.3 | 1.23 | 4.73 | 24.633 | 138.882 | 1 | 1 | 1400 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1597711.3464 | 144350.2202 | 1908.931 | 23122.9222 | 121227.2981 | 146130.1106 | 0.053341 | -1128377.9791 | 1128377.9791
C | Xist Rating 9891 | -62.6 | 710.976 | 150.306 | 35.8 | 2278.75 | 7228.11 | 29956.8 | 1.21 | 4.67 | 24.605 | 135.641 | 1 | 1 | 1410 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1620136.56 | 146253.3876 | 1936.2988 | 23288.0859 | 122965.3017 | 142744.6397 | 0.053722 | -1102236.2701 | 1102236.2701
C | Xist Rating 9892 | -61.24 | 739.369 | 150.305 | 35.8 | 2271.67 | 7219.24 | 29050.8 | 1.22 | 4.49 | 24.671 | 126.157 | 1 | 1 | 1420 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1679602.3762 | 148168.925 | 1963.8614 | 23453.2496 | 124715.6754 | 132929.6524 | 0.054103 | -1026447.54 | 1026447.54
C | Xist Rating 9893 | -60.99 | 744.478 | 150.305 | 35.8 | 2271.16 | 7224.15 | 28909.8 | 1.19 | 4.47 | 24.563 | 124.83 | 1 | 1 | 1430 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1690828.6545 | 150096.8326 | 1991.6188 | 23618.4133 | 126478.4193 | 131509.3768 | 0.054484 | -1015480.5481 | 1015480.5481
C | Xist Rating 9894 | -60.34 | 757.048 | 150.305 | 35.8 | 2271.6 | 7255.57 | 28541.2 | 1.17 | 4.39 | 24.555 | 121.171 | 1 | 1 | 1440 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1719710.2368 | 152037.1104 | 2019.571 | 23783.5771 | 128253.5333 | 127690.2995 | 0.054865 | -985990.6459 | 985990.6459
C | Xist Rating 9895 | -59.86 | 765.055 | 150.305 | 35.8 | 2275.63 | 7313.9 | 28316.3 | 1.14 | 4.35 | 24.533 | 119.007 | 1 | 1 | 1450 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1740982.1096 | 153989.7583 | 2047.718 | 23948.7408 | 130041.0175 | 125406.3576 | 0.055246 | -968354.6516 | 968354.6516
C | Xist Rating 9896 | -59.48 | 769.805 | 150.305 | 35.8 | 2283.63 | 7407.75 | 28183.2 | 1.13 | 4.32 | 24.579 | 117.737 | 1 | 1 | 1460 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1757949.7921 | 155954.7763 | 2076.0598 | 24113.9045 | 131840.8717 | 124087.3474 | 0.055627 | -958169.6044 | 958169.6044
C | Xist Rating 9897 | -58.08 | 801.71 | 150.305 | 35.8 | 2268.87 | 7323.97 | 27309.9 | 1.12 | 4.16 | 24.533 | 109.405 | 1 | 1 | 1470 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1818975.7677 | 157932.1644 | 2104.5964 | 24279.0683 | 133653.0961 | 115427.4378 | 0.056008 | -891300.0786 | 891300.0786
C | Xist Rating 9898 | -57.58 | 811.24 | 150.305 | 35.8 | 2269.94 | 7355.67 | 27065.8 | 1.1 | 4.11 | 24.519 | 107.184 | 1 | 1 | 1480 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1841466.1256 | 159921.9227 | 2133.3277 | 24444.232 | 135477.6907 | 113099.677 | 0.056389 | -873325.7267 | 873325.7267
C | Xist Rating 9899 | -57.14 | 819.25 | 150.305 | 35.7 | 2271.73 | 7391.73 | 26866 | 1.08 | 4.07 | 24.505 | 105.4 | 1 | 1 | 1490 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1861114.8025 | 161924.0511 | 2162.2539 | 24609.3957 | 137314.6553 | 111225.3238 | 0.05677 | -858852.4676 | 858852.4676
C | Xist Rating 9900 | -56.73 | 827.351 | 150.305 | 35.7 | 2271.85 | 7410.29 | 26669.5 | 1.06 | 4.03 | 24.461 | 103.675 | 1 | 1 | 1500 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1879617.3693 | 163938.5496 | 2191.3748 | 24774.5595 | 139163.9901 | 109409.6882 | 0.057151 | -844832.6113 | 844832.6113
C | Xist Rating 9901 | -56.22 | 836.909 | 150.305 | 35.7 | 2272.83 | 7441.51 | 26438 | 1.04 | 3.99 | 24.45 | 101.639 | 1 | 1 | 1510 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1902151.8825 | 165965.4183 | 2220.6906 | 24939.7232 | 141025.6951 | 107273.0406 | 0.057532 | -828333.9847 | 828333.9847
C | Xist Rating 9902 | -54.73 | 868.497 | 150.305 | 35.7 | 2265.56 | 7434.53 | 25680.1 | 1.06 | 3.84 | 24.47 | 94.972 | 1 | 1 | 1520 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1967632.0633 | 168004.6571 | 2250.2011 | 25104.8869 | 142899.7701 | 100395.5314 | 0.057913 | -775227.6812 | 775227.6812
C | Xist Rating 9903 | -54.29 | 878.398 | 150.305 | 35.7 | 2262.39 | 7421 | 25467.5 | 1.03 | 3.8 | 24.377 | 93.24 | 1 | 1 | 1530 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 1987278.8512 | 170056.266 | 2279.9064 | 25270.0506 | 144786.2153 | 98551.5635 | 0.058294 | -760989.0504 | 760989.0504
C | Xist Rating 9904 | -53.95 | 883.422 | 150.305 | 35.7 | 2267.73 | 7489.26 | 25362.1 | 1 | 3.78 | 24.354 | 92.408 | 1 | 1 | 1540 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2003362.5721 | 172120.245 | 2309.8065 | 25435.2144 | 146685.0307 | 97646.7176 | 0.058675 | -754002.0697 | 754002.0697
C | Xist Rating 9905 | -53.15 | 899.201 | 150.305 | 35.7 | 2267.4 | 7520.57 | 25019.8 | 0.99 | 3.72 | 24.349 | 89.582 | 1 | 1 | 1550 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2038848.3474 | 174196.5942 | 2339.9013 | 25600.3781 | 148596.2161 | 94705.573 | 0.059056 | -731291.3309 | 731291.3309
C | Xist Rating 9906 | -52.69 | 904 | 150.305 | 35.7 | 2278.13 | 7650.85 | 24919.2 | 0.98 | 3.7 | 24.407 | 88.782 | 1 | 1 | 1560 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2059429.52 | 176285.3136 | 2370.191 | 25765.5418 | 150519.7717 | 93872.5277 | 0.059437 | -724858.776 | 724858.776
C | Xist Rating 9907 | -51.14 | 940.836 | 150.305 | 35.7 | 2261.12 | 7543.82 | 24160.9 | 0.97 | 3.56 | 24.358 | 82.7 | 1 | 1 | 1570 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2127343.0963 | 178386.403 | 2400.6755 | 25930.7056 | 152455.6975 | 87546.5806 | 0.059818 | -676011.4893 | 676011.4893
C | Xist Rating 9908 | -50.66 | 948.966 | 150.305 | 35.7 | 2264.43 | 7598.49 | 24006.3 | 0.95 | 3.53 | 24.352 | 81.532 | 1 | 1 | 1580 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2148867.0794 | 180499.8626 | 2431.3547 | 26095.8693 | 154403.9933 | 86309.2995 | 0.0602 | -666457.5325 | 666457.5325
C | Xist Rating 9909 | -50.18 | 957.132 | 150.305 | 35.7 | 2267.67 | 7652.96 | 23853.8 | 0.93 | 3.5 | 24.341 | 80.395 | 1 | 1 | 1590 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2170459.5224 | 182625.6923 | 2462.2288 | 26261.033 | 156364.6593 | 85103.4557 | 0.060581 | -657146.3262 | 657146.3262
C | Xist Rating 9910 | -49.53 | 968.237 | 150.305 | 35.7 | 2271.44 | 7721.45 | 23644.1 | 0.92 | 3.46 | 24.365 | 78.81 | 1 | 1 | 1600 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2199292.2513 | 184763.8922 | 2493.2976 | 26426.1968 | 158337.6954 | 83451.709 | 0.060962 | -644391.9764 | 644391.9764
C | Xist Rating 9911 | -49.2 | 973.456 | 150.305 | 35.7 | 2274.11 | 7763.39 | 23555.8 | 0.9 | 3.45 | 24.338 | 78.197 | 1 | 1 | 1610 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2213746.0242 | 186914.4622 | 2524.5612 | 26591.3605 | 160323.1017 | 82788.2363 | 0.061343 | -639268.816 | 639268.816
C | Xist Rating 9912 | -47.39 | 1014.76 | 150.305 | 35.7 | 2260.3 | 7699.06 | 22803.9 | 0.9 | 3.31 | 24.363 | 72.598 | 1 | 1 | 1620 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2293662.028 | 189077.4023 | 2556.0196 | 26756.5242 | 162320.8781 | 76985.136 | 0.061724 | -594458.8136 | 594458.8136
C | Xist Rating 9913 | -46.93 | 1019.63 | 150.305 | 35.7 | 2269.13 | 7813.5 | 22722.7 | 0.89 | 3.29 | 24.405 | 72.037 | 1 | 1 | 1630 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2313673.0219 | 191252.7126 | 2587.6728 | 26921.6879 | 164331.0246 | 76397.2975 | 0.062105 | -589919.6803 | 589919.6803
C | Xist Rating 9914 | -46.49 | 1027.94 | 150.305 | 35.7 | 2270.2 | 7844.72 | 22587.9 | 0.87 | 3.27 | 24.375 | 71.117 | 1 | 1 | 1640 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2333629.388 | 193440.3929 | 2619.5208 | 27086.8517 | 166353.5413 | 75413.8149 | 0.062486 | -582325.489 | 582325.489
C | Xist Rating 9915 | -45.94 | 1039.41 | 150.305 | 35.7 | 2268.94 | 7855.62 | 22402.3 | 0.86 | 3.23 | 24.341 | 69.842 | 1 | 1 | 1650 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2358358.9254 | 195640.4435 | 2651.5635 | 27252.0154 | 168388.4281 | 74079.0446 | 0.062867 | -572018.7459 | 572018.7459
C | Xist Rating 9916 | -45.29 | 1050.62 | 150.305 | 35.7 | 2272.48 | 7924.64 | 22220.1 | 0.84 | 3.2 | 24.354 | 68.587 | 1 | 1 | 1660 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2387512.9376 | 197852.8641 | 2683.8011 | 27417.1791 | 170435.685 | 72749.7011 | 0.063248 | -561753.9081 | 561753.9081
C | Xist Rating 9917 | -43.68 | 1087.51 | 150.305 | 35.7 | 2260.46 | 7866.44 | 21632.4 | 0.84 | 3.09 | 24.372 | 64.55 | 1 | 1 | 1670 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2458272.8546 | 200077.6549 | 2716.2334 | 27582.3429 | 172495.312 | 68567.5848 | 0.063629 | -529460.7143 | 529460.7143
C | Xist Rating 9918 | -43.29 | 1092.49 | 150.305 | 35.7 | 2266.36 | 7949.68 | 21559.9 | 0.83 | 3.08 | 24.387 | 64.092 | 1 | 1 | 1680 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2475975.6364 | 202314.8158 | 2748.8606 | 27747.5066 | 174567.3092 | 68083.7133 | 0.06401 | -525724.3873 | 525724.3873
C | Xist Rating 9919 | -42.61 | 1107.15 | 150.305 | 35.7 | 2263.71 | 7950.79 | 21345.7 | 0.81 | 3.04 | 24.351 | 62.706 | 1 | 1 | 1690 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2506266.5265 | 204564.3469 | 2781.6825 | 27912.6703 | 176651.6765 | 66614.2705 | 0.064391 | -514377.7393 | 514377.7393
C | Xist Rating 9920 | -42.06 | 1116.87 | 150.305 | 35.7 | 2266.35 | 8006.29 | 21205.4 | 0.8 | 3.02 | 24.358 | 61.809 | 1 | 1 | 1700 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2531218.3245 | 206826.248 | 2814.6992 | 28077.834 | 178748.414 | 65673.4496 | 0.064772 | -507112.9695 | 507112.9695
C | Xist Rating 9921 | -41.49 | 1128.28 | 150.305 | 35.7 | 2266.28 | 8032.12 | 21044.4 | 0.79 | 2.99 | 24.346 | 60.792 | 1 | 1 | 1710 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2556998.3984 | 209100.5194 | 2847.9107 | 28242.9978 | 180857.5216 | 64606.6343 | 0.065153 | -498875.3048 | 498875.3048
C | Xist Rating 9922 | -39.99 | 1162.16 | 150.305 | 35.7 | 2257.07 | 7997.96 | 20566.8 | 0.79 | 2.9 | 24.372 | 57.747 | 1 | 1 | 1720 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2623076.4712 | 211387.1608 | 2881.317 | 28408.1615 | 182978.9993 | 61454.6115 | 0.065534 | -474536.2202 | 474536.2202
C | Xist Rating 9923 | -39.29 | 1176.69 | 150.305 | 35.7 | 2255.8 | 8015.84 | 20374 | 0.78 | 2.87 | 24.361 | 56.571 | 1 | 1 | 1730 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2654377.302 | 213686.1724 | 2914.9181 | 28573.3252 | 185112.8471 | 60222.4028 | 0.065915 | -465021.4314 | 465021.4314
C | Xist Rating 9924 | -38.88 | 1183.35 | 150.305 | 35.7 | 2258.89 | 8070.32 | 20289.6 | 0.77 | 2.85 | 24.364 | 56.078 | 1 | 1 | 1740 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2673057.4815 | 215997.5541 | 2948.714 | 28738.489 | 187259.0651 | 59700.1203 | 0.066296 | -460988.5044 | 460988.5044
C | Xist Rating 9925 | -38.28 | 1196.49 | 150.305 | 35.7 | 2256.45 | 8069.68 | 20123.2 | 0.75 | 2.82 | 24.338 | 55.093 | 1 | 1 | 1750 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2699819.8605 | 218321.3059 | 2982.7046 | 28903.6527 | 189417.6532 | 58645.8552 | 0.066677 | -452847.7486 | 452847.7486
C | Xist Rating 9926 | -37.84 | 1206.32 | 150.305 | 35.7 | 2255 | 8073.95 | 20000.4 | 0.74 | 2.8 | 24.332 | 54.374 | 1 | 1 | 1760 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2720251.6 | 220657.4279 | 3016.8901 | 29068.8164 | 191588.6115 | 57887.806 | 0.067058 | -446994.2939 | 446994.2939
C | Xist Rating 9927 | -36.1 | 1246.49 | 150.305 | 35.7 | 2243.83 | 8027.16 | 19497 | 0.74 | 2.71 | 24.365 | 51.381 | 1 | 1 | 1770 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2796911.6567 | 223005.92 | 3051.2703 | 29233.9802 | 193771.9399 | 54789.5887 | 0.067439 | -423070.6811 | 423070.6811
C | Xist Rating 9928 | -35.57 | 1256.43 | 150.305 | 35.7 | 2245.18 | 8067.04 | 19382.6 | 0.73 | 2.69 | 24.357 | 50.746 | 1 | 1 | 1780 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2820911.5074 | 225366.7823 | 3085.8453 | 29399.1439 | 195967.6384 | 54118.3179 | 0.06782 | -417887.3056 | 417887.3056
C | Xist Rating 9929 | -35.21 | 1261.68 | 150.305 | 35.7 | 2248.79 | 8125.27 | 19325.9 | 0.72 | 2.68 | 24.352 | 50.451 | 1 | 1 | 1790 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2837253.3672 | 227740.0146 | 3120.6151 | 29564.3076 | 198175.707 | 53800.099 | 0.068201 | -415430.1036 | 415430.1036
C | Xist Rating 9930 | -34.4 | 1279.44 | 150.305 | 35.7 | 2246.44 | 8136.67 | 19121.2 | 0.71 | 2.65 | 24.34 | 49.303 | 1 | 1 | 1800 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2874185.1936 | 230125.6171 | 3155.5797 | 29729.4713 | 200396.1458 | 52595.4264 | 0.068582 | -406127.9413 | 406127.9413
C | Xist Rating 9931 | -34.14 | 1289.26 | 150.306 | 35.7 | 2237.47 | 8042.31 | 19012.9 | 0.7 | 2.63 | 24.665 | 48.698 | 1 | 1 | 1810 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2884680.5722 | 232523.5898 | 3190.7391 | 29894.6351 | 202628.9547 | 51973.5912 | 0.068963 | -401326.2945 | 401326.2945
C | Xist Rating 9932 | -32.41 | 1329.68 | 150.306 | 35.7 | 2226.68 | 7997.27 | 18563.5 | 0.7 | 2.55 | 24.696 | 46.21 | 1 | 1 | 1820 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 37 | E | Rod | 2960771.8624 | 234933.9326 | 3226.0933 | 30059.7988 | 204874.1337 | 49399.3166 | 0.069344 | -381448.4287 | 381448.4287
C | Xist Rating 9933 | -32.42 | 1323.28 | 150.306 | 35.6 | 2242.03 | 8183.83 | 18630.7 | 0.7 | 2.56 | 24.702 | 46.591 | 1 | 1 | 1830 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 2966833.4584 | 237356.6455 | 3261.6423 | 30224.9625 | 207131.6829 | 49803.078 | 0.069725 | -384566.1668 | 384566.1668
C | Xist Rating 9934 | -31.89 | 1331.38 | 150.306 | 35.6 | 2245.33 | 8247.32 | 18545 | 0.69 | 2.55 | 24.729 | 46.138 | 1 | 1 | 1840 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 2989387.4554 | 239791.7285 | 3297.386 | 30390.1263 | 209401.6022 | 49321.552 | 0.070106 | -380847.9509 | 380847.9509
C | Xist Rating 9935 | -31.3 | 1344.63 | 150.306 | 35.6 | 2242.15 | 8235.57 | 18409.1 | 0.68 | 2.52 | 24.717 | 45.431 | 1 | 1 | 1850 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3014862.1545 | 242239.1817 | 3333.3246 | 30555.29 | 211683.8917 | 48573.7987 | 0.070487 | -375073.9981 | 375073.9981
C | Xist Rating 9936 | -30.63 | 1359.51 | 150.306 | 35.6 | 2240.13 | 8243.12 | 18258.8 | 0.66 | 2.5 | 24.702 | 44.655 | 1 | 1 | 1860 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3045479.1363 | 244699.005 | 3369.4579 | 30720.4537 | 213978.5512 | 47733.4174 | 0.070868 | -368584.7967 | 368584.7967
C | Xist Rating 9937 | -28.97 | 1396.67 | 150.306 | 35.6 | 2233.42 | 8243.03 | 17879.1 | 0.67 | 2.43 | 24.755 | 42.661 | 1 | 1 | 1870 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3119350.7114 | 247171.1984 | 3405.7861 | 30885.6175 | 216285.5809 | 45693.6418 | 0.071249 | -352834.1896 | 352834.1896
C | Xist Rating 9938 | -28.29 | 1411.53 | 150.306 | 35.6 | 2231.35 | 8249.4 | 17738.4 | 0.65 | 2.41 | 24.745 | 41.963 | 1 | 1 | 1880 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3149617.4655 | 249655.762 | 3442.309 | 31050.7812 | 218604.9808 | 44933.9344 | 0.07163 | -346967.9308 | 346967.9308
C | Xist Rating 9939 | -27.71 | 1421.39 | 150.306 | 35.6 | 2233.86 | 8307.24 | 17646.1 | 0.65 | 2.39 | 24.771 | 41.511 | 1 | 1 | 1890 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3175186.2654 | 252152.6957 | 3479.0267 | 31215.9449 | 220936.7507 | 44473.1746 | 0.072011 | -343410.0655 | 343410.0655
C | Xist Rating 9940 | -27.27 | 1431.71 | 150.306 | 35.7 | 2230.71 | 8286.98 | 17555.1 | 0.63 | 2.38 | 24.754 | 41.081 | 1 | 1 | 1900 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3193729.8141 | 254661.9995 | 3515.9392 | 31381.1086 | 223280.8908 | 43990.732 | 0.072392 | -339684.7722 | 339684.7722
C | Xist Rating 9941 | -26.78 | 1441.74 | 150.306 | 35.7 | 2230.33 | 8305.07 | 17464.7 | 0.62 | 2.36 | 24.771 | 40.65 | 1 | 1 | 1910 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3215555.9742 | 257183.6734 | 3553.0464 | 31546.2724 | 225637.4011 | 43529.8389 | 0.072773 | -336125.8772 | 336125.8772
C | Xist Rating 9942 | -24.81 | 1486.86 | 150.306 | 35.7 | 2221.45 | 8291.84 | 17050 | 0.62 | 2.29 | 24.822 | 38.601 | 1 | 1 | 1920 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3302985.147 | 259717.7175 | 3590.3485 | 31711.4361 | 228006.2814 | 41411.5611 | 0.073154 | -319769.0979 | 319769.0979
C | Xist Rating 9943 | -24.14 | 1501.79 | 150.306 | 35.7 | 2218.89 | 8290.77 | 16923.8 | 0.61 | 2.27 | 24.823 | 38.015 | 1 | 1 | 1930 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3332306.8131 | 262264.1318 | 3627.8454 | 31876.5998 | 230387.5319 | 40788.4783 | 0.073535 | -314957.8172 | 314957.8172
C | Xist Rating 9944 | -23.7 | 1506.68 | 150.306 | 35.7 | 2225.16 | 8390.93 | 16881.8 | 0.61 | 2.26 | 24.857 | 37.827 | 1 | 1 | 1940 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3352604.0688 | 264822.9161 | 3665.537 | 32041.7636 | 232781.1526 | 40601.8315 | 0.073916 | -313516.5802 | 313516.5802
C | Xist Rating 9945 | -23.23 | 1520.51 | 150.306 | 35.7 | 2218.39 | 8326.21 | 16772.1 | 0.59 | 2.24 | 24.833 | 37.338 | 1 | 1 | 1950 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3373084.1789 | 267394.0706 | 3703.4235 | 32206.9273 | 235187.1433 | 40056.1106 | 0.074297 | -309302.6687 | 309302.6687
C | Xist Rating 9946 | -22.49 | 1536.94 | 150.306 | 35.7 | 2215.99 | 8330.93 | 16637 | 0.58 | 2.22 | 24.858 | 36.719 | 1 | 1 | 1960 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3405843.6706 | 269977.5952 | 3741.5047 | 32372.091 | 237605.5042 | 39399.3042 | 0.074678 | -304230.9831 | 304230.9831
C | Xist Rating 9947 | -20.72 | 1577.49 | 150.307 | 35.7 | 2208.72 | 8326.17 | 16303.1 | 0.59 | 2.16 | 24.935 | 35.175 | 1 | 1 | 1970 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3484233.7128 | 272573.49 | 3779.7807 | 32537.2547 | 240036.2353 | 37828.2877 | 0.075059 | -292100.0102 | 292100.0102
C | Xist Rating 9948 | -20.15 | 1589.13 | 150.307 | 35.7 | 2208.83 | 8354.69 | 16214.1 | 0.58 | 2.15 | 24.97 | 34.789 | 1 | 1 | 1980 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3510118.0179 | 275181.7549 | 3818.2515 | 32702.4185 | 242479.3364 | 37413.6929 | 0.07544 | -288898.6193 | 288898.6193
C | Xist Rating 9949 | -19.54 | 1604.26 | 150.307 | 35.7 | 2205.01 | 8334.62 | 16101.3 | 0.57 | 2.13 | 24.988 | 34.304 | 1 | 1 | 1990 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3537409.3426 | 277802.3899 | 3856.9171 | 32867.5822 | 244934.8077 | 36895.1546 | 0.075821 | -284894.6043 | 284894.6043
C | Xist Rating 9950 | -18.99 | 1616.02 | 150.307 | 35.7 | 2204.3 | 8351.44 | 16014.8 | 0.56 | 2.12 | 24.99 | 33.937 | 1 | 1 | 2000 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3562192.886 | 280435.3951 | 3895.7775 | 33032.7459 | 247402.6491 | 36498.109 | 0.076202 | -281828.7232 | 281828.7232
C | Xist Rating 9951 | -18.49 | 1624.59 | 150.307 | 35.7 | 2206.51 | 8402.6 | 15953.5 | 0.55 | 2.11 | 25.001 | 33.685 | 1 | 1 | 2010 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3584674.0809 | 283080.7704 | 3934.8326 | 33197.9097 | 249882.8607 | 36220.7101 | 0.076583 | -279686.722 | 279686.722
C | Xist Rating 9952 | -16.66 | 1670.14 | 150.307 | 35.7 | 2195.01 | 8345.89 | 15614.6 | 0.55 | 2.05 | 25.032 | 32.207 | 1 | 1 | 2020 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3665974.0014 | 285738.5158 | 3974.0826 | 33363.0734 | 252375.4424 | 34693.5168 | 0.076964 | -267894.1408 | 267894.1408
C | Xist Rating 9953 | -15.81 | 1686.52 | 150.307 | 35.7 | 2196.04 | 8399.07 | 15499.6 | 0.54 | 2.03 | 25.047 | 31.729 | 1 | 1 | 2030 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3703665.3808 | 288408.6313 | 4013.5273 | 33528.2371 | 254880.3942 | 34181.2453 | 0.077345 | -263938.5157 | 263938.5157
C | Xist Rating 9954 | -15.41 | 1697.04 | 150.307 | 35.7 | 2193.17 | 8380.16 | 15431.6 | 0.53 | 2.02 | 25.035 | 31.464 | 1 | 1 | 2040 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3721897.2168 | 291091.117 | 4053.1669 | 33693.4009 | 257397.7162 | 33888.6208 | 0.077726 | -261678.9469 | 261678.9469
C | Xist Rating 9955 | -14.75 | 1706.74 | 150.307 | 35.7 | 2197.98 | 8474.32 | 15364.2 | 0.53 | 2.01 | 25.07 | 31.188 | 1 | 1 | 2050 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3751380.3852 | 293785.9728 | 4093.0012 | 33858.5646 | 259927.4082 | 33609.6474 | 0.078107 | -259524.7882 | 259524.7882
C | Xist Rating 9956 | -14.19 | 1722.27 | 150.307 | 35.7 | 2192.94 | 8434.58 | 15264.3 | 0.52 | 1.99 | 25.048 | 30.795 | 1 | 1 | 2060 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3776834.7738 | 296493.1988 | 4133.0303 | 34023.7283 | 262469.4705 | 33183.2677 | 0.078488 | -256232.3974 | 256232.3974
C | Xist Rating 9957 | -12.18 | 1771.13 | 150.307 | 35.7 | 2182.92 | 8403.56 | 14936.2 | 0.52 | 1.94 | 25.085 | 29.449 | 1 | 1 | 2070 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3866235.0996 | 299212.7949 | 4173.2542 | 34188.892 | 265023.9028 | 31793.0725 | 0.078869 | -245497.6781 | 245497.6781
C | Xist Rating 9958 | -11.69 | 1781.44 | 150.307 | 35.7 | 2182.79 | 8424.61 | 14873.5 | 0.51 | 1.93 | 25.088 | 29.213 | 1 | 1 | 2080 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3888509.4176 | 301944.7611 | 4213.6729 | 34354.0558 | 267590.7053 | 31530.5884 | 0.07925 | -243470.846 | 243470.846
C | Xist Rating 9959 | -11.07 | 1794.9 | 150.307 | 35.7 | 2181.98 | 8443.24 | 14790.9 | 0.5 | 1.91 | 25.1 | 28.898 | 1 | 1 | 2090 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3916435.902 | 304689.0974 | 4254.2864 | 34519.2195 | 270169.8779 | 31186.2555 | 0.079631 | -240811.9982 | 240811.9982
C | Xist Rating 9960 | -10.47 | 1808.37 | 150.307 | 35.7 | 2180.75 | 8455.65 | 14709.2 | 0.5 | 1.9 | 25.102 | 28.589 | 1 | 1 | 2100 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3943602.8775 | 307445.8039 | 4295.0947 | 34684.3832 | 272761.4207 | 30871.0791 | 0.080012 | -238378.2896 | 238378.2896
C | Xist Rating 9961 | -9.95 | 1820.22 | 150.307 | 35.7 | 2179.64 | 8465.95 | 14638.6 | 0.49 | 1.89 | 25.105 | 28.325 | 1 | 1 | 2110 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 3967424.3208 | 310214.8805 | 4336.0977 | 34849.547 | 275365.3336 | 30578.939 | 0.080393 | -236122.4614 | 236122.4614
C | Xist Rating 9962 | -8.1 | 1866.22 | 150.307 | 35.7 | 2169.93 | 8428.57 | 14359 | 0.49 | 1.84 | 25.14 | 27.243 | 1 | 1 | 2120 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4049566.7646 | 312996.3273 | 4377.2956 | 35014.7107 | 277981.6166 | 29462.4275 | 0.080774 | -227501.0557 | 227501.0557
C | Xist Rating 9963 | -7.41 | 1882.94 | 150.307 | 35.7 | 2167.35 | 8427.61 | 14263.6 | 0.48 | 1.83 | 25.138 | 26.894 | 1 | 1 | 2130 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4080990.009 | 315790.1441 | 4418.6882 | 35179.8744 | 280610.2697 | 29081.4189 | 0.081155 | -224559.0081 | 224559.0081
C | Xist Rating 9964 | -6.83 | 1899.69 | 150.307 | 35.7 | 2162.29 | 8389.07 | 14169.7 | 0.48 | 1.81 | 25.133 | 26.553 | 1 | 1 | 2140 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4107680.6901 | 318596.3311 | 4460.2756 | 35345.0382 | 283251.293 | 28732.4694 | 0.081536 | -221864.5123 | 221864.5123
C | Xist Rating 9965 | -6.42 | 1908.4 | 150.307 | 35.7 | 2162.24 | 8407.19 | 14123.3 | 0.47 | 1.8 | 25.137 | 26.393 | 1 | 1 | 2150 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4126418.816 | 321414.8883 | 4502.0578 | 35510.2019 | 285904.6864 | 28547.6769 | 0.081917 | -220437.5942 | 220437.5942
C | Xist Rating 9966 | -5.87 | 1920.2 | 150.307 | 35.7 | 2161.98 | 8429.65 | 14058.9 | 0.47 | 1.79 | 25.145 | 26.165 | 1 | 1 | 2160 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4151433.996 | 324245.8156 | 4544.0348 | 35675.3656 | 288570.4499 | 28316.5591 | 0.082298 | -218652.9636 | 218652.9636
C | Xist Rating 9967 | -3.94 | 1969.71 | 150.307 | 35.7 | 2151.27 | 8381.48 | 13785.9 | 0.46 | 1.75 | 25.173 | 25.167 | 1 | 1 | 2170 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4237378.0317 | 327089.113 | 4586.2066 | 35840.5293 | 291248.5836 | 27262.2296 | 0.082679 | -210511.7102 | 210511.7102
C | Xist Rating 9968 | -3.2 | 1986.21 | 150.307 | 35.7 | 2150.22 | 8402.81 | 13699 | 0.46 | 1.74 | 25.187 | 24.862 | 1 | 1 | 2180 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4270788.4662 | 329944.7805 | 4628.5732 | 36005.6931 | 293939.0874 | 26951.3073 | 0.08306 | -208110.8513 | 208110.8513
C | Xist Rating 9969 | -2.69 | 1998.24 | 150.307 | 35.7 | 2149.04 | 8410.81 | 13638.9 | 0.45 | 1.73 | 25.187 | 24.661 | 1 | 1 | 2190 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4294297.6896 | 332812.8182 | 4671.1346 | 36170.8568 | 296641.9614 | 26723.0375 | 0.083441 | -206348.212 | 206348.212
C | Xist Rating 9970 | -2.22 | 2010.68 | 150.307 | 35.7 | 2146.5 | 8398.14 | 13579.4 | 0.45 | 1.72 | 25.17 | 24.467 | 1 | 1 | 2200 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4315924.62 | 335693.226 | 4713.8907 | 36336.0205 | 299357.2054 | 26525.8949 | 0.083822 | -204825.9291 | 204825.9291
C | Xist Rating 9971 | -1.52 | 2027.43 | 150.307 | 35.7 | 2144.5 | 8404.59 | 13495.4 | 0.44 | 1.7 | 25.173 | 24.181 | 1 | 1 | 2210 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4347823.635 | 338586.0039 | 4756.8417 | 36501.1843 | 302084.8197 | 26209.1581 | 0.084203 | -202380.1719 | 202380.1719
C | Xist Rating 9972 | 0.4 | 2076.81 | 150.307 | 35.7 | 2134.77 | 8368 | 13246.2 | 0.44 | 1.66 | 25.209 | 23.316 | 1 | 1 | 2220 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4433511.6837 | 341491.152 | 4799.9874 | 36666.348 | 304824.804 | 25317.3981 | 0.084584 | -195494.2372 | 195494.2372
C | Xist Rating 9973 | 0.98 | 2090.24 | 150.307 | 35.7 | 2133.83 | 8382.91 | 13182.5 | 0.44 | 1.65 | 25.214 | 23.108 | 1 | 1 | 2230 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4460216.8192 | 344408.6702 | 4843.3279 | 36831.5117 | 307577.1585 | 25106.5823 | 0.084965 | -193866.3732 | 193866.3732
C | Xist Rating 9974 | 1.54 | 2105.73 | 150.307 | 35.7 | 2130.46 | 8363.93 | 13111.8 | 0.43 | 1.64 | 25.208 | 22.882 | 1 | 1 | 2240 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4486173.5358 | 347338.5585 | 4886.8633 | 36996.6755 | 310341.8831 | 24851.2788 | 0.085346 | -191894.9877 | 191894.9877
C | Xist Rating 9975 | 2.17 | 2122.79 | 150.307 | 35.7 | 2126.86 | 8344.99 | 13034.1 | 0.43 | 1.63 | 25.204 | 22.633 | 1 | 1 | 2250 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4514877.1394 | 350280.817 | 4930.5934 | 37161.8392 | 313118.9778 | 24597.378 | 0.085727 | -189934.4327 | 189934.4327
C | Xist Rating 9976 | 2.58 | 2131.47 | 150.307 | 35.7 | 2127.14 | 8367.59 | 12995.6 | 0.42 | 1.62 | 25.213 | 22.515 | 1 | 1 | 2260 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4533935.0958 | 353235.4456 | 4974.5182 | 37327.0029 | 315908.4427 | 24454.5435 | 0.086108 | -188831.5025 | 188831.5025
C | Xist Rating 9977 | 4.51 | 2184.45 | 150.307 | 35.7 | 2115.11 | 8299.31 | 12752 | 0.42 | 1.59 | 25.233 | 21.713 | 1 | 1 | 2270 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4620352.0395 | 356202.4443 | 5018.6379 | 37492.1666 | 318710.2777 | 23627.2691 | 0.086489 | -182443.5095 | 182443.5095
C | Xist Rating 9978 | 5.09 | 2199.9 | 150.307 | 35.7 | 2112.31 | 8288.3 | 12686.3 | 0.41 | 1.58 | 25.228 | 21.512 | 1 | 1 | 2280 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4646870.769 | 359181.8132 | 5062.9524 | 37657.3304 | 321524.4828 | 23397.2837 | 0.08687 | -180667.6231 | 180667.6231
C | Xist Rating 9979 | 5.82 | 2218.31 | 150.307 | 35.7 | 2109.81 | 8288.93 | 12607 | 0.41 | 1.56 | 25.231 | 21.265 | 1 | 1 | 2290 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4680212.6211 | 362173.5522 | 5107.4617 | 37822.4941 | 324351.0581 | 23145.5373 | 0.087251 | -178723.7039 | 178723.7039
C | Xist Rating 9980 | 6.3 | 2230.51 | 150.307 | 35.7 | 2108.23 | 8289.34 | 12557.2 | 0.41 | 1.56 | 25.232 | 21.117 | 1 | 1 | 2300 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4702428.0973 | 365177.6613 | 5152.1657 | 37987.6578 | 327190.0035 | 22996.5188 | 0.087632 | -177573.0224 | 177573.0224
| Xist Rating 9981 | 6.74 | 2242.97 | 150.307 | 35.7 | 2105.58 | 8273.28 | 12507.8 | 0.4 | 1.55 | 25.236 | 20.974 | 1 | 1 | 2310 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4722752.7726 | 368194.1406 | 5197.0645 | 38152.8216 | 330041.319 | 22826.6899 | 0.088013 | -176261.6487 | 176261.6487
C | Xist Rating 9982 | 8.76 | 2297.41 | 150.307 | 35.7 | 2095.02 | 8227.76 | 12277.3 | 0.4 | 1.51 | 25.254 | 20.251 | 1 | 1 | 2320 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4813119.8982 | 371222.99 | 5242.1582 | 38317.9853 | 332905.0047 | 22081.1291 | 0.088394 | -170504.6256 | 170504.6256
| Xist Rating 9983 | 9.34 | 2312.88 | 150.307 | 35.7 | 2092.7 | 8223.32 | 12217.1 | 0.39 | 1.5 | 25.261 | 20.076 | 1 | 1 | 2330 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4840163.976 | 374264.2095 | 5287.4466 | 38483.149 | 335781.0605 | 21877.8293 | 0.088775 | -168934.799 | 168934.799
| Xist Rating 9984 | 9.97 | 2328.33 | 150.307 | 35.7 | 2091.16 | 8230.7 | 12157.4 | 0.39 | 1.49 | 25.261 | 19.903 | 1 | 1 | 2340 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4868910.5628 | 377317.7991 | 5332.9298 | 38648.3127 | 338669.4864 | 21702.5851 | 0.089156 | -167581.6097 | 167581.6097
| Xist Rating 9985 | 10.57 | 2342.26 | 150.307 | 35.7 | 2090.64 | 8250.47 | 12104.9 | 0.38 | 1.49 | 25.27 | 19.754 | 1 | 1 | 2350 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4896822.4464 | 380383.7589 | 5378.6078 | 38813.4765 | 341570.2825 | 21526.0158 | 0.089537 | -166218.1877 | 166218.1877
| Xist Rating 9986 | 11.17 | 2359.37 | 150.307 | 35.7 | 2087.1 | 8230.2 | 12040.1 | 0.38 | 1.48 | 25.257 | 19.568 | 1 | 1 | 2360 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 4924241.127 | 383462.0889 | 5424.4805 | 38978.6402 | 344483.4487 | 21336.6368 | 0.089918 | -164755.8536 | 164755.8536
| Xist Rating 9987 | 12.97 | 2409.17 | 150.307 | 35.7 | 2077.61 | 8187.64 | 11847.1 | 0.38 | 1.45 | 25.285 | 18.993 | 1 | 1 | 2370 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5005315.6837 | 386552.7889 | 5470.5481 | 39143.8039 | 347408.985 | 20744.9327 | 0.090299 | -160186.8711 | 160186.8711
| Xist Rating 9988 | 13.49 | 2424.86 | 150.307 | 35.7 | 2074.14 | 8164.43 | 11791.5 | 0.38 | 1.44 | 25.275 | 18.84 | 1 | 1 | 2380 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5029499.1204 | 389655.8591 | 5516.8105 | 39308.9677 | 350346.8914 | 20589.9439 | 0.09068 | -158990.0889 | 158990.0889
| Xist Rating 9989 | 14.13 | 2441.53 | 150.307 | 35.7 | 2071.96 | 8164.42 | 11730.3 | 0.37 | 1.43 | 25.274 | 18.667 | 1 | 1 | 2390 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5058752.4988 | 392771.2994 | 5563.2676 | 39474.1314 | 353297.168 | 20387.4719 | 0.091061 | -157426.6536 | 157426.6536
C | Xist Rating 9990 | 26.31 | 2797.27 | 150.307 | 35.7 | 2001.68 | 7792.02 | 10538.4 | 0.41 | 1.25 | 25.233 | 15.388 | 1 | 1 | 2400 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5599239.4136 | 395899.1099 | 5609.9196 | 39639.2951 | 356259.8148 | 17093.3771 | 0.091442 | -131990.527 | 131990.527
C | Xist Rating 9991 | 26.37 | 2798.72 | 150.307 | 35.7 | 2002.02 | 7797.11 | 10538.4 | 0.41 | 1.25 | 25.236 | 15.399 | 1 | 1 | 2410 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5603093.4144 | 399039.2905 | 5656.7663 | 39804.4589 | 359234.8316 | 17109.5708 | 0.091823 | -132115.5705 | 132115.5705
C | Xist Rating 9992 | 26.49 | 2800.12 | 150.307 | 35.7 | 2003.33 | 7816.99 | 10538.5 | 0.4 | 1.25 | 25.273 | 15.41 | 1 | 1 | 2420 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5609564.3996 | 402191.8412 | 5703.8078 | 39969.6226 | 362222.2186 | 17099.8627 | 0.092204 | -132040.6072 | 132040.6072
C | Xist Rating 9993 | 26.59 | 2801.48 | 150.307 | 35.7 | 2004.48 | 7834.57 | 10538.5 | 0.39 | 1.25 | 25.274 | 15.421 | 1 | 1 | 2430 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5615510.6304 | 405356.762 | 5751.0441 | 40134.7863 | 365221.9757 | 17088.3317 | 0.092585 | -131951.5681 | 131951.5681
C | Xist Rating 9994 | 26.75 | 2802.85 | 150.307 | 35.7 | 2006.36 | 7863.46 | 10538.4 | 0.39 | 1.25 | 25.279 | 15.432 | 1 | 1 | 2440 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5623526.126 | 408534.053 | 5798.4752 | 40299.95 | 368234.103 | 17104.3868 | 0.092966 | -132075.5411 | 132075.5411
C | Xist Rating 9995 | 26.7 | 2804.17 | 150.307 | 35.7 | 2005.55 | 7851 | 10538.3 | 0.38 | 1.25 | 25.272 | 15.443 | 1 | 1 | 2450 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5623903.1435 | 411723.7141 | 5846.1011 | 40465.1138 | 371258.6004 | 17092.1758 | 0.093347 | -131981.2513 | 131981.2513
C | Xist Rating 9996 | 26.7 | 2805.65 | 150.307 | 35.7 | 2004.33 | 7832.25 | 10538.5 | 0.37 | 1.25 | 25.277 | 15.454 | 1 | 1 | 2460 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5623448.4645 | 414925.7454 | 5893.9217 | 40630.2775 | 374295.4679 | 17080.2409 | 0.093728 | -131889.0928 | 131889.0928
C | Xist Rating 9997 | 26.71 | 2807 | 150.307 | 35.7 | 2003.98 | 7826.92 | 10538.5 | 0.37 | 1.25 | 25.312 | 15.465 | 1 | 1 | 2470 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5625171.86 | 418140.1468 | 5941.9372 | 40795.4412 | 377344.7055 | 17097.2904 | 0.094109 | -132020.7445 | 132020.7445
C | Xist Rating 9998 | 26.71 | 2808.35 | 150.307 | 35.7 | 2003.49 | 7819.48 | 10538.5 | 0.36 | 1.25 | 25.304 | 15.475 | 1 | 1 | 2480 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5626501.1415 | 421366.9183 | 5990.1474 | 40960.605 | 380406.3133 | 17083.4151 | 0.09449 | -131913.6033 | 131913.6033
C | Xist Rating 9999 | 26.72 | 2809.74 | 150.307 | 35.7 | 2002.97 | 7811.56 | 10538.5 | 0.35 | 1.25 | 25.297 | 15.486 | 1 | 1 | 2490 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5627824.9278 | 424606.0599 | 6038.5525 | 41125.7687 | 383480.2912 | 17070.4058 | 0.094871 | -131813.1486 | 131813.1486
C | Xist Rating 10000 | 26.74 | 2810.73 | 150.307 | 35.7 | 2003.17 | 7814.65 | 10538.5 | 0.35 | 1.25 | 25.295 | 15.495 | 1 | 1 | 2500 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5630370.0141 | 427857.5717 | 6087.1523 | 41290.9324 | 386566.6393 | 17083.6426 | 0.095252 | -131915.3597 | 131915.3597
C | Xist Rating 10001 | 26.75 | 2812.58 | 150.307 | 35.7 | 2002.73 | 7808.03 | 10538.4 | 0.34 | 1.25 | 25.277 | 15.507 | 1 | 1 | 2510 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5632838.3434 | 431121.4536 | 6135.9469 | 41456.0962 | 389665.3574 | 17070.9251 | 0.095633 | -131817.1584 | 131817.1584
C | Xist Rating 10002 | 26.73 | 2814.03 | 150.307 | 35.7 | 2002.1 | 7798.36 | 10538.3 | 0.34 | 1.25 | 25.311 | 15.518 | 1 | 1 | 2520 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5633969.463 | 434397.7056 | 6184.9363 | 41621.2599 | 392776.4458 | 17087.5067 | 0.096014 | -131945.197 | 131945.197
C | Xist Rating 10003 | 26.72 | 2815.37 | 150.307 | 35.7 | 2001.08 | 7783.01 | 10538.4 | 0.33 | 1.25 | 25.31 | 15.529 | 1 | 1 | 2530 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5633780.5996 | 437686.3278 | 6234.1205 | 41786.4236 | 395899.9042 | 17074.0459 | 0.096395 | -131841.2568 | 131841.2568
C | Xist Rating 10004 | 26.72 | 2816.52 | 150.307 | 35.7 | 2000.66 | 7776.59 | 10538.4 | 0.33 | 1.25 | 25.308 | 15.538 | 1 | 1 | 2540 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5634898.9032 | 440987.3201 | 6283.4995 | 41951.5873 | 399035.7328 | 17087.0612 | 0.096776 | -131941.757 | 131941.757
C | Xist Rating 10005 | 26.75 | 2818.07 | 150.307 | 35.7 | 2000.65 | 7776.43 | 10538.3 | 0.32 | 1.25 | 25.297 | 15.549 | 1 | 1 | 2550 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5637971.7455 | 444300.6826 | 6333.0732 | 42116.7511 | 402183.9315 | 17072.8981 | 0.097157 | -131832.3938 | 131832.3938
C | Xist Rating 10006 | 26.75 | 2819.52 | 150.307 | 35.7 | 2000.04 | 7767.24 | 10538.3 | 0.32 | 1.25 | 25.292 | 15.56 | 1 | 1 | 2560 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5639152.7808 | 447626.4151 | 6382.8418 | 42281.9148 | 405344.5003 | 17087.7666 | 0.097538 | -131947.204 | 131947.204
C | Xist Rating 10007 | 26.77 | 2820.91 | 150.307 | 35.7 | 1999.93 | 7765.67 | 10538.3 | 0.31 | 1.25 | 25.311 | 15.57 | 1 | 1 | 2570 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5641622.5363 | 450964.5178 | 6432.8051 | 42447.0785 | 408517.4393 | 17073.3217 | 0.097919 | -131835.6647 | 131835.6647
C | Xist Rating 10008 | 26.77 | 2822.27 | 150.308 | 35.7 | 1999.47 | 7758.66 | 10538.3 | 0.31 | 1.25 | 25.346 | 15.58 | 1 | 1 | 2580 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5643044.1969 | 454314.9907 | 6482.9633 | 42612.2423 | 411702.7484 | 17088.4786 | 0.0983 | -131952.7021 | 131952.7021
C | Xist Rating 10009 | 26.79 | 2823.63 | 150.308 | 35.7 | 1999.24 | 7755.18 | 10538.3 | 0.3 | 1.25 | 25.343 | 15.59 | 1 | 1 | 2590 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5645114.0412 | 457677.8337 | 6533.3162 | 42777.406 | 414900.4277 | 17072.8554 | 0.098681 | -131832.0642 | 131832.0642
C | Xist Rating 10010 | 26.82 | 2824.81 | 150.308 | 35.7 | 1999.39 | 7757.5 | 10538.3 | 0.3 | 1.25 | 25.344 | 15.6 | 1 | 1 | 2600 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5647896.8659 | 461053.0468 | 6583.8639 | 42942.5697 | 418110.477 | 17086.6834 | 0.099062 | -131938.8397 | 131938.8397
C | Xist Rating 10011 | 26.78 | 2826.5 | 150.308 | 35.7 | 1998.12 | 7738.46 | 10538.3 | 0.3 | 1.25 | 25.337 | 15.611 | 1 | 1 | 2610 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5647686.18 | 464440.63 | 6634.6064 | 43107.7334 | 421332.8965 | 17101.2693 | 0.099443 | -132051.4682 | 132051.4682
C | Xist Rating 10012 | 26.81 | 2827.89 | 150.308 | 35.7 | 1997.97 | 7736.22 | 10538.3 | 0.29 | 1.25 | 25.338 | 15.621 | 1 | 1 | 2620 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5650039.3833 | 467840.5834 | 6685.5437 | 43272.8972 | 424567.6862 | 17085.3396 | 0.099824 | -131928.4632 | 131928.4632
C | Xist Rating 10013 | 26.83 | 2829.32 | 150.308 | 35.7 | 1997.72 | 7732.48 | 10538.2 | 0.29 | 1.25 | 25.376 | 15.632 | 1 | 1 | 2630 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5652189.1504 | 471252.9069 | 6736.6758 | 43438.0609 | 427814.8459 | 17101.3559 | 0.10021 | -132052.1372 | 132052.1372
C | Xist Rating 10014 | 26.85 | 2830.57 | 150.308 | 35.7 | 1997.61 | 7730.85 | 10538.2 | 0.28 | 1.25 | 25.375 | 15.641 | 1 | 1 | 2640 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5654374.9377 | 474677.6005 | 6788.0027 | 43603.2246 | 431074.3758 | 17083.9387 | 0.10059 | -131917.6462 | 131917.6462
C | Xist Rating 10015 | 26.87 | 2832.07 | 150.308 | 35.7 | 1997.19 | 7724.59 | 10538.2 | 0.28 | 1.25 | 25.378 | 15.652 | 1 | 1 | 2650 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5656181.8833 | 478114.6643 | 6839.5243 | 43768.3884 | 434346.2759 | 17098.6467 | 0.10097 | -132031.2178 | 132031.2178
C | Xist Rating 10016 | 26.89 | 2833.41 | 150.308 | 35.7 | 1997.12 | 7723.47 | 10538.2 | 0.28 | 1.25 | 25.379 | 15.662 | 1 | 1 | 2660 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5658659.7792 | 481564.0981 | 6891.2408 | 43933.5521 | 437630.546 | 17112.2503 | 0.10135 | -132136.2608 | 132136.2608
C | Xist Rating 10017 | 26.95 | 2834.8 | 150.308 | 35.7 | 1997.35 | 7726.98 | 10538.2 | 0.27 | 1.25 | 25.384 | 15.672 | 1 | 1 | 2670 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5662087.78 | 485025.9022 | 6943.152 | 44098.7158 | 440927.1863 | 17095.6081 | 0.10173 | -132007.7541 | 132007.7541
C | Xist Rating 10018 | 26.99 | 2836.21 | 150.308 | 35.7 | 1997.44 | 7728.25 | 10538.2 | 0.27 | 1.25 | 25.422 | 15.682 | 1 | 1 | 2680 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5665159.3024 | 488500.0763 | 6995.258 | 44263.8796 | 444236.1968 | 17110.2977 | 0.10211 | -132121.1837 | 132121.1837
C | Xist Rating 10019 | 27.05 | 2837.59 | 150.308 | 35.7 | 1997.86 | 7734.58 | 10538.3 | 0.26 | 1.25 | 25.423 | 15.692 | 1 | 1 | 2690 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5669107.5574 | 491986.6206 | 7047.5588 | 44429.0433 | 447557.5773 | 17093.1374 | 0.10249 | -131988.6761 | 131988.6761
C | Xist Rating 10020 | 27.12 | 2838.79 | 150.308 | 35.7 | 1998.64 | 7746.18 | 10538.3 | 0.26 | 1.25 | 25.425 | 15.701 | 1 | 1 | 2700 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5673719.2456 | 495485.5351 | 7100.0544 | 44594.207 | 450891.328 | 17105.5097 | 0.10287 | -132084.2119 | 132084.2119
C | Xist Rating 10021 | 27.18 | 2840.45 | 150.308 | 35.6 | 1999.09 | 7753.05 | 10538.2 | 0.26 | 1.25 | 25.426 | 15.712 | 1 | 1 | 2710 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5678315.1905 | 498996.8196 | 7152.7448 | 44759.3707 | 454237.4489 | 17119.9279 | 0.10325 | -132195.5454 | 132195.5454
C | Xist Rating 10022 | 27.23 | 2841.79 | 150.308 | 35.6 | 1999.52 | 7759.5 | 10538.1 | 0.25 | 1.25 | 25.423 | 15.721 | 1 | 1 | 2720 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5682215.9408 | 502520.4743 | 7205.63 | 44924.5345 | 457595.9398 | 17101.1461 | 0.10363 | -132050.5168 | 132050.5168
C | Xist Rating 10023 | 27.21 | 2843.11 | 150.308 | 35.6 | 1998.66 | 7746.59 | 10538.1 | 0.25 | 1.25 | 25.457 | 15.731 | 1 | 1 | 2730 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5682410.2326 | 506056.4991 | 7258.71 | 45089.6982 | 460966.8009 | 17115.4201 | 0.10402 | -132160.7375 | 132160.7375
C | Xist Rating 10024 | 27.19 | 2844.4 | 150.308 | 35.6 | 1998.02 | 7737.05 | 10538.2 | 0.25 | 1.25 | 25.453 | 15.74 | 1 | 1 | 2740 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5683168.088 | 509604.8941 | 7311.9847 | 45254.8619 | 464350.0322 | 17127.4966 | 0.1044 | -132253.9884 | 132253.9884
C | Xist Rating 10025 | 27.16 | 2845.94 | 150.308 | 35.6 | 1996.95 | 7721.04 | 10538.1 | 0.25 | 1.25 | 25.448 | 15.75 | 1 | 1 | 2750 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5683199.883 | 513165.6592 | 7365.4543 | 45420.0257 | 467745.6335 | 17140.5798 | 0.10478 | -132355.0135 | 132355.0135
C | Xist Rating 10026 | 27.13 | 2847.37 | 150.308 | 35.6 | 1995.98 | 7706.57 | 10538.1 | 0.24 | 1.25 | 25.442 | 15.76 | 1 | 1 | 2760 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5683293.5726 | 516738.7944 | 7419.1186 | 45585.1894 | 471153.605 | 17122.1551 | 0.10516 | -132212.743 | 132212.743
C | Xist Rating 10027 | 27.13 | 2848.6 | 150.308 | 35.6 | 1995.49 | 7699.22 | 10538.2 | 0.24 | 1.25 | 25.441 | 15.769 | 1 | 1 | 2770 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5684352.814 | 520324.2998 | 7472.9777 | 45750.3531 | 474573.9466 | 17134.2088 | 0.10554 | -132305.8186 | 132305.8186
C | Xist Rating 10028 | 27.1 | 2850.15 | 150.308 | 35.6 | 1994.43 | 7683.41 | 10538.1 | 0.24 | 1.25 | 25.474 | 15.779 | 1 | 1 | 2780 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5684424.6645 | 523922.1752 | 7527.0316 | 45915.5169 | 478006.6584 | 17148.3176 | 0.10592 | -132414.7633 | 132414.7633
C | Xist Rating 10029 | 27.1 | 2851.56 | 150.308 | 35.6 | 1993.85 | 7674.93 | 10538.2 | 0.23 | 1.25 | 25.474 | 15.789 | 1 | 1 | 2790 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5685582.906 | 527532.4209 | 7581.2803 | 46080.6806 | 481451.7403 | 17129.5851 | 0.1063 | -132270.1157 | 132270.1157
C | Xist Rating 10030 | 27.08 | 2852.53 | 150.308 | 35.6 | 1993.3 | 7666.69 | 10538.2 | 0.23 | 1.25 | 25.462 | 15.797 | 1 | 1 | 2800 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5685948.049 | 531155.0366 | 7635.7238 | 46245.8443 | 484909.1923 | 17140.173 | 0.10668 | -132351.8724 | 132351.8724
C | Xist Rating 10031 | 27.07 | 2854.28 | 150.308 | 35.6 | 1992.48 | 7654.63 | 10538.1 | 0.23 | 1.25 | 25.462 | 15.808 | 1 | 1 | 2810 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5687095.8144 | 534790.0225 | 7690.3621 | 46411.008 | 488379.0145 | 17154.2215 | 0.10706 | -132460.3514 | 132460.3514
C | Xist Rating 10032 | 27.06 | 2855.76 | 150.308 | 35.6 | 1991.88 | 7645.68 | 10538.1 | 0.23 | 1.25 | 25.466 | 15.818 | 1 | 1 | 2820 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5688331.2288 | 538437.3785 | 7745.1952 | 46576.1718 | 491861.2067 | 17167.3478 | 0.10744 | -132561.7094 | 132561.7094
C | Xist Rating 10033 | 27.03 | 2857.13 | 150.308 | 35.6 | 1990.89 | 7631.18 | 10538.1 | 0.22 | 1.25 | 25.499 | 15.827 | 1 | 1 | 2830 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5688231.5457 | 542097.1047 | 7800.223 | 46741.3355 | 495355.7692 | 17147.9362 | 0.10783 | -132411.8176 | 132411.8176
C | Xist Rating 10034 | 27.05 | 2858.44 | 150.308 | 35.6 | 1990.7 | 7628.42 | 10538.1 | 0.22 | 1.25 | 25.505 | 15.836 | 1 | 1 | 2840 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5690296.508 | 545769.2009 | 7855.4457 | 46906.4992 | 498862.7017 | 17159.9652 | 0.10821 | -132504.703 | 132504.703
C | Xist Rating 10035 | 27.08 | 2859.89 | 150.308 | 35.6 | 1990.69 | 7628.2 | 10538.2 | 0.22 | 1.25 | 25.515 | 15.846 | 1 | 1 | 2850 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5693154.4241 | 549453.6674 | 7910.8631 | 47071.663 | 502382.0044 | 17173.1464 | 0.10859 | -132606.4847 | 132606.4847
C | Xist Rating 10036 | 27.02 | 2861.29 | 150.308 | 35.6 | 1989.25 | 7607.12 | 10538.1 | 0.22 | 1.25 | 25.504 | 15.855 | 1 | 1 | 2860 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5691821.1325 | 553150.5039 | 7966.4753 | 47236.8267 | 505913.6772 | 17184.6988 | 0.10897 | -132695.6892 | 132695.6892
C | Xist Rating 10037 | 27.12 | 2862.48 | 150.308 | 35.6 | 1990.37 | 7623.48 | 10538.2 | 0.21 | 1.25 | 25.525 | 15.864 | 1 | 1 | 2870 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5697394.3176 | 556859.7106 | 8022.2824 | 47401.9904 | 509457.7202 | 17164.3176 | 0.10935 | -132538.311 | 132538.311
C | Xist Rating 10038 | 27.22 | 2863.99 | 150.308 | 35.6 | 1991.34 | 7637.73 | 10538.2 | 0.21 | 1.25 | 25.588 | 15.874 | 1 | 1 | 2880 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 36 | E | Rod | 5703177.8466 | 560581.2874 | 8078.2842 | 47567.1542 | 513014.1332 | 17178.8133 | 0.10973 | -132650.2424 | 132650.2424
C | Xist Rating 10039 | 27.19 | 2865.34 | 150.308 | 35.6 | 1990.49 | 7625.19 | 10538.2 | 0.21 | 1.25 | 25.583 | 15.883 | 1 | 1 | 2890 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 35 | E | Rod | 5703430.6166 | 564315.2343 | 8134.4807 | 47732.3179 | 516582.9165 | 17190.4324 | 0.11011 | -132739.9621 | 132739.9621
C | Xist Rating 10040 | 27.33 | 2866.72 | 150.308 | 35.6 | 1992.2 | 7650.39 | 10538.3 | 0.21 | 1.25 | 25.61 | 15.892 | 1 | 1 | 2900 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 35 | E | Rod | 5711079.584 | 568061.5514 | 8190.8721 | 47897.4816 | 520164.0698 | 17202.9241 | 0.11049 | -132836.4197 | 132836.4197
C | Xist Rating 10041 | 27.53 | 2868.26 | 150.308 | 35.6 | 1994.76 | 7688.27 | 10538.4 | 0.2 | 1.25 | 25.652 | 15.902 | 1 | 1 | 2910 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 35 | E | Rod | 5721490.3176 | 571820.2386 | 8247.4583 | 48062.6453 | 523757.5933 | 17183.4099 | 0.11087 | -132685.7361 | 132685.7361
C | Xist Rating 10042 | 27.75 | 2869.65 | 150.308 | 35.6 | 1997.75 | 7732.81 | 10538.4 | 0.2 | 1.25 | 25.702 | 15.912 | 1 | 1 | 2920 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 35 | E | Rod | 5732843.2875 | 575591.296 | 8304.2393 | 48227.8091 | 527363.4869 | 17197.4034 | 0.11125 | -132793.7906 | 132793.7906
C | Xist Rating 10043 | 27.85 | 2871.04 | 150.308 | 35.6 | 1998.77 | 7748.07 | 10538.5 | 0.2 | 1.25 | 25.752 | 15.921 | 1 | 1 | 2930 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 35 | E | Rod | 5738548.6208 | 579374.7234 | 8361.215 | 48392.9728 | 530981.7506 | 17210.3674 | 0.11164 | -132893.8952 | 132893.8952
C | Xist Rating 10044 | 28.51 | 2872.4 | 150.308 | 35.6 | 2008.81 | 7901.09 | 10538.6 | 0.2 | 1.25 | 25.831 | 15.931 | 1 | 1 | 2940 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 35 | E | Rod | 5770105.844 | 583170.521 | 8418.3855 | 48558.1365 | 534612.3845 | 17225.1432 | 0.11202 | -133007.9903 | 133007.9903
C | Xist Rating 10045 | 29.16 | 2873.81 | 150.308 | 35.6 | 2018.71 | 8056.44 | 10538.7 | 0.19 | 1.25 | 25.907 | 15.942 | 1 | 1 | 2950 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 35 | E | Rod | 5801388.9851 | 586978.6888 | 8475.7509 | 48723.3003 | 538255.3885 | 17206.6349 | 0.1124 | -132865.0735 | 132865.0735
C | Xist Rating 10046 | 29.65 | 2875.18 | 150.308 | 35.6 | 2025.98 | 8173.36 | 10538.7 | 0.19 | 1.25 | 25.962 | 15.951 | 1 | 1 | 2960 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 35 | E | Rod | 5825057.1764 | 590799.2266 | 8533.311 | 48888.464 | 541910.7627 | 17219.5743 | 0.11278 | -132964.9882 | 132964.9882
C | Xist Rating 10047 | 30.12 | 2876.57 | 150.308 | 35.6 | 2032.91 | 8287.44 | 10538.7 | 0.19 | 1.25 | 26.017 | 15.961 | 1 | 1 | 2970 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 35 | E | Rod | 5847807.9187 | 594632.1347 | 8591.0659 | 49053.6277 | 545578.5069 | 17233.5616 | 0.11316 | -133072.9943 | 133072.9943
C | Xist Rating 10048 | 31.01 | 2877.79 | 150.308 | 35.6 | 2046.83 | 8523.87 | 10538.5 | 0.18 | 1.25 | 26.129 | 15.971 | 1 | 1 | 2980 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 35 | E | Rod | 5890346.9057 | 598477.4128 | 8649.0156 | 49218.7914 | 549258.6213 | 17214.1024 | 0.11354 | -132922.7359 | 132922.7359
C | Xist Rating 10049 | 30.99 | 2879.35 | 150.308 | 35.6 | 2045.98 | 8509.09 | 10538.5 | 0.18 | 1.25 | 26.123 | 15.98 | 1 | 1 | 2990 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 35 | E | Rod | 5891092.513 | 602335.0611 | 8707.16 | 49383.9552 | 552951.1059 | 17225.4124 | 0.11392 | -133010.0683 | 133010.0683
C | Xist Rating 10050 | 30.98 | 2880.78 | 150.308 | 35.6 | 2045.22 | 8496.07 | 10538.5 | 0.18 | 1.25 | 26.118 | 15.99 | 1 | 1 | 3000 | 152.4 | 2 | 5.9 | 19.05 | 1.3333 | 35 | E | Rod | 5891828.8716 | 606205.0795 | 8765.4993 | 49549.1189 | 556655.9605 | 17237.784 | 0.1143 | -133105.5991 | 133105.5991
C | Xist Rating 10051 | -83.57 | 301.693 | 150.315 | 35.9 | 2328.34 | 6765.05 | 58744.9 | 2.5 | 10.95 | 28.775 | 683.543 | 1 | 1 | 1000 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 702443.8796 | 79695.2901 | 973.9444 | 16796.3115 | 62898.9786 | 713082.898 | 0.038101 | -5506237.121 | 5506237.121
C | Xist Rating 10052 | -83.44 | 304.789 | 150.316 | 35.9 | 2324.25 | 6737.67 | 58283.4 | 2.48 | 10.84 | 28.885 | 670.651 | 1 | 1 | 1010 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 708405.8333 | 81127.5227 | 993.5206 | 16964.2746 | 64163.2481 | 699713.118 | 0.038482 | -5402999.2239 | 5402999.2239
C | Xist Rating 10053 | -82.21 | 328.405 | 150.316 | 35.9 | 2316.91 | 6729.85 | 54966.8 | 2.49 | 10.07 | 28.934 | 581.196 | 1 | 1 | 1020 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 760884.8285 | 82572.3351 | 1013.2917 | 17132.2377 | 65440.0973 | 606865.137 | 0.038863 | -4686051.7257 | 4686051.7257
C | Xist Rating 10054 | -81.99 | 334.743 | 150.314 | 35.9 | 2302.1 | 6619.74 | 54177.6 | 2.4 | 9.89 | 28.196 | 561.527 | 1 | 1 | 1030 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 770611.8603 | 84029.7272 | 1033.2576 | 17300.2008 | 66729.5264 | 586269.2027 | 0.039244 | -4527015.3806 | 4527015.3806
C | Xist Rating 10055 | -81.87 | 337.913 | 150.314 | 35.9 | 2296.71 | 6581.9 | 53793.6 | 2.36 | 9.8 | 28.037 | 552.123 | 1 | 1 | 1040 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 776088.1662 | 85499.6992 | 1053.4182 | 17468.164 | 68031.5352 | 576463.4266 | 0.039625 | -4451297.7764 | 4451297.7764
C | Xist Rating 10056 | -81.59 | 344.129 | 150.314 | 35.9 | 2290.08 | 6540.68 | 53042.6 | 2.33 | 9.63 | 27.927 | 533.735 | 1 | 1 | 1050 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 788082.9403 | 86982.251 | 1073.7737 | 17636.1271 | 69346.1239 | 557345.5264 | 0.040006 | -4303674.4185 | 4303674.4185
C | Xist Rating 10057 | -81.46 | 347.28 | 150.313 | 35.9 | 2285.81 | 6512.38 | 52675.8 | 2.29 | 9.54 | 27.877 | 524.986 | 1 | 1 | 1060 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 793816.0968 | 88477.3825 | 1094.3239 | 17804.0902 | 70673.2923 | 548230.3536 | 0.040387 | -4233289.4706 | 4233289.4706
C | Xist Rating 10058 | -80.24 | 372.599 | 150.313 | 35.9 | 2272.01 | 6452.63 | 49856.5 | 2.27 | 8.9 | 27.576 | 459.283 | 1 | 1 | 1070 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 846548.654 | 89985.0939 | 1115.0689 | 17972.0533 | 72013.0406 | 479966.9951 | 0.040768 | -3706177.9109 | 3706177.9109
C | Xist Rating 10059 | -80 | 377.329 | 150.312 | 35.9 | 2270.93 | 6453.12 | 49380.2 | 2.23 | 8.79 | 27.412 | 448.895 | 1 | 1 | 1080 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 856887.746 | 91505.385 | 1136.0087 | 18140.0164 | 73365.3686 | 469136.0291 | 0.041149 | -3622544.0621 | 3622544.0621
C | Xist Rating 10060 | -79.67 | 383.625 | 150.312 | 35.9 | 2271.57 | 6470.71 | 48760.4 | 2.17 | 8.65 | 27.185 | 435.575 | 1 | 1 | 1090 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 871431.0413 | 93038.256 | 1157.1433 | 18307.9795 | 74730.2765 | 455226.2043 | 0.04153 | -3515136.0825 | 3515136.0825
C | Xist Rating 10061 | -79.35 | 388.323 | 150.312 | 35.9 | 2280.12 | 6550.04 | 48306.5 | 2.13 | 8.55 | 27.192 | 425.963 | 1 | 1 | 1100 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 885423.0388 | 94583.7067 | 1178.4727 | 18475.9426 | 76107.7641 | 445217.7188 | 0.041911 | -3437853.2106 | 3437853.2106
C | Xist Rating 10062 | -79.17 | 391.661 | 150.311 | 35.9 | 2281.16 | 6564.97 | 48010.1 | 2.04 | 8.48 | 26.75 | 420.008 | 1 | 1 | 1110 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 893441.4068 | 96141.7373 | 1199.9969 | 18643.9058 | 77497.8315 | 438892.794 | 0.042292 | -3389013.8177 | 3389013.8177
C | Xist Rating 10063 | -77.72 | 419.901 | 150.312 | 35.9 | 2275.7 | 6577.91 | 45447.3 | 2.09 | 7.92 | 27.129 | 367.503 | 1 | 1 | 1120 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 955568.7057 | 97712.3476 | 1221.7158 | 18811.8689 | 78900.4787 | 384497.8094 | 0.042673 | -2968990.1653 | 2968990.1653
C | Xist Rating 10064 | -77.52 | 423.193 | 150.311 | 35.9 | 2279.44 | 6615.55 | 45188.3 | 2.02 | 7.86 | 26.849 | 362.705 | 1 | 1 | 1130 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 964643.0519 | 99295.5378 | 1243.6296 | 18979.832 | 80315.7058 | 379415.6713 | 0.043054 | -2929747.2421 | 2929747.2421
C | Xist Rating 10065 | -77.2 | 429.559 | 150.31 | 35.9 | 2278.13 | 6617.2 | 44680.4 | 1.96 | 7.75 | 26.409 | 353.151 | 1 | 1 | 1140 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 978591.2447 | 100891.3077 | 1265.7381 | 19147.7951 | 81743.5126 | 369391.7802 | 0.043435 | -2852345.4115 | 2852345.4115
C | Xist Rating 10066 | -76.86 | 435.863 | 150.31 | 35.9 | 2279.79 | 6643.92 | 44185.5 | 1.92 | 7.64 | 26.314 | 343.924 | 1 | 1 | 1150 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 993676.1088 | 102499.6574 | 1288.0414 | 19315.7582 | 83183.8992 | 359768.9012 | 0.043816 | -2778040.0908 | 2778040.0908
C | Xist Rating 10067 | -76.53 | 442.245 | 150.309 | 35.9 | 2278.97 | 6649.64 | 43702.9 | 1.86 | 7.53 | 26.09 | 335.129 | 1 | 1 | 1160 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1007863.0876 | 104120.5869 | 1310.5395 | 19483.7213 | 84636.8656 | 350554.1961 | 0.044197 | -2706886.581 | 2706886.581
C | Xist Rating 10068 | -75.26 | 467.55 | 150.31 | 35.9 | 2273.53 | 6655.27 | 41831.8 | 1.89 | 7.13 | 26.281 | 301.417 | 1 | 1 | 1170 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1062988.9515 | 105754.0962 | 1333.2324 | 19651.6844 | 86102.4118 | 315626.0703 | 0.044578 | -2437180.8518 | 2437180.8518
C | Xist Rating 10069 | -75.13 | 469.29 | 150.309 | 35.9 | 2277.49 | 6692.55 | 41723.9 | 1.84 | 7.1 | 26.147 | 299.729 | 1 | 1 | 1180 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1068803.2821 | 107400.1854 | 1356.1201 | 19819.6476 | 87580.5378 | 313812.8044 | 0.044959 | -2423179.293 | 2423179.293
C | Xist Rating 10070 | -74.55 | 481.882 | 150.309 | 35.9 | 2270.72 | 6659.38 | 40884.9 | 1.79 | 6.92 | 25.902 | 285.584 | 1 | 1 | 1190 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1094219.095 | 109058.8543 | 1379.2026 | 19987.6107 | 89071.2436 | 299051.681 | 0.04534 | -2309197.8107 | 2309197.8107
C | Xist Rating 10071 | -74.25 | 485.066 | 150.309 | 35.9 | 2283.03 | 6772.84 | 40681.1 | 1.76 | 6.88 | 25.968 | 282.269 | 1 | 1 | 1200 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1107420.23 | 110730.103 | 1402.4799 | 20155.5738 | 90574.5292 | 295594.292 | 0.045721 | -2282500.7691 | 2282500.7691
C | Xist Rating 10072 | -73.91 | 491.518 | 150.308 | 35.8 | 2283.1 | 6786.42 | 40280.5 | 1.7 | 6.8 | 25.758 | 275.816 | 1 | 1 | 1210 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1122184.7458 | 112413.9315 | 1425.9519 | 20323.5369 | 92090.3946 | 288809.4784 | 0.046102 | -2230110.2372 | 2230110.2372
C | Xist Rating 10073 | -72.54 | 520.112 | 150.308 | 35.8 | 2271.92 | 6746.89 | 38537.5 | 1.71 | 6.43 | 25.762 | 247.962 | 1 | 1 | 1220 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1181652.855 | 114110.3398 | 1449.6188 | 20491.5 | 93618.8397 | 259917.2316 | 0.046483 | -2007011.9661 | 2007011.9661
C | Xist Rating 10074 | -72.14 | 526.413 | 150.308 | 35.8 | 2277.47 | 6808.84 | 38182.9 | 1.68 | 6.35 | 25.784 | 242.599 | 1 | 1 | 1230 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1198889.8151 | 115819.3279 | 1473.4804 | 20659.4631 | 95159.8647 | 254326.9379 | 0.046864 | -1963845.1995 | 1963845.1995
C | Xist Rating 10075 | -71.78 | 532.855 | 150.308 | 35.8 | 2279.84 | 6842.99 | 37835.7 | 1.63 | 6.28 | 25.652 | 237.487 | 1 | 1 | 1240 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1214824.1432 | 117540.8957 | 1497.5369 | 20827.4263 | 96713.4695 | 248953.9345 | 0.047245 | -1922356.2918 | 1922356.2918
C | Xist Rating 10076 | -71.56 | 536.183 | 150.308 | 35.8 | 2284.66 | 6893.14 | 37664.5 | 1.59 | 6.24 | 25.562 | 235.061 | 1 | 1 | 1250 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1224995.8528 | 119275.0434 | 1521.7881 | 20995.3894 | 98279.6541 | 246387.7697 | 0.047626 | -1902541.0471 | 1902541.0471
C | Xist Rating 10077 | -71.06 | 545.659 | 150.308 | 35.8 | 2285.24 | 6918.26 | 37161.1 | 1.56 | 6.14 | 25.496 | 227.703 | 1 | 1 | 1260 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1246961.7732 | 121021.7709 | 1546.2341 | 21163.3525 | 99858.4184 | 238715.59 | 0.048007 | -1843298.5096 | 1843298.5096
C | Xist Rating 10078 | -69.73 | 572.73 | 150.308 | 35.8 | 2277.92 | 6908.23 | 35777.3 | 1.57 | 5.85 | 25.573 | 207.891 | 1 | 1 | 1270 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1304633.1216 | 122781.0782 | 1570.8749 | 21331.3156 | 101449.7626 | 218180.0839 | 0.048388 | -1684728.7749 | 1684728.7749
C | Xist Rating 10079 | -69.4 | 579.24 | 150.308 | 35.8 | 2277.88 | 6920.85 | 35477.1 | 1.52 | 5.79 | 25.417 | 203.886 | 1 | 1 | 1280 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1319439.2112 | 124552.9652 | 1595.7105 | 21499.2787 | 103053.6865 | 213951.9265 | 0.048769 | -1652080.0643 | 1652080.0643
C | Xist Rating 10080 | -69.05 | 585.698 | 150.307 | 35.8 | 2279.22 | 6946.37 | 35182.1 | 1.49 | 5.73 | 25.344 | 199.981 | 1 | 1 | 1290 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1334934.5956 | 126337.4321 | 1620.7408 | 21667.2418 | 104670.1903 | 209863.527 | 0.04915 | -1620510.5266 | 1620510.5266
C | Xist Rating 10081 | -68.54 | 595.152 | 150.307 | 35.8 | 2280.61 | 6978.98 | 34750.8 | 1.47 | 5.64 | 25.396 | 194.239 | 1 | 1 | 1300 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1357309.6027 | 128134.4788 | 1645.966 | 21835.2049 | 106299.2738 | 203892.3134 | 0.049531 | -1574402.3979 | 1574402.3979
C | Xist Rating 10082 | -68.28 | 600.074 | 150.307 | 35.8 | 2281.48 | 6997 | 34539.4 | 1.43 | 5.59 | 25.34 | 191.547 | 1 | 1 | 1310 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1369056.8295 | 129944.1052 | 1671.3859 | 22003.1681 | 107940.9372 | 201049.0569 | 0.049912 | -1552447.5249 | 1552447.5249
C | Xist Rating 10083 | -66.95 | 627.243 | 150.307 | 35.8 | 2274.48 | 6988.54 | 33362.4 | 1.44 | 5.35 | 25.394 | 176.337 | 1 | 1 | 1320 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1426651.6586 | 131766.3115 | 1697.0007 | 22171.1312 | 109595.1803 | 185289.3329 | 0.050293 | -1430755.1141 | 1430755.1141
C | Xist Rating 10084 | -66.48 | 636.914 | 150.307 | 35.8 | 2272.64 | 6990.71 | 32979.3 | 1.4 | 5.28 | 25.25 | 171.675 | 1 | 1 | 1330 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1447476.233 | 133601.0975 | 1722.8102 | 22339.0943 | 111262.0032 | 180391.6694 | 0.050674 | -1392936.6545 | 1392936.6545
C | Xist Rating 10085 | -65.95 | 646.483 | 150.307 | 35.8 | 2274.8 | 7030.82 | 32606 | 1.37 | 5.2 | 25.126 | 167.175 | 1 | 1 | 1340 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1470619.5284 | 135448.4634 | 1748.8145 | 22507.0574 | 112941.406 | 175678.5689 | 0.051055 | -1356543.3419 | 1356543.3419
C | Xist Rating 10086 | -65.65 | 651.423 | 150.306 | 35.8 | 2278.7 | 7078.24 | 32422.7 | 1.34 | 5.16 | 25.059 | 165.051 | 1 | 1 | 1350 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1484397.5901 | 137308.409 | 1775.0136 | 22675.0205 | 114633.3885 | 173437.1815 | 0.051436 | -1339235.9425 | 1339235.9425
C | Xist Rating 10087 | -65.27 | 654.554 | 150.307 | 35.8 | 2293.43 | 7229.21 | 32302.3 | 1.33 | 5.14 | 25.178 | 163.627 | 1 | 1 | 1360 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1501173.7802 | 139180.9344 | 1801.4075 | 22842.9836 | 116337.9508 | 171967.7835 | 0.051817 | -1327889.6405 | 1327889.6405
C | Xist Rating 10088 | -63.62 | 692.962 | 150.306 | 35.8 | 2270.27 | 7084.07 | 30901.5 | 1.32 | 4.86 | 25.054 | 147.337 | 1 | 1 | 1370 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1573210.8397 | 141066.0397 | 1827.9962 | 23010.9467 | 118055.0929 | 155040.1413 | 0.052198 | -1197178.8742 | 1197178.8742
C | Xist Rating 10089 | -63.45 | 696.355 | 150.306 | 35.8 | 2270.11 | 7089.15 | 30793.2 | 1.29 | 4.84 | 25 | 146.202 | 1 | 1 | 1380 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1580802.4491 | 142963.7247 | 1854.7797 | 23178.9099 | 119784.8148 | 153825.4669 | 0.052579 | -1187799.4807 | 1187799.4807
C | Xist Rating 10090 | -63.01 | 704.448 | 150.306 | 35.8 | 2271.69 | 7121.04 | 30526.2 | 1.27 | 4.78 | 24.954 | 143.304 | 1 | 1 | 1390 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1600287.4771 | 144873.9895 | 1881.7579 | 23346.873 | 121527.1165 | 150795.5614 | 0.05296 | -1164403.3533 | 1164403.3533
C | Xist Rating 10091 | -62.54 | 712.537 | 150.306 | 35.8 | 2275.31 | 7173.51 | 30264.3 | 1.24 | 4.73 | 24.929 | 140.492 | 1 | 1 | 1400 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1621242.5615 | 146796.8341 | 1908.931 | 23514.8361 | 123281.998 | 147840.5848 | 0.053341 | -1141585.8074 | 1141585.8074
C | Xist Rating 10092 | -62.06 | 722.167 | 150.306 | 35.8 | 2274.59 | 7186.44 | 29956.4 | 1.22 | 4.67 | 24.888 | 137.214 | 1 | 1 | 1410 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1642633.8365 | 148732.2585 | 1936.2988 | 23682.7992 | 125049.4593 | 144415.5701 | 0.053722 | -1115138.752 | 1115138.752
C | Xist Rating 10093 | -60.66 | 751.004 | 150.306 | 35.8 | 2268.51 | 7187.41 | 29050.9 | 1.22 | 4.49 | 24.971 | 127.617 | 1 | 1 | 1420 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1703660.084 | 150680.2628 | 1963.8614 | 23850.7623 | 126829.5004 | 134469.1563 | 0.054103 | -1038335.1815 | 1038335.1815
C | Xist Rating 10094 | -60.4 | 756.184 | 150.306 | 35.8 | 2268.95 | 7201.83 | 28909.7 | 1.19 | 4.47 | 24.856 | 126.272 | 1 | 1 | 1430 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1715743.6868 | 152640.8468 | 1991.6188 | 24018.7254 | 128622.1213 | 133029.241 | 0.054484 | -1027216.5367 | 1027216.5367
C | Xist Rating 10095 | -59.71 | 768.945 | 150.306 | 35.8 | 2270.43 | 7243.59 | 28541.5 | 1.17 | 4.39 | 24.859 | 122.572 | 1 | 1 | 1440 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1745835.7963 | 154614.0106 | 2019.571 | 24186.6886 | 130427.322 | 129168.1941 | 0.054865 | -997402.5558 | 997402.5558
C | Xist Rating 10096 | -59.27 | 777.073 | 150.306 | 35.8 | 2271.81 | 7274.63 | 28316.2 | 1.14 | 4.35 | 24.827 | 120.379 | 1 | 1 | 1450 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1765362.2121 | 156599.7542 | 2047.718 | 24354.6517 | 132245.1025 | 126852.9614 | 0.055246 | -979524.9427 | 979524.9427
C | Xist Rating 10097 | -58.86 | 781.894 | 150.306 | 35.8 | 2281.47 | 7385.03 | 28183.2 | 1.13 | 4.32 | 24.873 | 119.093 | 1 | 1 | 1460 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 38 | E | Rod | 1783867.7042 | 158598.0776 | 2076.0598 | 24522.6148 | 134075.4628 | 125517.293 | 0.055627 | -969211.2658 | 969211.2658
C | Xist Rating 10098 | -57.46 | 814.289 | 150.306 | 35.8 | 2265.6 | 7290.01 | 27309.7 | 1.12 | 4.16 | 24.793 | 110.661 | 1 | 1 | 1470 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 1844853.1584 | 160608.9807 | 2104.5964 | 24690.5779 | 135918.4028 | 116750.9797 | 0.056008 | -901520.1178 | 901520.1178
C | Xist Rating 10099 | -56.93 | 823.963 | 150.306 | 35.8 | 2267.91 | 7334.38 | 27065.8 | 1.1 | 4.11 | 24.783 | 108.414 | 1 | 1 | 1480 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 1868673.9273 | 162632.4637 | 2133.3277 | 24858.541 | 137773.9227 | 114396.2954 | 0.056389 | -883337.8697 | 883337.8697
C | Xist Rating 10100 | -56.48 | 832.093 | 150.306 | 35.7 | 2269.71 | 7370.35 | 26866.1 | 1.08 | 4.07 | 24.769 | 106.608 | 1 | 1 | 1490 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 1888609.803 | 164668.5265 | 2162.2539 | 25026.5041 | 139642.0224 | 112498.8727 | 0.05677 | -868686.4745 | 868686.4745
C | Xist Rating 10101 | -56.06 | 840.314 | 150.306 | 35.7 | 2269.83 | 7388.83 | 26669.5 | 1.06 | 4.03 | 24.725 | 104.862 | 1 | 1 | 1500 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 1907369.9266 | 166717.1691 | 2191.3748 | 25194.4672 | 141522.7018 | 110661.2015 | 0.057151 | -854496.4646 | 854496.4646
C | Xist Rating 10102 | -55.54 | 850.015 | 150.306 | 35.7 | 2270.98 | 7421.83 | 26438 | 1.04 | 3.99 | 24.715 | 102.801 | 1 | 1 | 1510 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 1930367.0647 | 168778.3914 | 2220.6906 | 25362.4304 | 143415.9611 | 108498.4298 | 0.057532 | -837796.1153 | 837796.1153
C | Xist Rating 10103 | -54.03 | 882.094 | 150.306 | 35.7 | 2263.37 | 7410.97 | 25680.2 | 1.06 | 3.84 | 24.734 | 96.056 | 1 | 1 | 1520 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 1996505.0968 | 170852.1936 | 2250.2011 | 25530.3935 | 145321.8001 | 101540.3301 | 0.057913 | -784067.5138 | 784067.5138
C | Xist Rating 10104 | -53.59 | 892.139 | 150.305 | 35.7 | 2260.25 | 7398.02 | 25467.5 | 1.03 | 3.8 | 24.64 | 94.302 | 1 | 1 | 1530 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2016457.1748 | 172938.5756 | 2279.9064 | 25698.3566 | 147240.219 | 99673.0269 | 0.058294 | -769648.6937 | 769648.6937
C | Xist Rating 10105 | -53.24 | 897.234 | 150.305 | 35.7 | 2265.72 | 7467.44 | 25362.1 | 1 | 3.78 | 24.617 | 93.46 | 1 | 1 | 1540 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2032881.0185 | 175037.5373 | 2309.8065 | 25866.3197 | 149171.2176 | 98757.3728 | 0.058675 | -762578.2549 | 762578.2549
C | Xist Rating 10106 | -52.43 | 913.252 | 150.305 | 35.7 | 2265.34 | 7497.97 | 25019.8 | 0.99 | 3.72 | 24.612 | 90.6 | 1 | 1 | 1550 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2068826.2857 | 177149.0789 | 2339.9013 | 26034.2828 | 151114.7961 | 95780.8544 | 0.059056 | -739594.3691 | 739594.3691
C | Xist Rating 10107 | -51.96 | 918.123 | 150.305 | 35.7 | 2276.17 | 7628.71 | 24919.2 | 0.98 | 3.7 | 24.671 | 89.79 | 1 | 1 | 1560 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2089804.0289 | 179273.2002 | 2370.191 | 26202.2459 | 153070.9543 | 94937.4255 | 0.059437 | -733081.6343 | 733081.6343
C | Xist Rating 10108 | -50.39 | 955.523 | 150.305 | 35.7 | 2259.26 | 7523.15 | 24160.9 | 0.97 | 3.56 | 24.623 | 83.636 | 1 | 1 | 1570 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2158774.893 | 181409.9014 | 2400.6755 | 26370.209 | 155039.6923 | 88536.7049 | 0.059818 | -683656.967 | 683656.967
C | Xist Rating 10109 | -49.9 | 963.772 | 150.305 | 35.7 | 2262.54 | 7577.25 | 24006.3 | 0.95 | 3.53 | 24.617 | 82.454 | 1 | 1 | 1580 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2180572.7009 | 183559.1823 | 2431.3547 | 26538.1722 | 157021.0102 | 87284.6247 | 0.0602 | -673988.7353 | 673988.7353
C | Xist Rating 10110 | -49.43 | 972.057 | 150.305 | 35.7 | 2265.16 | 7624.49 | 23853.9 | 0.93 | 3.5 | 24.605 | 81.302 | 1 | 1 | 1590 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2201864.6341 | 185721.0431 | 2462.2288 | 26706.1353 | 159014.9078 | 86062.8722 | 0.060581 | -664554.6866 | 664554.6866
C | Xist Rating 10111 | -48.76 | 983.33 | 150.305 | 35.7 | 2269.46 | 7698.68 | 23644.1 | 0.92 | 3.46 | 24.63 | 79.699 | 1 | 1 | 1600 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2231628.1018 | 187895.4836 | 2493.2976 | 26874.0984 | 161021.3852 | 84392.4193 | 0.060962 | -651655.892 | 651655.892
C | Xist Rating 10112 | -48.42 | 988.621 | 150.305 | 35.7 | 2272.14 | 7740.56 | 23555.8 | 0.9 | 3.45 | 24.604 | 79.078 | 1 | 1 | 1610 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2246285.3189 | 190082.5039 | 2524.5612 | 27042.0615 | 163040.4424 | 83720.4304 | 0.061343 | -646466.9714 | 646466.9714
C | Xist Rating 10113 | -46.59 | 1030.56 | 150.305 | 35.7 | 2258.38 | 7676.91 | 22803.9 | 0.9 | 3.31 | 24.629 | 73.413 | 1 | 1 | 1620 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2327396.0928 | 192282.104 | 2556.0196 | 27210.0246 | 165072.0794 | 77848.8965 | 0.061724 | -601128.543 | 601128.543
C | Xist Rating 10114 | -46.12 | 1035.5 | 150.305 | 35.7 | 2267.19 | 7790.57 | 22722.6 | 0.89 | 3.29 | 24.672 | 72.845 | 1 | 1 | 1630 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2347675.245 | 194494.284 | 2587.6728 | 27377.9877 | 167116.2962 | 77253.7664 | 0.062105 | -596533.1066 | 596533.1066
C | Xist Rating 10115 | -45.67 | 1043.93 | 150.305 | 35.7 | 2268.22 | 7821.17 | 22587.9 | 0.87 | 3.27 | 24.642 | 71.913 | 1 | 1 | 1640 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2367862.9046 | 196719.0437 | 2619.5208 | 27545.9509 | 169173.0928 | 76257.5359 | 0.062486 | -588840.4785 | 588840.4785
C | Xist Rating 10116 | -45.12 | 1055.56 | 150.305 | 35.7 | 2267 | 7832.45 | 22402.3 | 0.86 | 3.23 | 24.608 | 70.622 | 1 | 1 | 1650 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2392954.52 | 198956.3832 | 2651.5635 | 27713.914 | 171242.4692 | 74906.0562 | 0.062867 | -578404.7104 | 578404.7104
C | Xist Rating 10117 | -44.45 | 1066.95 | 150.305 | 35.7 | 2270.64 | 7902.23 | 22220.1 | 0.85 | 3.2 | 24.621 | 69.353 | 1 | 1 | 1660 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2422659.348 | 201206.3025 | 2683.8011 | 27881.8771 | 173324.4254 | 73580.1995 | 0.063248 | -568166.7969 | 568166.7969
C | Xist Rating 10118 | -42.82 | 1104.39 | 150.305 | 35.7 | 2258.41 | 7841.66 | 21632.3 | 0.84 | 3.09 | 24.639 | 65.268 | 1 | 1 | 1670 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2494165.4199 | 203468.8016 | 2716.2334 | 28049.8402 | 175418.9614 | 69330.0156 | 0.063629 | -535348.0031 | 535348.0031
C | Xist Rating 10119 | -42.42 | 1109.45 | 150.306 | 35.7 | 2264.42 | 7925.78 | 21559.9 | 0.83 | 3.08 | 24.655 | 64.804 | 1 | 1 | 1680 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2512260.769 | 205743.8805 | 2748.8606 | 28217.8033 | 177526.0772 | 68839.8751 | 0.06401 | -531563.2683 | 531563.2683
C | Xist Rating 10120 | -41.76 | 1124.33 | 150.305 | 35.7 | 2260.68 | 7913.56 | 21345.5 | 0.82 | 3.04 | 24.615 | 63.4 | 1 | 1 | 1690 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2541750.3444 | 208031.5392 | 2781.6825 | 28385.7664 | 179645.7728 | 67369.8343 | 0.064391 | -520212.0029 | 520212.0029
C | Xist Rating 10121 | -41.17 | 1134.19 | 150.305 | 35.7 | 2264.56 | 7983.98 | 21205.4 | 0.8 | 3.02 | 24.627 | 62.494 | 1 | 1 | 1700 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2568441.3064 | 210331.7777 | 2814.6992 | 28553.7295 | 181778.0481 | 66401.2196 | 0.064772 | -512732.6171 | 512732.6171
C | Xist Rating 10122 | -40.59 | 1145.77 | 150.305 | 35.7 | 2264.56 | 8010.49 | 21044.4 | 0.79 | 2.99 | 24.615 | 61.464 | 1 | 1 | 1710 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2594664.9112 | 212644.596 | 2847.9107 | 28721.6927 | 183922.9033 | 65320.7942 | 0.065153 | -504389.8579 | 504389.8579
C | Xist Rating 10123 | -39.07 | 1180.17 | 150.306 | 35.7 | 2255.31 | 7975.94 | 20566.8 | 0.79 | 2.9 | 24.64 | 58.384 | 1 | 1 | 1720 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2661649.2027 | 214969.994 | 2881.317 | 28889.6558 | 186080.3383 | 62132.4583 | 0.065534 | -479770.3732 | 479770.3732
C | Xist Rating 10124 | -38.35 | 1194.91 | 150.306 | 35.7 | 2254.2 | 7995.71 | 20374 | 0.78 | 2.87 | 24.63 | 57.193 | 1 | 1 | 1730 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2693566.122 | 217307.9719 | 2914.9181 | 29057.6189 | 188250.353 | 60884.6197 | 0.065915 | -470134.8944 | 470134.8944
C | Xist Rating 10125 | -37.93 | 1201.66 | 150.306 | 35.7 | 2257.41 | 8051.45 | 20289.6 | 0.77 | 2.85 | 24.633 | 56.694 | 1 | 1 | 1740 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2712639.3006 | 219658.5296 | 2948.714 | 29225.582 | 190432.9476 | 60355.9904 | 0.066296 | -466052.9596 | 466052.9596
C | Xist Rating 10126 | -37.33 | 1215 | 150.306 | 35.7 | 2255.03 | 8051.6 | 20123.2 | 0.75 | 2.82 | 24.608 | 55.697 | 1 | 1 | 1750 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2739861.45 | 222021.6671 | 2982.7046 | 29393.5451 | 192628.1219 | 59288.993 | 0.066677 | -457813.888 | 457813.888
C | Xist Rating 10127 | -36.89 | 1224.97 | 150.306 | 35.7 | 2252.9 | 8047.15 | 20000.3 | 0.74 | 2.8 | 24.6 | 54.969 | 1 | 1 | 1760 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2759734.913 | 224397.3843 | 3016.8901 | 29561.5082 | 194835.8761 | 58521.3583 | 0.067058 | -451886.4168 | 451886.4168
C | Xist Rating 10128 | -35.11 | 1265.75 | 150.306 | 35.7 | 2242.39 | 8008.77 | 19497 | 0.74 | 2.71 | 24.635 | 51.941 | 1 | 1 | 1770 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2838305.1425 | 226785.6814 | 3051.2703 | 29729.4713 | 197056.21 | 55386.9999 | 0.067439 | -427683.7318 | 427683.7318
C | Xist Rating 10129 | -34.59 | 1275.83 | 150.306 | 35.7 | 2243.45 | 8044.8 | 19382.4 | 0.73 | 2.69 | 24.624 | 51.297 | 1 | 1 | 1780 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2862260.8135 | 229186.5582 | 3085.8453 | 29897.4345 | 199289.1238 | 54706.082 | 0.06782 | -422425.864 | 422425.864
C | Xist Rating 10130 | -34.23 | 1281.15 | 150.306 | 35.7 | 2246.99 | 8101.98 | 19325.7 | 0.72 | 2.68 | 24.619 | 50.998 | 1 | 1 | 1790 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2878731.2385 | 231600.0149 | 3120.6151 | 30065.3976 | 201534.6173 | 54383.5822 | 0.068201 | -419935.6064 | 419935.6064
C | Xist Rating 10131 | -33.36 | 1299.18 | 150.307 | 35.7 | 2245.24 | 8121 | 19121.3 | 0.71 | 2.65 | 24.612 | 49.838 | 1 | 1 | 1800 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2916970.9032 | 234026.0513 | 3155.5797 | 30233.3607 | 203792.6906 | 53166.6048 | 0.068582 | -410538.4297 | 410538.4297
C | Xist Rating 10132 | -32.8 | 1309.14 | 150.307 | 35.7 | 2247.28 | 8170.7 | 19012.2 | 0.7 | 2.63 | 24.615 | 49.234 | 1 | 1 | 1810 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 2942004.1392 | 236464.6676 | 3190.7391 | 30401.3238 | 206063.3438 | 52527.3867 | 0.068963 | -405602.5567 | 405602.5567
C | Xist Rating 10133 | -31.36 | 1350.18 | 150.307 | 35.6 | 2228.16 | 8016.54 | 18562.7 | 0.7 | 2.55 | 24.957 | 46.704 | 1 | 1 | 1820 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3008417.0688 | 238915.8636 | 3226.0933 | 30569.2869 | 208346.5767 | 49927.2397 | 0.069344 | -385524.9105 | 385524.9105
C | Xist Rating 10134 | -31.38 | 1343.68 | 150.307 | 35.7 | 2236.55 | 8111.04 | 18631.8 | 0.69 | 2.56 | 25.023 | 47.099 | 1 | 1 | 1830 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3005207.504 | 241379.6394 | 3261.6423 | 30737.25 | 210642.3894 | 50328.541 | 0.069725 | -388623.6528 | 388623.6528
C | Xist Rating 10135 | -30.85 | 1351.89 | 150.307 | 35.6 | 2244.25 | 8232.78 | 18544.9 | 0.69 | 2.55 | 25.017 | 46.634 | 1 | 1 | 1840 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3033979.1325 | 243855.9951 | 3297.386 | 30905.2131 | 212950.7819 | 49853.0371 | 0.070106 | -384951.938 | 384951.938
C | Xist Rating 10136 | -30.26 | 1365.34 | 150.307 | 35.6 | 2240.72 | 8216.3 | 18408.9 | 0.68 | 2.52 | 25.004 | 45.919 | 1 | 1 | 1850 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3059344.6448 | 246344.9305 | 3333.3246 | 31073.1763 | 215271.7542 | 49096.7697 | 0.070487 | -379112.2415 | 379112.2415
C | Xist Rating 10137 | -29.59 | 1380.43 | 150.307 | 35.6 | 2237.26 | 8204.4 | 18258.8 | 0.67 | 2.5 | 24.989 | 45.134 | 1 | 1 | 1860 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3088380.8218 | 248846.4457 | 3369.4579 | 31241.1394 | 217605.3063 | 48267.4851 | 0.070868 | -372708.726 | 372708.726
C | Xist Rating 10138 | -27.92 | 1418.15 | 150.307 | 35.6 | 2230.29 | 8200.52 | 17879.1 | 0.67 | 2.43 | 25.04 | 43.117 | 1 | 1 | 1870 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3162885.7635 | 251360.5407 | 3405.7861 | 31409.1025 | 219951.4382 | 46183.2029 | 0.071249 | -356614.4507 | 356614.4507
C | Xist Rating 10139 | -27.19 | 1433.23 | 150.307 | 35.6 | 2228.93 | 8216.38 | 17738.6 | 0.65 | 2.41 | 25.042 | 42.411 | 1 | 1 | 1880 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3194569.3439 | 253887.2155 | 3442.309 | 31577.0656 | 222310.1499 | 45415.4501 | 0.07163 | -350686.0672 | 350686.0672
C | Xist Rating 10140 | -26.59 | 1443.23 | 150.307 | 35.6 | 2232.17 | 8283.78 | 17646.2 | 0.65 | 2.39 | 25.062 | 41.953 | 1 | 1 | 1890 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3221534.7091 | 256426.4702 | 3479.0267 | 31745.0287 | 224681.4414 | 44948.2154 | 0.072011 | -347078.2048 | 347078.2048
C | Xist Rating 10141 | -26.14 | 1453.69 | 150.307 | 35.7 | 2229.6 | 8271.66 | 17555 | 0.63 | 2.38 | 25.046 | 41.517 | 1 | 1 | 1900 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3241147.224 | 258978.3046 | 3515.9392 | 31912.9918 | 227065.3127 | 44459.1846 | 0.072392 | -343302.039 | 343302.039
C | Xist Rating 10142 | -25.66 | 1463.88 | 150.307 | 35.7 | 2228.45 | 8278.98 | 17464.8 | 0.62 | 2.36 | 25.057 | 41.08 | 1 | 1 | 1910 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3262183.386 | 261542.7188 | 3553.0464 | 32080.955 | 229461.7638 | 43991.5744 | 0.072773 | -339691.277 | 339691.277
C | Xist Rating 10143 | -23.65 | 1509.67 | 150.307 | 35.7 | 2219.73 | 8267.94 | 17050.1 | 0.62 | 2.29 | 25.111 | 39.007 | 1 | 1 | 1920 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3351059.7891 | 264119.7128 | 3590.3485 | 32248.9181 | 231870.7947 | 41848.6123 | 0.073154 | -323143.8913 | 323143.8913
C | Xist Rating 10144 | -22.96 | 1524.82 | 150.307 | 35.7 | 2217.7 | 8274.27 | 16923.8 | 0.61 | 2.27 | 25.11 | 38.414 | 1 | 1 | 1930 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3381593.314 | 266709.2865 | 3627.8454 | 32416.8812 | 234292.4054 | 41217.9847 | 0.073535 | -318274.3522 | 318274.3522
C | Xist Rating 10145 | -22.53 | 1529.78 | 150.307 | 35.7 | 2223.42 | 8366.2 | 16881.9 | 0.61 | 2.26 | 25.149 | 38.224 | 1 | 1 | 1940 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3401343.4476 | 269311.4401 | 3665.537 | 32584.8443 | 236726.5958 | 41029.6046 | 0.073916 | -316819.7311 | 316819.7311
C | Xist Rating 10146 | -22.05 | 1543.8 | 150.307 | 35.7 | 2216.98 | 8306.35 | 16772.2 | 0.59 | 2.24 | 25.123 | 37.729 | 1 | 1 | 1950 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3422573.724 | 271926.1735 | 3703.4235 | 32752.8074 | 239173.3661 | 40477.119 | 0.074297 | -312553.584 | 312553.584
C | Xist Rating 10147 | -21.3 | 1560.47 | 150.307 | 35.7 | 2214.59 | 8311.27 | 16637 | 0.58 | 2.22 | 25.145 | 37.103 | 1 | 1 | 1960 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3455801.2573 | 274553.4867 | 3741.5047 | 32920.7705 | 241632.7162 | 39812.7121 | 0.074678 | -307423.2097 | 307423.2097
C | Xist Rating 10148 | -19.5 | 1601.63 | 150.307 | 35.7 | 2207.34 | 8306.65 | 16303.1 | 0.59 | 2.16 | 25.223 | 35.541 | 1 | 1 | 1970 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3535341.9642 | 277193.3797 | 3779.7807 | 33088.7336 | 244104.646 | 38223.3828 | 0.075059 | -295150.8301 | 295150.8301
C | Xist Rating 10149 | -18.92 | 1613.44 | 150.307 | 35.7 | 2207.45 | 8335.01 | 16214 | 0.58 | 2.15 | 25.259 | 35.15 | 1 | 1 | 1980 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3561588.128 | 279845.8524 | 3818.2515 | 33256.6968 | 246589.1557 | 37803.4676 | 0.07544 | -291908.356 | 291908.356
C | Xist Rating 10150 | -18.3 | 1628.78 | 150.307 | 35.7 | 2203.6 | 8314.54 | 16101.3 | 0.57 | 2.13 | 25.277 | 34.659 | 1 | 1 | 1990 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3589179.608 | 282510.905 | 3856.9171 | 33424.6599 | 249086.2451 | 37278.5157 | 0.075821 | -287854.8165 | 287854.8165
C | Xist Rating 10151 | -17.74 | 1640.71 | 150.307 | 35.7 | 2202.96 | 8332.2 | 16014.7 | 0.56 | 2.12 | 25.279 | 34.287 | 1 | 1 | 2000 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3614418.5016 | 285188.5374 | 3895.7775 | 33592.623 | 251595.9144 | 36876.0923 | 0.076202 | -284747.4099 | 284747.4099
C | Xist Rating 10152 | -17.28 | 1649.4 | 150.307 | 35.7 | 2203.83 | 8363.88 | 15953.7 | 0.55 | 2.11 | 25.29 | 34.032 | 1 | 1 | 2010 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3634997.202 | 287878.7495 | 3934.8326 | 33760.5861 | 254118.1634 | 36595.39 | 0.076583 | -282579.9013 | 282579.9013
C | Xist Rating 10153 | -15.35 | 1695.64 | 150.307 | 35.7 | 2194.3 | 8335.49 | 15614.7 | 0.55 | 2.05 | 25.327 | 32.537 | 1 | 1 | 2020 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3720742.852 | 290581.5415 | 3974.0826 | 33928.5492 | 256652.9923 | 35050.9124 | 0.076964 | -270653.8544 | 270653.8544
C | Xist Rating 10154 | -14.52 | 1712.25 | 150.307 | 35.7 | 2194.77 | 8380.67 | 15499.5 | 0.55 | 2.03 | 25.334 | 32.053 | 1 | 1 | 2030 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3757994.9325 | 293296.9132 | 4013.5273 | 34096.5123 | 259200.4009 | 34554.8735 | 0.077345 | -266823.5734 | 266823.5734
C | Xist Rating 10155 | -14.11 | 1722.92 | 150.307 | 35.7 | 2191.78 | 8360.01 | 15431.6 | 0.53 | 2.02 | 25.326 | 31.784 | 1 | 1 | 2040 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3776261.5976 | 296024.8648 | 4053.1669 | 34264.4754 | 261760.3893 | 34235.0434 | 0.077726 | -264353.9307 | 264353.9307
C | Xist Rating 10156 | -13.46 | 1732.76 | 150.308 | 35.7 | 2196.09 | 8446.27 | 15364.3 | 0.53 | 2.01 | 25.36 | 31.506 | 1 | 1 | 2050 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3805296.9084 | 298765.3961 | 4093.0012 | 34432.4386 | 264332.9575 | 33954.0135 | 0.078107 | -262183.8917 | 262183.8917
C | Xist Rating 10157 | -12.87 | 1748.5 | 150.307 | 35.7 | 2191.49 | 8413.2 | 15264.3 | 0.52 | 1.99 | 25.339 | 31.108 | 1 | 1 | 2060 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3831820.265 | 301518.5072 | 4133.0303 | 34600.4017 | 266918.1056 | 33522.2904 | 0.078488 | -258850.2409 | 258850.2409
C | Xist Rating 10158 | -10.86 | 1798.09 | 150.308 | 35.7 | 2180.71 | 8370.93 | 14936.2 | 0.52 | 1.94 | 25.373 | 29.745 | 1 | 1 | 2070 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3921112.8439 | 304284.1982 | 4173.2542 | 34768.3648 | 269515.8334 | 32114.3638 | 0.078869 | -247978.6045 | 247978.6045
C | Xist Rating 10159 | -10.33 | 1808.56 | 150.308 | 35.7 | 2181.43 | 8404.36 | 14873.5 | 0.51 | 1.93 | 25.379 | 29.507 | 1 | 1 | 2080 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3945247.0408 | 307062.4689 | 4213.6729 | 34936.3279 | 272126.141 | 31849.744 | 0.07925 | -245935.2808 | 245935.2808
C | Xist Rating 10160 | -9.7 | 1822.2 | 150.308 | 35.7 | 2180.66 | 8423.53 | 14790.9 | 0.5 | 1.91 | 25.391 | 29.188 | 1 | 1 | 2090 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 3973598.652 | 309853.3194 | 4254.2864 | 35104.291 | 274749.0284 | 31501.051 | 0.079631 | -243242.7655 | 243242.7655
C | Xist Rating 10161 | -9.09 | 1835.86 | 150.308 | 35.7 | 2179.59 | 8438.19 | 14709.2 | 0.5 | 1.9 | 25.395 | 28.875 | 1 | 1 | 2100 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4001422.0974 | 312656.7497 | 4295.0947 | 35272.2541 | 277384.4956 | 31181.8799 | 0.080012 | -240778.2114 | 240778.2114
C | Xist Rating 10162 | -8.55 | 1847.89 | 150.308 | 35.7 | 2178.57 | 8449.73 | 14638.7 | 0.49 | 1.89 | 25.399 | 28.609 | 1 | 1 | 2110 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4025757.7173 | 315472.7598 | 4336.0977 | 35440.2173 | 280032.5426 | 30887.4977 | 0.080393 | -238505.0702 | 238505.0702
C | Xist Rating 10163 | -6.68 | 1894.57 | 150.308 | 35.7 | 2168.89 | 8412.92 | 14358.9 | 0.49 | 1.84 | 25.433 | 27.514 | 1 | 1 | 2120 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4109113.9273 | 318301.3498 | 4377.2956 | 35608.1804 | 282693.1694 | 29757.5038 | 0.080774 | -229779.5565 | 229779.5565
C | Xist Rating 10164 | -5.97 | 1911.53 | 150.308 | 35.7 | 2166.32 | 8412.14 | 14263.6 | 0.48 | 1.83 | 25.43 | 27.16 | 1 | 1 | 2130 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4140985.6696 | 321142.5195 | 4418.6882 | 35776.1435 | 285366.376 | 29371.0415 | 0.081155 | -226795.3968 | 226795.3968
C | Xist Rating 10165 | -5.38 | 1928.51 | 150.308 | 35.7 | 2161.25 | 8373.57 | 14169.7 | 0.48 | 1.81 | 25.426 | 26.815 | 1 | 1 | 2140 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4167992.2375 | 323996.269 | 4460.2756 | 35944.1066 | 288052.1624 | 29018.0468 | 0.081536 | -224069.6656 | 224069.6656
C | Xist Rating 10166 | -4.97 | 1937.34 | 150.308 | 35.7 | 2161.22 | 8391.84 | 14123.3 | 0.47 | 1.8 | 25.429 | 26.653 | 1 | 1 | 2150 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4187017.9548 | 326862.5983 | 4502.0578 | 36112.0697 | 290750.5285 | 28830.9128 | 0.081917 | -222624.6662 | 222624.6662
C | Xist Rating 10167 | -4.41 | 1949.31 | 150.308 | 35.7 | 2160.99 | 8414.67 | 14058.9 | 0.47 | 1.79 | 25.438 | 26.422 | 1 | 1 | 2160 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4212439.4169 | 329741.5074 | 4544.0348 | 36280.0328 | 293461.4745 | 28596.7865 | 0.082298 | -220816.8049 | 220816.8049
C | Xist Rating 10168 | -2.45 | 1999.55 | 150.308 | 35.7 | 2150.42 | 8368.57 | 13785.9 | 0.46 | 1.75 | 25.466 | 25.412 | 1 | 1 | 2170 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4299872.311 | 332632.9962 | 4586.2066 | 36447.9959 | 296185.0003 | 27529.7717 | 0.082679 | -212577.5993 | 212577.5993
C | Xist Rating 10169 | -1.7 | 2016.29 | 150.308 | 35.7 | 2149.34 | 8389.38 | 13699 | 0.46 | 1.74 | 25.48 | 25.104 | 1 | 1 | 2180 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4333692.7486 | 335537.0649 | 4628.5732 | 36615.9591 | 298921.1059 | 27215.7944 | 0.08306 | -210153.1499 | 210153.1499
C | Xist Rating 10170 | -1.19 | 2028.49 | 150.308 | 35.7 | 2147.96 | 8394.29 | 13638.9 | 0.45 | 1.73 | 25.478 | 24.9 | 1 | 1 | 2190 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4357115.3804 | 338453.7134 | 4671.1346 | 36783.9222 | 301669.7912 | 26984.0934 | 0.083441 | -208364.0169 | 208364.0169
C | Xist Rating 10171 | -0.72 | 2041.1 | 150.308 | 35.7 | 2145.31 | 8379.93 | 13579.4 | 0.45 | 1.72 | 25.463 | 24.704 | 1 | 1 | 2200 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4378792.241 | 341382.9417 | 4713.8907 | 36951.8853 | 304431.0564 | 26785.0213 | 0.083822 | -206826.8346 | 206826.8346
C | Xist Rating 10172 | -0.0293 | 2058.09 | 150.308 | 35.7 | 2142.91 | 8380.33 | 13495.4 | 0.44 | 1.7 | 25.465 | 24.415 | 1 | 1 | 2210 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4410301.6419 | 344324.7497 | 4756.8417 | 37119.8484 | 307204.9013 | 26464.8943 | 0.084203 | -204354.8989 | 204354.8989
C | Xist Rating 10173 | 1.89 | 2108.19 | 150.308 | 35.7 | 2132.53 | 8333.64 | 13246.2 | 0.44 | 1.66 | 25.5 | 23.54 | 1 | 1 | 2220 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4495778.4207 | 347279.1376 | 4799.9874 | 37287.8115 | 309991.3261 | 25562.7631 | 0.084584 | -197388.8807 | 197388.8807
C | Xist Rating 10174 | 2.48 | 2121.82 | 150.308 | 35.7 | 2131.58 | 8348.25 | 13182.6 | 0.44 | 1.65 | 25.506 | 23.329 | 1 | 1 | 2230 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4522829.0756 | 350246.1053 | 4843.3279 | 37455.7746 | 312790.3306 | 25348.9331 | 0.084965 | -195737.7425 | 195737.7425
C | Xist Rating 10175 | 3.05 | 2137.53 | 150.308 | 35.7 | 2128.17 | 8328.76 | 13111.8 | 0.43 | 1.64 | 25.499 | 23.1 | 1 | 1 | 2240 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4549027.2201 | 353225.6527 | 4886.8633 | 37623.7377 | 315601.915 | 25090.2354 | 0.085346 | -193740.1473 | 193740.1473
C | Xist Rating 10176 | 3.69 | 2154.82 | 150.308 | 35.7 | 2124.59 | 8310.1 | 13034.1 | 0.43 | 1.63 | 25.495 | 22.848 | 1 | 1 | 2250 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4578109.0238 | 356217.78 | 4930.5934 | 37791.7009 | 318426.0791 | 24833.2752 | 0.085727 | -191755.9684 | 191755.9684
C | Xist Rating 10177 | 4.1 | 2163.62 | 150.308 | 35.7 | 2124.79 | 8331.25 | 12995.7 | 0.42 | 1.62 | 25.502 | 22.728 | 1 | 1 | 2260 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4597238.1398 | 359222.487 | 4974.5182 | 37959.664 | 321262.8231 | 24688.0399 | 0.086108 | -190634.4999 | 190634.4999
C | Xist Rating 10178 | 6.06 | 2217.38 | 150.308 | 35.7 | 2112.77 | 8263.43 | 12752 | 0.42 | 1.59 | 25.523 | 21.917 | 1 | 1 | 2270 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4684813.9426 | 362239.7739 | 5018.6379 | 38127.6271 | 324112.1468 | 23851.5162 | 0.086489 | -184175.0859 | 184175.0859
C | Xist Rating 10179 | 6.65 | 2233.04 | 150.308 | 35.7 | 2110.04 | 8253.42 | 12686.3 | 0.41 | 1.58 | 25.519 | 21.713 | 1 | 1 | 2280 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4711803.7216 | 365269.6405 | 5062.9524 | 38295.5902 | 326974.0503 | 23618.2154 | 0.08687 | -182373.599 | 182373.599
C | Xist Rating 10180 | 7.39 | 2251.72 | 150.308 | 35.7 | 2107.5 | 8253.42 | 12607 | 0.41 | 1.56 | 25.52 | 21.464 | 1 | 1 | 2290 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4745499.9 | 368312.087 | 5107.4617 | 38463.5533 | 329848.5336 | 23364.3613 | 0.087251 | -180413.4048 | 180413.4048
C | Xist Rating 10181 | 7.87 | 2264.09 | 150.308 | 35.7 | 2105.92 | 8253.79 | 12557.2 | 0.41 | 1.56 | 25.522 | 21.314 | 1 | 1 | 2300 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4767992.4128 | 371367.1132 | 5152.1657 | 38631.5164 | 332735.5968 | 23213.3612 | 0.087632 | -179247.4218 | 179247.4218
| Xist Rating 10182 | 8.33 | 2276.72 | 150.308 | 35.7 | 2103.57 | 8242.38 | 12507.8 | 0.4 | 1.55 | 25.523 | 21.169 | 1 | 1 | 2310 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4789239.8904 | 374434.7192 | 5197.0645 | 38799.4796 | 335635.2397 | 23041.084 | 0.088013 | -177917.1435 | 177917.1435
C | Xist Rating 10183 | 10.37 | 2331.95 | 150.308 | 35.7 | 2092.93 | 8195.68 | 12277.3 | 0.4 | 1.51 | 25.542 | 20.437 | 1 | 1 | 2320 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4880608.1135 | 377514.905 | 5242.1582 | 38967.4427 | 338547.4624 | 22286.2698 | 0.088394 | -172088.6679 | 172088.6679
| Xist Rating 10184 | 10.97 | 2347.64 | 150.308 | 35.7 | 2090.63 | 8191.48 | 12217.1 | 0.4 | 1.5 | 25.547 | 20.26 | 1 | 1 | 2330 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4908046.6132 | 380607.6707 | 5287.4466 | 39135.4058 | 341472.2649 | 22107.2441 | 0.088775 | -170706.2789 | 170706.2789
| Xist Rating 10185 | 11.58 | 2363.3 | 150.308 | 35.7 | 2088.76 | 8193.65 | 12157.5 | 0.39 | 1.49 | 25.549 | 20.085 | 1 | 1 | 2340 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4936366.508 | 383713.0161 | 5332.9298 | 39303.3689 | 344409.6472 | 21903.3731 | 0.089156 | -169132.0409 | 169132.0409
| Xist Rating 10186 | 12.21 | 2377.42 | 150.308 | 35.7 | 2088.42 | 8216.03 | 12105 | 0.39 | 1.49 | 25.56 | 19.935 | 1 | 1 | 2350 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4965051.4764 | 386830.9413 | 5378.6078 | 39471.332 | 347359.6093 | 21752.5166 | 0.089537 | -167967.1671 | 167967.1671
| Xist Rating 10187 | 12.81 | 2394.77 | 150.308 | 35.7 | 2084.89 | 8195.97 | 12040.2 | 0.38 | 1.47 | 25.549 | 19.746 | 1 | 1 | 2360 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 4992832.0253 | 389961.4463 | 5424.4805 | 39639.2951 | 350322.1512 | 21533.2275 | 0.089918 | -166273.8753 | 166273.8753
| Xist Rating 10188 | 14.64 | 2445.31 | 150.308 | 35.7 | 2075.39 | 8153.2 | 11847.2 | 0.38 | 1.45 | 25.576 | 19.164 | 1 | 1 | 2370 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5074971.9209 | 393104.5311 | 5470.5481 | 39807.2582 | 353297.2729 | 20934.2633 | 0.090299 | -161648.832 | 161648.832
| Xist Rating 10189 | 15.14 | 2461.21 | 150.308 | 35.7 | 2071.13 | 8117.96 | 11791.5 | 0.38 | 1.44 | 25.572 | 19.01 | 1 | 1 | 2380 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5097485.8673 | 396260.1957 | 5516.8105 | 39975.2214 | 356284.9743 | 20778.5288 | 0.09068 | -160446.2918 | 160446.2918
| Xist Rating 10190 | 15.78 | 2478.11 | 150.308 | 35.7 | 2068.97 | 8118.15 | 11730.4 | 0.37 | 1.43 | 25.571 | 18.835 | 1 | 1 | 2390 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5127135.2467 | 399428.4401 | 5563.2676 | 40143.1845 | 359285.2556 | 20573.7122 | 0.091061 | -158864.7523 | 158864.7523
C | Xist Rating 10191 | 28.18 | 2839.16 | 150.308 | 35.7 | 1999.64 | 7761.12 | 10538.4 | 0.41 | 1.25 | 25.523 | 15.518 | 1 | 1 | 2400 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5677297.9024 | 402609.2643 | 5609.9196 | 40311.1476 | 362298.1167 | 17241.1731 | 0.091442 | -133131.7682 | 133131.7682
C | Xist Rating 10192 | 28.26 | 2840.61 | 150.308 | 35.7 | 2000.33 | 7771.65 | 10538.4 | 0.41 | 1.25 | 25.517 | 15.529 | 1 | 1 | 2410 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5682157.4013 | 405802.6683 | 5656.7663 | 40479.1107 | 365323.5576 | 17257.0214 | 0.091823 | -133254.1452 | 133254.1452
C | Xist Rating 10193 | 28.34 | 2842.01 | 150.308 | 35.7 | 2001 | 7781.65 | 10538.4 | 0.4 | 1.25 | 25.563 | 15.54 | 1 | 1 | 2420 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5686862.01 | 409008.652 | 5703.8078 | 40647.0738 | 368361.5782 | 17247.4507 | 0.092204 | -133180.2423 | 133180.2423
C | Xist Rating 10194 | 28.46 | 2843.37 | 150.308 | 35.7 | 2002.28 | 7801.11 | 10538.5 | 0.39 | 1.25 | 25.564 | 15.551 | 1 | 1 | 2430 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5693222.8836 | 412227.2156 | 5751.0441 | 40815.0369 | 371412.1787 | 17235.6558 | 0.092585 | -133089.1657 | 133089.1657
C | Xist Rating 10195 | 28.57 | 2844.74 | 150.308 | 35.7 | 2003.47 | 7819.2 | 10538.4 | 0.38 | 1.25 | 25.574 | 15.562 | 1 | 1 | 2440 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5699351.2478 | 415458.359 | 5798.4752 | 40983 | 374475.359 | 17224.004 | 0.092966 | -132999.1936 | 132999.1936
C | Xist Rating 10196 | 28.58 | 2846.07 | 150.308 | 35.7 | 2002.99 | 7811.83 | 10538.5 | 0.38 | 1.25 | 25.568 | 15.573 | 1 | 1 | 2450 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5700649.7493 | 418702.0822 | 5846.1011 | 41150.9632 | 377551.119 | 17239.5332 | 0.093347 | -133119.106 | 133119.106
C | Xist Rating 10197 | 28.57 | 2847.54 | 150.308 | 35.7 | 2002.25 | 7800.61 | 10538.5 | 0.37 | 1.25 | 25.561 | 15.584 | 1 | 1 | 2460 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5701486.965 | 421958.3851 | 5893.9217 | 41318.9263 | 380639.4589 | 17226.8327 | 0.093728 | -133021.036 | 133021.036
C | Xist Rating 10198 | 28.57 | 2848.89 | 150.308 | 35.7 | 2001.78 | 7793.39 | 10538.5 | 0.37 | 1.25 | 25.602 | 15.595 | 1 | 1 | 2470 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5702851.0242 | 425227.2679 | 5941.9372 | 41486.8894 | 383740.3785 | 17244.1751 | 0.094109 | -133154.9493 | 133154.9493
C | Xist Rating 10199 | 28.58 | 2850.24 | 150.308 | 35.7 | 2001.34 | 7786.85 | 10538.5 | 0.36 | 1.25 | 25.595 | 15.606 | 1 | 1 | 2480 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5704299.3216 | 428508.7304 | 5990.1474 | 41654.8525 | 386853.8779 | 17231.1041 | 0.09449 | -133054.0183 | 133054.0183
C | Xist Rating 10200 | 28.63 | 2851.64 | 150.308 | 35.7 | 2001.34 | 7786.84 | 10538.5 | 0.35 | 1.25 | 25.585 | 15.616 | 1 | 1 | 2490 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5707101.1976 | 431802.7728 | 6038.5525 | 41822.8156 | 389979.9572 | 17216.6612 | 0.094871 | -132942.4942 | 132942.4942
C | Xist Rating 10201 | 28.65 | 2852.62 | 150.308 | 35.7 | 2001.89 | 7795.19 | 10538.4 | 0.35 | 1.25 | 25.578 | 15.625 | 1 | 1 | 2500 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5710631.4518 | 435109.3949 | 6087.1523 | 41990.7787 | 393118.6162 | 17229.7471 | 0.095252 | -133043.5399 | 133043.5399
C | Xist Rating 10202 | 28.61 | 2854.47 | 150.308 | 35.7 | 2000.6 | 7775.76 | 10538.4 | 0.34 | 1.25 | 25.566 | 15.638 | 1 | 1 | 2510 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 37 | E | Rod | 5710652.682 | 438428.5969 | 6135.9469 | 42158.7419 | 396269.855 | 17218.0236 | 0.095633 | -132953.0141 | 132953.0141
C | Xist Rating 10203 | 28.58 | 2855.93 | 150.308 | 35.7 | 1999.51 | 7759.22 | 10538.4 | 0.34 | 1.25 | 25.601 | 15.649 | 1 | 1 | 2520 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5710460.5943 | 441760.3786 | 6184.9363 | 42326.705 | 399433.6737 | 17234.6876 | 0.096014 | -133081.6894 | 133081.6894
C | Xist Rating 10204 | 28.56 | 2857.26 | 150.308 | 35.7 | 1998.64 | 7746.11 | 10538.4 | 0.33 | 1.25 | 25.598 | 15.659 | 1 | 1 | 2530 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5710634.1264 | 445104.7402 | 6234.1205 | 42494.6681 | 402610.0721 | 17219.8289 | 0.096395 | -132966.954 | 132966.954
C | Xist Rating 10205 | 28.62 | 2858.41 | 150.308 | 35.7 | 1999.19 | 7754.48 | 10538.4 | 0.33 | 1.25 | 25.591 | 15.668 | 1 | 1 | 2540 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5714504.6879 | 448461.6815 | 6283.4995 | 42662.6312 | 405799.0503 | 17232.6988 | 0.096776 | -133066.3325 | 133066.3325
C | Xist Rating 10206 | 28.61 | 2859.96 | 150.308 | 35.7 | 1998.42 | 7742.85 | 10538.4 | 0.32 | 1.25 | 25.582 | 15.679 | 1 | 1 | 2550 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5715401.2632 | 451831.2026 | 6333.0732 | 42830.5943 | 409000.6083 | 17218.3273 | 0.097157 | -132955.3596 | 132955.3596
C | Xist Rating 10207 | 28.63 | 2861.41 | 150.308 | 35.7 | 1998.23 | 7740.02 | 10538.4 | 0.32 | 1.25 | 25.597 | 15.69 | 1 | 1 | 2560 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5717755.3043 | 455213.3035 | 6382.8418 | 42998.5574 | 412214.7461 | 17233.9711 | 0.097538 | -133076.1564 | 133076.1564
C | Xist Rating 10208 | 28.63 | 2862.8 | 150.308 | 35.7 | 1997.75 | 7732.76 | 10538.4 | 0.31 | 1.25 | 25.599 | 15.7 | 1 | 1 | 2570 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5719158.7 | 458607.9842 | 6432.8051 | 43166.5205 | 415441.4637 | 17218.6115 | 0.097919 | -132957.5539 | 132957.5539
C | Xist Rating 10209 | 28.63 | 2864.16 | 150.308 | 35.7 | 1997.35 | 7726.8 | 10538.4 | 0.31 | 1.25 | 25.633 | 15.71 | 1 | 1 | 2580 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5720729.976 | 462015.2448 | 6482.9633 | 43334.4837 | 418680.7611 | 17233.7726 | 0.0983 | -133074.6236 | 133074.6236
C | Xist Rating 10210 | 28.64 | 2865.52 | 150.308 | 35.7 | 1997.04 | 7722.19 | 10538.3 | 0.3 | 1.25 | 25.63 | 15.721 | 1 | 1 | 2590 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5722558.0608 | 465435.0851 | 6533.3162 | 43502.4468 | 421932.6383 | 17218.8946 | 0.098681 | -132959.7398 | 132959.7398
C | Xist Rating 10211 | 28.68 | 2866.7 | 150.308 | 35.7 | 1997.21 | 7724.77 | 10538.3 | 0.3 | 1.25 | 25.631 | 15.73 | 1 | 1 | 2600 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5725401.907 | 468867.5052 | 6583.8639 | 43670.4099 | 425197.0953 | 17231.7226 | 0.099062 | -133058.7943 | 133058.7943
C | Xist Rating 10212 | 28.66 | 2868.39 | 150.308 | 35.7 | 1996.21 | 7709.89 | 10538.3 | 0.3 | 1.25 | 25.627 | 15.741 | 1 | 1 | 2610 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5725908.8019 | 472312.5051 | 6634.6064 | 43838.373 | 428474.1321 | 17246.4524 | 0.099443 | -133172.5339 | 133172.5339
C | Xist Rating 10213 | 28.66 | 2869.78 | 150.308 | 35.7 | 1995.75 | 7703.05 | 10538.3 | 0.29 | 1.25 | 25.624 | 15.752 | 1 | 1 | 2620 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5727363.435 | 475770.0848 | 6685.5437 | 44006.3361 | 431763.7487 | 17231.1234 | 0.099824 | -133054.1672 | 133054.1672
C | Xist Rating 10214 | 28.68 | 2871.21 | 150.308 | 35.7 | 1995.48 | 7698.94 | 10538.3 | 0.29 | 1.25 | 25.662 | 15.762 | 1 | 1 | 2630 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5729442.1308 | 479240.2443 | 6736.6758 | 44174.2992 | 435065.945 | 17246.1384 | 0.10021 | -133170.1092 | 133170.1092
C | Xist Rating 10215 | 28.7 | 2872.46 | 150.308 | 35.7 | 1995.36 | 7697.19 | 10538.3 | 0.28 | 1.25 | 25.662 | 15.771 | 1 | 1 | 2640 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5731591.7856 | 482722.9835 | 6788.0027 | 44342.2623 | 438380.7212 | 17228.4531 | 0.10059 | -133033.5478 | 133033.5478
C | Xist Rating 10216 | 28.75 | 2873.96 | 150.308 | 35.7 | 1995.32 | 7696.66 | 10538.3 | 0.28 | 1.25 | 25.671 | 15.782 | 1 | 1 | 2650 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5734469.8672 | 486218.3026 | 6839.5243 | 44510.2255 | 441708.0772 | 17243.3967 | 0.10097 | -133148.9385 | 133148.9385
C | Xist Rating 10217 | 28.75 | 2875.3 | 150.308 | 35.7 | 1994.93 | 7690.84 | 10538.3 | 0.28 | 1.25 | 25.667 | 15.792 | 1 | 1 | 2660 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5736022.229 | 489726.2015 | 6891.2408 | 44678.1886 | 445048.0129 | 17256.8701 | 0.10135 | -133252.9764 | 133252.9764
C | Xist Rating 10218 | 28.8 | 2876.69 | 150.308 | 35.7 | 1995.18 | 7694.56 | 10538.2 | 0.27 | 1.25 | 25.671 | 15.802 | 1 | 1 | 2670 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5739514.3542 | 493246.6802 | 6943.152 | 44846.1517 | 448400.5285 | 17239.887 | 0.10173 | -133121.8378 | 133121.8378
C | Xist Rating 10219 | 28.84 | 2878.11 | 150.309 | 35.7 | 1995.28 | 7695.96 | 10538.2 | 0.27 | 1.25 | 25.709 | 15.812 | 1 | 1 | 2680 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5742635.3208 | 496779.7386 | 6995.258 | 45014.1148 | 451765.6238 | 17254.6114 | 0.10211 | -133235.5357 | 133235.5357
C | Xist Rating 10220 | 28.9 | 2879.48 | 150.309 | 35.7 | 1995.7 | 7702.22 | 10538.3 | 0.26 | 1.25 | 25.711 | 15.822 | 1 | 1 | 2690 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5746578.236 | 500325.3769 | 7047.5588 | 45182.0779 | 455143.299 | 17237.1711 | 0.10249 | -133100.8661 | 133100.8661
C | Xist Rating 10221 | 28.98 | 2880.68 | 150.309 | 35.7 | 1996.46 | 7713.54 | 10538.3 | 0.26 | 1.25 | 25.712 | 15.831 | 1 | 1 | 2700 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5751162.3928 | 503883.595 | 7100.0544 | 45350.041 | 458533.5539 | 17249.5455 | 0.10287 | -133196.4181 | 133196.4181
C | Xist Rating 10222 | 29.04 | 2882.34 | 150.309 | 35.7 | 1996.83 | 7719.16 | 10538.3 | 0.26 | 1.25 | 25.713 | 15.842 | 1 | 1 | 2710 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5755542.9822 | 507454.3928 | 7152.7448 | 45518.0041 | 461936.3887 | 17263.9972 | 0.10325 | -133308.0099 | 133308.0099
C | Xist Rating 10223 | 29.1 | 2883.68 | 150.309 | 35.6 | 1997.5 | 7729.22 | 10538.2 | 0.25 | 1.25 | 25.71 | 15.852 | 1 | 1 | 2720 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5760150.8 | 511037.7705 | 7205.63 | 45685.9673 | 465351.8032 | 17245.9373 | 0.10363 | -133168.5567 | 133168.5567
C | Xist Rating 10224 | 29.07 | 2885.01 | 150.309 | 35.6 | 1996.58 | 7715.43 | 10538.2 | 0.25 | 1.25 | 25.744 | 15.861 | 1 | 1 | 2730 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5760153.2658 | 514633.7279 | 7258.71 | 45853.9304 | 468779.7976 | 17259.2051 | 0.10402 | -133271.0067 | 133271.0067
C | Xist Rating 10225 | 29.05 | 2886.29 | 150.309 | 35.6 | 1995.92 | 7705.65 | 10538.2 | 0.25 | 1.25 | 25.74 | 15.87 | 1 | 1 | 2740 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5760803.9368 | 518242.2652 | 7311.9847 | 46021.8935 | 472220.3717 | 17271.3137 | 0.1044 | -133364.5059 | 133364.5059
C | Xist Rating 10226 | 29.02 | 2887.84 | 150.309 | 35.6 | 1994.85 | 7689.72 | 10538.2 | 0.25 | 1.25 | 25.735 | 15.881 | 1 | 1 | 2750 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5760807.624 | 521863.3822 | 7365.4543 | 46189.8566 | 475673.5256 | 17285.4675 | 0.10478 | -133473.7983 | 133473.7983
C | Xist Rating 10227 | 28.99 | 2889.26 | 150.309 | 35.6 | 1993.87 | 7675.18 | 10538.2 | 0.24 | 1.25 | 25.729 | 15.89 | 1 | 1 | 2760 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5760808.8362 | 525497.0791 | 7419.1186 | 46357.8197 | 479139.2593 | 17265.6814 | 0.10516 | -133321.0154 | 133321.0154
C | Xist Rating 10228 | 28.99 | 2890.5 | 150.309 | 35.6 | 1993.4 | 7668.22 | 10538.2 | 0.24 | 1.25 | 25.728 | 15.899 | 1 | 1 | 2770 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5761922.7 | 529143.3557 | 7472.9777 | 46525.7828 | 482617.5728 | 17277.766 | 0.10554 | -133414.3294 | 133414.3294
C | Xist Rating 10229 | 28.95 | 2892.04 | 150.309 | 35.6 | 1992.27 | 7651.44 | 10538.2 | 0.24 | 1.25 | 25.76 | 15.91 | 1 | 1 | 2780 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5761724.5308 | 532802.2121 | 7527.0316 | 46693.746 | 486108.4662 | 17292.9143 | 0.10592 | -133531.3006 | 133531.3006
C | Xist Rating 10230 | 28.95 | 2893.45 | 150.309 | 35.6 | 1991.64 | 7642.2 | 10538.2 | 0.23 | 1.25 | 25.757 | 15.919 | 1 | 1 | 2790 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5762710.758 | 536473.6483 | 7581.2803 | 46861.7091 | 489611.9393 | 17272.7301 | 0.1063 | -133375.4434 | 133375.4434
C | Xist Rating 10231 | 28.92 | 2894.43 | 150.309 | 35.6 | 1991.04 | 7633.38 | 10538.2 | 0.23 | 1.25 | 25.749 | 15.927 | 1 | 1 | 2800 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5762925.9072 | 540157.6644 | 7635.7238 | 47029.6722 | 493127.9922 | 17283.4626 | 0.10668 | -133458.317 | 133458.317
C | Xist Rating 10232 | 28.92 | 2896.17 | 150.309 | 35.6 | 1990.28 | 7622.19 | 10538.2 | 0.23 | 1.25 | 25.746 | 15.938 | 1 | 1 | 2810 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5764189.2276 | 543854.2602 | 7690.3621 | 47197.6353 | 496656.6249 | 17297.4538 | 0.10706 | -133566.3534 | 133566.3534
C | Xist Rating 10233 | 28.93 | 2897.65 | 150.309 | 35.6 | 1989.97 | 7617.63 | 10538.2 | 0.23 | 1.25 | 25.754 | 15.948 | 1 | 1 | 2820 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5766236.5705 | 547563.4358 | 7745.1952 | 47365.5984 | 500197.8374 | 17310.7257 | 0.10744 | -133668.8355 | 133668.8355
C | Xist Rating 10234 | 28.88 | 2899.02 | 150.309 | 35.6 | 1988.67 | 7598.6 | 10538.1 | 0.22 | 1.25 | 25.782 | 15.957 | 1 | 1 | 2830 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5765194.1034 | 551285.1912 | 7800.223 | 47533.5615 | 503751.6297 | 17290.8389 | 0.10783 | -133515.2744 | 133515.2744
C | Xist Rating 10235 | 28.89 | 2900.34 | 150.309 | 35.6 | 1988.39 | 7594.64 | 10538.2 | 0.22 | 1.25 | 25.786 | 15.966 | 1 | 1 | 2840 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5767007.0526 | 555019.5264 | 7855.4457 | 47701.5246 | 507318.0017 | 17302.8399 | 0.10821 | -133607.9429 | 133607.9429
C | Xist Rating 10236 | 28.92 | 2901.78 | 150.309 | 35.6 | 1988.3 | 7593.24 | 10538.2 | 0.22 | 1.25 | 25.797 | 15.976 | 1 | 1 | 2850 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5769609.174 | 558766.4414 | 7910.8631 | 47869.4878 | 510896.9536 | 17316.0769 | 0.10859 | -133710.1555 | 133710.1555
C | Xist Rating 10237 | 28.86 | 2903.18 | 150.309 | 35.6 | 1986.92 | 7573.15 | 10538.2 | 0.22 | 1.25 | 25.786 | 15.985 | 1 | 1 | 2860 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5768386.4056 | 562525.9362 | 7966.4753 | 48037.4509 | 514488.4853 | 17327.6571 | 0.10897 | -133799.5747 | 133799.5747
C | Xist Rating 10238 | 28.95 | 2904.38 | 150.309 | 35.6 | 1987.95 | 7588.11 | 10538.2 | 0.21 | 1.25 | 25.807 | 15.994 | 1 | 1 | 2870 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5773762.221 | 566298.0108 | 8022.2824 | 48205.414 | 518092.5968 | 17306.9409 | 0.10935 | -133639.61 | 133639.61
C | Xist Rating 10239 | 29.04 | 2905.88 | 150.309 | 35.6 | 1988.8 | 7600.44 | 10538.3 | 0.21 | 1.25 | 25.869 | 16.004 | 1 | 1 | 2880 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5779214.144 | 570082.6651 | 8078.2842 | 48373.3771 | 521709.288 | 17321.4359 | 0.10973 | -133751.537 | 133751.537
C | Xist Rating 10240 | 29.01 | 2907.23 | 150.309 | 35.6 | 1987.82 | 7586.2 | 10538.2 | 0.21 | 1.25 | 25.861 | 16.013 | 1 | 1 | 2890 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5779049.9386 | 573879.8993 | 8134.4807 | 48541.3402 | 525338.5591 | 17332.9999 | 0.11011 | -133840.8307 | 133840.8307
C | Xist Rating 10241 | 29.16 | 2908.61 | 150.309 | 35.6 | 1989.67 | 7613.24 | 10538.3 | 0.21 | 1.25 | 25.89 | 16.022 | 1 | 1 | 2900 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5787174.0587 | 577689.7133 | 8190.8721 | 48709.3033 | 528980.41 | 17345.5724 | 0.11049 | -133937.9121 | 133937.9121
C | Xist Rating 10242 | 29.35 | 2910.15 | 150.309 | 35.6 | 1992.12 | 7649.18 | 10538.4 | 0.2 | 1.25 | 25.931 | 16.033 | 1 | 1 | 2910 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5797368.018 | 581512.1071 | 8247.4583 | 48877.2664 | 532634.8406 | 17326.7317 | 0.11087 | -133792.4293 | 133792.4293
C | Xist Rating 10243 | 29.57 | 2911.54 | 150.309 | 35.6 | 1995.01 | 7691.87 | 10538.5 | 0.2 | 1.25 | 25.978 | 16.042 | 1 | 1 | 2920 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5808551.4154 | 585347.0806 | 8304.2393 | 49045.2296 | 536301.8511 | 17339.6332 | 0.11125 | -133892.0515 | 133892.0515
C | Xist Rating 10244 | 29.64 | 2912.93 | 150.309 | 35.6 | 1995.65 | 7701.39 | 10538.5 | 0.2 | 1.25 | 26.034 | 16.051 | 1 | 1 | 2930 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5813188.7545 | 589194.634 | 8361.215 | 49213.1927 | 539981.4413 | 17352.7796 | 0.11164 | -133993.5642 | 133993.5642
C | Xist Rating 10245 | 30.17 | 2914.3 | 150.309 | 35.6 | 2003.37 | 7817.64 | 10538.6 | 0.2 | 1.25 | 26.099 | 16.061 | 1 | 1 | 2940 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5838421.191 | 593054.7672 | 8418.3855 | 49381.1558 | 543673.6114 | 17367.2117 | 0.11202 | -134105.0051 | 134105.0051
C | Xist Rating 10246 | 30.98 | 2915.7 | 150.309 | 35.6 | 2015.73 | 8009.1 | 10538.7 | 0.19 | 1.25 | 26.195 | 16.072 | 1 | 1 | 2950 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5877263.961 | 596927.4801 | 8475.7509 | 49549.1189 | 547378.3612 | 17348.8754 | 0.1124 | -133963.4174 | 133963.4174
C | Xist Rating 10247 | 31.43 | 2917.08 | 150.309 | 35.6 | 2022.22 | 8112.59 | 10538.8 | 0.19 | 1.25 | 26.246 | 16.081 | 1 | 1 | 2960 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5898977.5176 | 600812.7729 | 8533.311 | 49717.082 | 551095.6908 | 17361.7385 | 0.11278 | -134062.743 | 134062.743
C | Xist Rating 10248 | 31.94 | 2918.46 | 150.309 | 35.6 | 2029.67 | 8233.85 | 10538.7 | 0.19 | 1.25 | 26.306 | 16.091 | 1 | 1 | 2970 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5923510.7082 | 604710.6454 | 8591.0659 | 49885.0451 | 554825.6003 | 17375.8765 | 0.11316 | -134171.9124 | 134171.9124
C | Xist Rating 10249 | 32.89 | 2919.68 | 150.309 | 35.6 | 2044.41 | 8481.99 | 10538.6 | 0.18 | 1.25 | 26.425 | 16.101 | 1 | 1 | 2980 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5969022.9888 | 608621.0977 | 8649.0156 | 50053.0083 | 558568.0895 | 17356.2242 | 0.11354 | -134020.1628 | 134020.1628
C | Xist Rating 10250 | 32.88 | 2921.24 | 150.309 | 35.6 | 2043.56 | 8467.43 | 10538.6 | 0.18 | 1.25 | 26.419 | 16.111 | 1 | 1 | 2990 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5969729.2144 | 612544.1299 | 8707.16 | 50220.9714 | 562323.1585 | 17368.5965 | 0.11392 | -134115.6986 | 134115.6986
C | Xist Rating 10251 | 32.86 | 2922.67 | 150.309 | 35.6 | 2042.81 | 8454.5 | 10538.6 | 0.18 | 1.25 | 26.414 | 16.12 | 1 | 1 | 3000 | 152.4 | 2 | 6 | 19.05 | 1.3333 | 36 | E | Rod | 5970459.5027 | 616479.7418 | 8765.4993 | 50388.9345 | 566090.8073 | 17379.9536 | 0.1143 | -134203.3948 | 134203.3948
[26 empty] | #VALUE! | #VALUE! | #VALUE!